Quad Cities Nuclear Power Station | Unit 1 | Low Pressure Coolant Injection Manually Isolated Due To Valve Test Equipment Issue | 07-08-2022 | On May 10, 2022, with Unit 1 operating at 100% power, motor operated valve (MOV) thrust testing was being performed on Residual Heat Removal (RHR) Low Pressure Coolant Injection (LPCI) valve 1-1001-28B, 1B LPCI Loop Upstream Stop Valve. Inadequate thrust conditions were discovered on this valve, which also serves as a Primary Containment Isolation Valve (PCIV). Technical Specification (TS) 3.6.1.3 Condition A requires that a containment penetration with a degraded valve be manually isolated within 4 hours. Manual closure of the companion PCIV valve 1-1001-29B, 1B LPCI Loop Downstream Stop Valve, including opening of the electrical breaker MCC 18/19-5 Cubicle F1 to the valve, rendered both loops of LPCI incapable of either manual or automatic injection as described in TS 3.5.1 Condition E for two LPCI Subsystems inoperable. The cause of the low MOV thrust value was found to be insufficient installation bond between the valve stem and the thrust sensor instrument. Thrust was eventually found to be sufficient, but this was not identified prior to the 4 hour TS action requirement. A new sensor was installed, and the valve thrust results were found to be satisfactory. This report is being submitted in accordance with 10 CFR 50.73(a)(2)(v)(B) and 10 CFR 50.73(a)(2)(v)(D) for an event or condition that could have prevented the fulfillment of a safety function needed to (B) remove residual heat and (D) mitigate the consequences of an accident. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 72517th Street NW, Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of infonmation unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Quad Cities Nuclear Power Station Unit 1 05000- 254 YEAR NUMBER NO. 2022 - 002 00 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Low Pressure Coolant Injection Manually Isolated Due To Valve Test Equipment Issue CONDITION PRIOR TO EVENT Unit: 1 Event Date: May 10, 2022 Event Time: 17 46 CST Reactor Mode: 1 Mode Name: Run Power Level: 100% No structures, systems or components were inoperable at the start of this event that contributed to the event. A. DESCRIPTION OF EVENT On May 10, 2022, Unit 1 was operating at 100% power. Motor Operated Valve (MOV) [VJ diagnostic testing was being performed on Residual Heat Removal (RHR) Low Pressure Coolant Injection (LPCI) [BO] valve 1-1001-288, 1B LPCI Loop Upstream Stop Valve, when a low thrust was measured at 1359 hours causing the valve to be declared inoperable. Inadequate grease volume was also identified in one chamber of the MOV actuator, which was considered an initial contributor to the insufficient thrust measurement. The grease was later eliminated as a cause or a contributor to this event. This valve is also a Primary Containment Isolation (PCIV) [BD] valve for containment penetration X-0138, resulting in TS 3.6.1.3 Condition A to be entered for a penetration flow path with one PCIV inoperable. TS 3.6.1.3 Condition A requires that the affected flow path be isolated within 4 hours by use of one closed and de-activated valve. Engineering review of thrust data and grease quantities did not reach a conclusion during the 4 hour window to provide confidence in valve performance. Operations de-activated the affected penetration at 1746 hours by closing the 1-1001-298, 18 LPCI Loop Downstream Stop Valve, and electrically isolating it by opening breaker [BKR] MCC 18/19-5 Cubicle F1. LPCI Loop Select Logic will determine if LPCI flow is injected into the A or B loop of the Reactor Recirculation (RR) [AD] System depending upon the appropriate accident's line break location. The isolated penetration is part of the injection flow path into the B loop of the RR system with either the A or B loop of LPCI providing injection. Because the LPCI injection path cannot be predicted ahead of an event, this penetration isolation renders both the A and B LPCI loops inoperable, causing entry into TS 3.5.1 Condition E for two LPCI subsystems inoperable. | ML22189A029 | 0 | good
Monticello Nuclear Generating Plant | Unknown Unit | Loss of Control Room Envelope Operability | 07-07-2022 | On May 13, 2022, the Monticello Nuclear Generating Plant was operating in Mode 1 at 100% power. Following an inspection in the Steam Jet Air Ejector room, it was identified that the steam leakage from two valves exceeded the assumptions in the Alternate Source Term dose analysis calculation. As a result, the Control Room Envelope (CRE) was declared inoperable and LCO 3.7.4, "Control Room Emergency Filtration (CREF) System," Condition B was entered. The leaks were mitigated such that the CRE was declared operable on May 20, 2022. This report is being submitted as an "event or condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety" per 10 CFR 50.73(a)(2)(ii)(B); as an "event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident" per 10 CFR 50.73(a)(2)(v)(D); and as "any event where a single cause or condition caused at least one independent train or channel to become inoperable in multiple systems or two independent trains or channels to become inoperable in a single system designed to mitigate the consequences of an accident" per 10 CFR 50.73(a)(2)(vii). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 3. LER NUMBER 1.FACILITY NAME 2.DOCKET NUMBER YEAR SEQUENTIAL REV 05000- NUMBER NO. Monticello Nuclear Generating Plant -263 2022 - 001 - 00 | EVENT DESCRIPTION On May 13, 2022, the Monticello Nuclear Generating Plant was operating in Mode 1 at 100% power. Following an inspection in the Steam Jet Air Ejector (SJAE) room, it was identified that the steam leakage from two valves exceeded the assumptions in the Alternate Source Term (AST) dose analysis calculation. As a result, the Control Room Envelope (CRE) was declared inoperable and LCO 3.7.4, "Control Room Emergency Filtration (CREF) System," Condition B was entered. The leaks were mitigated such that the CRE was declared operable on May 20, 2022. EVENT ANALYSIS Steam leakage from the 12 SJAE Pressure Control outlet valve [PCV], MS-23-2, was originally identified on May 5, 2022. As part of an investigation into the leakage, Operators opened the 12 SJAE Pressure Control bypass valve [PCV], MS-24-2, to allow maintenance to remove insulation from MS-23-2. Upon entry into the SJAE room to remove the insulation from MS-23-2 it was discovered that the valve packing from MS-24-2 had failed and was also leaking steam. After removal of the insulation from MS-23-2, it was determined that the leakage from MS-23-2 and MS-24-2 both exceeded the leakage rate assumptions of the AST dose analysis calculation and evaluation. As a result, the Control Room CRE was declared inoperable. The CRE was inoperable from May 5, 2022 until May 20, 2022 when the leakage sources were mitigated. This condition was determined to be reportable in accordance with 10 CFR 50.73(a)(2)(ii)(B) as an "event or condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety,” 10 CFR 50.73(a)(2)(v)(D), as an "event or condition that could have prevented fulfillment of a safety function to mitigate the consequences of an accident," and 10 CFR 50.73(a)(2)(vii) as "any event where a single cause or condition caused at least one independent train or channel to become inoperable in multiple systems or two independent trains or channels to become inoperable in a single system designed to mitigate the consequences of an accident." This event will be reported as a Safety System Functional Failure in accordance with Nuclear Energy Institute 99-02, "Regulatory Assessment Performance Indicator Guideline". SAFETY SIGNIFICANCE There was no actual safety consequence from this condition. During the time the CRE was inoperable radiation levels in the Turbine Building and on the Wide Range Gas Monitors remained stable. Compensatory measures were put in place, including assigning a dedicated operator to promptly isolate the portion of the SJAE system that was leaking in the event of a design basis event. In addition, the control room operators were directed to don a self-contained breathing apparatus (SCBA) on breathing air if a design basis event were to occur. An engineering analysis determined that donning SCBAs would ensure control room operator doses remained below 5 Rem Total Effective Dose Equivalent (TEDE). Prior to the implementation of the compensatory measures described above on May 13, 2022, it is estimated the post-accident dose limit for the control room operators could have been exceeded. During the time the steam leakage in the SJAE Room exceeded the assumptions of the AST analysis both CREF subsystems were otherwise available. | ML22189A111 | 0 | good
Browns Ferry Nuclear Plant | Unit 3 | Main Steam Relief Valves Lift Settings Outside of Technical Specifications Required Setpoints | 07-11-2022 | On May 10, 2022, the Tennessee Valley Authority was notified of As-Found testing results that four Main Steam Relief Valves (MSRVs) from Browns Ferry Nuclear Pant (BFN), Unit 3 were outside the +/- 3 percent set-point band required for operability. More than the one allowed MSRV was considered to be inoperable during the entire operating cycle and longer than permitted by Technical Specifications. During this time, BFN Unit 3 made entries into Modes of Operation that were not allowed under this condition. The affected valves remained capable of maintaining reactor pressure within the American Society of Mechanical Engineers code limits. It was determined that the MSRVs failed due to corrosion bonding to the valve seats and non-quantifiable leakage known as simmering. All thirteen of the MSRV pilot valves were replaced during the Unit 3 spring 2022 refueling outage. The Boiling Water Reactor Owners' Group is continuing to work toward a solution to improve the quality and adhesion of the platinum coating on the discs. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 3 05000-296 NUMBER NO. 2022 - 001 - 00 | I. Plant Operating Conditions before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN) Unit 3 was in Mode 1 at approximately 100 percent power. II. Description of Event A. Event Summary On May 10, 2022, NWS Technologies notified the Tennessee Valley Authority (TVA) with the as found testing results of the thirteen Main Steam Relief Valves (MSRVs) [RV], which were removed during the spring 2022 Unit 3 Refueling Outage 20 (U3R20). Four MSRVs (BFN-3-PCV-001-0004, BFN-3-PCV-001-0022, BFN-3-PCV-001-0034, and BFN-3-PCV-001-0041) had as found lift settings which were outside of the +/- 3 percent band of their setpoints required for operability. Technical Specification (TS) 3.4.3, Safety/Relief Valves (S/RVs), requires twelve of the thirteen S/RVs to be operable for S/RV system [SB] operability. The four MSRVs were found to have been inoperable for an indeterminate period of time during the entire operating cycle between March 25, 2020, and February 26, 2022, and longer than permitted by TS 3.4.3. Throughout this event, the two stage MSRV pilot valves remained capable of maintaining the reactor pressure below 1375 pounds per square inch gauge (psig), which is the American Society of Mechanical Engineers (ASME) code limit of 110 percent of the vessel design pressure. The valves remained capable of performing their required safety function. The TVA is submitting this report in accordance with Title 10 of the Code of Federal Regulations 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant’s TS. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML22192A036 | 0 | good
Peach Bottom Atomic Power Station | Unit 2 | Automatic Reactor Scram due to Loss of Power to Both RPS Buses | 07-15-2022 | On 5/16/22 at 1537 hours, the Unit 2A reactor protection system motor generator set (RPS MG set) tripped in response to grid perturbations, causing a half scram condition as expected. At 1552 hours, Unit 2 experienced an automatic scram and Group 1 isolation. The scram was the result of a self-revealing technical human performance event during the execution of a procedure to return 2A RPS to service. The loss of both RPS buses resulted in a reactor scram, Primary Containment Isolation System Group 1 Isolation (main steam isolation valve closure), safety relief valve actuation, and loss of the normal heat sink. Emergency Core Cooling Systems were utilized to maintain reactor pressure vessel level and pressure. At no time was there a public safety risk and there were no safety consequences as a result of the event. All control rods inserted, and all safety systems performed as expected. Operations safely stabilized Unit 2 and brought it to a cold shutdown condition. The root cause of this event was a breakdown in technical human performance, which led to directing the wrong procedure steps and resulted in a reactor scram. Immediate corrective actions included increased oversight and reinforced stop work criteria. Longer term corrective actions include procedure and training enhancements. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Peach Bottom Atomic Power Station, YEAR NUMBER NO. 05000- 277 Unit 2 2022 - 001 - 00 | Plant Operating Conditions Before the Event Prior to the event Peach Bottom Atomic Power Station Unit 2 was operating at approximately 100% power in MODE 1. All 4kV (EIIS: EB) buses were aligned to one source due to a planned offsite source outage window. Because of this alignment, the Unit 2 B bus of the Reactor Protection System (RPS)(EIIS: JC) was being powered by an alternate feed. The 4kV and RPS power supply alignment had been in this configuration for four weeks prior to the event. There were no other structures, systems or components (SSC) that were inoperable at the start of the event that contributed to the event. Event Description At 1532 hours on 5/16/22, an offsite electrical transient(s) occurred which caused a main generator perturbation and multiple control room alarms for both units. The 2A Recirculation (EIIS: AD) pump speed lowered slightly (10 RPM). The operations crew entered the procedure for unexpected change in core flow. The Unit 2 Reactor Water Cleanup (EIIS: CE) system also tripped as a result of the event. At 1537 hours on 5/16/22, another offsite electrical transient occurred with a large main generator perturbation, and the 2A RPS motor generator set output breaker tripped which caused a loss of power to the 2A RPS bus, a half scram, and Unit 2 Primary Containment Isolation System Group II/III inboard isolations (EIIS: JM). Loss of RPS power also caused a trip of Unit 2 Reactor Building Ventilation (EIIS: VA). One of two main generator output breaker (EIIS: EL) for each unit opened and there was a <1K Ohm ground indicated on the 2A/C and 2B/D batteries (EIIS: EJ). In response to the 2A RPS trip, operations supervision directed performance of procedures to restore the tripped 2A RPS motor generator set to service. During this evolution, a self-revealing technical human performance event occurred when an operator was directed by shift management to utilize a version of the procedure that was not annotated to account for the abnormal electrical alignment. The operator opened the breakers from the alternate electrical feed to the 2B RPS bus which was powering the B RPS at the time. At 1552 hours on 5/16/22, the loss of power to the second RPS bus resulted in a Reactor scram and Primary Containment Isolation System (EIIS:JM) Group I isolation which closed all main steam isolation valves (MSIVs). All safety systems performed as expected in response to the scram. Reactor pressure increased as a result of MSIV closure. Safety relief valves (EIIS: SB) initially lifted within their setpoints to control pressure, then the valves were utilized manually for pressure control. Closure of the MSIVs isolated the normal heat sink (condenser, EIIS: SG) and the steam supply to the feedwater (EIIS: SJ) pumps, so emergency systems were utilized for injection. High Pressure Coolant Injection (EIIS: BJ) was manually used for injection into the reactor pressure vessel and was used for pressure control. Reactor Core Isolation Cooling (RCIC)(EIIS:BN) was manually utilized for reactor pressure vessel level control. Operations safely stabilized Unit 2 and brought it to a cold shutdown condition. Unit 3 was affected by the grid transient, with both Unit 3 Recirculation pump speeds lowering and entering speed hold, but was unaffected by the Unit 2 scram. This event is reportable under 10CFR50.73(a)(2)(iv)(A) due to manual or automatic actuation of systems listed in 10CFR50.73(a)(2)(iv)(B) including RPS, containment isolation signals, actuation of an emergency core cooling system and RCIC. An ENS notification was made within 4 hours of the event, reference ENS 55899. | ML22196A020 | 0 | good
Cooper Nuclear Station 05000 298 1 OF 4 | Unknown Unit | Secondary Containment Differential Pressure Perturbation Exceeds Technical Specifications Limit | 07-20-2022 | On May 23, 2022, Reactor Building differential pressure (d/p) became unstable and exceeded the Technical Specifications limit of -0.25 inches of water gauge resulting in Secondary Containment being declared inoperable. The direct cause of the d/p perturbation was determined to be a failure of the valve stem O-ring in the Reactor Building 'A' Exhaust Fan vortex damper actuator. The d/p controller responded to the condition and restored Secondary Containment pressure without Operator action. The O-ring and case gaskets were replaced and 'A' Exhaust Fan was returned to service. There was no impact on nuclear safety, plant reliability, radiological safety, or industrial safety. Event Notification 55907 was submitted on May 23, 2022, due to the unplanned inoperability of Secondary Containment. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocolleds.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: Cira sabmlssioo@omb.eQp.gov. The NRC may not conduct or https:/twww.nrc.qov/reading-rm/doc-colleclions/hureqs/slaff/sr1022/r3/) sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Cooper Nuclear Station 05000- 298 NUMBER NO. 2022 - 001 00 NARRATNE PLANT STATUS Cooper Nuclear Station was in Mode 1, Power Operation, at 95 percent power at the time of the event on May 23, 2022. BACKGROUND Secondary Containment serves as a barrier to confine and monitor potential releases during fuel handling operations and is a system that limits the release of radioactive materials to the environment. Secondary Containment consists of four subsystems. One of the subsystems is the Reactor Building [EIIS: NG], which encloses the Reactor Pressure Vessel [EIIS: RPV] and Primary Containment [EIIS: NH]. The Secondary Containment area (most of the Reactor Building) has supply and exhaust ventilating systems. The supply system furnishes filtered 100% outdoor air to all floors of the building through ductwork. The supply unit has an operating and standby (100% capacity) fan with vortex dampers [EIIS: COMP] to provide regulation of air capacity. The fans will deenergize in the event of loss of offsite power. The exhaust air is induced from the ventilated areas to a common plenum connected to the two exhaust fans, each of 100% capacity. The air is then exhausted to the atmosphere. During normal plant operation, a minimum average negative pressure of 0.25 inches of water gauge (wg) is maintained by differential pressure controllers [EIIS: PDC] which receive signals proportional to the pressure difference between outside air and the Secondary Containment atmosphere, and control the position of the exhaust fan vortex dampers. The differential pressure (d/p) is detected by four separate probes, with one on each side of the Reactor Building. Control action is initiated from the average value of the four sensor probes. If a Loss of Coolant Accident should occur, all ventilation systems of the Primary Containment area and Secondary Containment area will be isolated automatically, and the Standby Gas Treatment (SGT) [EIIS: BH] system will be automatically initiated. EVENT DESCRIPTION On May 23, 2022, at 0400, Reactor Building Exhaust Fan 'A' was placed in service to maintain Reactor Building d/p while Exhaust Fan 'B' was secured for planned maintenance. After Exhaust Fan 'A' was placed in service, Reactor Building d/p controller output trended down for 40 minutes to adjust d/p to match the setpoint. Reactor Building effluent flow was unchanged during this timeframe. The continuous downward trend in pressure with no change in effluent flow indicated that the fan vortex damper actuator was not responding to the changes in demand from the d/p controller. The fan vortex damper actuator responded causing a sudden reduction in exhaust flow which caused a pressure spike in the Reactor Building at 0455 to -0.20 inches wg. This exceeded the Technical Specification (TS) Surveillance Reauirement 3.6.4.1.1 limit of -0.25 inches wa for Secondary Containment. The d/p NRC FORM 366A (08-2020) Page 2 of 4 NRC FORM 366A U.S. NUCLEAR REGULAT ORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (Q8.20r20) :·~\ Estimated burden per response to comply with this mandatory collection request: 80 hours Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T•6 A1 O M), U.S. ; ... Z. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555·0001, or by e.mail to ,. !nfocollects.R!ISOurce@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs. (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e•mail: olra submission@omb.eop.goy. The NRC may not conduct or https://www.nrc.gov/reading-rm/doc-collecUons/nuregs/staff/sr1022/r3/) sponsor, and a person is not required lo respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Cooper Nuclear Station 05000- 298 NUMBER NO. 2022 - 001 00 controller immediately responded to this pressure rise and restored Reactor Building pressure to within TS limits. Secondary Containment was Operable at 0457 with no operator actions required. Reactor Building Exhaust Fan 'A' was removed from service. Troubleshooting was performed and found that when the vortex damper for Reactor Building Exhaust Fan 'A' was cycled, the under diaphragm area of the damper actuator would not hold pressure and the valve stem O ring appeared to not seal. The vortex damper actuator was refurbished including replacement of the stem O ring. The condition of the stem O-ring was brittle and fell apart during removal. This prevented the under diaphragm area from being pressurized. The stem O-ring and case gaskets were replaced, and the 'A' Exhaust Fan was returned to service. A review of maintenance plan history revealed that the diaphragm required routine replacement to prevent failure. However, the maintenance plan did not contain direction on replacing the valve stem O-ring, or that a failure of the O-ring would cause a pressure transient. BASIS FOR REPORT This event is reportable under 10 CFR 50. 73(a)(2)(v)(C and D) - An event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material or mitigate the consequences of an accident. Event Notification 55907 was submitted on May 23, 2022, due to the unplanned inoperability of Secondary Containment. An engineering review was performed for Loss of Safety Function and it documented that the SGT system remained capable of drawing the Reactor Building to vacuum conditions within a period of time sufficient to ensure acceptance criteria would not be exceeded. Based on the engineering review, this event will not be counted as a Safety System Functional Failure for the Nuclear Regulatory Commission performance indicator since no loss of safety function occurred. SAFETY SIGNIFICANCE This condition is non-consequential. The pressure excursion in the Reactor Building resulted in an unexpected plant condition and met the entry condition for required action pursuant to TS. This event resulted in a minor excursion of Reactor Building d/p above the TS limit of -0.25 inches wg for several minutes until the non-essential Reactor Building HVAC controls restored the required d/p. This event did not negate the ability of the Standby Gas Treatment system to maintain Secondary Containment d/p if required. There was no impact on nuclear safety, plant reliability, radiological safety, or industrial safety. NRC FORM 366A (08-2020) Page 3 of 4 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response lo comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back lo industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A1 O M), U S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnrooollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for !he Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira submlssion@omb.eop.gov. The NRC may not conduct or https://www.nrc.gov/readlng-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Cooper Nuclear Station 05000- 298 NUMBER NO. 2022 - 001 00 CAUSE The causal factor for this event was failure to previously identify all potential failure modes for the Exhaust Fan vortex damper actuator. CORRECTIVE ACTIONS The stem O-ring and case gaskets for the Reactor Building Exhaust Fans have been replaced, and the 'A' Exhaust Fan was returned to service. The maintenance plan has been revised to include replacing the valve stem O-ring during routine maintenance. PREVIOUS EVENTS On February 9, 2021 - Secondary Containment declared inoperable due to a rise in d/p. This was reported under LER 2021-001-00 as a loss of safety function under 10 CFR 50. 73(a)2(v)(C and D) - An event or condition that could have prevented to fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material or mitigate the consequences of an accident. On November 11, 2020 - Secondary Containment declared inoperable due to a rise in d/p. This was reported under LER 2020-004-00 as a loss of safety function under 10 CFR 50. 73(a)(2)(v)(C and D) - An event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material or mitigate the consequences of an accident. On August 6, 2020, Secondary Containment was declared inoperable due to a rise in d/p. This was reported under LER 2020-002-00 as a loss of safety function under 10 CFR 50. 73(a)(2)(v)(C and D) - An event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material or mitigate the consequences of an accident. On May 1, 2020, Secondary Containment was breached due to both airlock doors in the Reactor Building being inadvertently opened simultaneously. This was reported under LER 2020-001-00 as a loss of safety function under 10 CFR 50. 73(a)(2)(v)(C and D) -An event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material or mitigate the consequences of an accident. On August 8, 2019, Secondary Containment was declared inoperable due to a rise in d/p. This was reported under LER 2019-002-00 as a loss of safety function under 10 CFR 50. 73(a)(2)(v)(C and D) - An event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material or mitiQate the consequences of an accident. NRG FORM 366A (08-2020) Page 4 of 4 | Not Found | ML22201A521 | 1 | ok
Not Found | Unknown Unit | Low Pressure Core Spray Inoperable dueto Loss ofMinimum FlowValve 6. EventDate 6. LERNumber 7. ReportDate 8. OtherFacilitiesInvolved Month Day Year Year Sequential Revision Month Day Year FacilityName DocketNumber Number No. 05000 06 24 2022 2022 001 00 08 17 2022 FacilityName DocketNumber 05000 9. OperatingMode 10. PowerLevel 1 100 11.ThisReportisSubmittedPursuanttotheRequirementsof10CFR§: (Checkallthatapply) 20.2203(a)(2)(vi) ¦[ 50.36(c)(2) 10 CFR Part20 50.73<a)(2)(iv)(A) 50.73(a)(2)(x) 20.2201(b) 20.2203(a)(3)(l) 50.46(a)(3)(ii) 50.73(a)(2)(v)(A) 10CFR Part73 20.2201(d) 20.2203(a)(3)(ii) 50.69(g) 50.73(a)(2)(v)(B) 73.71(a)(4) 20.2203(a)(1) 20.2203(a)(4) 50.73(a)(2)(i)(A) 50.73<a)(2)(v)(C) 73.71(a)(5) 20.2203(a)(2)(i) 10 CFRPart21 50.73<a)(2)(IMB) [7] 50.73(a)(2)(v)(D) 73.77(a)(1)(i) 20.2203(a)(2)(ii) 21.2(c) 50.73(a)(2)(i)(C) 50.73(a)(2)(vll) 73.77(a)(2)(l) 20.2203(a)(2)(iii) 10 CFR Part50 50.73(a)(2)(ii)(A) 50.73(a)(2Hviii)(A) 73.77(a)(2)(ii) 20.2203(a)(2)(iv) 50.36(c)(1)(i)(A) 50.73(a)(2)(li)(B) 50.73(a)(2)(viii)(B) 20.2203(a)(2)(v) 50.73(a)(2)(iii) 50.73(a)(2)(ix)(A) OTHER(Specifyhere,inabstract,orNRC366A). 12.LicenseeContactforthisLER LicenseeContact PhoneNumber(Includeareacode) GeorgeDujanovic, Regulatory Compliance 440-280-5200 13.CompleteOneLineforeachComponentFailureDescribedinthisReport Cause System Component Manufacturer ReportabletoIRIS Cause System Component Manufacturer ReportabletoIRIS BM FCV L200 14. SupplementalReportExpected Month Day Year 16. ExpectedSubmissionDate No Yes(Ifyes,complete15. ExpectedSubmissionDate) 16. Abstract(Limitto1560spaces,i.e.,approximately15single-spacedtypewrittenlines) On June24, 2022, at 1257 hours, the Low Pressure Core Spray (LPCS) systemwas declared INOPERABLEduetoa lossof powertothe pump minimumflowvalve. Since LPCS is a singletrain safety system as specified in site procedures, LPCS inoperability is considered a loss ofsafety function and is reportable. ThecauseforLPCS inoperability isthe failure ofthe minimumflowvalve actuatorto valve bonnet bolts. The most probable cause ofthefailed adapterto actuatorboltswas fatiguefailure. The bolting and thefuses have been sentto a laboratoryfor furtheranalysis. Corrective actions included replacement ofthevalve actuatormotorand the mounting bolts. Laboratory analysis may necessitate additional corrective actions oncethe results are known, inwhich casean LER revisionwill be submitted. The safety significance ofthis event is considered to bevery small. This event is being reported in accordancewith 10 CFR 50.73(a)(2)(v)(D) as an eventorcondition thatcould have preventedthefulfillmentofasafetyfunction needed to mitigatethe consequences ofan accident. NRC FORM366A U.S.NUCLEARREGULATORYCOMMISSION APPROVEDBYOMB: NO.3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimatedburdenperresponsetocomplywiththismandatorycollectionrequest80hours.Reported lessonsteamedareincorporatedintothelicensingprocessandfedbacktoindustry.Sendcomments LICENSEE EVENT REPORT (LER) regardingburdenestimatetotheFOIA,Library,andInformationCollectionsBranch(T-6A10M),U.S Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail tc CONTINUATION SHEET lnfocoltects.Resource@nrc.gov,andtheOMBrevieweratOMBOfficeofInformationandRegulator) Affairs,(3150-0104),Attn:DeskOfficerfortheNuclearRegulatoryCommission,72517thStreetNW (See NUREG-1022, R.3forinstructionandguidanceforcompletingthisform Washington,DC20503;e-mail:oira submissioniSjomb.eoD.gov.TheNRCmaynotconductorsponsor http://www.nrc.gov/readinq-rm/cloc-collections/nureqs/staff/sr1022/r3/) andapersonisnotrequiredtorespondto,acollectionofinformationunlessthedocumentrequesting orrequiringthecollectiondisplaysacurrentlyvalidOMBcontrolnumber. 1. FACILITYNAME 2. DOCKETNUMBER 3.LERNUMBER YEAR SEQUENTIAL REV 05000- NUMBER NO. Perry NuclearPowerPlant 00440 2022 001 00 NARRATIVE Energy Industry Identification System (EMS) codes are identified inthetext as [XX]. INTRODUCTION The inoperabilityand lossofsafetyfunction ofLow Pressure Core Spray (LPCS) [BM] system occurred as a resultofa loss ofelectrical powertothe LPCS pump minimum flowvalve [FCV] based upon the receiptofunexpected alarms in the Control Room, during surveillancetesting. Subsequent investigation ofthe LPCS minimumflowvalve revealedthatthe mounting boltsforthe motoroperated valveactuatorwere broken, and thefuses [FU] inthe disconnectforthe actuatorwerefound to be blown. With LPCS being a singletrain safety system, this resulted in a loss ofsafetyfunction resulting in a 10 CFR 50.72 notification and a 10 CFR 50.73 report. EVENT DESCRIPTION On June 24, 2022, at 1257 hours, and with the reactor in MODE 1 at 100 percent rated thermal power, a surveillance was being performed toverifythe operation ofthe LPCS system. During performance ofthe surveillance, itwas observed thatthe LPCS minimum flowvalve experienced a loss ofposition indication while stroking closed. Upon investigation ofthe MotorControl Center(MCC) disconnect [DISC]forthe LPCS minimum flowvalve, itwas determined thattwoofthreemain-line powerfuseswere blown. Examination ofthe LPCS minimum flowvalve revealed thatthe motor- operated actuator had becomeseparated fromthevalve. This resulted inthe LPCS system being declared inoperable. LPCS is described as a singletrain safety system in accordancewith site procedures. As such, when LPCS has an unplanned inoperability, it is reportabletothe NRC under 10 CFR 50.72(b)(3)(v)(D) and 10 CFR 50.73(a)(2)(v)(D) as a Loss ofSafety Function. On June 24, 2022, at 1628 hours, Event Notification (EN 55962)was made under 10 CFR 50.72(b)(3)(v)(D) tothe NRC. This Licensee Event Report is being reported under 10 CFR 50.73(a)(2)(v)(D) as a loss ofsafetyfunction. Newactuatortovalve bolts, a newactuator motor, and new disconnectfuseswere installed forthe LPCS minimumflow valve. The system performed satisfactorily during post maintenancetesting. LPCSwas declared OPERABLE on June 27, 2022, at 1300 hours. CAUSE OF EVENT The most probable cause ofthefailed adapterto actuatorboltswasfatiguefailure. The bolting andthefuses have been sentto a laboratoryforfurtheranalysis. Based upon the informationfromthe analyses, an LER revision may need to be submitted. NRCFORM366A (08-2020) Page of NRCFORM366A U.S.NUCLEARREGULATORYCOMMISSION APPROVEDBYOMB: NO.3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimatedburdenperresponsetocomplywiththismandatorycollectionrequest:80hours.Reportec lessonslearnedareincorporatedintothelicensingprocessandfedbacktoindustry.Sendcomment! LICENSEE EVENT REPORT (LER) regardingburdenestimatetotheFOIA,Library,andInformationCollectionsBranch(T-6A10M),U.S Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail tc CONTINUATION SHEET lnfocollects.Resource@nrc.gov,andtheOMBrevieweratOMBOfficeofInformationandRegulator) Affairs,(3150-0104),Attn:DeskOfficerfortheNuclearRegulatoryCommission,72517thStreetNW (SeeNUREG-1022, R.3forinstructionandguidanceforcompletingthisform Washington,DC20503;e-mail:oira submission@omb.eoD.gov.TheNRCmaynotconductorsponsor http://www.nrc.gov/readinq-rm/doc-collections/nureqs/staff/sr1022/r3A andapersonisnotrequiredtorespondto,acollectionofinformationunlessthedocumentrequesting orrequiringthecollectiondisplaysacurrentlyvalidOMBcontrolnumber. 1. FACILITYNAME 2. DOCKETNUMBER 3.LbKNUMbbK YEAR SEQUENTIAL REV 05000- NUMBER NO. Perry NuclearPowerPlant 00440 2022 001 00 NARRATIVE EVENTANALYSIS A Probabilistic RiskAssessment (PRA) evaluation was performed forthe June 24, 2022, LPCS Minimum FlowValve Inoperability event. Fire and otherexternal hazardswere qualitatively addressed to be oflow risk. The analysis ofthis eveni results in delta CDF and delta LERF values that are belowthe acceptablethresholds of 1.OE-06/yrand 1.OE-07/yr, as discussed in Regulatory Guide 1.174. Sensitivities performed that varied the exposurewindowtothe maximum possible exposurewindowofoneyeardid not changethese conclusions. The riskofthis event isthereforeconsidered very small in accordancewith the Regulatory Guidance. CORRECTIVEACTIONS Thevalve actuatorwas re-installed tothevalvewith newbolts. The actuatormotorwas also replaced. Newfuseswere installed intheelectrical disconnect. Thefailed bolts andfuses have been sent outforlaboratoryanalysis. PREVIOUS SIMILAR EVENTS None COMMITMENTS None NRCFORM366A (08-2020) Page of | 08-17-2022 | On June24, 2022, at 1257 hours, the Low Pressure Core Spray (LPCS) systemwas declared INOPERABLEduetoa lossof powertothe pump minimumflowvalve. Since LPCS is a singletrain safety system as specified in site procedures, LPCS inoperability is considered a loss ofsafety function and is reportable. ThecauseforLPCS inoperability isthe failure ofthe minimumflowvalve actuatorto valve bonnet bolts. The most probable cause ofthefailed adapterto actuatorboltswas fatiguefailure. The bolting and thefuses have been sentto a laboratoryfor furtheranalysis. Corrective actions included replacement ofthevalve actuatormotorand the mounting bolts. Laboratory analysis may necessitate additional corrective actions oncethe results are known, inwhich casean LER revisionwill be submitted. The safety significance ofthis event is considered to bevery small. This event is being reported in accordancewith 10 CFR 50.73(a)(2)(v)(D) as an eventorcondition thatcould have preventedthefulfillmentofasafetyfunction needed to mitigatethe consequences ofan accident. NRC FORM366A U.S.NUCLEARREGULATORYCOMMISSION APPROVEDBYOMB: NO.3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimatedburdenperresponsetocomplywiththismandatorycollectionrequest80hours.Reported lessonsteamedareincorporatedintothelicensingprocessandfedbacktoindustry.Sendcomments LICENSEE EVENT REPORT (LER) regardingburdenestimatetotheFOIA,Library,andInformationCollectionsBranch(T-6A10M),U.S Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail tc CONTINUATION SHEET lnfocoltects.Resource@nrc.gov,andtheOMBrevieweratOMBOfficeofInformationandRegulator) Affairs,(3150-0104),Attn:DeskOfficerfortheNuclearRegulatoryCommission,72517thStreetNW (See NUREG-1022, R.3forinstructionandguidanceforcompletingthisform Washington,DC20503;e-mail:oira submissioniSjomb.eoD.gov.TheNRCmaynotconductorsponsor http://www.nrc.gov/readinq-rm/cloc-collections/nureqs/staff/sr1022/r3/) andapersonisnotrequiredtorespondto,acollectionofinformationunlessthedocumentrequesting orrequiringthecollectiondisplaysacurrentlyvalidOMBcontrolnumber. 1. FACILITYNAME 2. DOCKETNUMBER 3.LERNUMBER YEAR SEQUENTIAL REV 05000- NUMBER NO. Perry NuclearPowerPlant 00440 2022 001 00 | Energy Industry Identification System (EMS) codes are identified inthetext as [XX]. INTRODUCTION The inoperabilityand lossofsafetyfunction ofLow Pressure Core Spray (LPCS) [BM] system occurred as a resultofa loss ofelectrical powertothe LPCS pump minimum flowvalve [FCV] based upon the receiptofunexpected alarms in the Control Room, during surveillancetesting. Subsequent investigation ofthe LPCS minimumflowvalve revealedthatthe mounting boltsforthe motoroperated valveactuatorwere broken, and thefuses [FU] inthe disconnectforthe actuatorwerefound to be blown. With LPCS being a singletrain safety system, this resulted in a loss ofsafetyfunction resulting in a 10 CFR 50.72 notification and a 10 CFR 50.73 report. EVENT DESCRIPTION On June 24, 2022, at 1257 hours, and with the reactor in MODE 1 at 100 percent rated thermal power, a surveillance was being performed toverifythe operation ofthe LPCS system. During performance ofthe surveillance, itwas observed thatthe LPCS minimum flowvalve experienced a loss ofposition indication while stroking closed. Upon investigation ofthe MotorControl Center(MCC) disconnect [DISC]forthe LPCS minimum flowvalve, itwas determined thattwoofthreemain-line powerfuseswere blown. Examination ofthe LPCS minimum flowvalve revealed thatthe motor- operated actuator had becomeseparated fromthevalve. This resulted inthe LPCS system being declared inoperable. LPCS is described as a singletrain safety system in accordancewith site procedures. As such, when LPCS has an unplanned inoperability, it is reportabletothe NRC under 10 CFR 50.72(b)(3)(v)(D) and 10 CFR 50.73(a)(2)(v)(D) as a Loss ofSafety Function. On June 24, 2022, at 1628 hours, Event Notification (EN 55962)was made under 10 CFR 50.72(b)(3)(v)(D) tothe NRC. This Licensee Event Report is being reported under 10 CFR 50.73(a)(2)(v)(D) as a loss ofsafetyfunction. Newactuatortovalve bolts, a newactuator motor, and new disconnectfuseswere installed forthe LPCS minimumflow valve. The system performed satisfactorily during post maintenancetesting. LPCSwas declared OPERABLE on June 27, 2022, at 1300 hours. CAUSE OF EVENT The most probable cause ofthefailed adapterto actuatorboltswasfatiguefailure. The bolting andthefuses have been sentto a laboratoryforfurtheranalysis. Based upon the informationfromthe analyses, an LER revision may need to be submitted. NRCFORM366A (08-2020) Page of NRCFORM366A U.S.NUCLEARREGULATORYCOMMISSION APPROVEDBYOMB: NO.3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimatedburdenperresponsetocomplywiththismandatorycollectionrequest:80hours.Reportec lessonslearnedareincorporatedintothelicensingprocessandfedbacktoindustry.Sendcomment! LICENSEE EVENT REPORT (LER) regardingburdenestimatetotheFOIA,Library,andInformationCollectionsBranch(T-6A10M),U.S Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail tc CONTINUATION SHEET lnfocollects.Resource@nrc.gov,andtheOMBrevieweratOMBOfficeofInformationandRegulator) Affairs,(3150-0104),Attn:DeskOfficerfortheNuclearRegulatoryCommission,72517thStreetNW (SeeNUREG-1022, R.3forinstructionandguidanceforcompletingthisform Washington,DC20503;e-mail:oira submission@omb.eoD.gov.TheNRCmaynotconductorsponsor http://www.nrc.gov/readinq-rm/doc-collections/nureqs/staff/sr1022/r3A andapersonisnotrequiredtorespondto,acollectionofinformationunlessthedocumentrequesting orrequiringthecollectiondisplaysacurrentlyvalidOMBcontrolnumber. 1. FACILITYNAME 2. DOCKETNUMBER 3.LbKNUMbbK YEAR SEQUENTIAL REV 05000- NUMBER NO. Perry NuclearPowerPlant 00440 2022 001 00 NARRATIVE EVENTANALYSIS A Probabilistic RiskAssessment (PRA) evaluation was performed forthe June 24, 2022, LPCS Minimum FlowValve Inoperability event. Fire and otherexternal hazardswere qualitatively addressed to be oflow risk. The analysis ofthis eveni results in delta CDF and delta LERF values that are belowthe acceptablethresholds of 1.OE-06/yrand 1.OE-07/yr, as discussed in Regulatory Guide 1.174. Sensitivities performed that varied the exposurewindowtothe maximum possible exposurewindowofoneyeardid not changethese conclusions. The riskofthis event isthereforeconsidered very small in accordancewith the Regulatory Guidance. CORRECTIVEACTIONS Thevalve actuatorwas re-installed tothevalvewith newbolts. The actuatormotorwas also replaced. Newfuseswere installed intheelectrical disconnect. Thefailed bolts andfuses have been sent outforlaboratoryanalysis. PREVIOUS SIMILAR EVENTS None COMMITMENTS None NRCFORM366A (08-2020) Page of | ML22229A090 | 1 | ok
McGuire Nuclear Station | Unit 1 | Both Control Room Area Chilled Water System Trains Inoperable Due to Human Error | 08-18-2022 | At 2240 [EST] on June 21, 2022, with Unit 1 and Unit 2 operating at approximately 100 percent power and the A train of the Control Room Area Chilled Water System (CRACWS) inoperable for planned maintenance, a loss of safety function occurred when the B train CRACWS chiller tripped. A clearance required for maintenance on the A train was being performed when a non-licensed auxiliary operator (AO) opened the breaker feeding the oil pump associated with the running and operable B train. This resulted in an inadvertent trip of the B Chiller. With both CRACWS trains inoperable, Operations entered Abnormal Procedure AP-39 (Control Room High Temperature) and restored the B train within thirty-five minutes. The cause of this event is attributed to a human performance error in which the AO did not effectively use human performance tools to ensure the correct component was identified prior to operation. In addition to prompt restoration of the B Train of CRACWS and the system's safety function, corrective actions were initiated to improve accountability of the operator associated with this event, and implementation of additional layers of defense when placing clearances. This event had no impact on the health and safety of the public. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Repcrted lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICE NS EE EVE NT REPORT ( LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira submission@omb.eop.gov. The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form spcnsor, and a person is not required to respond to, a collection of information unless the document https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LERNUMBER YEAR SEQUENTIAL REV McGuire Nuclear Station, Unit 1 05000-369 NUMBER NO. 2022 - 001 - 00 | BACKGROUND The following information is provided to assist readers in understanding the event described in this LER. Applicable Energy Industry Identification [EIIS] system and component codes are enclosed within brackets. Control Room Area Chilled Water System [KM] The purpose of the Control Room Area Chilled Water System (CRACWS) [KM] is to provide chilled water to the Control Room and Control Room Area Ventilation (CRAV S) [VI] equipment to maintain temperature within Technical Specification limits. The CRACWS system has two redundant trains (A and B) serving the CRAV S air handling units providing cooling of recirculated control room air. The CRACWS operates in conjunction with the CRAV S and are shared between both McGuire units. These trains are normally not cross-connected. Each CRACWS train consists of a compression tank to provide water surge protection, a chilled water pump and a control area chiller. Chilled water circulates in a closed loop. Each chiller has its own separate refrigeration system. The CRACWS water exchanges heat with the refrigerant in the evaporator to be chilled to a desired temperature. The CRACWS is an emergency system which also operates during normal unit operations. A single train will provide the required temperature control to maintain the control room at approximately 75°F. The control room is shared between units. NRC FORM 3666 (08-2020) Page 2 of 5 | ML22230C557 | 0 | good
Fermi 2 05000 341 1 OF 4 | Unknown Unit | Turbine trip and subsequent reactor trip due to Mayflies | 08-23-2022 | At 2338 EDT on June 24, 2022, while in Mode 1, 100 percent power, Fermi 2 experienced a turbine trip followed by a reactor SCRAM, due to differential relaying sensing a generator output fault. The generator output fault occurred when a swarm of mayflies caused an arc from a 345 kV bus bar to the bottom of the insulator during a hatch. The National Weather Service data indicated the Mayfly hatch that occurred near Fermi 2 site on June 24, 2022 was significant, and compensatory actions were taken, however, additional subsequent actions were taken to minimize the potential for future switchyard operations being impacted from mayflies. Area and building lighting has been reduced further to limit attracting mayflies to sensitive plant equipment and the mayfly infestation buildup and forecast will be closely monitored as part of the mayfly mitigation plan. The seasonal mayfly control procedure has been updated to reflect these changes. A 4-hour event notification (EN 55964) was made to the NRC pursuant to Title 10 Code of Federal Regulations (10 CFR) 50.72(b)(2)(iv)(B) for RPS Actuation (Reactor Scram) and 10 CFR 50.72(b)(3)(iv)(A) as an event or condition that resulted in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Fermi 2 341 YEAR SEQUENTIAL REV 05000- NUMBER NO. 2022 - 003 - 00 | INITIAL PLANT CONDITIONS Mode – 1 Reactor Power – 100 Percent There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT At 2338, on June 24th, 2022 with the unit in Mode 1 at 100 percent power, the reactor automatically scrammed due to a Reactor Protection System (RPS) actuation on a Main Turbine Trip. Concurrent with the Turbine Trip and Reactor Scram, Security reported a flash from an intermediate switchyard between the generator output transformers and the 345kV switchyard. Additionally, operators noted the main control room lights dimmed; and field operators reported a large sound in the vicinity of the 345 kV switchyard. A large mayfly hatch was in progress at the time of the scram. During the investigation, it was identified that the reported flash from the switchyard was due to arcing from a conductor (bus bar) to ground. This arc damaged the base of the insulator and the bus bar. The scram occurred with no surveillances or activities in progress. As a result of the scram, an expected low reactor water level (Level 3) occurred resulting in isolation of Primary Containment Groups 4, 13, and 15, as expected. Group 4, RHR Shutdown Cooling and Head Spray, was already isolated, Group 13, Drywell Sumps, isolated and Group 15, Traversing In-Core Probe System was already isolated. A 4-hour event notification (EN 55964) was made to the NRC pursuant to Title 10 Code of Federal Regulations (10 CFR) 50.72(b)(2)(iv)(B) for RPS Actuation (Reactor Scram) and 10 CFR 50.72(b)(3)(iv) (A)as an event or condition that resulted in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B). Additionally, Div. 2 CCHVAC (Control Center [Main Control Room] Heating Ventilation and Air Conditioning) shifted to recirculation mode at the time of the scram, when the trouble annunciators associated with CCHVAC Radiation Monitors (3D39/3D38) were received. This was determined to be from the voltage transient from the generator fault. Following verification of proper recirculation mode lineup, Div. 2 CCHVAC was returned to normal mode. Offsite power supplied to the plant was not affected by the scram, thus all ECCS equipment remained operable and available. The cause is a large hatch of mayflies flew or landed in close proximity to the equipment, creating a conductive path from the bus (conductor) to ground at the bottom of the insulator. The mayfly infestation was substantial enough to create an arc across the insulator, damaging the insulator and bus bar. Indications were identified on the insulator consistent with a tracking arc strike through the conducting material (Mayflies) and not indicative of an insulator failure. Mayfly infestation is a natural phenomenon in the Great Lakes occurring during late spring and early summer months. Fermi 2 has seasonal procedural measures to reduce the potential impact on the plant and switchyard operations from mayfly accumulation. These measures were confirmed to be in place at the time of the event. A review of the National Weather Service data indicated a significant hatch of mayflies occurred near Fermi 2 site at the time of the event. | ML22235A106 | 0 | good
Grand Gulf Nuclear Station | Unit 1 | Not Found | 08-29-2022 | On June 30, 2022, at 1445 hours, with the Grand Gulf Nuclear Station in MODE 1 and 100 percent power, the reactor was manually tripped due to the loss of balance of plant (BOP) transformer 23. All control rods fully inserted into the core and all systems responded appropriately. The plant was stabilized in MODE 3. Standby Service Water A and B were manually initiated to supply cooling to the Control Room Air conditioning, Engineering Safety Feature (ESF) switchgear room coolers and plant auxiliary loads. The direct cause of the BOP transformer 23 trip was an instantaneous ground overcurrent most likely caused by a lightning strike (environmental) flashover event. There were no consequences to the safety of the public, nuclear safety, industrial safety, or radiological safety. No radiological releases occurred due to this event. This report is made in accordance with 10 CFR 50.73(a)(2)(iv)(A), for any event or condition that resulted in manual or automatic actuation of the Reactor Protection System (RPS). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. CON.TINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocol!ecls.Rescurce@nrc.aov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: ma subrn1ss1on@omb.eoo.gov_. The NRG may not conduct or llttps:// www .nrc.gov/reading-rm/doc·collections/nuregs/stafl/sr1022/r3/) sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 50-416 NUMBER NO. 2022 001 -00 | PLANT CONDITIONS: DESCRIPTION OF EVENT Prior to this event, the plant was at 100 precent power and Radial Well 3 was out of service. No activities were in progress that would have initiated the event. A thunderstorm was in the area. On June 30, 2022, at 1441 hours, balance of plant (BOP) transformer 23 feeder breaker tripped due to an instantaneous ground overcurrent lock out. This caused Radial Wells 4 and 5 to trip. Control Room received alarm indications on the instrument panel for 4.16kV BUS 28AG UNDERVOLTAGE and BOP XFMR 23 INCM FDR TRIP followed by several alarms on the Radial Well HMI and other control room panels as a result of feeder breaker tripping on ground overcurrent. After the loss of BOP transformer 23, the air release valves at Radial Well 6 lifted and diverted well output back to the caisson, resulting in the loss of all Plant Service Water (PSW) forward flow. Standby Service Water A and B were manually initiated to supply cooling to the Control Room Air conditioning, Engineering Safety Feature (ESF) switchgear room coolers and plant auxiliary loads. At 1443, Operations immediately entered loss of PSW procedure and lowered core flow to 70 Mlbm/hr in fast descent. At 1445, operators placed the reactor mode switch into shutdown due to Turbine Building Cooling Water trends being unable to be maintained less than 100 degrees (and rising). During radial well recovery, E radial well pump (Radial Well 5) was able to be started remotely but the valves would not operate remotely, and F radial well pump would not start remotely. REPORT ABILITY This report is made in accordance with 10 CFR 50. 73(a)(2)(iv)(A), for any event or condition that resulted in manual or automatic actuation of the Reactor Protection System (RPS). CAUSE The direct cause of the BOP transformer 23 trip was an instantaneous ground overcurrent most likely caused by a lightning strike (environmental) flashover event. The direct cause was determined based on troubleshooting using the Failure Mode Analysis (FMA) and evaluation performed after the event in conjunction with a vendor and Entergy Distribution. It was found that there were several areas near the poles where lightning strikes had occurred, but that there was no evidence of a direct lightning strike on any of the poles or instrumentation. CORRECTIVE ACTIONS Completed actions to address the direct cause: 1. Initiated Operational Decision Making (ODM) to start plant up post-trip with all radial well loads powered from BOP 13 transformer. 2. Engineering performed post-event and post-maintenance walkdowns with a vendor and peer engineers to verify the readiness to re-energize the BOP 23 transformer. 3. Removed the wire mesh off all the BOP 23 Overhead Feeder Line poles and ensured that there were no stray ground wires running up above the neutral per Entergy Distribution recommendations. | ML22241A113 | 1 | ok
River Bend Station | Unit 1 | Division 1 Standby Diesel Generator Speed Sensor Power Supply Failure | 09-01-2022 | On July 04, 2022, at 2115 Central Time, while River Bend Station, Unit 1 was operating in Mode 1 at 100 percent power, the Division 1 Standby Diesel Generator was declared Inoperable due to failure of redundant power supplies in the speed control circuitry. This was discovered during monthly surveillance testing. The failedpower supplies provide power to the exciter flash circuitry and ramp governor control. This condition would have prevented the Division 1 Standby Diesel Generator from providing power to Division 1 Emergency Loads. The issue was determined to be reportable in accordance with 10 CFR 50.73(a)(2)(v)(A), (B), (C), and (D) as any event or condition that could have prevented the fulfillment of the safety function of structures or systems. This event was not reportable in accordance with 10 CFR 50. 72 because the Division 2 Standby Diesel Generator was operable and available at the time of discovery. The condition was corrected by replacing the power supplies on July 07, 2022. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/l sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITYNAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV River Bend Station, Unit 1 05000-458 NUMBER NO. 2022 003 00 | EVENT DESCRIPTION On July 04, 2022, at 2115 Central Time, River Bend Station, Unit 1 (RBS) was operating in Mode 1 at 100 percent power. There were no other structures, systems, or components (SSCs) that were inoperable that contributed to this event. A failure was identified in the speed control circuitry of the Division 1 Standby Diesel Generator (EGS-EG1A) [EK] [DG] during monthly surveillance testing per STP-309-0201, Division I Diesel Generator Operability Test. EGS-EG1A was,declared inoperable due to the speed control circuitry failure and documented in the RBS Corrective Action Program in CR-RBS-2022-03801. EGS-EG1A speed control circuit contains redundant Dynalco SDC-2000, 125 VDC to 24 VDC power supply converters (EGS-E/EX43A and EGS-E/EY4 3A) [CNV]. These components supply power to individual speed switches and tachometers. EGS-E/EY43A also supplies power to Emergency Response Information System (ERIS) [ID] computer point (EGSEY009) [SI]. The speed control circuit is designed such that either one of the power supplies is sufficient to allow field flash and loading of the diesel genetator. These power supplies were refurbished by Paragon and installed in December 2020. The failures occurred after approximately 1.5 years with an expected replacement frequency of 8 years. Timeline of events: 06/01/22 - STP-309-0201, Division 1 Diesel Generator Operability Test completed. This was the last known successful operability run for EGS-EG1A. This verified that both EGS-E/EX43A and EGS-E/EY4 3A were functioning properly on 06/01/22 because the local tachometers and EGSEY009 provided proper indication. 06/08/22 - ERIS computer point, EGSEY009 "flatlined" starting on 06/08/22, which is most likely when EGS-E/EY43A lost power. This was not a normally monitored component and went undetected until troubleshooting identified the condition on 07/05/22. 06/12-13/22-Performed STP-309-0202, Division 2 Diesel Generator Operability Test.The normal requirements of this test resulted in 0.63 hours of Unavailability for the Division 2 Standby Diesel Generator (EGS-EG 1B ) [EK] [DG]. 07/04/22-EGS-EG1A, Division 1 Emergency Diesel Generator was declared inoperable. 07/05/22 - Trouble shooting determined the failure of both power supplies EGS-E/EX43A and EGSE/EY43A. 07 /05/22 - Trouble shooting determined that both power supplies had blown fuses. 07 /05/22 - Common Mode Failure evaluation determined that EGS-EG 1B utilizes the same exact design and manufacturer for these components. However, voltage readings for EGS-E/EX43B and EGS-E/EY4 3B were satisfactory leading to the conclusion that the failure was not currently present in EGS-EG 1B . 07 /05/22 - Common Mode Failure evaluation excluded the Division 3 High Pressure Core Spray Diesel Generator due to differing designs. 07/06/22 - RBS function testing to determine the cause of the blown fuses was inconclusive. 07/07/22-Completed installation of EGS-E/EX43A and EGS-E/EY43A power supplies per Engineering Change (EC-87792). The new Phoenix power supplies are designed with external lights to provide positive indication of power status. 07/07/22 - Completed post maintenance testing and declared EGS-EG1A operable. 08/04/22 - The failed Dynalco SDC-2000 power supplies were shipped to an outside vendor, Engine Systems Inc., to perform a detailed failure analysis. Preliminary results are expected in September 2022. As stated in the timeline above, monthly surveillance testing rendered EGS-EG1 B unavailable for a total of 0.63 hours during June 12-13, 2022. The discovery of EGSEY009 "flatlined" starting on June 08, 2022, means that EGS-E/EY 43A most likely lost power at that time. Although either EGS-E/EY 43A or EGS-E/EX43A functioning properly would allow EGS-EG1A to load, the timing of EGS E/EX43A power loss is unknown. Therefore, this condition is being reported in accordance with 10 CFR 50.73(a)(2)(v) as "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: (A) Shut down the reactor and maintain it in a safe shutdown condition; (B) Remove residual heat; (C) Control the release of radioactive material; or (D) Mitigate the consequences of an accident." This event was not an ENS notification because EGS-EG1 B was operable and available at the time of discovery. | ML22244A098 | 0 | good
LICENSEE EVENT REPORT (LER) | Unknown Unit | Estimated burden per response to comply with this mandatory conecoori request 80 hours. Repor1e<f lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollec1s.Resource@nrc.gov, and 1he 0MB reviewer at 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currentiy valid 0MB control number. 2. Docket Number· 3. Page . 05000 - 254 1 OF 5 Both Trains of Standby Gas Treatment Inoperable Due to Blockage in the Common Discharge Line | 09-01-2022 | On 7/4/22 at 0104, Unit 2 experienced a reactor scram. As a result, the 1/2 B Standby Gas Treatment (SGT) train.auto started and was found to have lower than Technical Specification (TS) required flow. The 1/2 B SGT train was secured and the 1/2 A SGT train was manually started and found to have the same low flow condition. On 7/4/22 at 0130, both units entered TS 3.6.4.3 Condition D for having both SGT trains inoperable. On 7/4/22 at 0230 TS 3.6.4.3 Condition E was entered. SGT flow slowly increased with the running of the train and on 7/4/22 at 1122 the 1/2 B SGT train was declared operable, and TS 3.6.4.3 Condition E was exited. The cause of the SGT low flow condition was water in the common SGT discharge line. This event is being reported under 10 CFR 50.73(a)(2)(v)(C) and (D) - "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are n_eeded to: (C) control the release of radioactive material, and (D) mitigate the consequences of an accident." This event is also reportable under 10 CFR 50.73(a)(2)(i)(B) - "Any operation or condition which was prohibited by the plant's Technical Specifications." NRC FORM 366A (08-2020) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (;-•'" """,,,o\ 'l, .,,'41 *"'*•"" .,.o' LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www. nrc. g ov/readi ng-rm/d oc-col lections/nu reqs/staff/sr1 022/r3/) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A 10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 72517th Street NW, Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER· Quad Cities Nuclear Power Station Unit 1 05000- 254 YEAR SEQUENTIAL NUMBER REV NO. 2022 - | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. EVENT IDENTIFICATION 003 Both Trains of Standby Gas Treatment Inoperable Due to Blockage in the Common Discharge line CONDITION PRIOR TO EVENT Unit: 1 Event Date: July 4, 2022 Reactor Mode: 1 Mode Name: Power Operation Event Time: 0130 CST Power Level: 100% No structures, systems or components were inoperable at the start of this event that contributed to the event. A. DESCRIPTION OF EVENT 00 On July 4, 2022, at 0104, Unit 2 experienced a manual scram. As a result of the reactor scram, the 1/2 B train of Standby Gas Treatment (SGT)[BH] auto started; however, the train was running with degraded and oscillating flow between 2400-2600 scfm. Technical Specification 5.5.7 requires a SGT flow of 4000 cfm +/- 10%. TS 3.6.4.3 Condition A was entered on July 4, 2022, at 0127 for one SGT subsystem being inoperable. TS 3.6.4.1 Condition A was also entered for inoperable Secondary Containment because Secondary Containment vacuum was found to be less than 0.25 inches water gauge vacuum required by TS surveillance requirement (SR) 3.6.4.1.3. On July 4, 2022, at 0130, Operations manually secured the 1/2 B SGT train and started the 1/2 A SGT train and it also indicated degraded and oscillating flow of a similar flowrate and signature to the 1/2 B SGT train. TS 3.6.4.3 Condition D was entered on July 4, 2022, at 0130 for two SGT subsystems being inoperable. Operations initiated troubleshooting efforts that identified a partial blockage in the 24 inch common discharge line [PSX] from both trains of SGT to the main chimney. The SGT flow control valves (FCV)[FCV] were also observed as being fully open, when during normal operation the FCV is partially open and controlling the flow through the train. As the SGT system continued to operate, the flowrate through the train slowly increased. On July 4, 2022, at 0230, TS 3.6.4.3 Condition E was entered for not having restored one SGT subsystem within 1 hour. · Condition E requires both Unit 1 and Unit 2 to be in Mode 3 within 12 hours. Unit 2 was already in Mode 3 due to the earlier manual scram. On July 4, 2022, at 0853 (CT), Event Notification System (ENS) notification #55976 was completed for the immediate reportability required under 10 CFR 50.72(b)(3)(v)(C) and (D) - "Any event or condition | ML22244A134 | 0 | good
LICENSEE EVENT REPORT (LER) | Unknown Unit | Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of lnfonmation and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira submission@omb.eop.gov. The NRG may not conductor sponsor, and a person is not required to respond to, a collection of infonmation unless the document requesting or requiring the collection displays a currently valid 0MB control number. 2. Docket Number 3.Page 05000 - 265 1 OF 4 Manual Scram Due To Feedwater Regulator Valve Failure Decreasing Reactor Water Level | 09-01-2022 | On July 4, 2022, Unit 2 was at 100% power with no surveillance activities in progress that contributed to the event. At 0103 hours the 2A Feedwater Regulating Valve (FRV) failed in the closed position and locked up, causing a decrease in reactor vessel water level. Attempts at manual control of the feedwater system to increase level were not successful. At 0104, a manual scram was inserted in accordance with operating procedures. All control rods inserted, and the scram was uncomplicated. The cause of this event is foreign material partially or completely blocking hydraulic oil flow internal to a servo valve in the 2A FRV that caused it to move rapidly from the half open position to the full closed position. This caused Unit 2 reactor vessel water level to rapidly lower until it reached the established scram criteria of +11 inches, at which time a manual scram was inserted. This report is being submitted in accordance with 10 CFR 50.73(a)(2)(iv)(A) for an event or condition that resulted in manual or automatic actuation of the reactor protection system including a reactor scram. NRC FORM 366A (08-2020) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 0!!/31/2023 LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.govlreading-rmldoc-collectionslnuregslstafflsr1022/r31) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Quad Cities Nuclear Power Station Unit 2 05000- 265 YEAR SEQUENTIAL NUMBER REV NO. 2022 - | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. EVENT IDENTIFICATION 002 Manual Scram Due To Feedwater Regulator Valve Failure Decreasing Reactor Water Level CONDITION PRIOR TO EVENT Unit: 2 Event Date: July 4, 2022 Reactor Mode: 1 Mode Name: Power Operation Event Time: 0104 CDT Power Level: 100% No structures, systems or components were inoperable at the start of this event that contributed to the event. A. DESCRIPTION OF EVENT On July 4, 2022, Unit 2 was operating at 100% power. There were no surveillances in progress that contributed to the event. At 0103 hours, main control room (MCR) alarms indicated the 2A Feedwater (FW) [JB] Regulating Valve (FRV) [FCV] failed in a manner that drove it to a closed position and caused the valve to lock up. As a result, reactor vessel water level began to decrease. MCR Operators took manual control of the FW system in an effort to increase water level prior to reaching the scram threshold. The 2A FRV was locked up in the closed position. The 2B FRV rapidly opened to maintain level, but the single FRV was incapable of passing sufficient flow to maintain vessel level at full reactor power. Manual control of the FRVwas not successful at maintaining level. It is noted that there was a potential missed opportunity to perform an emergency power reduction which could have reduced reactor power, allowing the single FRV to maintain sufficient vessel level. At 0104 hours, the decreasing water level reached the +11 inches threshold at which a manual scram was ordered. All control rods inserted, and the scram was not complicated. The NRC was notified via ENS Report 55975 at 0557 EDT. Following replacement of the 2A FRV, Unit 2 returned to power operations on July 6, 2022. 00 NRG FORM 366A (08-2020) Page_2_. of _4_ | ML22244A135 | 0 | good
byron station | Unknown Unit | OB Control Room Ventilation Supply Fan Failed to Start due to Erroneous Position Indication from the Closed Limit Switch for Charcoal Deluge Valve Interlock | 09-09-2022 | 12. Licensee Contact for this LER Licensee Contact Phone Number (Include area code) Zoe Cox, Regulatory Assurance Manager (815) 406-2800 13. Complete One Line for each Component Failure Described in this Report Cause System Component Manufacturer Reportable to IRIS Cause System Component Manufacturer Reportable to IRIS B VI ZIS N007 y NIA NIA NIA NIA NIA 14. Supplemental Report Expected Month Day Year I 15, Expected Submission Date D ~ No Yes (If yes, complete 15. Expected Submission Date) NA NA NA 16, Abstract (Limit to 1560 spaces, ie., approximately 15 single-spaced typewritten lines) On July 12, 2022, the OB Control Room Ventilation (VC)[VI] supply fan (0VC01 CB) failed to start when commanded due to an erroneous position indication from the closed limit switch (0ZS-FP432B-A) for the OB VC recirculation charcoal deluge valve (0FP432B). The deluge valve was closed but the limit switch operating lever had rolled under the limit switch finger, causing the operating lever to be in the same position as if the deluge valve were in the "intermediate" or "open" position. This resulted in the OB train of VC not being operable for 48 days. Once identified, the actuator arm and limit switch were adjusted to properly make up the closed limit and the fan was started, restoring the OB train of VC to operable. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) for any operation or condition which was prohibited by the plant's Technical Specifications. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 72517th Street NW, Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www. nrc. gov/ read i nq-rm/d oc-collection sin u reg s/staff/sr1 0 2 2/ r3/) requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Byron Station, Unit 1 05000454 NUMBER NO. 2022 - 001 00 | A. Plant Operating Conditions Before the Event: Event Date: July 12, 2022 Unit 1 - Mode 1 - Power Operations, Reactor Power 100 percent Unit 2 - Mode 1 - Power Operations, Reactor Power 100 percent Reactor Coolant System (RCS) [AB): Normal Operating Temperature and Pressure No structures, systems or components were inoperable at the start of this event that contributed to the event B. Description of Event: On July 12, 2022, at 03:24 CDT, the OB Control Room (VC)[VI) supply fan (0VC01 CB) failed to start when commanded due to an erroneous position indication from the closed limit switch (0ZS-FP432B-A) for the OB VC recirculation charcoal deluge valve (0FP432B). The deluge valve was in the closed position; however, the limit switch operating lever had rolled under the limit switch finger, resulting in the operating lever being in the same position as if the deluge valve was in the intermediate or open position. In accordance with the OB VC Supply Fan control logic drawing (6E-0-4030VC02), if the 0FP432B valve limit switch is in the intermediate or open position (i.e., not closed), the supply fan shunt trip coil is energized, preventing the supply fan breaker from remaining closed after a start command, causing the fan to trip immediately. A review was completed to determine the last time the 0FP432B valve was manipulated. On May 23, 2022, the OB VC System makeup filter and recirculation charcoal adsorber were placed in service for OB VC chiller performance verification testing. This was the last documented run of 0VC01 CB supply fan prior to July 12, 2022. On May 25, 2022, 0FP432B, recirculation charcoal deluge valve was manually cycled to support performance of a Fire Protection (FP) surveillance. On July 12, 2022, at 03:24 CDT, the attempted start of the 0VC01 CB supply fan resulted in it immediately tripping. The 0A VC train was restarted 1 hour and 13 minutes later in accordance with procedural guidance. On July 12, 2022, at 14:05 CDT, the OB VC train was started after the actuator arm and limit switch were adjusted to properly make up the closed limit interlock. On July 12, 2022, at 19:48, after completion of post-maintenance testing, Limiting Condition for Operation (LCO) Condition A for Technical Specifications 3. 7.10, "Control Room Ventilation (VC) Filtration System" and LCO Condition A for TS 3.7.11, "Control Room Ventilation (VC) Temperature Control System" were exited, and operability of the OB train of VC was restored. C. Cause of Event The cause of the OB VC supply fan to not start was the limit switch operating lever had rolled under the limit switch finger which made the 0FP432B valve appear to be in the intermediate or open position causing the supply fan shunt trip coil to remain energized, thereby preventing the fan breaker from remaining closed after the start command. There were inadequate margins in the length of the limit switch operating levers to be made up with the limit switch finger. D. Safety Consequences: This condition had no actual safety consequences impacting plant or public safety. This event is not considered an event or condition that could have prevented fulfillment of a safety function. The VC system has two full capacity, redundant equipment trains that perform the same function. The VC HVAC system is designed to ensure control of environmental conditions within specified maximum and minimum | ML22252A138 | 0 | good
Brunswick Steam Electric Plant (BSEP) | Unit 1 | High Pressure Coolant Injection (HPCI) Inoperable | 09-12-2022 | At 20:20 Eastern Daylight Time (EDT) on July 15, 2022, with Unit 1 in Mode 1 at approximately 96% power for planned maintenance on the ‘1A’ Condensate Deep-bed Demineralizer (unrelated to this event), the High Pressure Coolant Injection (HPCI) system was declared inoperable upon discovering the HPCI flow controller without power. The HPCI flow controller lost power as a result of an intermittent connection in the flow controller fuse holder. The fuse was secured in the fuse holder and HPCI was declared operable on July 16, 2022, at 12:10 EDT following associated post maintenance testing. The Reactor Core Isolation Cooling (RCIC) System and Automatic Depressurization System (ADS) remained operable during this event. There was no impact on the health and safety of the public or plant personnel. The safety significance of this event is minimal. This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant (BSEP), 05000- 325 YEAR NUMBER NO. Unit 1 2022 - 001 - 00 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. Background Initial Conditions At the time of the event, Unit 1 was in Mode 1 (i.e., Power Operation), at approximately 96 percent rated thermal power for planned maintenance on the ‘1A’ Condensate Deep-bed Demineralizer (unrelated to this event). There was no inoperable equipment that contributed to the event. Reportability Criteria The High Pressure Coolant Injection (HPCI) [BJ] inoperability is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented fulfillment of the safety function needed to mitigate the consequences of an accident. The NRC was notified of this event per 10 CFR 50.72(b)(3)(v)(D) via Event Notification 55997 at 23:41 Eastern Daylight Time (EDT) on July 15, 2022. Event Description At 20:20 EDT on July 15, 2022, with Unit 1 in Mode 1 at approximately 96% power for planned maintenance on the ‘1A’ Condensate Deep-bed Demineralizer (unrelated to this event), the HPCI system was declared inoperable upon discovering the HPCI flow controller without power during Reactor Operator control board walkdowns. Event Cause Upon initial investigation into the issue, a loose lead to the HPCI flow controller was discovered. Upon tightening the loose lead power returned to the HPCI flow controller, and availability of the HPCI system was restored at 20:23 EDT on July 15, 2022. However, the HPCI system remained inoperable at this time while additional troubleshooting and testing were performed. Additional troubleshooting determined that the identified loose lead could not have caused loss of power to the device and some other intermittent connection was present. While performing a calibration check on the device, a loose fuse holder connection was identified on the backside of the flow controller. The fuse was secured in the fuse holder and HPCI was declared operable on July 16, 2022, at 12:10 EDT following associated post maintenance testing. The HPCI flow controllers are refurbished and replaced on a 10-year frequency. This flow controller had been replaced in the May 2022 timeframe. However, fuse replacement is not part of the refurbishment instructions, and checking fuse holder tightness is not included in the installation instructions. This allowed the fuse holder to work its way loose over time due to normal handling/inspection/maintenance. Therefore, the cause of this event was determined to be inadequate procedural guidance associated with ensuring tightness of the fuse holder. Safety Assessment There was no impact on the health and safety of the public or plant personnel as a result of this event. HPCI system availability was restored at 20:23 EDT on July 15, 2022, following power restoration to the HPCI flow controller. Therefore, the system was available to perform its safety function of injecting the required flow rate into the Reactor Pressure Vessel at this time. In addition, the Reactor Core Isolation Cooling (RCIC) [BN] System and Automatic Depressurization System (ADS) remained operable during this event. | ML22255A164 | 0 | good
Surry Power Station | Unit 1 | Failure of Unit 1 Emergency Diesel Generator Results in an Operation or Condition Prohibited by Technical Specifications | 09-19-2022 | On July 25, 2022, with both Surry Power Station Units 1 and 2 at 100% power, the 7-day Technical Specification (TS) Allowed Outage Time (AOT) for an emergency diesel generator (EDG) was exceeded due to a partial loss of load during monthly surveillance testing for the Unit 1 emergency diesel generator (EDG-1 ), requiring repair and restoration. To complete the EDG-1 repair, balancing, testing, and return to service, a request for enforcement discretion was submitted and approved that extended the TS AOT by two days (for a total of nine days). During event troubleshooting, it was revealed that the cause was corrosion between the lugs of the field lead causing a hard ground on one pole of the generator rotor. The risk analysis performed for this event concluded that the increase in core damage and large early release probability remained within the NRC Enforcement Manual, Appendix F limits. Completed corrective actions included the replacement of the EDG-1 generator and verification of operability of the EDG-2 and EDG-3. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document http://www.n rc.g ov /reading-rm/doc-co Il ections/n ur egs/staff/ sr 10 22/r3/} requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER DYEA R SEQUENTIAL REV Surry Power Station, Unit 1 05000- , 280 ~-I NUMBER 1-NGO. I 002 | PLANT OPERAT ING CONDITIONS BEFORE THE EVENT Surry Power Station (SPS) Unit 1 and Unit 2 were at 100% power. 1.0 DESCRIPTION OF THE EVENT The SPS emergency diesel generator (EDG) [EIIS: DG] for Unit 1 (EDG-1) and Unit 2 EOG (EDG-2) are dedicated to emergency buses 1H and 2H [EIIS: BU], respectively. A third diesel generator (EDG-3) is provided as a "swing diesel" and is shared by both units (the "J" bus). Each EDG has 100% capacity and is connected to an independent 4160 V emergency bus. EDG-1 provides emergency power to certain equipment and systems common to Units 1 and 2, including the Auxiliary Feedwater system (AFW) [EIIS: BA] cross-tie between Units 1 and 2, the Auxiliary building [EIIS: NF] filter exhaust fan [EIIS: FAN], Main Control Room (MCR) [EIIS: NA] chiller [EIIS: CHU], and MGR/Emergency Switchgear Room [EIIS: EK] filtered supply fans [EIIS: FAN]. At 0956 on July 18, 2022, the SPS EDG-1 for Unit 1 was removed from service to perform the monthly surveillance test. Approximately 20 minutes after reaching full load, EDG-1 experienced a partial loss of load. The MCR operators noted that the generator load had lowered and the generator output current indication was above the normal amps for fully loaded. Local field operators noted a change in engine sound normally associated with decreasing load; subsequently, EDG-1 was unloaded and ran unloaded for 30 minutes before being secured in accordance with the normal shutdown sequence. Following shutdown, EDG-1 was removed from service for investigation. Troubleshooting was performed, and it was discovered that a lead to the generator exciter [EIIS: EXC] was grounded. A physical inspection of this lead revealed a failure between the generator brush rigging and the panel wiring at the bolted connection point. A bridge and megger check on the generator stator was satisfactory. Further troubleshooting of the generator rotor indicated a hard ground on one out of eight (8) rotor poles. It was concluded that repairs to EDG-1 were necessary, including replacement of the generator. During the return-to service testing portion of the repair effort, activities required to complete the repair, perform post-maintenance testing, and return the SPS Unit 1 EDG-1 to service would not be accomplished within the 7-day Allowed Outage Time (AOT) (reference: TS 3.16.B.1.a.3 for an inoperable EOG), and as such, a request for enforcement discretion was requested and verbally approved on July 24, 2022, at 14:27. This enforcement discretion allowed a 2-day extension to the 7-day AOT to complete the EDG-1 return to service activities. TS 3.16.B.1.a.3 requires an inoperable EDG to be restored to service within seven (7) days or action be initiated to place the appropriate unit in a shutdown condition. In addition, TS 3.0.2 states that TS action statements associated with any individual systems, subsystems, trains, components, and devices that EDG-1 supports also would be governed by the 7- day EOG AOT. Since EDG-1 provides emergency power to certain equipment and systems common to Units 1 and 2, the shutdown of Unit 2 also would be required upon the expiration of the EDG-1, 7-day AOT. During final return-to-service testing, at 0956 on July 25, 2022, with both Surry Power Station (SPS) Unit 1 and Unit 2 at 100% power, the AOT for TS 3.16.B.1.a.3 was exceeded for Unit 1. Additionally, TS 3.0.2 for Unit 2 was not satisfied due to the inoperability of EDG-1 beyond that allowed by TS 3.16.B.1.a.3. Both units remained at 100% power throughout the restoration of EDG-1 that was declared operable at 1705 on July 26, 2022. | ML22263A429 | 0 | good
Palo Verde Nuclear Generating Station (PVNGS) | Unit 1 | Units 1 and 3 Emergency Diesel Generator Actuation on Loss of Offsite Power to Class 4.16 kV Buses | 10-11-2022 | On August 14, 2022, at 1702 Mountain Standard Time, a valid actuation of the emergency diesel generators (EDGs) for Palo Verde Nuclear Generating Station (PVNGS) Unit 1 B-train and Unit 3 A-train occurred due to an undervoltage condition on their respective 4.16 kilovolt (kV) Class 1E buses. Both EDGs started and loaded as designed, including associated train essential spray pond pumps and the Unit 1 B-train auxiliary feedwater pump. The loss of power to the Unit 1 and Unit 3 Class 1E buses and resulting component actuations were the result of startup transformer NAN-X02 tripping offline. Unit 1 and Unit 3 both entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1, Condition A, for one required offsite circuit inoperable. In addition, both units also entered TS LCO 3.8.9, Condition A, for the loss of the Class 1E bus, which was exited when the EDGs started and restored power to their respective Class 1E buses. TS LCO 3.8.1, Condition A, was exited by both units on August 15, 2022. The direct cause of the undervoltage condition and the EDG and pump actuations was startup transformer NAN-X02 tripping offline due to the opening of the NAN-X02 startup transformer 525 kV breakers and 13.8 kV breakers due to protective relay actuation. The apparent cause of the event was attributed to water intrusion into the 2E-NAN-S05A cubicle as the result of a heavy rainstorm and high winds, in combination with degraded weatherstripping and conductor insulating boots that are not waterproof. No similar events have been reported by PVNGS in the last three years due to the same initial cause. NRC FORM 366A (08-2020) Page 2 of 5 NRC FORM 366A (08-2020) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Palo Verde Nuclear Generating Station 05000-528 YEAR SEQUENTIAL NUMBER REV NO. 2022 001 00 | All times are Mountain Standard Time and approximate unless otherwise indicated. 1. REPORTING REQUIREMENT(S): This Licensee Event Report (LER) is being submitted pursuant to 10 CFR 50.73 (a)(2)(iv)(A) to report a valid automatic actuation of the circuitry that starts the emergency diesel generator (EDG) (EIIS: EK) for Unit 1 and Unit 3 following an undervoltage condition on the affected Class 1E bus for each unit on August 14, 2022. The event included actuations of the associated essential spray pond (SP) pumps (EIIS: BS) and the Unit 1 B auxiliary feedwater (AF) pump (EIIS: BA). This event was reported to the NRC on August 14, 2022 via the event notification system (ENS 56044). 2. DESCRIPTION OF STRUCTURE(S), SYSTEM(S) AND COMPONENT(S): The safety related equipment for each Palo Verde Nuclear Generating Station (PVNGS) unit is powered by one of two load groups (A-train and B-train). Either of the associated trains can provide power for safe plant shutdown. Each alternating current (AC) train includes one Class 1E 4.16 kilovolt (kV) bus (EIIS: EB). The preferred and alternate power sources for each load group is offsite 525 kV AC power (EIIS: EK) and is supplied via the 13.8 kV secondary windings from two of the three startup transformers (EIIS: EA) to six 13.8 kV intermediate buses. Each unit receives 13.8 kV power from two of the intermediate buses. Class 1E 4.16 kV safety load group power is provided from the associated intermediate bus engineered safety feature (ESF) transformers. The standby power supply for each safety load group consists of one EDG (EIIS: EK), including its auxiliary and fuel systems. The standby power supply functions as a source of AC power for safe plant shutdown in the event of loss of preferred power and for post-accident operation of ESF loads. 3. INITIAL PLANT CONDITIONS: On August 14, 2022, PVNGS Units 1, 2 and 3 were in Mode 1 (Power Operation) at 100 percent power, normal operating temperature and normal operating pressure. There were no inoperable structures, systems or components at the time that contributed to this event. 4. EVENT DESCRIPTION: On August 14, 2022, at 1702, a valid loss of power (LOP) actuation occurred due to an undervoltage condition on the Unit 1 B-train and Unit 3 A-train Class 1E buses which resulted in an automatic actuation of the circuitry that starts the Unit 1 B-train EDG and Unit 3 A-train EDG. The undervoltage condition on the Units 1 and 3 Class 1E 4.16 KV buses resulted from startup transformer NAN-X02 tripping offline. Both EDGs started and loaded as designed. The EDG actuations were accompanied by the start of associated train essential SP pumps in both units. The Unit 1 B-train EDG actuation was also accompanied by the start of the Unit 1 B-train auxiliary feedwater pump, as required for the undervoltage condition. By design, actuation of the Unit 3 A-train steam-driven auxiliary feedwater pump was not required in response to the EDG actuation. | ML22285A000 | 0 | good
YEAR SEQUENTIAL REV | Unknown Unit | Not Found | 10-17-2022 | 12. Licensee Contact for this LER NLicaetnhsaeen C Foentdacotr a, Senior Nuclear Regulatory Engineer Phone N6um1b2e-r3 (4In2cl-u8d9e 7ar1ea code) 13. Complete One Line for each Component Failure Described in this Report Cause System Component Manufacturer Reportable to IRIS Cause System Component Manufacturer Reportable to IRIS Month Day Year 14. Supplemental Report Expected 0 ID 15. Expected Submission Date No Yes (If yes, complete 15. Expected Submission Date) On August 17, 2022, with both Unit 1 and Unit 2 of the Prairie Island Nuclear Generating Plant (PINGP) operating in Mode 1 at 100 percent power, it was discovered that 38 fuel assemblies had been placed in an incorrect location of the Spent Fuel Pool (SFP) during the move of fuel assemblies which commenced at 12:30 on August 15, 2022 and was completed on August 16, 2022. The location of 29 of these 38 fuel assemblies did not comply with Technical Specification Design Feature 4.3.1.1, resulting in Technical Specification 3.7.17 Action Statement A being entered on August 17, 2022, at 10:53. The cause of this condition was a procedural step that wasn't followed resulting in an incorrect date being entered in the software configuration tool. This incorrect date caused the software configuration tool to calculate longer fuel assembly cooling times resulting in mis-categorization of the fuel assemblies. Following discovery, the correct date in the software configuration tool was used to ensure the non-complying fuel assemblies were moved to the correct locations to restore compliance and Technical Specification LCO 3. 7 .17 Action Statement A was exited on August 19, 2022, at 10:32. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by technical specifications. NRG FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden eslimale to the FOIA, Library. and Information Collections Branch {T-6 A1 0M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001. or by e-mail to CONTINUATION SHEET tnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104). Attn: Desk Officer for the Nuclear Regulatory Commission, 72517th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira submissioo@omb.eop,gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document http·/ twww.nrc.gov/readinq-rm/doc-collections/nuregs/staff/sr1022/r3/\ requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Prairie Island Nuclear Generating Plant 05000-1 -282 I ~ □ - I NUMBER 1-0 NO. 001 | EVENT DESCRIPTION On August 17, 2022, with both Unit 1 and Unit 2 of the Prairie Island Nuclear Generating Plant (PINGP) operating in Mode 1 at 100 percent power, it was discovered that 38 fuel assemblies had been placed in an incorrect location of the Spent Fuel Pool (SFP). The location of 29 of the 38 fuel assemblies did not comply with Technical Specification Design Feature 4.3.1.1 resulting in Technical Specification 3.7.17 Action Statement A being entered on August 17, 2022, at 10:53. On August 4, 2022 Fuel Transfer Logs were generated using the software configuration tool in preparation for upcoming fuel assembly moves in anticipation of a core offload scheduled to occur during an upcoming refueling outage on Unit 1. The generation of the Fuel Transfer Logs unknowingly carried over a planning date of June 1, 2029 which had been previously used for a scoping study of future SFP configurations. This incorrect planning date resulted in the software configuration tool calculating longer fuel assembly cooling times and mis-categorizing 38 fuel assemblies such that they were assigned a less reactive category than they should have been. The fuel assemblies were classified as Fuel Category 6 when they should have been classified as Fuel Category 4 or 5. On August 15, 2022, the move of fuel assemblies commenced at 12:30 using the Fuel Transfer Logs that were generated on August 4, 2022 with the incorrect planning date. The fuel assembly moves were completed on August 16, 2022. On August 17, 2022, during preparations for the move of new fuel assemblies from the new fuel pit to the SFP, new Fuel Transfer Logs were generated in software configuration tool using a correct planning date. This process resulted in receipt of multiple warnings which alerted engineering of the configuration errors. Investigation into the warnings identified the incorrect planning date that had been previously used. These fuel assembly configuration errors resulted in non-shutdown Technical Specification 3.7.17 Action Statement A being entered on August 17, 2022, at 10:53. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by technical specifications. Human Performance The Reactor Engineer did not use the guidance contained within the work instructions for the SFP fuel assembly verification when entering the planning date in the software configuration tool. CAUSE OF THE EVENT The cause of this condition was a procedural step that was not followed resulting in an incorrect planning date being allowed to remain in the software configuration tool. Contributing to this was the lack of adequate guidance for verification of critical parameters within the associated surveillance procedure that would ensure SFP configuration would conform to Technical Specification Design Feature 4.3.1.1. | ML22290A172 | 1 | ok
Fermi 2 05000 341 1 OF 4 | Unknown Unit | Containment Isolation Valve Actuator Found Disconnected from its Bonnet Resulting in Condition Prohibited by Technical ~n..c.r-ifir-~+innc | 10-31-2022 | On 06/27/2022 during start up walkdowns for Forced Outage 22-01, engineering personnel discovered the B2103F019 (Main Steam Outboard Drain Isolation valve) motor operator separated from the valve bonnet yoke arm flange. The motor operator was energized (motor and gear train freely running) and agitating on the end of the vertically oriented valve stem. The inboard isolation valve (B2103F016) was capable to isolate during the entire time the B2103F019 was inoperable. Upon identification, the Containment Isolation Valve was declared inoperable per Technical Specification 3.6.1.3. The cause was determined to be improper thread engagement, due to personnel error of installing the incorrect bolts following testing using an installed testing device. B2103F019 was secured and is planned to be reworked during the next availability (refueling outage). The cycle schedule was reviewed for the impact of B2103F016 and 82103F019 isolated with no issues identified. An extent of condition was performed on the other motor operated valves tested during the previous refueling outage. This event is being reported under 10 CFR 50.73(a)(2)(i)(B) for operation or condition prohibited by TS. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to co~ly with this mandatory collection request 80 hows. Reported lessons learned are incorporated ilto the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A1 0M), U. S. Nuclear Regulatory Comnission, Washington, DC 20555--0001, or by e-mail to CONTINUATION SHEET lnfocolleds.Resource@nrc.gov, and the 0MB reviewer at 0MB Office of Information and Regulatory Affairs, (3150--0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, {See NUREG-1022, R3 for instruction and guidance for completing this form Washington, DC 20503; e-mai: oira submission@omb.eop.gov. The NRG may not conduct or http://www.nrc.gov/readinq-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a petson is not required to respond to, a oolleclion of ilformation unless the document requesting or requiring the colection displays a currentiy valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV I 05000- 1 341 a□ -I NUMBER 1-0 N O. 004 | INITIAL PLANT CONDITIONS Mode-1 Reactor Power - 9 Percent There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to his event. DESCRIPTION OF THE EVENT On 06/27/2022 during start up walkdowns for Forced Outage 22-01, engineering personnel discovered the B2103F019 (Main Steam Outboard Drain Isolation valve) [SBJ[ISV] motor operator [84] separated from the valve bonnet yoke arm flange [V]. The motor operator was energized (motor and gear train freely running) and agitating on the end of the vertically oriented valve stem. Having run out of stem threads, the actuator was being restrained on the end of the valve stem by the unthreaded portion of the stem nut counterbore and by the electrical conduit that serves the motor operated valve (MOV). The MOV was de-energized by shutting off the actuator power supply at the Motor Control Center. During the initial investigation, the (4) actuator mounting bolts had pulled out of the actuator housing, with visible damage to he threaded actuator mounting holes. After inspection it was identified that the removed bolts were 1 in long 5/16 inch cap bolts that, when fully tightened, only had 2 or 3 threads of engagement into the actuator. Based on the sequence of events, as noted per plant computer data, during the 06/27/2022 closing stroke the actuator-to-bonnet yoke flange-threaded connections failed. This allowed the unrestrained actuator to traverse up the valve stem as the stem nut rotated about the valve-stem threads. SIGNIFICANT SAFETY CONSEQUENCES AND IMPLICATIONS There were no safety consequences or radiological releases associated with this event. At no time during this event was here a potential for endangering the public health and safety. B2103F019 is a normally closed Primary Containment Isolation Valve (PCIV) [JM] and has a safety function to automatically close on a Reactor Vessel Low Level 1, and on Accident Isolation Signals E-Main Steam Line High Flow, F-Main Steam Line Tunnel High Temperature, G- Main Steam Line Low Pressure, J- Low Condenser Vacuum, P-Turbine Building High Temperatures to provide primary containment isolation of penetration, X-8. B2103F019 does not have a safety function in he open position. It is opened to provide a drain path for Main Steam line moisture to the turbine drain system during plant start-up or similar conditions. It is an 1ST Appendix Ill (formerly NRC GL 96-05) MOV with an active safety function to close within a design basis stroke time of 23 seconds per TRM 3.6.3 Table TR3.6.3-1 Group 1 Main Steam Automatic Isolation Valves. It is Type C Leak Tested and Bypass Leakage Tested under the Appendix J program. It is classified as Seismic Class I. NRG FORM 366A (08-2020) Page 2 of 4 | ML22304A009 | 0 | good
Dresden Nuclear Power Station | Unit 2 | Ultimate Heat Sink Declared Inoperable due to River Grass Accumulation | 10-28-2022 | On July 29, 2022, at 2217 CDT, Technical Specification (TS} 3.7.3, "Ultimate Heat Sink (UHS}" Limiting Conditions for Operation (LCO} was not met, and Condition A, UHS inoperable, was entered since UHS water level was determined to be below 501.5 feet. On July 30, 2022, at 0135 CDT, UHS water level was restored to be>/= 501.5 feet. On July 30, 2022, at 1116 CDT, TS 3.7.3 LCO was not met, and Condition A was entered for water level identified to be less than 501.5 feet. At 1800 CDT, UHS water level was restored to be>/= 501.5 feet. The cause of low water level was due to accumulation of river vegetation and grass on the Unit 2/3 Intake Bay 13 bar racks. The root cause was procedures and processes were not aligned with industry excellence standards to prevent intake blockage events. Corrective actions included clearing river vegetation from the Unit 2/3 Intake Bay 13 bar racks, securing one Circulating Water pump, and transitioning to closed cycle to restore UHS water level. Additional corrective actions included implementing tools and management model process changes to monitor and prevent future fouling of the intake. This event is being reported in accordance with 10 CFR 50. 73(a}(2}(v}(B}, "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat." NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response lo comply with this mandatory collection request 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A1 0M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollecls.Resource@nrc.gov. and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 72517th Street NW, Washington, DC 20503; e-mail: oira subm1ss1on@omb eop gov. The NRC may not conduct or (See NUREG-1022, R3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Dresden Nuclear Power Station, Unit 2 05000237 YEAR NUMBER NO. 2022 - 002 01 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 megawatts thermal rated core power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. A. CONDITIONS PRIOR TO EVENT Unit: 2 Event Date: July 29, 2022 Event Time: 2217 CDT Reactor Mode: 1 Mode Name: Power Operation Power Level: 100% B. DESCRIPTION OF EVENT The Ultimate Heat Sink (UHS) [BS] provides a suction pathway for the cooling water associated with Containment Cooling Service Water (CCSW) [Bl) and Diesel Generator Cooling Water (DGCW) [LBJ systems. The Technical Specification (TS) Surveillance Requirement (SR) verifies water level in the suction bays is sufficient for proper operation of the CCSW and DGCW pumps [P]. The CCSW pumps take suction from intake Bay 13. On July 29, 2022, at approx. 1000 CDT, station Operators performed routine rounds in the Unit 2/3 Cribhouse [NN], which included review of traveling screen [SCN] differential pressure recorders [PDR], observing intake suction Bay 13 water level, and general condition of the Unit 2/3 Cribhouse. Station Operations recorded the intake bar racks were free of debris, the traveling screen differential pressure recorders were satisfactory, and the Cribhouse intake suction Bay water levels were satisfactory. On July 29, 2022, at 2217 CDT, an equipment operator identified the Unit 2/3 intake suction Bay 13 water level was less than the TS SR value of>/= 501.5 feet. This condition did not meet TS 3.7.3, "Ultimate Heat Sink (UHS)," and required entering Condition A, UHS inoperable. The associated Required Actions and Completion Times were A.1, be in Mode 3 in 12 hours, and A.2, be in Mode 4 in 36 hours. Actions were taken to clear river vegetation and grass from the intake bar racks, troughs and traveling screens. On July 30, 2022, at 0135 CDT, Bay 13 water level was restored to>/= 501.5 feet and TS 3.7.3 Condition A was exited. On July 30, 2022, at 1116 CDT, accumulation of river vegetation and grass occurred and the TS 3. 7 .3 Condition A, UHS inoperable, was entered due to UHS water level in Bay 13 being less than 501.5 feet. The station continued clearing debris, secured a Circulating Water [KE] pump, and transitioned the plant to closed cycle (see Safety Analysis section below for further explanation) to restore intake suction Bay 13 water level. At 1800 CDT, intake suction Bay 13 water level was restored to>/= 501.5 feet and TS 3.7.3 Condition A was exited. | ML22304A225 | 0 | good
Dresden Nuclear Power Station | Unit 2 | Unit 2 Reactor Scram due to Turbine Trip on High Reactor Water Level caused by Feedwater Regulating Valve Failure | 10-28-2022 | On July 12, 2022, at 0803 CDT, an automatic reactor protection system actuation occurred following a main turbine trip due to high reactor water level. The safety significance of this event was minimal. All control rods inserted to their full- in position. Following the reactor scram, all systems operated as expected. The cause of high reactor water level is due to a feedwater regulating valve unexpectedly failing full-open. The root cause of the feedwater regulating valve failing full-open was due to the feedwater regulating valve pilot valve assembly not operating due to a manufacturing byproduct inside the pilot valve introduced during the manufacturing process. Corrective actions included replacement of the respective air solenoid valve. Additional corrective actions include inspecting and certifying these incoming valves are free of foreign material. Also, the solenoid valves for the feedwater regulating valves were reclassified as single point vulnerabilities. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), an event that resulted in automatic actuation of a system listed in paragraph 10 CFR 50. 73(a)(2)(iv)(B}, specifically the reactor protection system including reactor scram. NRC FORM 366A (08-2020) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 c.,.t.~1111111rou,1> +" o,. f r,~-.. B ~ LICENSEE EVENT REPORT (LER) \~''i!!!';t:/ CONTINUATION SHEET ., ...... (See NUREG-1022, R.3 for instruction and guidance for completing this form http·/twww.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collecbons Branch (T-6 A 10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Oesk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira subm,ss,on@omb eoo gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR Dresden Nuclear Power Station, Unit 2 05000- 237 2022 - | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 megawatts thermal rated core power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. A. CONDITIONS PRIOR TO EVENT Unit: 2 Reactor Mode: 1 Event Date: July 12, 2022 Mode Name: Power Operation 8. DESCRIPTION OF EVENT Event Time: 0803 CDT Power Level: 100% SEQUENTIAL NUMBER 001 REV NO. 01 On July 12, 2022, at 0759 CDT, one of two Feedwater [JB] regulating valves (FWRV) [FCV]. which are used to control feedwater flow to the reactor vessel, unexpectedly failed to the full-open position from its initial position of 42% open, resulting in a Reactor Feedwater [SK] Pump [P] trip on low suction pressure and an automatic Reactor Recirculation [AD] runback. This condition resulted in reactor water level rising due to the inability of the Feedwater system to regulate flow. At 0803 CDT, an automatic reactor protection system [JC] actuation occurred following a main turbine [TA] trip due to high reactor water level. Plant systems operated as expected in response to the automatic scram. All control rods [AA] inserted to their full-in position and the scram was not complicated. Reactor pressure was maintained in the normal control band. Reactor water level was restored and maintained in the normal control band. The NRC was notified via ENS Report 55988 at 1147 EDT. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), an event that resulted in automatic actuation of a system listed in paragraph 10 CFR 50.73(a)(2)(iv)(B), specifically the reactor protection system including reactor scram. C. CAUSE OF EVENT The cause of the FWRV failure was due to failure of the respective air solenoid valve [SOL], which is used to control FWRV position. The solenoid valve failure prevented the FWRV from repositioning. Failure analysis and root cause of the air solenoid valve failure was due to a manufacturing byproduct on the pilot valve plunger, which prevented the pilot valve from seating. A small piece of plastic was found on the internal seat surface. The plastic is the same material as the valve body construction. This material is not consistent with any other component in the instrument air system. Evidence supports the conclusion that the material was present when the valve was assembled at the factory. | ML22304A228 | 0 | good
Susquehanna Steam Electric Station | Unit 2 | Unit 2 Main Turbine Pressure Regulator Inoperable for Longer Than Allowed by Technical Specifications due to Inadequate Valve Modification | 11-03-2022 | At approximately 13:21 on October 11, 2021, the Susquehanna Steam Electric Station, Unit 2, experienced an automatic reactor scram due to a main turbine trip. All turbine bypass valves (TBVs) opened, as expected, to control reactor pressure but did not subsequently re-close. Troubleshooting identified Pressure Transmitter PT-20101B as the cause of the TBVs failure to re-close. To control reactor pressure, operators manually closed the four main steam isolation valves and utilized the main steam line drains and the High Pressure Coolant Injection System. Further analyses showed the Pressure Transmitter PT-20101B failure was caused by failure of the pressure transmitter root valve resulting from main steam line vibrations created by the scram. The root valve was previously modified; however, station personnel did not validate that the modification would perform properly in all plant operating conditions. To correct the condition, the failed valve was replaced and applicable procedures were updated. Based on failure information, it is likely that Pressure Transmitter PT-20101B was inoperable for longer than allowed by Technical Specification (TS) 3.7.8. Therefore, this event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. There were no actual safety consequences associated with the described condition. NRC FORM 366A U. S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, a collection of information unles s the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station, 05000-388 NUMBER NO. Unit 2 2021 - 004 - 01 | CONDITIONS PRIOR TO EVENT Unit 1 – Mode 1, approximately 100 percent Rated Thermal Power (RTP) Unit 2 – Mode 1, approximately 95 percent RTP At approximately 13:21 on October 11, 2021, the Susquehanna Steam Electric Station (SSES), Unit 2, experienced an automatic reactor scram due to a main turbine trip. Subsequently, all turbine bypass valves (TBVs) [EIIS System/Component Codes: JI/PCV] immediately opened as expected. EVENT DESCRIPTION On October 11, 2021, at approximately 13:21, the Susquehanna Steam Electric Station Unit 2 reactor automatically scrammed due to a main turbine [TA/TRB] trip. The scram event is reported under LER-2021- 003. The Unit 2 Control Room received indication of a main turbine trip with both divisions of the Reactor Protection System (RPS) [EIIS System Code: JC] actuated and all control rods inserted. The TBVs opened automatically, as expected, to control reactor pressure but subsequently remained open. Reactor pressure was initially stabilized through manual closure of the Main Steam Isolation Valves (MSIVs) [SB/ISV] and maintained using the main steam line drains [SB/DRN] and the High Pressure Coolant Injection (HPCI) [BJ] System. Based on failure information, it is likely that Pressure Transmitter PT-20101B was inoperable for longer than allowed by Technical Specification (TS) 3.7.8, “Main Turbine Pressure Regulation System.” Therefore, this event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. CAUSE OF EVENT Previous to the scram, the root valve (2RV-PT20101B) [RTV] for the ‘B’ Mains Steam Pressure Secondary Transmitter, PT-20101B, experienced a steam leak on the valve packing. A temporary repair was installed to seal the leak using 2X sealant. During the Unit 2 scram vibrations from the main steam lines caused the 2X sealant to crack and separate from the valve stem. The valve subsequently closed resulting in sustained pressure indication to the TBVs, which remained open longer than required. In preparation of the temporary repair, the station did not validate that 2X sealant would perform properly under all plant operating conditions. ANALYSIS/SAFETY SIGNIFICANCE While failure of the pressure transmitter is a potential transient initiator when operating at full power, it is not credited in the mitigation of any accident. The TBVs are credited in multiple Updated Final Safety Analysis Report Chapter 15 analyses, all of which assume the bypass valves will open to mitigate the pressure transient from the event. As noted in the event summary, the failure of the pressure transmitter did not prevent the bypass valves from opening nor was there any other impact to components credited with mitigation. The condition described herein did not result in a safety system functional failure. Accordingly, this event will not be counted as a safety system functional failure under the Reactor Oversight Process Performance Indicators. There were no actual consequences to the health and safety of the public as a result of this event. Page 2 of 3 | ML22307A260 | 0 | good
Susquehanna Steam Electric Station | Unit 2 | Inadequate Performance of Loss of Safety Determination Resulting in Both Divisions of Core Spray Being Inoperable | 11-23-2022 | On September 26, 2022, operators at the Susquehanna Steam Electric Station performed quarterly stroke time testing of Unit 2 Emergency Service Water (ESW) to Turbine Building Closed Cooling Water and ESW to Reactor Building Closed Cooling Water isolation valves. Performance of this surveillance results in the inoperability of Unit 2, Division 2 of the Core Spray system. This surveillance was performed while Unit 2, Division 1 of the Core Spray system was out of service for planned maintenance, resulting in both divisions of the Core Spray system being inoperable and a loss of safety function. The condition was identified during the subsequent shift while performing routine review of operator logs. The condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented fulfillment of a safety function. The cause of the event was determined to be inadequate performance of a loss of safety function determination, which failed to identify a loss of safety function resulting from concurrent inoperability of both divisions of Core Spray. This cause was attributed to human performance. There were no actual consequences to the health and safety of the public as a result of this event. <)P~ REc11~ /~ {Ko~ :; _2l_ i ~~~-Ir', ; ~,.,-:;-•'71 +01 •it-•~· I I I I I I I I I I I I I I I I I I I I I I I I I I I NRC FORM 366A (08-2020) Page 2 of 3 . NRC FORM 366A (08-2020) U. S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 LICENSEE EVENT REPORT (LER) CONTINUATION SHEET Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. (See NUREG-1022, R.3 for instruction and guidance for completing this form https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Susquehanna Steam Electric Station, Unit 2 05000-388 YEAR SEQUENTIAL NUMBER REV NO. 2022 - 001 - 00 | CONDITIONS PRIOR TO EVENT Unit 1 – Mode 1, approximately 100 percent Rated Thermal Power (RTP) Unit 2 – Mode 1, approximately 100 percent RTP EVENT DESCRIPTION On September 26, 2022, operators at the Susquehanna Steam Electric Station performed quarterly stroke time testing of the Unit 2 Emergency Service Water (ESW) [EIIS System Code: BI] to Turbine Building Closed Cooling Water (TBCCW) [EIIS System Code: CC] and ESW to Reactor Building Closed Cooling Water (RBCCW) [EIIS System Code: CC] isolation valves [EIIS Component Code: ISV]. Performance of this surveillance results in the inoperability of Unit 2, Division 2 of the Core Spray system [EIIS System Code: BG]. This surveillance was performed while Unit 2, Division 1 of the Core Spray system was out of service for planned maintenance, resulting in both divisions of the Core Spray system being inoperable and a loss of safety function. The condition was identified during the subsequent shift while performing routine review of operator logs. The following timeline demonstrates the sequence of events: 09/25/2022 ~ 09:00: The quarterly surveillance original start time is postponed due to conflicting work on the Unit 2 RBCCW heat exchangers [EIIS Component Code: HX]. A condition report is generated for the surveillance to be rescheduled after the completion of the Unit 2, Division 1 Core Spray planned maintenance. 09/25/2022 ~ 19:45: Unit 2, Division 1 Core Spray planned maintenance begins. Limited Condition of Operation (LCO) 3.5.1, “Emergency Core Cooling Systems (ECCS), Reactor Pressure Vessel (RPV) Water Inventory Control, and Reactor Core Isolation Cooling (RCIC) System,” Condition A is entered to support this work. 09/26/2022 ~ 05:00: During operations shift turnover, the need to track the postponed surveillance was discussed. However, the oncoming Unit Supervisor completed turnover with the misunderstanding that the surveillance needed to be completed during the Unit 2 RBCCW heat exchanger restoration. 09/26/2022 ~ 09:00: The surveillance is rescheduled for 09/27/2022, after the Unit 2, Division 1 Core Spray planned maintenance was scheduled to be complete. 09/26/2022 ~ 14:00: Unit 2 RBCCW heat exchanger work is reported completed. Operations begins preparation for performance of the quarterly surveillance. During this process, operations inadequately performed a loss of safety function determination using a previously completed copy of the station procedure, which did not identify the Unit 2, Division 1 Core Spray ongoing planned maintenance. 09/26/2022 ~ 14:08: Operations entered Condition C of LCO 3.7.2, “Emergency Service Water (ESW) System,” due to Division 2 ESW being inoperable for performance of the surveillance. A peer check for entry into the LCO condition was not received as required by station procedures. Investigation identified this as the time the loss of safety function occurred. 09/26/2022 ~ 14:17: The surveillance on Division 2 ESW is completed. Operations exited Condition C of LCO 3.7.2. | ML22327A176 | 0 | good
Grand Gulf Nuclear Station | Unit 1 | Primarv Containment Outer Airlock Door lnooerable Due To Unaccer table Leak Rate | 11-30-2022 | On February 22, 2021, Grand Gulf Nuclear Station's Primary Containment Outer Airlock located on 208' elevation exceeded the Technical Specification (TS) Surveillance Requirements 3.6.1.2.1 leakage rate during the pre- maintenance barrel test due to gross leakage of the equalizing valve associated with the outer airlock door. Analysis determined that the inner and outer airlock equalizing valves were leaking - caused by lack of lubrication during valve installation. This event is reportable under 10 CFR 50.73(a)(2)(i)(B), as an operation or condition which was prohibited by the plant's Technical Specifications. The event is also being reported under 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented the fulfillment of a safety function. This supplement expands the original Licensee Event Report to include applicability of 1O CFR 21.2(c). Actions taken were the lubrication and replacement of the equalizing valve on the outer door. The equalizing valve on the inner door was rebuilt with new O-rings and lubricated prior to reinstallation. Following replacement of the outer door and rebuild of the inner door, the local leak rate test (LLRT) was tested satisfactorily. There were no consequences to the general safety of the public, nuclear safety, industrial safety or radiological safety. No radiological releases occurred due to this event. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 ,,,. (O!l-2020) Estimated burden per response to comply with this mandatory collection request: 80 ....... hours. Reported lessons learned are incorporated into the licensing process and led "¥,' LICENSEE EVENT REPORT (LER) back to industry. Send comments regarding burden estimate to the FOIA, Library, !\ 11 and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory ...... CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects . Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and (See NUREG-1022, R.3 for instruction and guidance for completing this form Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1 o 221r3D Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira subm1ssion@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document reauesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 05000-416 NUMBER NO. 2021 -001 -01 | Plant Conditions: Grand Gulf Nuclear Station (GGNS) Unit 1 was operating at 100 percent power in MODE 1. There were no Structures, Systems, or Components that were inoperable that contributed to this event. Event Description: On February 22, 2021, GGNS's Primary Containment [NH] Airlock [AL] outer door located on 208' elevation exceeded the Technical Specification (TS) Surveillance Requirements (SR) 3.6.1.2.1 leakage rate during the pre-maintenance barrel test due to gross leakage of the 1 M23F018D equalizing valve [V] associated with the outer airlock door, resulting in a condition that could have prevented the fulfillment of a safety function during times when the inner airlock door was open. A maintenance work window for the 208' Containment Personnel Airlock outer door was scheduled for February 22, 2021. As part of the maintenance evolution, the airlock barrel local leak rate test (LLRT) was performed to identify any leaking components needing to be repaired during the maintenance window. Technical Specification 3.6.1.2, Primary Containment Airlocks, was entered on February 22, 2021, at 0530 hrs. for the maintenance window. Per calculation MC-O1 M23-16001, the maximum allowable primary containment leakage rate (La) for the calculated maximum peak containment pressure (Pa) 12.1 psig is 337,617 SCCM. Per SR 3.6.1.2.1 overall airlock leakage rate is less than or equal to 0.05 times La which is 16,880 SCCM. Analysis determined that the equalizing valves had failed prior to February 22 due to lack of lubrication during installation. The Containment Airlock outer door was declared inoperable due to excessive leakage. In accordance with TS 3.6.1.2 Condition (One or more primary containment airlocks with one primary containment airlock door inoperable), the OPERABLE door should be closed and locked in the affected airlock. The required actions were not met in the required completion time. This event is reportable under 10 CFR 50.73(a)(2)(i)(B), any operation or condition which was prohibited by the plant's Technical Specifications. This also resulted in a condition that could have prevented the fulfillment of a safety function to mitigate the consequences of an accident, during times when the inner airlock door was open, and is reportable under 10 CFR 50.73(a)(2)(v)(D). Subsequent investigation led to the determination that the equalizing valves had been dedicated by a vendor and that lubrication was to have been performed during the dedication process. Lubrication was not performed, leading to the failure of the leakage test. As a result, this event is reportable under 10 CFR 21.2(c). The site formally completed its 10 CFR 21 Evaluation on October 17, 2022. During the periods when the outer airlock door was inoperable, the inner airlock door either remained closed (Operable) or was opened for passage and under the control of site personnel. As a result, Entergy has determined that it did not result in a safety system functional failure. Therefore, in accordance with the guidance provided in NEI 99-02, Revision 7, Regulatory Assessment Performance Indicator Guideline, Section 2.2, Mitigating Systems Cornerstone, Sub-Section, Safety System Functional Failures, Page 30, Lines 27 through 30; this condition will not be counted as a safety system functional failure against Performance Indicator MS05, Safety System Functional Failures. | ML22334A222 | 0 | good
i | Unknown Unit | Steam Bypass Valve Demand Limited on the 'B' Train due to a Degraded Signal in the Max Combined Flow Limit Circuit | 12-05-2022 | On October 7, 2022 at 174 0, it was identified that the Maximum Combined Flow Limiter In Control light was lit with the Steam Bypass and Pressure Regulating system on the "B" channel. This light being lit indicates that the max combined flow limiter is in control, which limits steam flow to the main turbine and condenser hrough the control valves and bypass valves. This indication appeared to be an erroneous indication as reactor power and pressure remained stable. The system contains two channels of pressure regulation, an "A" and "B" channel. A failure in either channel could cause the light to illuminate. A troubleshooting earn was developed to determine the potential failure modes. On October 13, 2022 during problem solving for the Maximum Combined Flow Limiter In Control light, the problem solving team detennined the "A" channel was operating normally and that the "B" channel would prevent the bypass valves from responding to a pressure perturbation with the steam bypass and regulating system operating on the "B" channel. The control room shifted off the "B" channel to the "A" channel and declared the "B" channel inoperable. The direct cause of the Maximum Combined Flow Limiter Light was the failure of "B" Flow Demand circuit card based on the indications obtained and observable damage found on the card during replacement. Corrective action was taken to replace the failed card. The safety significance of this event is considered to be very low. This condition is reportable under 50. 73(a)(2)(i)(B) as an operation or condition prohibited by the plant's technical specifications. Technical Specification (TS) 3.7.6 requires the main turbine bypass system to be operable with rated power greater than 23.8 percent, when the "B" channel was in control it was determined that the system was not operable. TS 3.7.6 requires that bypass valve operability be restored within 2 hours, otherwise be less than 23.8 percent power within 4 hours. Vllith firm evidence that the issue had existed on October 7 and with the inoperable "B" channel in control until October 13 the required actions of TS 3.7.6 were not taken, and a condition prohibited by TS resulted. NRC FORM 366A U.S. NUCLEAR REGULA TORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this miw,datory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A1 0M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at 0MB Office of Information and Regulatory Affairs, (3150.0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting http:/lwww.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3Q or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER ;J. Lt:K numos;" YEAR SEQUENTIAL REV Perry Nuclear Power Plant 05000-1 00440 -I NUMBER 1-G NO. 20221 002 I | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. EVENT DESCRIPTION On October 7, 2022 at 1740 and with the reactor at mode 1 and 100% rated thermal power, it was identified that the Maximum Combined Flow Limiter In Control (MCFLC) light was lit with the Steam Bypass and Pressure Regulating system [JI] on the "B" channel, this light being lit indicates that the maximum combined flow limiter is in control, which results in a limitation of steam flow to the main turbine [TG] and condenser through the control valves and bypass valves. While observing plant parameters this appeared to be an erroneous indication as reactor power and pressure remained stable. The system contains two channels of pressure regulation, an "A" and "B" channel. A failure in either channel could cause the light to illuminate. A troubleshooting team was developed to determine the potential failure modes. On October 13, 2022 during problem solving on the MCFLC light, the problem solving team determined the "A" channel was operating normally while the "B" channel contained a degradation in the circuitry resulting in the illumination of the MCFLC light. The data also indicated the MCFLC signal could be limiting the "B" channel, which would prevent the bypass valves from responding to a pressure perturbation while operating on the "B" channel. At that time operations placed the "A" channel in operation and declared the "B" channel inoperable. During a maintenance outage on October 30, 2022, the "B" flow demand circuit card [CBD] was replaced. Following the card replacement, testing on the "B" channel determined the channel to bein proper working condition. CAUSE OF EVENT The direct cause of the failure of the MCFLC Light was the "B" flow demand circuit card based on the voltage readings and observable damage found on the card during replacement. The likely cause of failure of the circuit card is age-related failure of the components as they are plant original parts. The removed flow demand card had observable charring at several resistors on the circuit card, and it had degraded output voltage. Based on the voltage reading and the observed charred components on the card, the "B" flow demand circuit card is the direct cause of the MCFLC light illuminating. EVENT ANALYSIS A Probabilistic Risk Assessment (PRA) bounding evaluation was performed for this event. Fire and other external hazards were qualitatively addressed to be of low risk. The analysis of this event results in delta CDF and delta LERF values that are below the acceptable thresholds of 1.0E-06/yr an d 1.0E-07/yr, as discussed in Regulatory Guide 1.174 . Sensitivities performed that increased the frequency of a general transient initiating event did not change these conclusions. The risk of this event is therefore considered to be of very low safety significance in accordance with the Regulatory Guidance. | ML22339A029 | 0 | good
Susquehanna Steam Electric Station | Unit 1 | Automatic Reactor Scram Due to Reactor Protection System Actuation on High Reactor Vessel Pressure Signal Following Inadvertent Closure of Inboard Main Steam Isolation Valve | 12-05-2022 | At approximately 17:16 on May 23, 2022, Susquehanna Steam Electric Station, Unit 1, experienced an automatic reactor scram. Reactor Protection System (RPS) was actuated on a high reactor vessel pressure signal due to inadvertent closure of an inboard Main Steam Isolation Valve (MSIV) (HV141F022D). All control rods inserted, and operators placed the mode switch to shut down. All safety systems responded as designed during this event. Event Notification 55909 reported this event in accordance with 10 CFR 50.72(b)(2)(iv)(A), 10 CFR 50.72(b)(2)(iv)(B), and 10 CFR 50.72(b)(3)(iv)(A). This event is also reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of a system listed in 10 CFR 50.73(a)(2)(iv)(B). The cause of the scram was due to a loss of pneumatic pressure resulting in closure of an inboard MSIV (HV141F022D) which resulted in a high reactor vessel pressure signal and valid RPS actuation. The loss of pneumatic pressure occurred due to high cycle fatigue induced failure, most likely from vibration, of the 3/8” Containment Instrument Gas tubing. Affected tubing was replaced and the weld on 3/8” tubing to HV141F022D was repaired. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366A U. S. NUCLEAR REGULATORY COMMISSIONAPPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station, 05000-387 NUMBER NO. Unit 1 2022 - 002 - 01 | CONDITIONS PRIOR TO EVENT Unit 1 – Mode 1, approximately 100 percent Rated Thermal Power (RTP) Unit 2 – Mode 1, approximately 100 percent RTP EVENT DESCRIPTION At approximately 17:16 on May 23, 2022, Susquehanna Steam Electric Station, Unit 1, experienced an automatic reactor scram. Reactor Protection System (RPS) [EIIS System Code: JC] was actuated on a high reactor vessel pressure signal due to inadvertent closure of an inboard Main Steam Isolation Valve (MSIV) (HV141F022D) [EIIS System/Component Codes: SB/ISV] following loss of pneumatic pressure. All control rods inserted, and operators placed the mode switch to shut down. Containment isolations [JM] and both Reactor Recirculation Pump [AD/P] trips occurred as reactor water level dropped below the Anticipated Transient Without Scram – Reactor Pump Trip logic setpoint. High Pressure Coolant Injection [BJ] and Reactor Core Isolation Cooling [BN] initiated as designed when the reactor water level lowered. Subsequently, operators maintained reactor water level within normal band using Reactor Feedwater [SJ]. All other safety systems responded as designed. Event Notification 55909 reported this event in accordance with 10 CFR 50.72(b)(2)(iv)(A), 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). This event is also reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of a system listed in 10 CFR 50.73(a)(2)(iv)(B). CAUSE OF EVENT The cause of the scram was due to a loss of pneumatic pressure resulting in inadvertent closure of an inboard MSIV (HV141F022D) which resulted in a high reactor vessel pressure signal and valid RPS actuation. The loss of pneumatic pressure occurred due to high cycle fatigue induced failure, most likely from vibration, of the 3/8” Containment Instrument Gas [LK] tubing [TBG]. ANALYSIS/SAFETY SIGNIFICANCE The actual consequence of this event was an automatic reactor scram. All safety systems responded as designed during this event. Residual Heat Removal [BO] and Residual Heat Removal Service Water [BI] remained available to remove residual heat. No fuel or clad damage occurred during the scram, as evidenced by Main Steam Line and Off-Gas radiation levels decreasing post-scram. All applicable systems were available to control the release of any radioactive material. All safety systems were available to mitigate the consequences of an accident. The condition described herein did not result in a safety system functional failure. Accordingly, this event will not be counted as a safety system functional failure in the Reactor Oversight Process Performance Indicator. There were no actual consequences to the health and safety of the public as a result of this event. Page 2 of 3 | ML22339A095 | 0 | good
Limerick Generating Station | Unit 1 | Unit 1 HPCI Inoperable Due to Inadvertent Isolation Signal | 12-13-2022 | On October 14, 2022, during planned testing of the High Pressure Coolant Injection (HPCI) System, a spurious HPCI Division 2 isolation occurred due to a fault in an electrical connector associated with the HPCI Division 2 isolation reset circuit. The affected electrical connector carries signals for the control circuits of the outboard HPCI Turbine Exhaust Line Vacuum Breaker isolation valve and HPCI Test Line Flush isolation valve and the HPCI Division 2 isolation reset circuit. Closing the outboard HPCI Turbine Exhaust Line Vacuum Breaker isolation valve energized degraded pins within the electrical connector resulting in a fault that initiated the HPCI Division 2 isolation signal. The defective electrical connector was removed, and the affected cable spliced in accordance with an approved design change. This event is being reported as a condition that, at the time of discovery, could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident. An eight (8) hour ENS notification was completed on October 14, 2022, at 18:03 hours. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments ~¥' LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. ; i CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to ..... Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory <--+_, ~o' Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER •YEAR SEQUENTIAL REV 05000- NUMBER NO. Limerick Generating Station Unit 1 352 D 2022 - I 001 - 00 I I I I I | Unit Condition Prior to the Event Unit 1 was in Operational Condition (OPCON) 1 (Power Operation) at approximately 100% power. There were no structures, systems, or components out of service that contributed to this event. Description of the Event On October 14, 2022, a Unit 1 High Pressure Coolant Injection (HPCI) System [BJ] surveillance test was conducted on the HPCI Turbine Exhaust Vacuum Breakers. The purpose of this test is to ensure that the HPCI turbine exhaust line vacuum breakers function properly in both the forward and reverse flow directions. The HPCI turbine exhaust line vacuum breaker isolation valves, HV-055-1F093 and HV-055-1F095 must be closed to establish the required alignment to test the vacuum breaker check valves. The HPCI System is inoperable, but available in this test alignment. At 09:15 the HPCI turbine exhaust line vacuum breaker isolation valves were closed to establish the required alignment to perform the surveillance test. At 09:23, a Unit 1 Division 2 Safeguard Battery ground alarm was received, and all DC related testing was stopped to investigate the alarm. At 10:07, a HPCI Division 2 isolation signal was received accompanied by auto closure of the outboard HPCI Steam line isolation valve and the inboard HPCI Pump Suppression Pool suction valve. An eight (8) hour ENS notification (56163) was completed on October 14, 2022, at 18:03 hours. Troubleshooting and failure analysis of the removed electrical connector concluded that degradation of several of the pin connections within the affected electrical connector resulted in a fault that propagated to the HPCI Division 2 isolation reset circuit. The fault within the electrical connector was initiated when the degraded pin connections were energized by closure of the outboard HPCI turbine exhaust line vacuum breaker isolation valve, HV-055-1F093, for the planned surveillance test. The defective electrical connector was removed, and the affected cable spliced in accordance with an approved design change. The HPCI system was returned to service on October 17, 2022, at 21:15. (cid:3025) Analysis of the Event The inadvertent HPCI isolation that occurred during a planned surveillance test was attributed to a degraded electrical connector that was energized when closing one of the motor operated valves required to establish the alignment for the surveillance test. Failure analysis of the electrical connector identified that a fault propagated to the HPCI Division 2 isolation reset circuit when the outboard HPCI turbine exhaust vacuum breaker isolation valve, HV-055-1F093, was closed to establish the required alignment to perform the planned surveillance test. Additionally, due to the degradation on other pin connectors of the affected electrical connector, the failure analysis could not conclusively eliminate the possibility of a fault occurring through a different mechanism. With the unplanned loss of a single train system this condition is being reported per 10 CFR 50.73(a)(2)(v)(D), any condition that could have prevented the fulfillment of the safety function of structures or systems required to mitigate the consequences of an accident. | ML22347A286 | 0 | good
Peach Bottom Atomic Power Station | Unit 2 | Automatic Depressurization System Safety Relief Valve Actuator Diaphragm Degraded | 12-15-2022 | On October 17, 2022, with the unit in a refueling outage. Water was identified leaking from a fastener on the PB2 RV- 71B Main Steam Safety/Relief Valve (S/RV) body. The water leak was a small steady stream. The leakage was due to a degraded gasket and steam cut fastener threads. Subsequent laboratory analysis of the leaking valve identified the Automatic Depressurization System, (ADS) function performed by the pneumatic operator was non-functional. The pneumatic operator resilient components (diaphragm) were discovered to be embrittled and lost pressure retaining integrity. The timeframe for the degraded ADS capability cannot be reasonably determined at this time. The relief valve overpressure function was evaluated to be not impacted by the leak or the loss of ADS function. Therefore, Peach Bottom is submitting this report in accordance with 10 CFR 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant’s Technical Specifications, having exceeded the required 14 day action time or maximum Risk Informed Completion Time (RICT) to restore an ADS valve to OPERABLE status. There were no other systems which were inoperable during this identified condition that contributed to this event. There were no actual safety consequences as a result of this event. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Peach Bottom Atomic Power Station, Unit 2 05000- 277 NUMBER NO. 2022 - 002 - 00 | Plant Operating Conditions before the Event: Unit 2 was in Mode 4, Cold Shutdown, with the Main Steam Lines water solid, operating at 0% of rated thermal power on October 17, 2022. Unit 2 was shut down for its 24th Refueling Outage (P2R24) on October 16, 2022. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event: There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. The Energy Industry Identification System component function identifier and name of each component or system: EIIS: Safety Relief Valves [SB], RV-2-02-071B, B SAFETY RELIEF VALVE (RV-71B) Target Rock Model 67F pilot operated safety/relief valve Serial Number 024 Description of Event: On October 17, 2022, at 1337 hours, station personnel identified a small steady stream of water, approximately 0.2 gallons per minute leaking from the insulation around the ‘71B’ Main Steam/Relief Valve (S/RV). Subsequent investigation revealed that the leakage was from the relief valve pilot filter plug threaded connection. There was no through-wall leakage of any Reactor Coolant System (RCS) pressure boundary component. The RV-71B was emergently replaced in the scope of the planned outage, quarantined, and shipped to an off-site vendor for analysis and repair. As part of vendor testing the relief valve, the pneumatic operator is functionally tested with air. The pneumatic operator failed to actuate and air leakage was audible during testing, indicating potential resilient parts degradation. Disassembly and examination of the pneumatic operator revealed the actuator diaphragm elastomer had embrittled and delaminated, enabling gross leakage that inhibited the S/RV manual operation capability. This as-found condition represents a loss of the valve’s Automatic Depressurization System (ADS) function. Technical Specification (TS) 3.5.1 Limiting Condition of Operation (LCO) requires each Emergency Core Cooling System (ECCS) injection/spray subsystem and the Automatic Depressurization System (ADS) function of five (5) S/RVs to be OPERABLE in operating modes 1, 2 and 3. The remaining four (4) S/RVs that support ADS capability were verified to be operable for this function. Peach Bottom TS Limiting Condition for Operation 3.5.1, Condition E for one (1) ADS valve inoperable, has a Completion Time of 14 days or in accordance with the Risk Informed Completion Time Program. The event start time for the loss of ADS function of the RV-71B is indeterminate. The S/RV ADS function is considered inoperable for a period greater than permitted by TS since the start of the degradation cannot be reasonably determined. Therefore, the condition is reportable under criterion 10CFR 50.73(a)(2)(i)(B) as any operation or condition which was prohibited by the plant’s Technical Specifications. The RV-71B was installed as part of the planned preventive maintenance relief valve outage work scope in October of 2018 (P2R22). The valve was in-service approximately four (4) years at the time of discovery. The RV-71B ADS Safety Relief Valve was not actuated during Cycle 24 operations (October 2018 – October 2020). The RV-71B was used for manual pressure control during Cycle 25 (October 2020 – October 2022) as part of post U2 SCRAM actions on May 15, 2022 (ML22196A020). Control room operators manually operated the valve from the main control room and observed the expected response. | ML22349A084 | 0 | good
YEAR SEQUENTIAL REV | Unknown Unit | Inoperable 13.8kV Startup Transformer due to Misaligned Load Tap Charger Local/Remote Control Switch | 12-19-2022 | 12.Licensee Contact for this LER Licensee Contact Phone Number (Include Area Code) Derek R. Smith, Senior Engineer – Nuclear Regulatory Affairs I( 570)542-1377 13.Complete One Line for each Component Failure Described in this Report Cause I System Component I Manufacturer I Reportable to IRIS I Cause I System I Component I Manufacturer I Reportable to IRIS I I I I I I I I 14.Supplemental Report Expected I I Month I Day I Year 15.Expected Submission Date ☒ No I☐ Yes (If yes, complete 15. Expected Submission Date) I I I I 16.Abstract (Limit to 1560 spaces, i.e., approximately 15 single-spaced typewritten lines) On October 22, 2022, operators at the Susquehanna Steam Electric Station identified the load tap changer (LTC) local/remote control switch on one of the two 13.8 kV startup transformers was in the remote position, as opposed to the required local position. Upon identification of the condition, operators entered Technical Specification (TS) 3.8.1, “AC Sources-Operating,” Condition A for one offsite circuit inoperable. The switch was restored to the local position and the transformer was declared operable at 21:00 on October 22, 2022. Based on investigation and cause, the condition is likely to have existed since October 12, 2022, and is, therefore, being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. The cause of the event was determined to be inadvertent bumping of the LTC local/remote control switch during opening and closing of the transformer cabinet doors by maintenance personnel. This cause was attributed to a human performance error. Corrective actions include planned procedure revisions to verify the LTC control switches are properly positioned during transformer restoration. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366A U. S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station Unit 2 05000-388 NUMBER NO. 2022 - 003 - 00 | CONDITIONS PRIOR TO EVENT Unit 1 – Mode 1, approximately 85 percent Rated Thermal Power (RTP) Unit 2 – Mode 1, approximately 100 percent RTP There were no structures, systems, or components that were inoperable at the start of the event and contributed to the event. One of the two 13.8kV startup transformers was inoperable for planned maintenance. EVENT DESCRIPTION On October 22, 2022, operators at the Susquehanna Steam Electric Station identified the load tap changer (LTC) local/remote control switch [EIIS Component Code: 33] on one of the two 13.8kV startup transformers [EIIS System/Component Code: E/XFMR] was in the remote position, as opposed to the required local position. Upon identification of the condition, operators entered Technical Specification (TS) 3.8.1, “AC Sources-Operating,” Condition A for one offsite circuit inoperable. Investigation determined the control switch was most likely inadvertently manipulated while restoring the transformer to operable from planned maintenance on October 12, 2022. The switch was restored to the local position and the transformer was declared operable at 21:00 on October 22, 2022. The following timeline demonstrates the sequence of events: 10/10/2022 ~ 22:10: TS 3.8.1, Condition A is entered to support planned maintenance on one of the two 13.8 kV startup transformers. 10/11/2022 ~ 06:00: Routine preventative maintenance activities begin to inspect and change the oil in the transformer LTC. The LTC local/remote control switch is not manipulated per the work instructions. 10/11/2022 ~ 14:00: While removing the clearance order from the 480 V normal and alternate control cabinet [EIIS Component Code: CAB], the transformer cooling fans [EIIS Component Code: FAN] started unexpectedly, requiring troubleshooting to restore the transformer to operable. 10/11/2022 ~ 18:15: Maintenance of the LTC is completed and post maintenance testing (PMT) is completed successfully. 10/11/2022 through 10/12/2022 ~20:00: Troubleshooting on the unexpected fan start continued. Troubleshooting activities require access in the cabinet where the LTC local/remote control switch is located. Investigation determined this to be the most probable timeframe the switch was inadvertently bumped. 10/12/2022 ~ 20:00: The transformer is restored to service and declared Operable. TS 3.8.1, Condition A is exited. 10/22/2022 ~ 15:13: The control room received a report that the transformer LTC local/remote control switch was found in the remote position, as opposed to the expected local position. The transformer is declared inoperable and TS 3.8.1, Condition A is entered. 10/22/2022 ~ 21:00: The LTC local/remote control switch is placed in the correct position and the transformer is declared operable. TS 3.8.1, Condition A is exited. Based on the timeline above, the transformer was inoperable for longer than allowed by TS. Therefore, this condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. Page 2 of 3 | ML22353A082 | 0 | good
Grand Gulf Nuclear Station | Unit 1 | Loss of Secondary Containment during Standby Gas Treatment System Testing due to boundary leakage | 12-19-2022 | Between October 20 and October 27, 2022, Grand Gulf Nuclear Station, Unit 1 (GGNS) experienced two similar events. ODun rJinunge t h3e0, 2p0e2r2fo armt 1a1n4c5e h oouf rtsh,e w Sittha tnhdeb Gyr Ganads G Turlef aNtmucelenatr S Sytasttieomn iTn rMaiond Ae 1s uanrvde 1il0la0n pceer cteenstt pGowGeNr,S t hwea rse aucntoarb wlea st om manauianltlayi n tSriepcpoendd daurey tCo othnet aloinssm oefn bta plarnecses uofr ep,l aanst r(eBqOuPir)e tdra bnsyf oTremcehrn 2ic3a. l ASlpl ecocniftircoalt rioond sS fuulrlvye iinllsaenrcteed Rinetoq uthiree cmoeren ta n3d.6 a.l4l .s1y.s4t,e mgrse ater rthesapno nodr eedq aupaplr toop r0ia.2te6l6y. inches of water vacuum for 1 hour at a flow rate of less than or equal to 4000 cubic feet per minute (cfm). During both events the test was secured. Secondary Containment was declared inoperable and Technical Specification 3.6.4.1 A.1 was entered. Secondary Containment was restored to operable status by restoring Stathnedb cyo Snefirgvuicrea tWioant etor Aa apnrde vBio wuesrley mknaonwuanll yo pineirtaiabteled ctoo nsudpitpiolyn .c oTohlien gd itroe ctht ec Cauosnetr oolf R thoeomse A eivr ecnotnsd iwtiaosn itnhge, Ecnugminueleartiinvge Safety Feiantluerae k(aEgSeF )o sfw thitec hSgeeacro rnodoamry c oCoolenrtsa ainnmd epnlatn Bt aouuxnidliaarryy .l oads. Following corrective actions including repairing the source of inleakage the surveillance testing was successfully completed on December 9, 2022. There were no consequences to the safety of the public, nuclear safety, industrial safety, or radiological safety. No radiological releases occurred due to this event. This report is made in accordance with 10 CFR 50.73(a)(2)(v)(C) for an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the Release of Radioactive Material. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Grand Gulf Nuclear Station, Unit 1 50-416 2022 002 - 00 | PLANT CONDITIONS: Event # 1 - Mode 1, 100 percent power Event # 2 - Mode 1, 88 percent power DESCRIPTION OF EVENTS Event # 1: At 0427 on October 20, 2022, Grand Gulf Nuclear Station, Unit 1 (GGNS) was in Mode 1 at 100 percent power when a failure of the Standby Gas Treatment System Train [BH] A draw down surveillance resulted in the inoperability of Secondary Containment [NG]. During the performance of the surveillance GGNS was unable to maintain Secondary Containment pressure, as required by Technical Specification Surveillance Requirement 3.6.4.1.4, greater than or equal to 0.266 inches of water vacuum for 1 hour at a flow rate of less than or equal to 4000cfm. The test was secured. Secondary Containment was declared inoperable and Technical Specification 3.6.4.1 A.1 was entered at 0427. Secondary Containment was restored to operable status at 0520 by restoring the configuration to a previously known operable condition. Event # 2: At 1228 on October 27, 2022, GGNS was in Mode 1 at 88 percent power when a failure of the Standby Gas Treatment System Train A draw down surveillance resulted in the inoperability of Secondary Containment. During the performance of the surveillance GGNS was unable to maintain Secondary Containment pressure, as required by Technical Specification Surveillance Requirement 3.6.4.1.4, greater than or equal to 0.266 inches of water vacuum for 1 hour at a flow rate of less than or equal to 4000cfm. The test was secured. Secondary Containment was declared inoperable and Technical Specification 3.6.4.1 A.1 was entered at 1228. Secondary Containment was restored to operable status at 1240 by restoring the configuration to a previously known operable condition. REPORTABILITY This report is made in accordance with 10 CFR 50.73(a)(2)(v)(C) for an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the Release of Radioactive Material. CAUSE Direct Cause: The direct cause of these events was the cumulative inleakage of the Secondary Containment Boundary in the tested configuration. The two identified sources of inleakage to Secondary Containment are the Railroad Area Door and the Rail Bay Floor Plugs. CORRECTIVE ACTIONS 1. Replace door seals to improve the seal around the Secondary Containment doors to prevent inleakage to boundary. 2. Replace the Rail Bay Floor Plug gasket with a softer material approved by an Engineering Change. 3. Update the model work order for replacing the floor plug seals or reinstallation of floor plugs with a PMT. 4. Revise model work order to include steps to ensure the mating surface is cleaned and any sealant from past replacements. | ML22353A290 | 0 | good
Browns Ferry Nuclear Plant | Unit 3 | Both Standby Liquid Control Subsystems Inoperable Due to an Insufficient Boron Injection Rate | 12-19-2022 | On October 18, 2022 at 1440 Central Daylight Time (CDT), following a routine surveillance test, Browns Ferry Nuclear Plant, (BFN), Unit 3 declared both trains of the Standby Liquid Control (SLC) system inoperable for failing to meet boron injection rate acceptance criteria. This resulted in a single cause or condition that caused two independent trains or channels to become inoperable in a single system designed to shut down the reactor and maintain it in a safe shutdown condition. At the time, it was believed that this could have prevented the SLC system from fulfilling its safety function to shut down the reactor and maintain it in a safe shutdown condition. However, an engineering evaluation later determined that the SLC system remained capable of fulfilling its required safety function throughout this event. Upon investigation, it was discovered that this event resulted from an ineffective corrective action for the issue identified in Condition Report (CR) 1439832, where all of parameters used in the Anticipated Transient Without Scram (ATWS) equivalency equation could individually meet Technical Specifications (TS), yet still fail the acceptance criteria. SLC system operability was restored on October 18, 2022 at 2053 CDT, after an additional 80 kg of sodium pentaborate was added to the BFN, Unit 3 SLC tank. This increased the boron concentration of the SLC solution, which raised the boron injection rate to an acceptable level. As a corrective action to prevent or reduce the probability of recurrence, BFN will develop and implement an improved method for determining SLC pump flow rates. This will include benchmarking other plants to incorporate their best practices to improve the accuracy and repeatability of SLC pump flow rate measurements. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION (08-2020) LICENSEE EVENT REPORT (LER) CONTINUATION SHEET APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Browns Ferry Nuclear Plant, Unit 3 05000-296 YEAR SEQUENTIAL NUMBER REV NO. 2022 - 002 - 00 | Not Found | ML22353A631 | 1 | ok
i | Unknown Unit | Main Control Room and Auxiliary Electric Room HVAC Declared Inoperable Due to Multiple Component Failures. | 12-28-2022 | 12. Licensee Contact for this LER Licensee Contact 'Phone Number (Include area code) CJ Smith, Operations Director (815) 415-2200 13. Complete One Line for each Component Failure Described In this Report Cause System Component Manufacturer Reportable to IRIS . Cause System Component Manufacturer Reportable to IRIS D VI BKR E062 y 14. Supplemental Report Expected Month Day Year I I 15. Expected Submission Date 12:1 No D Yes (If yes, complete 15. Expected S4bmission Date) I 6. Abstract (Limit to 1560 spaces, i.e., approximately 15 single-spaced typewritten lines) On May 20, 2022, both Units 1 and 2 were in Mode 1 and at 100% power. The B train of the Main Control Room Ventilation (VC) and Auxiliary Electric Room Ventilation (VE) was inoperable due to a planned maintenance window. The Main Control Room ventilation envelope consists of both the Main Control Room and the Auxiliary Electric Equipment Room. Both trains of VC and VE were required to be operable at the time of these events. On 5/20/22 at 0905 and again on 5/23/22 at 1256, various equipment on the A VCNE train tripped following train swaps to support ongoing maintenance activities. This resulted in the A VCNE train being declared inoperable. With both the A and B trains being simultaneously inoperable, the VCNE system was in a condition that could have prevented fulfillment of a safety function. The cause of the event is an inadequate breaker setting resulting in the breaker tripping prematurely on fan start. NRC FORM 366A (08-2020) Page _2_ of _5_ NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply wilh lhis mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. LICENSEE EVENT REPORT (LER) Nudear Regulatory Commission, Wastington, DC 20555-0001, or by e-maU to CONTINUATION SHEET lnlocollects.Resource@nrc.gov, and lhe 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 171h Street NW, Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1O22, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of inlonnation unless lhe document http://www. n re.gov/reading-rm/ doc-col lections/nuregs/staff/sr1 022/r3/) requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR LaSalle County Station, Unit 1 05000- 373 NUMBER NO. 2022 • 003 02 | Plant and System Identification LaSalle County Station Unit 1 and 2 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the Main Control Room Area Ventilation system (VC) and the Auxiliary Equipment Room Ventilation System (VE). Condition Prior to Event Unit(s): 1/2 Date: May 20, 2022 Time: 0905 CDT Reactor Mode(s): 1/1 Mode(s) Name: Power Operation Power Level: 100%/100% Description On May 20, 2022 the station was executing a 8 VCNE work window and in the following TS actions: 3. 7.4 A.1, restore 8 train to operable status (expires 5/23/22 at 0500) and 3.7.5 A.1, restore B train to operable (expires 6/15/2022 at 0300). The station began procedures to swap to the A train to allow repairs identified during post maintenance testing on the 8 train. After swapping to A VCNE, the A VE return fan tripped and immediately tripped after a second attempt to start. At 0905, the A train was declared inoperable for both TS 3.7.4, (CRAF) and 3.7.5 (MCR ventilation). With both trains ofVCNE inoperable, the Station entered TS 3.7.4 RA E.1 be in mode 3 within 12 hours, TS 3.7.5 RA 8.1 to verify control room area temperature less than 90 degrees once per four hours, and RA 8.2 to restore one control room area ventilation air conditioning subsystem to operable status within 72 hours. The Electrical Maintenance department performed basic troubleshooting. The fan was restarted and following sufficient run time of the A VE return fan, the A VCNE train was declared operable at 1200. TS actions 3.7.5 E.1 and 3.7.4 B.1 and 8.2 were exited. On 5/23/2022 the station began activities to swap to A VCNE to allow for system restoration on 8 VCNE. After swapping to A VCNE, the A VE return fan tripped at 1256. Operations reset the breaker and restarted the fan. The A VCNE train was declared inoperable for CRAF (3.7.4) and MCR ventilation (3.7.5). The station entered the following time clocks: 3.7.4 A.1, restore A train to operable status within 7 days, 3.7.5 RA 8.1 to verify control room area temperature less than 90 degrees once per four hours, and RA 12 to restore one control room area ventilation ~ir conditioning subsystem to operable status within 72 hours (Note: The 8 train was declared operable for CRAF on 5/20/22 at 1841 following repairs, but the 8 train re ained in the 3.7.5 MCR ventilation LCO for continued maintenance activities from the previous week that resulted in the condition discussed above on 5/23.) The B train was fully restored to operable status at 1755 on 5/23/22. TS action 3.7.5 B.1/8.2 were exited. The station declared the A train operable on 5/24/22 at 2230 after completion of an Operability evaluation and subsequent run time. Cause The cause of the event is an inadequate breaker setting resulting in the A VE Return Fan breaker tripping prematurely on fan start. I | ML22362A013 | 0 | good
LaSalle County Station | Unit 1 | Not Found | 12-28-2022 | 12. Licensee Contact for this LER Licensee Contact IPhone Number (Include area code) CJ Smith, Operations Director (815) 415-2200 13. Complete One Line for each Component Failure Described In this Report Cause System Component Manufacturer Reportable to IRIS Cause System Component Manufacturer Reportable to IRIS y B VI COMP C147 I 14. Supplemental Report Expected Month Day Year [81 No I D Yes (If yes, complete 15. Expected Submission Date) 15. Expectet Submission Date 6. Abstract (Limit to 1560 spaces, i.e., approximately 15 single-spaced typewritten lines) On November 3, 2022, both Units 1 and 2 were in Mode 1 and at 100% power. At 2308 CDT the A Main Control Room Ventilation (VC) Compressor tripped on low oil pressure. The A train of the Main Control Room Ventilation (VC) was declared inoperable. The station swapped to the B VCNE train. On November 4 at 0006 CDT, the B Auxiliary Electric Room Ventilation (VE) compressor tripped on high oil temperature and the B VE train was declared inoperable. With both the A and B control room area ventilation air conditioning (CRAC) trains inoperable, the system was in a condition that could have prevented fulfillment of a safety function. The cause of the A VC Compressor trip was a leak on an oil pressure switch sensing line and the cause of the B VE compressor trip was high oil temperature due to slugging. 5NRC FORM 366A (08-2020) Page _2_ of _5_ NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send convnents regarding burden estimate lo the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail lo CONTINUATION SHEET lnfocollecls.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1O22, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www. n re.gov/reading-rm/doc-collections/nu regs/staff/ sr1 O22/r3/) requesting or requiring the collection displays a currenUy valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER LaSalle County Station, Unit 1 05000- 373 YEAR SE N Q U U M E B N E T R IA L R N E O V . 2022 - 004 00 | Plant and System Identification LaSalle County Station Unit 1 and 2 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the Main Control Room Area Ventilation system (VC) and the Auxiliary Equipment Room Ventilation System (VE). Condition Prior to Event Unit(s): 1/2 Date: November 4, 2022 Time: 0006 CDT Reactor Mode(s): 1/1 Mode(s) Name: Power Operation Power Level: 100%/100% Description On November 3, 2022, both Units 1 and 2 were in Mode 1 and at 100% power. At 2308 CDT the A Main Control Room Ventilation (VC) Compressor tripped on low oil pressure. Initial investigations by operations personnel identified an oil leak inside the control cabinet. An emergent swap to the B Main Control Room Ventilation (VC) and Auxiliary Electric Room Ventilation (VE) train was completed. The A train of VC was declared inoperable, and both units entered TS 3.7.5 Required Action (RA) A.1 to restore the A CRAC subsystem to Operable within 30 days. On November 4 at 0006 CDT, the B VE compressor tripped on high oil temperature and the B VE train was declared inoperable. Both units subsequently entered TS 3. 7 .5 RA B.1 to verify control room temperature is s 90 degF once per 4 hours and RA B.2 to restore one AC subsystem to Operable in 72 hours. With both the A and B trains being simultaneously inoperable, the system was in a condition that could have prevented fulfillment of a safety function. The B VE train was fully restored to operable status at 0357 CDT on 11/4/22. TS action 3.7.5 RA B.1/B.2 were exited. The A train was restored to operable on 11/4/22 at 1615 and TS action 3.7.5 RA A.1 was exited. Cause The cause of the A VC Compressor trip was a lrak on an oil pressure switch, resulting in a trip on low oil pressure. The cause of the B VE compressor trip on high oil temperature was liquid refrigerant slugging. This resulted in oil migrating into the compressor, causing the compressor to trip. Reportablllty and Safety Analysis Simultaneous inoperability of the A and B VCNE trains is reportable under 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfillment of the safety function of the structures or systems that are needed to mitigate the consequences of an accident. An ENS report was made to the NRC at 0804 CDT on November 8, 2022 (EN# 56203). The report was pursuant to 10 CFR 50.72(b)(3)(v)(D). The safety significance of this event was minimal. For approximately 4 hours on 11/4/22, both VCNE trains were inoperable for TS 3.7.5, Control Room Area Ventilation Air Conditioning. Main Control temperature did not exceed 90 degrees and online risk remained Green throughout the event. | ML22362A015 | 1 | ok
Nine Mile Point | Unit 2 | Reactor Protection System Actuation While Shutdown | 12-20-2022 | On Sunday, September 4, 2022, at approximately 1638 hours with reactor power at 0%, Nine Mile Point Unit 2 (NMP2) experienced a Reactor Protection System (RPS) actuation on Reactor Pressure Vessel (RPV) Low Water Level (Level 3) of 159.3 inches. At the time of the RPS actuation, the reactor was already in a shutdown condition with all rods fully inserted. The Level 3 condition also initiated an isolation signal to Groups 4 and 5 Primary Containment Isolation Valves (PCIVs), which were already closed. Operators took action to restore RPV water level to the normal operating band. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A). The cause of the event was due to a lack of procedural guidance in N2-SOP-101 C, Reactor SCRAM, the Control Room staff did not utilize the proper pressure reduction detail section for a planned cooldown. The Turbine Bypass Valve response to a pressure reduction strategy of 1.5 psig/second caused a rapid opening and closure of bypass valves that complicated level control resulting in Level 3 and RPS actuation. The event described in this LER is documented in the plant's Corrective Action Program (CAP) as IR 04520704. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08--2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and lnfonnation Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory I Affairs, (3150-0104), Atjn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRG may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document http·t/www nrc.govtreading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER I I • DYEA R SEQUENTIAL REV ~- I NUMBER 1- 0N O. 05000- 10 I 002 | THE ENERGY INDUSTRY IDENTIFICATION SYSTEM (EIIS) COMPONENT FUNCTION IDENTIFIER AND SYSTEM NAME OF EACH COMPONENT OR SYSTEM REFERRED TO IN THIS LER ARE ENCLOSED WITHIN [BRACKETS] L DESCRIPTION OF EVENT A PRE-EVENT PLANT CONDITIONS: Prior to the event, NMP2 was in Mode 3 (Hot Shutdown}, performing a cooldown to support a planned maintenance outage. 8_E VENT: On Sunday, September 4, 2022, at approximately 1638 hours, NMP2 experienced an actuation of the Reactor Protection System (RPS) [JC] due to Reactor Low Water Level (Level 3) while in Mode 3, Hot Shutdown. At the time of the RPS actuation, all control rods were already fully inserted and Groups 4 and 5 PCIVs were already closed. The Containment Isolation [JM] signal impacted Residual Heat Removal (RHR) [BO], Shutdown Cooling, RHR letdown to radwaste, and RHR sampling valves. Following the RPS actuation, Operators restored reactor water level utilizing level control valve CNM-LV137_ Nine Mile Point Unit 1 (NMP1) was unaffected by the NMP2 RPS actuation. On September 4, 2022 at approximately 2131 hours, this event was reported to the NRG via Event Notification #56089 pursuant to the requirements of of 10CFR50.72(b)(3)(iv)(A) Specified System Actuation of any of the systems listed in 10 CFR50.7 2(b )(3)(iv)(B). C. INOPERABLE STRUCTURES, COMPONENTS, OR SYSTEMS THAT CONTRIBUTED TO THE EVENT: None. D. DATES AND APPROXIMATE TIMES OF MAJOR OCCURENCES AND OPERATOR ACTIONS: September 4, 2022: 1506 - NMP2 entered Mode 3 on a planned reactor SCRAM to enter a maintenance outage. 1512 -Operators manually close the Main Steam Line (MSL) drain system due to reactor pressure lowering. 1534 -Operators suspected leak by past Feedwater Level Control Valve, Feedwater Pump 'B' Level Control Valve (2FWS-LV1 OB) and subsequently manually closed the blocking valve which stabilized reactor water level. 1556 - Reactor water level continued to rise. Operators suspected leak by past High Pressure - Low Feedwater Level Control Valve (2FWS-LV55B}, and subsequently manually isolated the valve which stabilized reactor water level. NRG FORM 366A (08-2020) Page 2 of 4 | ML22362A073 | 0 | good
Quad Cities Nuclear Power Station | Unit 2 | Manual Scram Due to Feedwater Regulator Valve Failure Increasing Reactor Water Level | 12-30-2022 | On November 4, 2022, Unit 2 was at 100% power with no surveillance activities in progress that contributed to the event. At 1359 hours the 2B Feedwater Regulating Valve (FRV) failed in the open position and locked up, causing an increase in reactor vessel water level. Attempts at manual control of the feedwater system to decrease level were not successful. At 1400, a manual scram was inserted in accordance with operating procedures. All control rods inserted, and the scram was uncomplicated. The cause of this event is foreign material partially or completely blocking hydraulic oil flow internal to a servo valve in the 2B FRV that caused it to move rapidly to the fully open position. This caused Unit 2 reactor vessel water level to rapidly rise until it reached the established scram criteria of +44 inches, at which time a manual scram was inserted. This report is being submitted in accordance with 10 CFR 50.73(a)(2)(iv)(A) for an event or condition that resulted in manual or automatic actuation of the reactor protection system including a reactor scram. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira submission@omb.eoo.gov. The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1 022/r3/) requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Quad Cities Nuclear Power Station Unit 2 05000- 265 YEAR SE N Q U U M E B N E T R IA L R N E O V . 2022 - 003 00 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Manual Scram Due to Feedwater Regulator Valve Failure Increasing Reactor Water Level CONDITION PRIOR TO EVENT Unit: 2 Event Date: November 4, 2022 Event Time: 1400 CDT Reactor Mode: 1 Mode Name: Power Operation Power Level: 100% No structures, systems or components were inoperable at the start of this event that contributed to the event. A. DESCRIPTION OF EVENT On November 4, 2022, Unit 2 was operating at 100% power. There were no surveillances in progress that contributed to the event. At 1359 hours, main control room (MCR) alarms indicated the 28 Feedwater (FW) [JB] Regulating Valve (FRV) [FCV] failed in a manner that drove it to an open position and caused the valve to lock up. As a result, reactor vessel water level began to rise. The other FRV, 2A was in service and responded as designed anq automatically closed to control reactor water level. With the 2A FRV fully closed, reactor water level continued to rise and when the level reached the established scram criteria of +44 inches, the Unit Supervisor directed a manual scram in accordance with station operating procedures. The scram was inserted at 1400 hours. All control rods were inserted, and the scram was uncomplicated. The NRC was notified via ENS Report 56210 at 1710 EDT on November 4, 2022. Following replacement of the 28 FRV servo valve [FSV], Unit 2 returned to power operations on November 6, 2022. NRG FORM 366A (08-2020) Page_2_ of _4_ | ML22364A273 | 0 | good
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Inadequate Protection Devices for DC Motor Field Shunt Cables Through Separate Fire Areas | 01-10-2023 | During an extent of condition review for unprotected circuits, the James A. FitzPatrick Nuclear Power Plant (JAF) staff identified three cables for which a postulated fire event could potentially short circuit and cause secondary cable damage. The main circuit breakers in the motor control center compartment do not provide adequate protection of the shunt field circuit cable. This condition affects the DC motors to 27MOV-123, torus exhaust isolation bypass valve, 23MOV-14, HPCI turbine steam inlet isolation valve, and 23MOV-24, HPCI full flow test return to condensate storage isolation valve. The cables for these circuits are routed thru fire areas in South Cable Tunnel, Reactor Building Eastside, and Reactor Building West Crescent; where safe shutdown equipment could be affected by this condition. The cause of the condition is that the original plant design, prior to 10 CFR 50 Appendix R, did not include overcurrent protection for DC motor shunt field cables in all applicable Safe Shutdown Analysis circumstances. Compensatory actions were established for the affected Fire Zones and modifications were completed for the affected circuits. NRC FORM 366 (08-2020) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments CONTINUATION SHEET regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 – 333 NUMBER N0. 2021 – 001 – 01 | Background The James A. FitzPatrick Nuclear Power Plant (JAF) 10 CFR 50 Appendix R Safe Shutdown Analysis is based on the occurrence of a single fire. The only failures that are considered are those directly attributable to the fire, and spurious operations that can be postulated to occur as a result of the fire. No other concurrent failures are assumed to occur (i.e., single failure). Fire areas are established to meet the separation requirements of Section III.G of Appendix R for safe shutdown systems. The fire areas at JAF are further sub-divided into fire zones. It is postulated that a fire in one fire area could cause a short-circuit, cause overcurrent and overheat cables, then produce secondary damage to adjacent cables in other fire areas where the cables are routed. Fuses in electrical circuits prevent this type of propagation. Secondary cable failures are outside the assumptions of the 10 CFR 50 Appendix R Safe Shutdown Analysis. In a direct current (DC) shunt motor, the armature and field (shunt) windings are connected in parallel. The shunt (field) windings of a DC shunt motor are made of smaller gauge wire, but they have many more turns than a series-wound DC motor. The high number of turns allows a strong magnetic field to be generated, but the smaller gauge wires provide a high resistance and limit the current flowing through the shunt coil. Event Description On August 24, 2021, an extent of condition evaluation from the condition reported by LER: 2020-002, identified three additional circuits, vulnerable to a potential hot short condition impacting secondary fire areas. The three circuits identified are associated with DC Motors with field shunt cables that transverse multiple fire areas. The feeder breaker protects the armature cables but the smaller 12 AWG (American Wire Gauge) field shunt cables are inadequately protected by the feeder breaker. In the event of a fire-induced hot short, the potential exists, based on the available fault current, cable size, and characteristics of the protective device, for the shunt cable to be overheated. This situation has the potential to cause secondary cable failures that are outside the assumptions of the 10 CFR 50 Appendix R Safe Shutdown Analysis. This condition was reported to the NRC on August 24, 2021 (ENS 55427) per 10 CFR 50.72(b)(3)(ii)(B). The required actions of the Technical Requirement Manual (TRM) 3.7.M, Fire Barrier Penetrations, were established for the affected fire areas. Page 2 of 4 | ML23010A180 | 0 | good
Cooper Nuclear Station 05000 298 1 OF 4 | Unknown Unit | Actuation of Reactor Protection System Initiates a Full Reactor Scram | 01-11-2023 | On November 12, 2022, during plant start up from Refueling Outage 32, operations personnel commenced a surveillance for High Pressure Coolant Injection (HPCI) Beginning of Cycle Testing. While performing the test, a HPCI injection valve unexpectedly opened, injecting water into the reactor vessel. The injected water increased reactivity and the Intermediate Range Monitors initiated a reactor scram. As such, the test was stopped. In April 2021, an undervoltage relay for the valve had been removed due to reliability concerns with that specific type of relay - if the relay would fail, it would cause the valve to fail. Investigation revealed that the modification process to remove the undervoltage relay did not identify a change was required to the HPCI surveillance procedure. There was no impact on nuclear safety, plant reliability, radiological safety, or industrial safety. This event was reported under Event Notification 56220 on November 12, 2022. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: (08-2020) 08/31/2023 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory (See NUREG-1022, R.3 for instruction and guidance for completing this form Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, https://www.nrc.gov/readinq-rm/doc-collections/nureqs/staff/sr1022/r3/) Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LERNUMBER YEAR SEQUENTIAL REV Cooper Nuclear Station 05000- 298 NUMBER NO. 2022 - 003 00 | PLANT STATUS Cooper Nuclear Station was in Mode 2, Startup, at 2 percent power at the time of the event on November 12, 2022. BACKGROUND The Reactor Protection System (RPS) provides timely protection against the onset and consequences of conditions that threaten the integrity of the fuel barrier and the reactor coolant pressure boundary. The RPS includes sensors, relays [EIIS: RL Y], bypass circuits, and switches that are necessary to cause initiation of a reactor [EIIS: RPV] scram. The Intermediate Range Monitors (IRM) generate a trip signal that can be used to prevent fuel damage resulting from abnormal operational transients that occur while operating in the intermediate power range. The Emergency Core Cooling System (ECCS) [EIIS: BJ, BM, BO] control and instrumentation initiates appropriate response from the various cooling systems so fuel is adequately cooled under abnormal and accident conditions. The controls and instrumentation for the ECCS are identified as that equipment required for the initiation and control of the High Pressure Coolant Injection System (HPCI), the Automatic Depressurization System, the Core Spray System, and the Low Pressure Coolant Injection System. When actuated, the HPCI system pumps water from either the emergency condensate [EIIS: SD] storage tanks (ECST) or the suppression chamber to the reactor vessel via the feedwater pipeline. 250 volt direct current (VDC) provides motive power and 125 VDC provides control power for pumps [El IS: P] and valves [EIIS: V]. At the beginning of the operating cycle, HPCI is tested to assess operational readiness prior to exceeding 165 pounds per square inch gauge. The surveillance aligns the system in the test return flow lineup, by placing HPCI-MO-21 (test bypass valve to ECST) and HPCI-MO-24 (ECST test line shutoff valve) in the OPEN position, and HPCI-MO-19 (injection valve) in the CLOSED position. 250 VDC power to the three valves is removed to prevent operation of the valves during the surveillance. A test switch is used to initiate the HPCI response. The HPCI system logic provides a CLOSE signal to HPCI-MO-21 and HPCI-MO-24, and an OPEN signal to HPCI-MO-19 via relay contacts. After HPCI system flow is verified and HPCI component functions are verified to have operated correctly, the test switch is placed to OFF, de-energizing the relays and the HPCI initiation signal is reset de-energizing other relays. 250 VDC power to the HPCI- MO-21, HPCI-MO-24, and HPCI-MO-19 valves is then restored. EVENT DESCRIPTION On November 12, 2022, during plant start up from Refueling Outage 32 (RE32), operations personnel commenced surveillance procedure HPCI Beginning of Cycle Test. The purpose of this surveillance is to | ML23011A111 | 0 | good
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Mode Switch Failed to Bypass Low Main Steam Line in Mode 2 Resulting in MSIV and RPS System Actuation | 01-31-2023 | On September 26, 2022, at 0306 EDT, while the reactor was sub-critical and inserting control rods for a planned refueling outage, James A. FitzPatrick Nuclear Power Plant (JAF) experienced a reactor scram and Group 1 isolation on low steam line pressure logic. As a result of Group 1 isolation signal seven out of eight Main Steam Isolation Valves (MSIV) isolated. ‘A’ outboard MSIV (29AOV-86A) failed to isolate on the initial signal. The Reactor Protection System (RPS) actuated, resulting in all control rods being fully inserted, and manual actuation of RCIC. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). The RPS actuation was determined to be a failure of the reactor mode switch (05A-S1) to enact the logic required to bypass MSIV isolation on low main steam line pressure and RPS actuation on MSIV closed position. Operating Procedure OP-65 was revised to ensure proper switch contact logic is validated by redundant indications. NRC FORM 366 (08-2020) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments CONTINUATION SHEET regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 – 333 NUMBER N0. 2022 – 002 – 01 | Background The Reactor Mode Switch (05A-S1) controls the operating Plant Mode of the Reactor. It has four positions, Shutdown, Refuel, Start & Hot Stby, and Run. The pistol grip locking handle assembly drives 4 banks of contacts with a total of 64 contacts. The Mode Switch contacts enact the plant parameter logic required by the Plant Mode for Reactor Protection System (RPS) [EIIS identifier: JE], Reactor Manual Control System [JD], Primary Containment Isolation System (PCIS) [JM], Refuel Interlocks [DF], Neutron Monitoring Systems [IG], and Plant Process Computer [ID] to ensure the correct setpoints and circuits are active. Event Description On September 26, 2022, James A. FitzPatrick Nuclear Power Plant (JAF) was reducing power for a planned plant shutdown for a refuel outage. At the time of the Scram, no structures, components, or systems were inoperable at the start of the event and contributed to the event. Control rods [AA] were being inserted and reactor power and pressure was decreasing. At 0230, operators placed the mode switch (05A-S1) in Startup/Hot Standby (Mode 2). At 0306, an unplanned Scram signal was received due to a Group 1 isolation on low main steam line [SB] pressure. All control rods were fully inserted. Main Steam Isolation Valves (MSIV) isolated except ‘A’ outboard MSIV (29AOV-86A) failed to close. PCIS isolated valves in multiple systems according to group 1 isolation. When the PCIS was reset, 29AOV-86A was then manually isolated. At 0530, Operators made the decision to place Reactor Core Isolation Cooling (RCIC) system [BN] in service to augment pressure and level to assist in transition to feedwater [SJ] and condensate [SD] systems. At 0751, RCIC was shut down and in a standby lineup. The NRC was notified of this event at 0541 by ENS 56119 in accordance with 10 CFR 50.72(b)(2)(iv)(B) RPS actuation while critical and 10 CFR 50.72(b)(3)(iv)(A) for systems actuation. A reactor engineering analysis of reactor criticality was performed for the period of time prior to the event, and it was determined that the reactor was sub-critical. On October 4, 2022, ENS 56119 was updated to retract 10 CFR 50.72(b)(2)(iv)(B). The ‘A’ outboard MSIV (29AOV-86A) failed to close, but the safety function for ‘A’ main steam line isolation was successful because the inboard MSIV isolated successfully. Failure of the MSIV to close was documented and evaluated under IR 04524581. Page 2 of 4 | ML23031A225 | 0 | good
Browns Ferry Nuclear Plant | Unit 1 | Main Steam Relief Valves Lift Settings Outside of Technical Specifications Required Setpoints | 02-06-2023 | On December 6, 2022, the Tennessee Valley Authority was notified of As-Found testing results that two Main Steam Relief Valves (MSRVs) from Browns Ferry Nuclear Pant (BFN), Unit 1 were outside of their Surveillance Requirement limits for an indeterminate amount of time. These affected valves remained capable of maintaining reactor pressure within the American Society of Mechanical Engineers code limits and were still able to perform their safety function. It was determined that the MSRVs failed due to corrosion bonding to the valve seats and non-quantifiable leakage known as simmering. All thirteen of the MSRV pilot valves were replaced during the Unit 1 fall 2022 refueling outage. The Boiling Water Reactor Owners' Group is continuing to work toward a solution to improve the quality and adhesion of the platinum coating on the discs. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION (01-10-2023) LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) APPROVED BY OMB: NO. 3150-0104 EXPIRES: 12/31/2023 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME ☒ 050 2. DOCKET NUMBER 3. LER NUMBER Browns Ferry Nuclear Plant, Unit 1 00259 YEAR SEQUENTIAL NUMBER REV NO. ☐ 052 2022 - 003 - 00 | Not Found | ML23037A992 | 1 | ok
Grand Gulf Nuclear Station | Unit 1 | Manual Reactor SCRAM due to a loss of the Condensate and Feed Water System | 02-16-2023 | At 2058 on December 19, 2022, Grand Gulf Nuclear Station, Unit 1 experienced a trip of Condensate Booster Pump A. At 2101, Reactor Feedwater Pump A tripped, and the reactor was manually scrammed. All control rods were fully inserted into the core. At 2104, Reactor Feedwater Pump B tripped. At 2121 High Pressure Core Spray (HPCS) was manually injected to maintain reactor water level. At 2126 Reactor Feedwater Pump A was successfully restarted. Following the reactor SCRAM, the HPCS system was used to maintain reactor water level. The direct cause of the SCRAM was the Heater Drain Tank (HOT) Level Control Valves were not capable of responding quickly enough to mitigate the HOT level oscillations during the transient caused by Condensate Booster Pump Trip and subsequent Fast Detent. There were no consequences to the safety of the public, nuclear safety, industrial safety, or radiological safety. No radiological releases occurred due to this event. This report is made in accordance with 10 CFR 50.73(a)(2)(iv)(A) for any event or condition that resulted in manual of automatic actuation of any system listed in paragraph 10 CFR 50.73 (a)(2)(iv)(B). The Reactor Protection System including reactor SCRAM or trip is included in 10 CFR 50.73 (a)(2)(iv)(B). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 12/31/2023 (01-10-2023) Estimated burden per response to comply wnh this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and lnfonmation Collection Branch (T-6 A10M), U.S Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of lnfonmation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 72517th Street NW, Washington, DC 20503; e-mail. crra sutmissl()n@omb.eop.gov. The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document https :// VNIW .n re. gov /reading-rm/doc-collectionsln ur egs/staff /sr1 022/r3/) requesting or requiring the colloction displays a currently valid 0MB conlrol number 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ~ 050 YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 >-------< 416 NUMBER NO. 2022 - 003 -00 □ 052 | PLANT CONDITIONS: Mode 1 , 78 percent power DESCRIPTION OF EVENTS At 2058 on December 19, 2022, while the plant was operating at 100 percent reactor power, Condensate Booster Pump (CBP)[SD] A tripped. Control Room Operators entered the Feedwater System Malfunction Off-Normal Event Procedure (ONEP) and reduced core flow to 70 million pound-mass per hour. While performing steps of the ONEP operators identified Reactor Feedwater Pump "A" and "B" suction pressures were rapidly lowering. At 2101, Reactor Feedwater Pump "A" tripped on low suction pressure. A recirc flow control valve runback occurred as designed. Reactor water level continued to lower because of a reduction in feed flow. At approximately 17 inches of water and trending down, the At-The-Controls Operator placed the Reactor Mode Switch in Shutdown at 2101. At 2121 High Pressure Core Spray (HPCS) [BG] was manually injected to maintain reactor water level. The manual SCRAM on low reactor water level resulted from constricting Feed Flow when the Heater Drain Tank Level Control Valves closed, which is a plant response that should have been found in the results of calculation for the "Condensate and Feedwater Transient Analysis" (CFTA ). This oversight, along with other issues found in the CFT A calculation led to the Root Cause of "Transients caused by CBP Trip have not been adequately analyzed", and this condition will be corrected by performing an analysis to determine the best corrective modification and implementing that modification during the next refueling outage. REPORT ABILITY This report is made in accordance with 10 CFR 50.73(a)(2)(iv)(A) for any event or condition that resulted in manual of automatic actuation of any system listed in paragraph 10 CFR 50. 73 (a)(2)(iv)(B). The Reactor Protection System including reactor SCRAM or trip is included in 10 CFR 50.73 (a)(2)(iv)(B). CAUSE Direct Cause: Heater Drain Tank (HOT) Level Control Valves were not capable of responding quickly enough to mitigate the HOT level oscillations during the transient caused by Condensate Booster Pump Trip and subsequent Fast Detent. Root Cause: Transients Caused by Condensate Booster Pump Trip have not been adequately analyzed. CORRECTIVE ACTIONS 1. Replace CBP A Motor - The CBP A Motor has been replaced. 2. Corrective Action to Prevent Recurrence (CAPR) - Modification will be performed to implement long term solutions as determined to analyze the transient effects of the following on Feed Flow and Post Extended Power Uprate (EPU) and Maximum Extended Load Line Limit Analysis Plus (MELLA+) conditions: Condensate Pump trip, CBP trip, HOP trip. Develop potential solutions to solve latent design issues in Feed Flow transient response. NRG FORM 366A (01-10-2023) Page 2 of 3 | ML23047A547 | 0 | good
i | Unknown Unit | : | 02-22-2023 | On January 5, 2023, at 1242, with the reactor in Mode 1 and at 98% rated thermal power, an automatic reactor trip occurred due to lowering water level in the reactor vessel. The High Pressure Core Spray (HPCS) and Reactor Core Isolation Cooling (RCIC) systems were manually initiated to restore and control water level in the reactor vessel. The direct cause of the reactor trip was attributed to the failure of the Digital Feedwater Control System (DFWCS) to control reactor water level, following corrective maintenance on one of the power sources to the system. A latent configuration control issue in the system caused unexpected indication losses during the maintenance. Upon re- energizing the power source, two component failures in DFWCS, and an overloaded communications network, caused the system to lower reactor water level, which resulted in a reactor trip. The failed components were replaced, and the reactor was re-started on January 8, 2023. This event is being reported in accordance with 10 CFR 50. 73(a)(2)(iv)(A) due to an automatic Reactor Protection System (RPS) actuation and the manual initiation of two Emergency Core Cooling System (ECCS) systems. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 12/31/2023 (01-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB CONTINUATION SHEET reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: (See NUREG-1022, R.3 for instruction and guidance for completing this form oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of infonmation unless the document requesting or requiring the collection displays http://www.n r e.gov /reading-rm/doc-collections/nu regs/staffl s r1 022/r3/ a currently valid 0MB control number. 2. DOCKET NUMBER ______3 _. _LE_R_N_U_M. .B_ E_R_ ____ 1- FACILITY NAME 050 SEQUENTIAL REV YEAR NUMBER NO. Perry Nuclear Power Plant 00440 2023 001 00 □ 052 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. EVENT DESCRIPTION On January 5, 2023, planned corrective maintenance was being performed on a voltage-regulating transformer [XFMR] which is one of the redundant power sources to the Digital Feedwater Control System (DFWCS) [SJ]. When the transformer was de-energized for the work to be performed, Operators received some unexpected losses of DFWCS indication, resulting in the loss of all of the DFWCS Operator interface screens. Reactor power, pressure and level remained stable at this time, indicating that DFWCS maintained control. Based on the plant remaining stable, a decision was made to continue with the work on the transformer. Upon the post-maintenance energization of the voltage regulating transformer, a reactor water level transient of three inches occurred, and then stabilized. A walkdown of DFWCS identified a failed level control processor module [CPU] and a degraded power supply [JX]. The decision was made to perform a Nodebus Check (online diagnostic test) to restore the lost indication in the system. Due to the loss of all the DFWCS interface screens, the Operators did not recognize that the system demanded zero level to the DFWCS controllers during a re-sync of the level control processor modules. This zero demand signal was sent to the Reactor Feed Pump Turbines (RFPTs) [Pl governor [65] thereby causing the RFPTs to reduce output to idle and minimum flow. The reduced feedwater flow resulted in the reactor water level lowering to Level 3, which caused an automatic reactor trip at 1242. Operators then manually initiated two Emergency Core Cooling Systems (ECCS), High Pressure Core Spray (HPCS) [BG] and Reactor Core Isolation Cooling (RCIC) [BN] to restore and control reactor water level. The Motor Feed Pump became available at 1251 and was started at 1253 to control reactor water level. At 1254, the Motor Feed Pump was controlling reactor water level through DFWCS. The Condition Report investigation revealed that the cause of the reactor trip was attributed to the failure of a DFWCS level control processor module along with a degraded power supply, concurrent with a DFWCS network communications overload. Additionally, a configuration control issue was found with some of the DFWCS media translators [CNV] being connected to the incorrect power source. This resulted in the unexpected loss of additional DFWCS workstations and indications to the Operators when power was removed for the maintenance. It also caused increased DFWCS network communication traffic, due to the loss of interface screens hindering the Operator's ability to acknowledge alarms. NRC notification (EN 56298) was made on January 5, 2023, at 1539, under 10 CFR 50.72(b)(2)(iv)(A) - ECCS Injection and 10 CFR 50.72(b)(2)(iv)(B) - RPS Actuation. The faulty DFWCS power supply and the failed secondary control processor module were replaced. The configuration control issue was also corrected with the media translators. Post maintenance testing for DFWCS was performed satisfactorily, and a successful reactor startup was completed on January 8, 2023. CAUSES OF EVENT The direct cause of the automatic reactor trip was attributed to the failure of one of the DFWCS level control processor modules, along with an intermittent power supply failure, and combined with a network traffic overload which overall resulted in a zero percent output demand signal to the Reactor Feed Pump Turbine (RFPTs) governor, causing the RFPTs to reduce speed to idle and minimum flow output. Page 2 of3 | ML23053A083 | 0 | good
Vogtle Electric Generating Plant | Unit 1 | Partial Loss of Offsite Power results in Emergency Diesel Generator and Auxiliary Feedwater Actuation | 02-27-2023 | On January 03, 2023 at 2259 EST, with both Unit 1 and Unit 2 in Mode 1 and 100 percent power, an automatic actuation of the Unit 1 Bravo and the Unit 2 Alpha Emergency Diesel Generator Systems and associated Auxiliary Feedwater Systems occurred. These systems actuated due to the failure of a lightning arrestor associated with the Unit 1 Bravo Reserve Auxiliary Transformer. This resulted in the upstream breaker to the Unit 1 Bravo and Unit 2 Alpha Reserve Auxiliary Transformers opening, causing the Unit 1 Bravo and Unit 2 Alpha emergency electrical buses to de-energize and the automatic start of the associated Emergency Diesel Generator and Auxiliary Feedwater Systems. The units remained in Mode 1 and 100 percent power, and the operating crew performed as expected. The lightning arrestor was replaced and the Reserve Auxiliary Transformers were returned to service. Due to the automatic actuation of the Emergency Diesel Generator and Auxiliary Feedwater Systems on each unit, this event is being reported under 10 CFR 50.73(a)(2)(iv)(A). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 12/31/2023 (01-10-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 YEAR SEQUENTIAL REV NUMBER NO. Vogtle Electric Generating Plant, Unit 1 00424 2023 052 - 001 - 00 | NARRATIVE A. Event Description On January 3, 2023 at 2259 EST, with both Unit 1 and Unit 2 in Mode 1 and 100 percent power, a partial loss of offsite power occurred due to a failed Hubbell MVN lightning arrestor [LAR] on the Unit 1 Bravo Reserve Auxiliary Transformer (RAT)[XFMR]. This resulted in the upstream breaker [BKR] to the Unit 1 Bravo and Unit 2 Alpha Reserve Auxiliary Transformers opening, causing the Unit 1 Bravo and Unit 2 Alpha emergency electrical buses to de-energize and the automatic start of the associated Emergency Diesel Generator (EDG)[EK] and Auxiliary Feedwater Systems (AFW)[BA]. There were no Structures, Systems, or Components (SSCs) that were out of service at the beginning of the event that contributed to the event. Due to the actuation of the EDG and the AFW systems this event is being reported in accordance with 10 CFR 50.73(a)(2) (iv)(A). B. Cause of Event The cause of the event was a failure of the lightning arrestor on the Unit 1 Bravo Reserve Auxiliary Transformer. C. Safety Assessment When the lightning arrestor failed, the upstream breaker for offsite power opened. This resulted in one safety-related electrical bus on each unit becoming de-energized. The EDGs associated with the affected electrical buses started automatically and re-energized the electrical buses. The AFW systems started as a result of the electrical bus being de- energized. All the systems operated as designed. The operating crew responded as expected. The event was within the analysis of the Updated Final Safety Analysis Report, Chapter 15. There were no safety consequences as a result of this event. D. Corrective Actions The lightning arrestor for the affected transformer was replaced. E. Previous Similar Events None. | ML23058A432 | 0 | good
Clinton Power Station | Unit 1 | Grid Fault Results in Switchyard Breaker Trips and Reactor Scram | 03-31-2023 | On 1/31/23, at 2343 CST, while operating at approximately 100% power, a phase-to-phase fault occurred on a 345 KV transmission line approximately 16 miles from Clinton Power Station (CPS). Gas Circuit Breaker Generator Output Breakers (GCBs) 4510 and 4514 tripped open to clear the fault. GCB 4510 failed to trip open properly, resulting in actuation of the GCB 451 O breaker failure protective relay, tripping open GCB 4506 and disconnecting the main generator from the grid. This resulted in a turbine trip and automatic reactor scram. The root cause of the failure of GCB 4510 to properly open, and subsequent trip open of GCB 4506, was due to corrosion of the GCB 4510 air system charging valve. Corrective actions taken and planned include: repairs to the 345 KV transmission line involved in the event, developing and implementing an improved Preventive Maintenance (PM) strategy for switchyard breakers, working with the switchyard operator to perform twelve-year breaker overhaul/replacement on affected GCBs/345 KV switchyard breakers, and providing training on effective design attribute review performance. There was no impact to the health and safety of the public or plant personnel from this event. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED.BY 0MB: NO. 3150-0104 EXPIRES: 12/31/2023 (01-10-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET ( lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-mi/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currenlly valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 SEQUENTIAL REV YEAR Clinton Power Station, Unit 1 00461 NUMBER NO. □ 052 ' 2023 - 001 - 00 | PLANT AND SYSTEM IDENTIFICATION General Electric -- Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in text as [XX]. EVENT IDENTIFICATION Grid Fault Results in Switchyard Breaker Trips and Reactor Scram A. Plant Operating Conditions Before the Event Unit: 1 Event Date: January 31, 2023 Event Time: 2343 CST Mode: 1 Mode Name: Power Operation Reactor Power: 100 B. Description of Event On January 31, 2023, at 2343 CST, while operating at approximately 100% power, a phase-to phase fault occurred on a 345 KV transmission line approximately 16 miles from Clinton Power Station (CPS). In response to the fault, Gas Circuit Breaker Generator Output Breakers (GCBs) 4510 and 4514 [FK:BRK] tripped open to clear the fault. GCB 4510 failed to trip open properly, resulting in actuation of the GCB 451 O breaker failure protective relay, tripping open GCB 4506 [FK:BRK] and disconnecting the main generator [EL:GEN] from the grid. This resulted in a turbine [TA:TRB] trip and automatic reactor [RCT] scram. Operators placed the reactor mode switch in shutdown and completed the scram response actions. All control rods fully inserted. As noted above, GCB 4514 tripped open successfully. However, breaker failure protective relaying was actuated due to detection of current flow through GCB 4510 after it received a trip open signal. This resulted in tripping open GCB 4506 to clear the fault. C. Cause of the Event When a GCB breaker opens, the breaker control circuits energize trip coils. Energizing the trip coils creates a magnetic force that releases a trip latch, allowing spring energy to open an air pilot valve. The pilot valve allows air from the associated air receiver to flow into the breaker's operating piston/operating cylinder. The compressed air forces the operating piston to stroke the operating rod, which is connected to the interrupter. In addition to opening the interrupter, the operating piston compresses the breaker's closing springs as it travels. The operating piston overtravels slightly allowing the breaker closing latch to cycle and capture the operating rod in the open position against closing spring pressure. The breaker will remain open until the closing latch is released by the associated closing coils. In this event, GCB 4510 failed to latch open. | ML23094A112 | 0 | good
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Primary Containment Isolation System Isolation due to Initiation of Main Condenser Fire Protection Foam System | 04-19-2023 | At 0105 EST on February 19, 2023, with the James A. FitzPatrick Nuclear Power Plant (JAF) at 100 percent power, a High Main Steam Line Radiation signal initiated a primary containment isolation valve closure signal in multiple systems. During the performance of FPP-3.25 “Fire Protection Manifold #5 Sprinkler System Main Drain and Water Flow Alarm Test”, the main condenser foam system was inadvertently initiated, resulting in firefighting foam intrusion into a sump which migrated to the main condenser and eventually to the reactor coolant system. The cause was determined to be a human performance related error during testing. Corrective actions include conducting human performance training and evaluations and hardening of the impacted plant sump system. NRC FORM 366 (08-2020) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (03-14-2023) Estimated burden per response to comply with this mandatory collection request: 80 LICENSEE EVENT REPORT (LER) hours. Reported lessons learned are incorporated into the licensing process and fed CONTINUATION SHEET back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 YEAR SEQUENTIAL REV NUMBER NO. James A. FitzPatrick Nuclear Power Plant 05000333  052 2023 – 001 – 00 | Background James A. FitzPatrick Nuclear Power Plant (JAF) has two firefighting foam systems: the main condenser foam system [EIIS identifier: KQ], which is the subject of this event, and the High Pressure Coolant Injection (HPCI) foam System. The purpose of main condenser foam system is to provide fire extinguishment for the Main Condenser Liquid Holding Pit. The foam system was provided on the basis that the oil from any major turbine oil leak would drain to the pit and a foam system would be effective in fire extinguishment in a confined pit area. Inside the same building, the turbine building equipment drain sump [WK], also known as the low conductivity sump, is designed to collect, and hold leakage from turbine building equipment drains. During power operation, the low conductivity water in the sump is drawn into the main condenser [SD] with vacuum drag. This water is combined with main condenser condensate water and returned to the Reactor Coolant System (RCS) [AB]. Two pumps are also available to move water out of the sump to the condenser or radwaste treatment. Event Description On February 18, 2023, at 23:00, with the JAF at 100 percent power, a scheduled test began for FPP-3.25, Fire Protection Manifold #5 Sprinkler System Main Drain and Water Flow Alarm Test. The purpose of the test is to demonstrate water supply is available to the sprinkler system supplied from Manifold #5 and to demonstrate operability of the waterflow alarm. The step in the procedure being performed by the control room stated to “Press Acknowledge button at Panel FPP and verify Red CONDENSER PIT FOAM SYS light is on, and alarm bell is off”; however, the operator depressed the main condenser foam system initiation pushbutton instead of the acknowledge pushbutton, at 00:42 on February 19. The foam system injected, per design, into the Main Condenser Liquid Holding Pit and a foam/water mixture migrated to the nearby turbine building equipment drain sump. The main condenser vacuum drag drew the foam/water mixture out of the sump into the main condenser hotwell which was then introduced into the RCS via the condensate and feedwater system [JB]. At 01:06, Main Steam Line Hi-Hi radiation actuated Primary Containment Isolation System (PCIS) [JM] Group 1 isolation signal. Reactor Water Recirculation (RWR) [AD] sample valve 02-2AOV-39 and 02-2AOV-40 closed. The isolation signal also isolated the normally closed Main Steam Line Drain System [SB] and Condenser Air Removal System [SH]. At 01:14, Operators isolated the high conductivity sump vacuum drag flow path and aligned it to radwaste. This stopped the intrusion of high conductivity foam into the condenser. Conductivity, off-gas radiation, and main steam line radiation then returned to pre-transient values. This event was reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) via ENS 56373. This report is submitted in accordance 10 CFR 50.73(a)(2)(iv)(A). Page 2 of 3 | ML23109A246 | 0 | good
LaSalle County Station | Unit 2 | Automatic Actuation of Reactor Protection System (RPS) | 05-02-2023 | At 0910 CST on March 4, 2023, with Unit 2 in Mode 4 at O percent power, an actuation of a reactor scram on low charging water header pressure occurred during restoration from ASME Class 1 System Leakage Test conditions. All control rods were already fully inserted prior to the receipt of the scram signal. The scram occurred due to a valid signal and all systems responded as expected. Low charging water header pressure is not required to be operable in Mode 4 but is active if not bypassed. The scram signal should have remained bypassed per station procedures. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 12/31/2023 (01-10-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira submission@omb.eop.gov. The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is nol required lo respond lo, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1 022/r3/l requesting or requiring lhe collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER (cid:127) 050 SEQUENTIAL REV YEAR NUMBER NO. LaSalle County Station, Unit 2 (cid:143) 374 052 - - 2023 003 00 | LaSalle County Station Unit 2 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the Reactor Protection System (RPS). RPS initiates a rapid insertion of all the control rods (scram) when monitored variables exceed their pre-established limits, neutron flux instrumentation becomes inoperable, or a manual scram signal is inserted by the operator. In addition, the setpoints, power sources, and controls and instrumentation are arranged in such a manner as to preclude spurious scrams. Condition Prior to Event Unit(s): 2 Date: March 4, 2023 Time: 0910 CST Reactor Mode(s): 4 Mode(s) Name: Cold Shutdown Power Level: 0% Description Following completion of required ASME Class 1 System Leakage Testing, actions were taken to commence reactor depressurization. As governed by the testing procedure, the Control Rod Drive (CRD) Charging Water Stop Valve was closed. The Low Charging Water Header Pressure scram signal was verified to be bypassed at the start of the Hydrostatic Test. The scram signal was then restored during the transition into scram time testing. With the CRD Charging water Stop valve closed and the Low Charging Water Header Pressure scram signal not bypassed, reactor depressurization resulted in an RPS Scram on Low Charging Water Header Pressure. At the time of the Scram, the unit was in Mode 4 with all rods inserted. The Low Charging Water Scram Signal is not required in Mode 4 for Rod Cycling and the Scram signal should have remained bypassed, in accordance with station procedures. Reportability and Safety Analysis The Low Charging Water Pressure Scram is only required to be enabled in Mode 2 and Mode 5 to ensure that a reactor scram is initiated before Scram capability is compromised during low reactor pressure operations. At the time of the event the reactor was in Mode 4 with all rods inserted. Therefore, there was no increased risk to the public as a result of this event. The event is reportable under 10 CFR 50. 72(b )(3)(iv)(A) as an event or condition that results in the valid actuation of the Unit 2 RPS system. An ENS report was made to the NRC at 1642 on March 4, 2023 (EN# 56389). Safety System Functional Failure Review The system equipment responses did not result in a safety system functional failure (SSFF) as defined in accordance with NEI 99-02, "Regulatory Assessment Performance Indicator Guideline." The RPS logic safety function was satisfied by its actuation for designed inputs. | ML23122A016 | 0 | good
cooper nuclear station | Unknown Unit | Valve Test Failures Result in Condition Prohibited by Technical Specifications | 05-08-2023 | On March 7 and March 8, 2023, two Target Rock safety relief valve (SRV) pilot assemblies, removed during Refueling Outage 32, failed to lift within Technical Specifications (TS) lift setpoint requirements. The pressure setpoint of the first failed pilot assembly was 1080 psig; the SRV pilot assembly lifted at 1166.4 psig. The pressure setpoint of the second failed pilot assembly was 1100 psig; the SRV pilot assembly lifted at 1186.1 psig. Three subsequent lifts were performed for the failed SRV pilot assemblies and the results were within the TS pressure setpoint tolerance. The cause of the failure was determined to be corrosion bonding. Although the setpoint lift pressures of the SRV pilot valve assemblies exceeded TS requirements, an analysis of the event concluded the thermal limits, and American Society of Mechanical Engineers overpressure transients, did not exceed allowable limits. Public safety was not at risk. Safety of plant personnel, and plant equipment, was not at risk. A TS Amendment to TS 3.4.3 will be submitted that will address the failure to meet the TS criteria for the Target Rock two-stage SRVs. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (03-14-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by CONTINUATION SHEET email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 (See NUREG-1022, R.3 for instruction and guidance for completing this form 17th Street NW, Washington, DC 20503; email: oira submission@omb.eop.gov. The NRC may not http://www.nrc.gov/readinq-rm/doc-collections/nureqs/staff/sr1022/r3/} conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. FACILITY NAME 2. DOCKET NUMBER J. LEK"'' X 050 YEAR SEQUENTIAL REV Cooper Nuclear Station 00298 NUMBER NO. 052 2023 - 001 - 00 | PLANT STATUS Cooper Nuclear Station was in Mode 1, Power Operation, at 100 percent power, when the event was discovered, i.e., March 8, 2023. BACKGROUND The pressure relief system includes three American Society of Mechanical Engineers (ASME) code safety valves (SV) [EIIS: SB] and eight safety relief valves (SRV) [EIIS: RV], all of which are located on the main steam lines [EIIS: SB] within the drywell [El IS: NH], between the reactor vessel [EIIS: RPV] and the first main steam isolation valve [EIIS: ISV]. The SVs provide protection against over pressurization of the nuclear system and discharge directly into the interior space of the drywell. The SRVs discharge to the suppression pool and provide three main functions: overpressure relief operation to limit the pressure rise and prevent safety valve opening, overpressure safety operation to prevent nuclear system over pressurization, and depressurization operation (opened automatically or manually) as part of the emergency core cooling system [EIIS: BJ, BM, BO]. Technical Specification (TS) Limiting Condition for Operation (LCO) 3.4.3 requires the safety function of seven SRVs and three SVs to be operable. The nominal set pressure tolerances for these valves are established in CNS TS Surveillance Requirement (SR) 3.4.3.1. The SRVs installed at CNS are Target Rock Model 7567F, two-stage, pilot-actuated valves with pilot assemblies comprised of Stellite 21 pilot discs and Stellite 68 pilot body seats. The pilot assemblies had been in continuous service since installation in Refueling Outage (RE) 31, (Fall of 2020). Corrosion bonding is an industry known problem with Target Rock Model 7567F two-stage relief valves in which the pilot valve bonds/sticks to the in-body seat, resulting in an increased pressure needed to lift the valve. After the corrosion bonding is "broken" following the initial lift, the subsequent lifts are within tolerance. EVENT DESCRIPTION In the Fall of 2022, three main SRV body/pilot assemblies and five SRV pilot assemblies were removed during RE32. In March 2023, the eight SRV pilot assemblies were as-found tested at National Technical Systems Laboratories. The pressure setpoint for SRV pilot assembly serial number 387 is 1080 psig. The TS SR 3.4.3.1 as-found limit acceptance is 1080 +/- 3%. The first actual lift pressure of this SRV pilot assembly was recorded at 1166.4 psig, 8.0% above the pressure setpoint. A second, third, and fourth lift was performed, and the results were 1088 psig, 1084 psig, and 1084 psig, all three within 3% of the pressure setpoint. The pressure setpoint for SRV pilot assembly serial number 386 is 1100 psig. The TS SR 3.4.3.1 as-found limit acceptance is 1100 +/- 3%. The first actual lift pressure of this SRV pilot assembly was recorded at 1186.1 psig, 7.8% above the pressure setpoint. A second, third, and fourth lift was performed, and the results were 1111 psig, 111 O psig, and 1109 psig, all three within 3% of the pressure setpoint. BASIS FOR REPORT CNS is reporting this event as an operation or condition prohibited by plant TS per 10 CFR 50.73(a)(2)(i)(B), and also as a condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident as defined under 10 CFR 50.73(a)(2)(v)(D). | ML23128A133 | 0 | good
cooper nuclear station | Unknown Unit | Manual Reactor Scram and Group I Isolation due to Main Turbine Bypass Valve Failing Open | 05-11-2023 | A reduction in power was performed on December 15, 2022, to repair a hydrogen leak on the main generator. On December 16, Operations personnel noted that both electro-hydraulic (EH) oil pressure and reactor vessel pressure were lowering and that two of three turbine bypass valves were closed with one full open. Operations personnel responded by starting a second EH fluid pump to restore EH system pressure, however, reactor vessel pressure continued to lower. As a result of reactor vessel pressure lowering, a manual reactor scram was inserted. Immediately following the manual reactor scram, a Primary Containment Group 1 Isolation was received. The cause of one of the turbine bypass valves being open was the failure of the fast-open solenoid operated valve (SOV) coil. All three of the SOV coils were sent to a lab for analysis to determine if there were any additional failure modes of the coil. The analysis determined the most likely cause of the premature failure of the SOV was a shorting of the coil due to a weak point along the coil wiring breaking down over time. The other two SOV coils, which did not fail, were also examined and found to be in good condition with no gross flaws. There was no impact to nuclear safety, radiological safety, or industrial safety. This event was reported under Event Notification 56278 on December 17, 2022. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (03-14-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by CONTINUATION SHEET email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 (See NUREG-1022, R.3 for instruction and guidance for completing this form 17th Street NW, Washington, DC 20503; email: oira submission@omb.eop.gov. The NRC may not http://www. nrc. gov/ reading-rm/doc-collections/nu regs/staffl s r1 022/r3/) conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. FACILITY NAME 2. DOCKET NUMBER 3. Lt:.K NUMccn: X 050 YEAR SEQUENTIAL REV Cooper Nuclear Station 00298 NUMBER NO. 052 2022 - 004 01 | PLANT STATUS Cooper Nuclear Station was in Mode 1, Power Operation, at approximately 13 percent power, with the main turbine generator [EIIS:TA] out of service, at the time of the event on December 16, 2022. BACKGROUND The Main Turbine Bypass System [EIIS:SO] is designed to control steam pressure when reactor steam generation exceeds turbine [EIIS:TB] requirements during unit startup, sudden load reduction, and cooldown. It allows excess steam flow from the reactor [EIIS:RPV] to the condenser without going through the turbine. The bypass capacity of the system is 25 percent of the Nuclear Steam Supply System (EIIS:SB] rated steam flow. Sudden load reductions within the capacity of the steam bypass can be accommodated without safety relief valves [EIIS:RV] opening or a reactor scram. The Main Turbine Bypass System consists of three bypass valves (BPV) [EIIS:V] connected to the main steam lines between the main steam isolation valves (EIIS:ISV] and the turbine stop valves. The turbine utilizes a Digital Electro-Hydraulic (DEH) [EIIS:TG] system to control reactor pressure by positioning governor valves and condenser bypass valves. It consists of solid state governor devices, governor, startup control devices, emergency devices for turbine and plant protection (overspeed governor, master trip, vacuum trip, motoring protection, thrust bearing wear trip, low bearing oil pressure trip) and special control and test devices. The control system operates the main stop valves, governor valves, bypass valves, reheat stop and intercept valves and other protective devices. DEH system oil pressure is maintained by two hydraulic pumps [EIIS:P] located at the DEH reservoir tank [EIIS:T]. The function of the fast open permissive solenoid operated valve (SOV) is controlled by the DEH control system to be energized and closed when reactor power is below 115 MWe with the output breaker closed, or anytime the output breaker is open. During normal operation, above 115 MWe, the SOV is de-energized and open. There is a single SOV on each of the bypass valve actuators and controlled by redundant interposing relays at the DEH control cabinet rack. The fast open permissive SOV is only installed on the bypass valves. EVENT DESCRIPTION On December 9, 2022, a hydrogen leak was detected on the main generator. To repair this leak, a reduction in power was performed on December 15. On December 16, the three turbine BPVs were 40 percent open for reactor pressure control. At 23:49 hours, Operations personnel noted that both the electro-hydraulic (EH) oil pressure and reactor vessel pressure were lowering and that two of the three BPVs were closed with one full open. Operations personnel initially diagnosed the cause as an EH leak and responded by starting a second EH fluid pump to restore EH system pressure, however, reactor vessel pressure continued to lower. As a result of reactor vessel pressure continuing to lower, Operations personnel inserted a manual reactor scram at 23:51 hours. Immediately following the manual reactor scram, a Primary Containment Group 1 Isolation on Main Steam Line Low Pressure was received, and all Main Steam Isolation Valves and Steam Line Drain Valves closed. As a result, the station entered Mode 3, Hot Shutdown. The nominal setpoint for a Group 1 Isolation is 835 pounds per square inch gage (psig) main steam line pressure. The manual scram was inserted at 841 psig reactor pressure. The automatic Group 1 Isolation signal was received before scram action response to remove the mode switch from the RUN position, which would have bypassed the Group 1 isolation per Procedure 2.1.5, Reactor Scram. While the unit was in Mode 3, repairs were completed to resolve the hydrogen leak and troubleshooting was performed to determine why one BPV failed open. Initial finding determined the cause to be the failure of the fast-open SOV (TGF- SOV-BV-1) coil. | ML23132A132 | 0 | good
MonticelloNuclearGeneratingPlant 052 | Unknown Unit | Main Steam Isolation Valve Leakage Exceeds Technical Specification Requirements Due to Stem Scoring | 05-17-2023 | A packing leak on valve AO-2-86C, “13 Outboard Main Steam Isolation Valve” (MSIV), exceeded the Technical Specification (TS) individual MSIV leakage limit of Surveillance Requirement (SR) 3.6.1.3.12 on March 4, 2023, based on subsequent evaluation. The condition was discovered on March 21, 2023, when it was concluded that a reasonable expectation of operability was not met, and the MSIV was declared inoperable in accordance with TS 3.6.1.3 Condition E. During a maintenance outage on March 26, 2023, the Local Leak Rate Test as-found leakage was 987.1 standard cubic feet per hour (scfh) which exceeded the TS SR limit for individual MSIV leakage. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the TSs. The cause of the packing leakage is attributed to scoring on the valve stem. During the planned maintenance outage, the MSIV was repacked to restore compliance with TS, and the valve packing gland was bored out and the stem was replaced during the 2023 Refuel Outage. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (03-14-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV NUMBER NO. Monticello Nuclear Generating Plant 263 2023 052 - 001 - 00 | EVENT DESCRIPTION While in Mode 1 at approximately 99 percent power, a packing leak being monitored on valve AO-2-86C, “13 Outboard Main Steam Isolation Valve” (MSIV), (i.e., the outboard MSIV on the “C” main steam line, hereafter referred to as the C outboard MSIV) exceeded the Technical Specification (TS) individual MSIV leakage limit of Surveillance Requirement (SR) 3.6.1.3.12 on March 4, 2023, based on subsequent evaluation. On March 21, 2023, engineering concluded that a reasonable expectation of operability for the C outboard MSIV [SB][ISV] was not met and operators declared the valve inoperable in accordance with TS 3.6.1.3 Condition E. During a planned maintenance outage on March 26, 2023, the 10 CFR 50, Appendix J Local Leak Rate Test (LLRT) as-found leakage for the C outboard MSIV was 987.1 standard cubic feet per hour (scfh) which exceeded the 100 scfh limit of SR 3.6.1.3.12 for individual MSIV leakage (when tested at greater than or equal to 44.1 psig). This condition is being reported within 60 days from the date of discovery, March 21, 2023, in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the TSs as discussed in the event analysis. Chronology In May 2021, the as-left LLRT leakage from the 2021 Refuel Outage (RFO) for the C outboard MSIV was 33.9 scfh. In June 2021 a packing leak on this valve was identified and an Adverse Condition Monitoring Plan established to monitor the leak. On March 4, 2023, packing material was observed on camera being ejected from the packing gland on this valve. On March 10, 2023, a four-degree Fahrenheit step change increase in main steam chase temperature occurred. On March 14, 2023, at 1645 hours, due to an increase in leakage, operators entered the procedure for steam leaks outside primary containment, and on March 16, 2023, a prompt operability determination was requested. On March 18, 2023, the C inboard MSIV was closed to isolate the leak. On March 21, 2023, engineering concluded that a reasonable expectation of operability for the C outboard MSIV was not met due to the estimated leakage, and operations declared the valve inoperable in accordance with the TS 3.6.1.3 Condition E. It was concluded that March 4, 2023, was likely the date the TS individual MSIV leakage limit had been exceeded. On March 26, 2023, during the maintenance outage the as-found LLRT for the C outboard MSIV was 987.1 scfh which exceeded the 100 scfh limit of SR 3.6.1.3.12 for individual MSIV leakage (when tested at greater than or equal to 44.1 psig). Following repacking of the C outboard MSIV during this outage an as- left LLRT leakage rate of 67.7 scfh was measured. The C main steam line was returned to service with startup from the maintenance outage until the 2023 RFO began. During the 2023 RFO the C outboard MSIV packing gland was bored out to provide additional clearance and the valve stem was replaced, and the valve tested satisfactorily. EVENT ANALYSIS The event was determined to be reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), “Any operation or condition which was prohibited by the plant's Technical Specifications.” Specifically, this occurrence is reportable as a condition prohibited by Specification 3.6.1.3, "Primary Containment Isolation Valves," because the MSIV had exceeded the individual leakage limit and had been inoperable for greater than the 8 hour Completion Time of Condition E and for greater than the Completion Times specified in Limiting Condition for Operation (LCO) 3.0.3, i.e., to be in Mode 2 within 7 hours, Mode 3 within 13 hours, and Mode 4 in 37 hours, respectively, when Condition E was not met. This event is not classified as a safety system functional failure since the C inboard MSIV was fully operational. | ML23137A275 | 0 | good
Susquehanna Steam Electric Station (SSES) | Unit 2 | Inadvertent Contact Between Relay Cover and Relay Trip Contacts Resulted in Automatic Actuation of the ‘B’ Emergency Diesel Generator | 05-22-2023 | On March 23, 2023, while reinstalling a relay cover on Engineered Safeguard System (ESS) Bus 2A202, inadvertent contact was made between the target reset lever on the relay cover and the relay trip contacts. This resulted in a trip of all 4.16 kV breakers on the 2B ESS Bus 2A202, an ESS bus lockout, and automatic start of the ‘B’ Emergency Diesel Generator (EDG). This condition is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in manual or automatic actuation of any system listed in 10 CFR 50.73(a)(2)(iv)(B). This event was also reported via Event Notification 56430 in accordance with 10 CFR 50.72(b)(3)(iv)(A). The cause of the event was a momentary loss of focus on the relay target reset lever during reinstallation of the relay cover. This cause was attributed to a human performance error. Additional investigation concluded the potential impacts of an inadvertent error associated with the relay reinstallation activities were not adequately mitigated. Corrective actions included performing accountability per station procedures and planned procedure revisions to include continuous use checklists identifying removal and restoration work steps associated with relays that have the potential to trip protective devices. There were no actual consequences to the health and safety of the public. NRC FORM 366A U. S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (03-14-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported r¥·1 lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. i,.,, ·~- ../ CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to ,.. Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW (See NUREG-1022, R.3 for instruction and guidance for completing this form https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME ~ 050 2. DOCKET NUMBER YEAR 3. LER N SE U Q M U B E E N R TI AL REV NUMBER NO. Susquehanna Steam Electric Station (SSES) □ 052 05000388 2023 - 001 - 00 Unit 2 | CONDITIONS PRIOR TO EVENT Unit 1 – Mode 1, approximately 100 percent Rated Thermal Power (RTP) Unit 2 – Mode 5, zero percent RTP The described activity was performed during the Division 2 electrical maintenance outage with Division 1 systems protected. There were no structures, systems, or components that were inoperable at the start of the event and contributed to the event. EVENT DESCRIPTION On March 23, 2023, while reinstalling a relay cover on Engineered Safeguard System (ESS) [EIIS System Code: B] Bus 2A202 [EIIS System/Component Code: E/BU], inadvertent contact was made between the target reset lever on the relay [EIIS Component Code: RLY] cover and the relay trip contacts. This resulted in a trip of all 4.16 kV breakers [EIIS Component Code: BKR] on the 2B ESS Bus 2A202, an ESS bus lockout, and automatic start of the ‘B’ Emergency Diesel Generator (EDG) [EIIS System/Component Code: EK/DG]. The ‘B’ EDG operated as expected. The following timeline demonstrates the sequence of events: 03/23/2023 ~ 15:45: Relay and Test lead technician conducted a pre-job brief for critical relay calibrations on ESS Bus 2A202. 03/23/2023 ~ 16:15 – 17:00: Technicians arrived at the work area and performed a two minute drill. Removal, calibration, and reinstallation of the A-phase bus differential relay was completed. 03/23/2023 ~ 17:00 – 17:30: Removal and calibration activities for the B-phase bus differential relay was completed. 03/23/2023 ~ 17:33: During installation of the relay cover, inadvertent contact was made between the target reset lever on the relay cover and the relay contacts. This resulted in a trip of the 2B Bus lockout relays which opened all the bus supply breakers and started the ‘B’ EDG. 3/23/23 ~ 17:37: All work was stopped and the Unit 2 control room was contacted. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in manual or automatic actuation of any system listed in 10 CFR 50.73(a)(2)(iv)(B). This event was also reported via Event Notification 56430 in accordance with 10 CFR 50.72(b)(3)(iv)(A). CAUSE OF EVENT The cause of the event was a momentary loss of focus on the relay target reset lever during reinstallation of the relay cover. This cause was attributed to a human performance error. Additional investigation concluded the potential impacts of an inadvertent error associated with the relay reinstallation activities were not adequately mitigated. Page 2 of 3 | ML23142A269 | 0 | good
i | Unknown Unit | Reactor Protection System Half Scram due to Motor Generator Set Output Breaker Trip | 05-25-2023 | On May 31, 2021, LaSalle Unit 2 was operating at 100 percent power, when the 2A reactor protection system (RPS) motor generator (MG) set output breaker tripped due to an overload condition, which resulted in a loss of 2A RPS bus. Loss of power to this bus created a half-scram and initiated closure of outboard isolation valves in multiple systems. The condition was an invalid actuation because it was not the result of actual plant conditions and not an intentional manual action. Actuations and isolations that occurred performed as designed, except for the outboard 2D main steam line isolation valve (MSIV) drain valve that was discovered later as having a slow closure time, rendering the component inoperable. The cause of the MG set breaker trip was a degraded voltage adjustment potentiometer on the associated MG set, which caused the output voltage to fluctuate. The RPS bus loss resulted in general containment isolation signals that affected containment isolation valves in more than one system while the unit was critical. Therefore, the condition is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). The cause of the MSIV drain valve slow closure was motor and bearing degradation from a nearby steam leak. There was no loss of safety function since an inboard isolation valve in the flow-path remained operable. However, the condition is reportable in accordance with 1O CFR 50. 73(a)(2)(i)(B) as an operation or condition prohibited by technical specifications (TS) due to having an inoperable component longer than permitted by TS. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory coUection request 80 hours. Reported .,,.. .. 1110"<-. lessons learned are incorporated into the licensing process and fed back to industry. Send comments (w,,.r..:.:1) regarding burden estimate to the FOIA, Libfary, and lnfonnation Collections Branch (T-6 A1 0M), U.S. LICENSEE EVENT REPORT (LER) Nudea.< Regulatory Commission, Washington, DC 20555-0001, or by e-mail to \~'~!~~/ CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at 0MB Office of lnfonnation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nudear Regulatory Commission, 725 17th Street NW. '1 ••••• Washington, DC 20503; e-mail: oira submission@lomb eoo gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of infonnation unless the document http://WfiW nrc.govtreadjng-rm/doc-coIIectjonstnuregs/s1afftsr1022/QD requesting or requiring the collection displays a currenUy valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR LaSalle County Station, Unit 2 05000- 374 NUMBER NO. 2021 002 02 | Plant and System Identification LaSalle Country Station Unit 2 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the "A" reactor protection system (RPS) logic and associated isolation functions. RPS initiates a rapid insertion of all the control rods (scram) when monitored variables exceed their pre-established limits, neutron flux instrumentation becomes inoperable, or a manual scram signal is inserted by the operator. In addition, the setpoints, power sources, and controls and instrumentation are arranged in such a manner as to preclude spurious scrams. Condition Prior to Event Unit(s): 2 Date: May 31, 2021 Time: 19:26 CDT Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 100 percent Description On May 31, 2021, the main control room (MCR) operating crew received an "A" RPS half scram due to loss of power to Unit 2 "A" (2A) RPS bus. The operating crew entered applicable abnormal operating procedure for the RPS power condition. Field operators determined that the 2A RPS MG set output breaker had overloaded and tripped. The loss of the power to the 2A RPS bus resulted in a half scram and closure of outboard isolation valves in multiple systems. The condition was considered an invalid actuation because it was not the result of a valid signal and not an intentional manual action. The actuations and isolations that occurred performed as designed except for the closure time of outboard main steam line isolation valve (MSIV) drain valve 2821-F067D. RPS MG Set The 2A RPS bus loss resulted in isolations of the reactor water cleanup system, main steam line (MSL) drains, RCS sampling, instrument nitrogen system, reactor recirculation hydraulic power unit outboard isolation valves, and containment monitoring valves. The condition also resulted in loss of power to portions of the average power range monitor, local power range monitor, oscillating power range monitor, control rod block systems; as well as portions of the radiation monitoring for main steam lines, reactor building ventilation, and fuel pool ventilation. Appropriate actuations and primary containment isolations occurred as designed. Due to the 2A RPS bus loss of power, applicable technical specification (TS) timeclocks were entered. Power was restored to 2A RPS bus in accordance with station procedures by transferring 2A RPS bus to the alternate power supply and resetting the half scram. When power was restored and the isolations were reset, the affected equipment was returned to operable status and timeclocks were exited. MSIV Drain Valve Position indication was lost on the Unit 2 "D" outboard MSIV drain valve (2821-F067D) while power was being restored. This condition caused the station to enter TS Required Action (RA) to restore required post-accident monitor (PAM) instrumentation channel within 30 days. Position indication was restored after a reset of thermal breaker overloads. The 2D MSIV drain valve indicated in the closed position, verifying it performed its design function when 2A RPS power had been lost. Subsequently, during reviews of computer traces from the loss of 2A RPS bus event, this valve was found to have exhibited closure time in excess of maximum isolation time limits specified in the technical requirements manual (TRM) and was declared inoperable as a primary containment isolation valve (PCIV). The station entered TS required actions to isolate the affected penetration flow path by use of at least one closed and de-activated automatic valve in four hours and to verify the affected penetration flow path is isolated once per 31 days. There was no loss of safety function as the penetration has two PCIVs in the flow-path, and the inboard PCIV remained operable. | ML23145A012 | 0 | good
edwin i. hatch | Unknown Unit | - .. Unit 2 Manual SCRAM due to trip of both Reactor Recirculation Pumps -- | 05-26-2023 | On March 31, 2023 at 1430, with Unit 2 in mode 1 at 97 percent power, the reactor was manually tripped due to a loss of both recirculaion pumps. The recirculation pumps tripped due to a loss of the 2A and 2B Adjustable Speed Drives (ASOs). All safety equipment responded as expected. · The cause of the ASD trip was due to the high speed stops for the ASDs being set at a value greater than the over frequency relay trip setpoints. This resulted in the relay over frequency trip setpoint being reached prior to the ASD High Speed Stops when increasing ASD speed. To correct the issue, the ASD High Speed Stop setpoints values were returned to values less than the relay setpoint, to ensure the drive will not be able to be raised to a speed that would result in a trip due to over frequency. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual actuation of the reactor protection system. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/io23 (03-14-2023) Estimated burden per re.sponse to comply with this mandatory coHection request 80 hours. Reportea LICENSEE EVENT REPORT (LER) l r e e s g s a o rd ns in g le a b r u n r e d d en a r e e s t i i n m c a o t r e p o to ra t t h e e d F in O to IA !h , e L ib lic ra e , n y s , in a g n d p r In o f c o e r s m s a a ti n o d n f C ed ol l b e a ct c io k n to s B in r d a u n s c t h ry . ( T S -6 e n A d 1 0 o M om ), m U e . n S ts . CONTINUATION SHEET Nudoar Regulatory Commission, Washington, DC 20555--0001, or by email lo lnfocoUects.Resource@nrc.gov, and lhe 0MB reviewer at 0MB Office of lnfonnation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for lhe Nudear Regulatory Commission, 725 17111 Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; email: oinuubmissloo@omb oop,gov. The NRC may not conduct or bltp://www.nrc.gov/reading-rmld~l~ctions/nuregs/staff/sr10221c3/} r s e p q o u n e s s o t r i , n g a n o d r r a e q p u e i r r s in o g n lh is e n c o o t l l r e e c q ti u o i n re d d i s to p la re ys s p a o c n u d r r t e o n , U a y c v o a ll li e d c t 0 io M n B o f c o in n fo tr n o n l n a u ti m on b e u r n . l ess lhe doC1JmcnI , E 1. d - w FA in C - I I L . - IT H Y a - N tc A h - M N E u - clear - Plan - t Un - it 2 ------, 0 ■ 0 050 2. DOCKET NUMBER ~ YEA M R , 3 S . E L Q E U R E N N U TI M A B i.. E R REV I □ NUMBER INGNO. □ 052 00366 I 002 | EVENT DESCRIPTION On March 31, 2023 at 1430, with Unit 2 in MODE 1 at 97 percent power, the reactor was manually tripped due to a loss of both recirculation pumps [EIIS Code: AD]. The recirculation pumps tripped due to a loss of the 2A and 2B Adjustable Speed Drives (ASDs) [EIIS Code: AD, SC]. Over frequency relays [EIIS Code: AD,81] associated with the ASD's actuated at their trip setpoints based on recirculation pump motor speed. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual actuation of the reactor protection system. EVENT CAUSE ANALYSIS Causal analysis revealed that the 2A and 2B ASDs tripped due to actuation of over frequency relays when recirculation pump motor speed reached the actuation setpoints. System parameters for the 2A and 28 ASD were reviewed and found that during implementation of a design modification the high speed stop setpoints for the ASD's were set higher than the over frequency relay trip setpoints. The conflicting setpoints is the reason the over frequency trip setpoint was reached prior to the ASD high speed stops and resulted in the ASD trips. SAFETY ASSESSMENT There were no actual safety consequences as a result of this event. The Recirculation Pumps tripped as designed to prevent damage due to overspeed. A manual scram was inserted as required by procedures and the reactor protection system worked as expected. Pressure was controlled by EHC and Bypass valves. CORRECTIVE ACTIONS To correct the issue the ASD High Speed Stop setpoint values were adjusted lower than the over frequency relay trip setpoint. This change ensures the drive is not able to be raised to a speed that will result in a premature over frequency trip. PREVIOUS SIMILAR EVENTS None | ML23146A191 | 0 | good
Susquehanna Steam Electric Station (SSES) | Unit 1 | Unplanned lnoperability of the High Pressure Coolant Injection (HPCI) System due Failure of the HPCI Turbine Stop | 08-31-2023 | On April 07, 2023, at approximately 20:52, during performance of the weekly Unit 1 High Pressure Coolant Injection (HPCI) Lube Oil System Functional Test, the HPCI Turbine Stop Valve failed to stroke fully closed as designed. Upon discovery of the condition, Operations entered Unit 1 Technical Specification (TS) 3.5.1, "ECCS [Emergency Core Cooling Systems]-Operating," Condition D for HPCI System inoperable. Operations exited TS 3.5.1, Condition D on April 08, 2023, at approximately 15:54 following valve cleaning and lubrication and satisfactory post maintenance testing. The cause of the HPCI Turbine Stop Valve failing to fully close was most likely internal corrosion and mechanical binding of the valve hydraulic drive mechanism caused by condensation from a steam leak past the HPCI Turbine Steam Supply Valve seat accumulating on the HPCI Turbine Stop Valve and dripping onto the hydraulic operating cylinder. The failure of HPCI Turbine Stop Valve as a result of the steam leak past the HPCI Turbine Steam Supply Valve seat was a previously unrecognized failure mode in the station's assessment of he steam leak, and therefore was not properly mitigated. Key corrective actions include repair of the HPCI Turbine Stop Valve and hydraulic operating cylinder and replacement of the HPCI Turbine Steam Supply Valve. In the interim, condition monitoring will be informed by weekly inspection of the HPCI Turbine Stop Valve. This event was reported by Event Notification 56458 in accordance with 10 CFR 50.72(b)(3)(v)(D). The condition is also being reported in accordance with 1O CFR 50. 73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of a safety function. There were no actual consequences to the health and safety of the public as a result of this event. U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory (See NUREG-1022, R.3 for instruction and guidance for completing this form Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 72517th Street NW https:/lwwN.nrc.gov/readinq-rm/doc-collections/nuregs/staff/sr1022/r3D Washington, DC 20503; email: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME ~ 050 2. DOCKET NUMBER 3. LERNUMBER YEAR SEQUENTIAL REV NUMBER NO. Susquehanna Steam Electric Station (SSES) D 052 05000387 2023 - 002 - 00 Unit 1 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, approximately 100 percent Rated Thermal Power (RTP) Unit 2 - Mode 5, zero percent RTP There were no structures, systems, or components that were inoperable at the start of the event and contributed to the event. EVENT DESCRIPTION On April 07, 2023, at approximately 20:52, during performance of the weekly Unit 1 High Pressure Coolant Injection (HPCI) [EIIS System Code: BJ] Lube Oil System Functional Test, the HPCI Turbine Stop Valve [EIIS Component Code: SHV] failed to stroke fully closed as designed. Upon discovery of the condition, Operations entered Unit 1 Technical Specification (TS) 3.5.1, "ECCS [Emergency Core Cooling Systems]- Operating," Condition D for HPCI System inoperable. Operations exited TS 3.5.1, Condition D on April 08, 2023, at approximately 15:54 following valve cleaning and lubrication and satisfactory post maintenance testing. This event was reported by Event Notification 56458 in accordance with 1O CFR 50. 72(b)(3)(v)(D). The condition is also being reported in accordance with 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of a safety function. CAUSE OF EVENT The cause of the HPCI Turbine Stop Valve failing to fully close was most likely internal corrosion and mechanical binding of the valve hydraulic drive mechanism caused by condensation from a steam leak past the HPCI Turbine Steam Supply Valve [EIIS Component Code: V] seat accumulating on the HPCI Turbine Stop Valve and dripping onto the hydraulic operating cylinder. The failure of HPCI Turbine Stop Valve as a result of the steam leak past the HPCI Turbine Steam Supply Valve seat was a previously unrecognized failure mode in the station's assessment of the steam leak, and therefore was not properly mitigated. ANALYSIS/SAFETY SIGNIFICANCE The condition described herein rendered the Unit 1 HPCI System inoperable. HPCI and Automatic Depressurization System (ADS) are independent high pressure ECCS. With HPCI rendered inoperable, the high pressure ECCS function would be fulfilled by ADS. During the period that HPCI was inoperable, both divisions of ADS were operable and available to fulfill the high pressure ECCS function. Since the high pressure ECCS function was maintained, the condition did not represent a safety system functional failure. Accordingly, this event will not be counted as a safety system functional failure in the Reactor Oversight Process Performance Indicators. There were no actual consequences to the health and safety of the public as a result of this event. | ML23157A176 | 0 | good
Browns Ferry Nuclear Plant | Unit 1 | High Pressure Coolant Injection System Inoperable Due to a Torn Valve Diaphragm | 06-13-2023 | On January 24, 2023 at 0121 CST, the Browns Ferry Nuclear Plant, Unit 1, High Pressure Coolant Injection (HPCI) was declared inoperable because the normally-open HPCI Steam Line Condensate Outboard Drain Valve failed closed, apparently due to a failed diaphragm. On January 24, 2023, at 0743 CST, eight-hour Event Notification 56321 was made to the NRC. The Tennessee Valley Authority (TVA) is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(v)(D), as any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. The diaphragm prematurely failed due to a part manufacturing issue, which led to the local delamination between the fabric and the ethylene propylene diene monomer (EPDM) material, in conjunction with a lack of complete reinforcement fabric coverage at the tear site. The failed diaphragm was replaced. TVA will proactively replace the diaphragms on Browns Ferry Nuclear Plant Units 2 and 3. HPCI Steam Line Condensate Outboard Drain Valve diaphragms will be reclassified and reprocured as QA 1 components, and any existing QA 3 diaphragms will be reclassified as obsolete. r"' f \: .... :; I I □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ ~ □ □ □ □ □ I I I I I I I I I I I I I I I I I I I I I ~ ID I I NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION (03-14-2023) LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME ☒ 050 2. DOCKET NUMBER 3. LER NUMBER Browns Ferry Nuclear Plant, Unit 1 00259 YEAR SEQUENTIAL NUMBER REV NO. ☐ 052 2023 - 001 - 01 | Not Found | ML23164A134 | 1 | ok
Brunswick Steam Electric Plant (BSEP) | Unit 1 | Loss of Redundant Power Supply Operation Causes Turbine Trip and Subsequent Reactor Scram | 06-15-2023 | At 01:48 Eastern Daylight Time (EDT) on April 20, 2023, with Unit 1 in Mode 1 at approximately 100% power, an automatic reactor scram occurred due to a turbine trip. All control rods inserted as expected. Turbine bypass valves did not open on the scram; Safety Relief Valves (SRVs) opened automatically to control reactor pressure. Reactor Pressure reached approximately 1100 psig on the scram, exceeding the Reactor Protection System (RPS) setpoint. Reactor water level reached low level 1 following the scram resulting in automatic actuation of Primary Containment Isolation System (PCIS) Group 2, 6, and 8 isolation valves, by design. Operations responded and stabilized the plant. Operations transitioned pressure control from SRVs to main steam line drains to the condenser. Following the scram, reactor water level was maintained via the condensate and feedwater systems. The turbine trip and subsequent inoperative turbine bypass valves resulted from a complete loss of 24 Vdc power to the Turbine Protection system. The power supplies were replaced prior to restart. There was no impact on the health and safety of the public or plant personnel. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) due to valid actuation of the RPS and PCIS. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (03-14-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 SEQUENTIAL REV YEAR NUMBER NO. Brunswick Steam Electric Plant (BSEP), Unit 1 00325  052 2023 - 001 - 00 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. Background Initial Conditions At the time of the event, Unit 1 was in Mode 1 (i.e., Power Operation), at approximately 100 percent rated thermal power. Reportability Criteria This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) because it involved actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B). Specifically, the Reactor Protection System [JC] and Primary Containment Isolation System [JM] actuated during this event. The NRC was notified of this event per 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) via Event Notification 56478 at 05:24 Eastern Daylight Time (EDT) on April 20, 2023. Event Description At 01:48 Eastern Daylight Time (EDT) on April 20, 2023, with Unit 1 in Mode 1 at approximately 100% power, an automatic reactor scram occurred due to a turbine trip. All control rods inserted as expected. The turbine bypass valves [JI] did not open on the scram; main steam [SB] Safety Relief Valves (SRVs) 1C, 1F, 1G, 1K, and 1L cycled open automatically to control reactor pressure. Reactor pressure reached approximately 1100 psig on the scram; exceeding the 1060 psig Reactor Protection System (RPS) setpoint. Reactor water level reached the low level 1 (LL1) setpoint following the scram. Per design, the LL1 signal resulted in Primary Containment Isolation System Group 2 (i.e., floor and equipment drain isolation valves), Group 6 (i.e., monitoring and sampling isolation valves) and Group 8 (i.e., shutdown cooling isolation valves) isolations. Operations responded and stabilized the plant. Operations manually cycled open SRV 1B then transitioned pressure control from SRVs to the main steam line drains [SB] to the condenser [SG]. Following the scram, reactor water level was maintained via the condensate [SD] and feedwater [SJ] systems. Event Cause The direct cause of the turbine trip and subsequent inoperative turbine bypass valves was a complete loss of 24 Vdc power to the Turbine Protection system [JJ]. When 24 Vdc power was lost, Turbine Protection system data inputs for required pressure and flow transmitters were lost. With the loss of monitoring capability, the Turbine Protection system responded as designed by initiating a turbine trip to protect the turbine and inhibiting the opening of the turbine bypass valves to protect the condenser. 24 Vdc power is supplied to the Turbine Protection system via redundant power supplies [RJX]. Due to inadequacies in the vendor design, a unique combination of internal component failures on one power supply impacted the operation of the redundant power supply. As a result, both power supplies failed/shutdown within a short timeframe of one another resulting in a total loss of 24 Vdc power. | ML23166A081 | 0 | good
LaSalle County Station | Unit 1 | Not Found | 06-16-2023 | During station surveillance testing, the Low Pressure Core Spray (LPCS) pump discharge flow differential pressure switch malfunctioned, preventing the LPCS pump minimum flow valve from opening on a low flow condition. As a result the LPCS pump was declared inoperable. The cause of the differential pressure switch failure was water leakage into the switch electrical housing caused by a failure of the shaft seal. The faulty switch was replaced and the LPCS pump was restored to operable status. This condition could have prevented the LPCS system from performing its safety function. This condition is reportable in accordance with 10 CFR 50. 73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. There were minimal safety consequences associated with the condition since other emergency safety systems remained operable. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 12/31/2023 (01-10-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A1 0M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira submission@omb.eop.gov. The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.n re.gov/read inq-rm/d oc-colleclions/nu regs/staff/sr1 022/r3/) requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER (cid:127) 050 SEQUENTIAL REV YEAR LaSalle County Station, Unit 1 (cid:143) 373 NUMBER NO. 052 2023 - 01 - 00 | LaSalle County Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The Low Pressure Core Spray (LPCS) system is part of the Division 1 Emergency Core Cooling System (ECCS). LPCS provides low-pressure coolant into the reactor core under accident conditions. The LPCS minimum flow switch, 1 E21- N004, monitors pump discharge flow. This flow switch initiates opening and closing the of LPCS minimum flow valve, 1E21-F011. Condition Prior to Event Unit(s): 1 Date: April 17, 2023 Time: 0246 CDT Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 100% Description At 0246 CDT on April 17, 2023, it was discovered that the single train Low Pressure Core Spray (LPCS) system was inoperable. To support Reactor Core Isolation Cooling (RCIC) surveillance testing, the LPCS pump was started for suppression pool mixing. When attempting to secure the LPCS pump, the LPCS minimum flow valve did not open on low flow as expected. It was identified that the pump discharge flow differential pressure switch had failed causing the minimum flow valve to not perform its design function. This resulted in inoperability of the LPCS pump. LPCS was declared inoperable and the appropriate Technical Specification (TS) required actions were entered in accordance with TS 3.5.1, "ECCS - Operating" and TS 3.3.5.1, "Emergency Core Cooling System (ECCS) Instrumentation." Cause The cause of the switch failure is process water intrusion into the switch electrical housing. The water intrusion was caused by a failure of the low pressure side u-cup seal around the shaft from the sensing element. Reportability and Safety Analysis There were minimal safety consequences associated with the condition since other emergency safety systems remained operable during the period of LPCS inoperability. This event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(D) as an event or condition that condition that could have prevented fulfillment of a safety function of structures or systems that are needed to mitigate the consequences of an accident. An 8 hour ENS report was made to the NRC at 0937 EDT on April 17, 2023 (EN# 56471 ). Safety System Functional Failure Review The condition is a safety system functional failure (SSFF) defined in accordance with NEI 99-02, Regulatory Assessment Performance Indicator Guidance. The failure of the 1 E21-N004 switch caused the minimum flow valve to not open when required. NRG FORM 366A (01-10-2023) Page_2_ of _3_ | ML23167A071 | 1 | ok
LaSalle County Station | Unit 2 | Manual Scram due to lsophase Bus Duct Fire followed by 2A RPS Normal Power Supply Trip | 06-16-2023 | 12. Licensee Contact for this LER Licensee Contact rhone Number (Include area code) CJ Smith, Operations Director (815) 415-2200 13. Complete One Line for each Component Failure Described in this Report Cause System Component Manufacturer Reportable to IRIS Cause System Component Manufacturer Reportable to IRIS X EF RHE 0026 y B EL IPBU D312 y 14. Supplemental Report Expected Month Day Year I 15. Expected Submission Date [8J No D Yes (If yes, complete 15. Expected Submission Date) 6. Abstract (Limit to 1560 spaces, i.e., approximately 15 single-spaced typewritten lines) At 0238 CDT on September 26, 2022 with Unit 2 in Mode 1 at 100 percent power, a manual scram was initiated due to a reported fire on the isophase bus duct. The scram was uncomplicated with all systems responding normally with the exception of a loss of 2A reactor protection system (RPS) normal power supply. The 2A RPS normal power supply output breaker tripped on over voltage. Operations successfully transferred 2A RPS power to the alternate power supply. The fire was reported extinguished at 0240 CDT on September 26, 2022. The cause of the 2A RPS loss of normal power was a degraded voltage adjust potentiometer (POT) on the output breaker. The cause of the isophase bus duct (IPBD) fire was incorrect joint compound having been supplied and subsequently used during planned maintenance, resulting in high resistances at the shunt bolted connections. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimaled burden per response lo comply with this mandalory collection request· 80 hours. Reported lessons learned are incorporated inlo the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S LICENSEE EVENT REPORT (LER) Nuclear Regulalory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollecls.Resource@nrc.gov, and the 0MB reviewer al: 0MB Office of Information and Regulalory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulalory Commission, 72517th Street NW, Washington, DC 20503; e-mail: oira submission@ombeop.gov. The NRG may nol conducl or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/readinq-rm/doc-col lections/nu regs/staff/sr1 022/r3/l requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV LaSalle County Station, Unit 2 05000- 374 NUMBER NO. 2022 - 003 02 | Plant and System Identification LaSalle County Station Unit 2 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected systems were the Main Power system (MP) and the Reactor Protection System (RPS). The MP system provides safe and reliable distribution of electrical power from the Main Generator to the off-site transmission network. RPS initiates a rapid insertion of all the control rods (scram) when monitored variables exceed their pre-established limits, neutron flux instrumentation becomes inoperable, or a manual scram signal is inserted by the operator. In addition, the setpoints, power sources, and controls and instrumentation are arranged in such a manner as to preclude spurious scrams. Condition Prior to Event Unit(s): 2 Date: September 26, 2022 Time: 0238 CDT Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 100% Description Fire and manual scram Electrical Maintenance personnel identified smoke coming from the general area in the Unit 2 Turbine Building that contains the Unit 2 isolated phase bus duct and notified the Main Control Room (MCR). The Field Supervisor was dispatched and at 0230 CDT they notified the MCR that there was visible sparks, smoke and indications of a fire from the bus duct enclosure. Operations dispatched the fire brigade and entered abnormal operations procedures for a fire. The unit was manually scrammed at 0238 CDT. The brigade was able to successfully gain control of the fire using dry chem and the fire was reported extinguished at 0240 CDT. 2A RPS Breaker trip Following the Manual Scram, the 2A RPS Breaker normal feed tripped on overvoltage. All Primary Containment isolations occurred as expected following the loss of A RPS power. Operations entered abnormal operating procedures, swapped 2A RPS power to the alternate feed and restored containment isolations. Cause The cause of the isophase bus duct (IPBD) fire was incorrect joint compound having been supplied and subsequently used during the planned maintenance performed during the previous Unit 2 refueling outage in 2021. This resulted in high shunt bolted connection resistance causing overheating in the bolted connections. The overheating resulted in a failure of the IPBD support structure hardware and ignition of the retractable cover neoprene gasket. The cause of the 2A RPS Breaker trip was a degraded voltage adjust potentiometer. Reportability and Safety Analysis Fire and manual scram The fire was extinguished in less than 15 minutes of identification and the reactor was safely shutdown. Offsite power sources and station emergency power sources were available at all times throughout the event. Emergency response personnel acted promptly to extinguish the fire and there was no personnel injury during this event or damage to plant property from the fire other than the bus duct itself. | ML23167A076 | 0 | good
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Emergency Diesel Generator Fuel Oil Supply Procedure Error “B” Subsystem | 06-23-2023 | On April 24, 2023, with the James A. FitzPatrick Nuclear Power Plant (JAF) at 100 percent power, Operators identified that the “B” Emergency Diesel Generator (EDG) subsystem fuel oil supply table in surveillance test (ST) ST-9AB contained incorrect information. This ST is performed to satisfy Surveillance Requirement (SR) 3.8.3.1. Due to the incorporate information contained in the ST, some previous SR performances for EDG fuel oil tanks 93TK-6B and 93TK- 6D resulted in fuel quantities that should have led to surveillance testing not meeting acceptance criteria. Therefore, circumstances for an operation prohibited by Technical Specifications occurred, reportable in accordance with 10 CFR 50.73(a)(2)(i)(B); and when reviewed with overlapping maintenance periods on the “A” EDG subsystem a condition that could have potentially prevented the fulfillment of a safety function, reportable per 10 CFR 50.73(a)(2)(v)(A), occurred. The cause of the event was an administrative error during the procedure revision to a new format. Once recognized, prompt action was taken to restore fuel oil quantities to meet surveillance test acceptance criteria. Corrective actions have been completed to perform a revision to the ST, completed an extent of condition on operations STs, and performance an engineering evaluation to determine the impact to safety function. NRC FORM 366 (08-2020) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (03-14-2023) Estimated burden per response to comply with this mandatory collection request: 80 LICENSEE EVENT REPORT (LER) hours. Reported lessons learned are incorporated into the licensing process and fed CONTINUATION SHEET back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB controlnumber. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 YEAR SEQUENTIAL REV NUMBER NO. James A. FitzPatrick Nuclear Power Plant 05000333  052 2023 – 003 – 00 | Background The Emergency Onsite Power Supply System [EIIS identifier: EK] consists of two redundant Emergency Diesel Generator (EDG) [DG] subsystems. Each EDG subsystem consists of two EDG units. Each EDG is provided with an independent Fuel Oil Storage and Transfer System [DE] consisting of a Diesel Fuel Oil Storage Tank (FOST), a Diesel Fuel Oil Day Tank (FODT) and two full-capacity motor-driven Fuel Oil Transfer Pumps. The Fuel Oil Transfer Pumps provide the capability to transfer fuel from the FOST to the FODT. Stored diesel fuel oil is required to have sufficient supply for 7 days of full load operation. This requirement, in conjunction with an ability to obtain replacement supplies within 7 days, supports the availability of EDGs required to shut down the reactor and to maintain it in a safe condition for an abnormal operational transient or a postulated Design Bases Accident with loss of power. Technical Specification (TS) Surveillance Requirement (SR) 3.8.3.1 verifies the capacity of the FOST. The acceptable quantity is calculated for each FOST and accommodates different fuel properties for American Petroleum Institute (API) gravity and tank geometry. SR 3.8.3.1 is performed monthly by procedure ST-9AB, EDG System B Fuel/Lube Oil Monthly Test, for the “B” EDG subsystem for FOST tanks 93TK-6B and 93TK-6D. Event Description On April 24, 2023, James A. FitzPatrick Nuclear Power Plant (JAF) was at 100% power, when a satisfactory performance of ST-9AB was reviewed by a Senior Reactor Operator (SRO) and the measured level was verified against the field support supervisor’s fuel ordering calculation spreadsheet, which recommended ordering fuel. The prompt investigation revealed the incorrect 6-day fuel oil supply table in place of the 7-day fuel oil supply table in ST-9AB. This procedure error affected the acceptable quantity of fuel oil in the “B” EDG subsystem, specifically, 93TK-6B and 93TK-6D FOST only. It was confirmed that procedure ST-9AA for the “A” EDG subsystem, 93TK-6A and 93TK-6C FOST, was not affected by this error and those fuel oil quantities met the required 7-day supply. Upon discovery, SR 3.8.3.1 was declared not met based on the required quantify of fuel oil being less than 7 days but greater than 6 days; the Limited Condition for Operation (LCO) 3.8.3 was declared not met on April 24 at 1406, a fuel delivery restored the required quantity, and the LCO was restored on April 25 at 0913. Event Analysis ST-9AB was converted to a electronic procedure with revision 9 on November 18, 2021. TS Bases 3.8.3 specifies a 6-day and a 7-day EDG Fuel Oil Supply table; however, these two tables were swapped. Between November 2021 and April 2023, this procedure error was effective. A review of records identified that the 7-day fuel oil supply requirement of SR 3.8.3.1 was not me for the “B” EDG subsystem between June 20, 2022 to September 12, 2022; November 7, 2022 to December 1, 2022; and March 27, 2023 to April 25, 2023. However, there was always a greater than 6-day supply. When SR 3.8.3.1 was not met, LCO 3.8.3 was not met. Action “A” states, when one or more EDGs with fuel oil level < a 7-day supply and > a 6-day supply in storage tank, then restore it within 48 hours. If this was not Page 2 of 4 | ML23174A067 | 0 | good
Fermi 2 | Unknown Unit | Loss of Mechanical Draft Cooling Tower Fan Brakes dming High Speeds Leads to Loss of Safety Function and Inoperability | 06-23-2023 | At 1145 Eastem Daylight Time (ED1) on March 23, 2023, it was detennined that all Mechanical Draft Cooling Tower (MDC1) fan brakes would not pe1fon11 theii· design function during a tomado due to the speed switch not functioning over its published voltage range. The MDCT fan brakes are required to prevent fan over speed from a design basis tomado. The MDCT fans are requii·ed to suppo1t operability of the Ultimate Heat Sink (UHS), and the service water subsystems. At the time of discovery, the provisions ofLiiniting Condition for Operation 3.0.9 were being utilized for loss of the "D" MDCT fan brakes (ban-ier loss) thus the 24-hotu· allowance for restoration of at least one division was entered. This supplement expands the repo1t to include applicability of 10 CFR 21.2(c). Coll'ective actions were taken to develop a design change and install a potentiometer on each MDCT fan speed control system retuming the MDCT fans, UHS and the service water subsystems to service on March 24, 2023. The fan brake system is only required for a tomado. No tomado watches or wamings occtu1·ed dtuing the timeframe when all MDCT fan brakes were nonfunctional. Since there was no credible threat of a tomado, the MDCT fans and associated UHS would have been capable of pe1fon11.ing cooling for the service water subsystems. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (03-14-2023) Estimated burden per response lo C0"1>IYw ith this mandatory collection request 80 hours. Reported lessons learned are inro,poraled into the licensing process and fed back lo industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate lo the FOIA, Library, and Information Collections Branch (Hi A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email lo CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; email: oira submission@omb.eop.gov. The NRC may not conduct ot sponsor, and a person is not required lo respond lo, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-eollections/nuregs/staff/sr1022/r3/} requesting or requiring the colection displays a cunenfly valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 I I YEAR SEQUENTIAL REV □ NUMBER NO. ~ -I 1-0 Fermi 2 00341 052 001 I | INITIAL PLANT CONDITIONS Mode-1 Reactor Power - 100 There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT At 0923 Eastern Daylight Time (EDT) on March 13, 2023, the Division 11 Residual Heat Removal Service Water (RHRSW) System [Bl] Mechanical Draft Cooling Tower (MDCT)[CTW] Fan "D" Brake [BRK], was declared inoperable due to loss of speed indication at high speeds, which was discovered during an over-speed protection system calibration. The loss of speed indication also affects the fan brake operability during a design basis accident (DBA) tornado event. Limiting Condition for Operation (LCO) 3.0.9 was invoked for loss of the MDCT fan brake (barrier loss) for fan "D". LCO 3.0.9 allows 30 days before declaring the supported system(s) inoperable and the LCO(s) associated with the supported system(s) not met. The MDCT fans are required to support operability of the Ultimate Heat Sink (UHS) [BS], and the brakes prevent the fans from experiencing over-speed from a design basis tornado as described in Updated Final Safety Analysis Report (UFSAR) Section 9.2.5.2.2. Technical Specification (TS) 3.7.2 requires the UHS reservoir to be operable in MODES 1, 2, and 3. The UHS operability requirements in MODES 4 and 5 are determined by the systems the UHS supports. The UHS reservoir is divided into two, one-half capacity reservoirs, corresponding to Division I and Division II. Each reservoir is the cooling source for that division's service water subsystem (e.g., the Emergency Diesel Generators (EDGs) [DG] cooling water [LG], Emergency Equipment Cooling Water (EECW) system [CC], Emergency Equipment Service Water (EESW), RHR [BO] system, Core Spray [BG] system). UHS Safety Functions are as follows: (1) Remove the heat rejected by the RHR heat exchangers after reactor shutdown, (2) Remove the heat rejected by the RHR heat exchangers after an accident, (3) Remove the heat rejected by the EECW heat exchangers and the diesel generator heat exchangers, and (4) Provide sufficient cooling water for at least 7 days to permit safe shutdown and cooldown of the reactor without makeup water and to maintain the reactor in a safe shutdown condition. A two-cell MDCT is located above each of the one-half capacity reservoirs. Each cell is equipped with a MDCT fan. Two MDCT fans above each one-half capacity reservoir are required for it to be considered operable. The "A" and "C" MDCT fans are in Division I and the "B" and "D" fans are in Division II. Troubleshooting determined the Dynalco speed switch [SIS] (model SST-2400A-1) did not function over its full voltage range. Vendor-published data shows the speed switch voltage range is Oto 50 root-mean-square Voltage (Vrms) (0 to 141.42 Volts Direct Current (VDC)). The actual field voltage measured during troubleshooting was approximately 8.5 VDC; therefore, the range of the speed switch fully encompassed the field condition and should have performed and activated the brakes during an overspeed event. Based on vendor discussion and troubleshooting during the event, a load resistance had to be installed for the switch to function over the operating voltage range of the circuit. The Dynalco speed switch is found on all four MDCT fans. During the cause analysis performed on May 25, 2023, it was determined that Engine Systems, Inc. (ESI), who purchased and assembled the Dynalco speed switch (model SST-2400A-1 ), had added a load resistor to the four speed switches during vendor testing to allow it to function over the full range. This modification was not tracked as a nonconformance to the purchase order.This modification was applied to all four of the controllers; thus, caused a common failure mode for all four of the MDCT Fans. ESI originally qualified and documented the switch with the additional load resistor, but mock-up testing by Fermi, ESI and Dynalco in March 2023 could not duplicate the qualification results. The switch with the added load resistor did not function over its full voltage range. As a result, this event is reportable under 10 CFR 21.2(c). | ML23177A043 | 0 | good
Limerick Generating Station | Unit 1 | Emergency Diesel Generator Lube Oil Pressure Sensing Line Leak Resulting in a Condition Prohibited by Technical Specifications | 06-26-2023 | On February 27, 2023, approximately 10 hours into a planned 24-hour endurance run for the 011 Emergency Diesel Generator (EOG), an oil leak was identified at a threaded fitting for an oil pressure indicator instrument line. The 011 EOG was emergently secured and declared inoperable. Subsequent investigation identified a crack in a threaded pipe nipple for the affected oil pressure indicator instrument line. Forensic analysis of the removed pipe nipple identified a crack initiated in the threaded fitting. The corrective action was to move the connection to a different location that does not experience high vibration. Although D11 EOG was not inoperable for greater than the allowed out of service time a second EOG was inoperable for greater than the allowed out of service time for two EDGs. This event is being reported as a condition prohibited by Technical Specifications (TS) in accordance with 10 CFR 50.73(a)(2)(i)(B). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection recuest: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and lnfonnation Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of lnfonnation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of infonnation unless the document http://www.nrc.gov/reading-rm/doc-col1ections/nuregs/staff/sr1022/r3/) requesting or recuiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER DYEA R SEQUENTIAL REV 05000-1 352 ~-I NUMBER NO. Limerick Generating Station Unit 1 I-~ I 001 | Unit Condition Prior to the event, Unit 1 was in Operational Condition (OPCON) 1 (Power Operation) at approximately 100% power. There were no structures, systems, or components out of service that contributed to this event. Description of the Event On February 27, 2023, during planned 24-hour endurance run of the D11 Emergency Diesel Generator (EOG) [EIIS-EK], an oil leak was identified at a threaded fitting for an oil pressure indicator instrument line. The one-quarter inch instrument line threaded connection tees off the 4-inch main lube oil piping near the discharge of the engine driven lube oil pump. The D11 EOG was started at 09:35 and fully loaded at 10:05. A dirty drip pan alarm came in at 19:42 and subsequently the lube oil leak was identified at 19:47. The EOG was secured and declared inoperable. Prior to the failure there was no leaks or degradation observed from the connection. The component was sent for failure analysis. The failure analysis identified a crack in a threaded pipe nipple for the affected oil pressure indicator instrument line. Forensic analysis of the removed pipe nipple concluded that the pipe nipple showed fatigue fracture that started from one side at the root of the last engaged thread, consistent with unidirectional cyclic bending loads due to vibration. The D11 EOG was determined to be inoperable from the last completed surveillance test on January 31, 2023, until restored to operable status following repair of the identified oil leak on February 28, 2023. Following the D11 EOG failure on February 27, 2023, vibration data was again collected on the 4-inch engine driven lube oil pump discharge piping. Comparison of this vibration data to vibration data previously collected for the D11 EOG in February 2020 concluded that the vibration signature of the piping had changed and that the D11 EOG was now susceptible to the same failure mechanism previously identified for the D24 EOG. Inspection of the pipe clamp on the 4- inch engine driven lube oil pump discharge piping adjacent to the instrument line connection identified that the nuts of the U-bolt clamp were not tight. A work order history review was completed, and no maintenance activity was identified that altered or adjusted the 4-inch engine driven lube oil pump discharge piping since vibration data was previously collected in February 2020. No engine operating data or maintenance activity could be cited as the cause for the change in the vibration signature of the 4-inch engine driven lube oil pump discharge piping other than vibration causing loosening of the U-bolt nuts. Analysis of the Event The failure analysis of the instrument line on the D11 EOG concluded the EOG was inoperable from the last completed surveillance test on January 31, 2023, until restored to operable status following repair of the identified oil leak on February 28, 2023. During the period that the D11 EOG was inoperable, the D13 EOG was also inoperable for approximately 7 days between, February 12, 2023, and February 19, 2023, for a planned system outage window. Based on the completion of the failure analysis and the component history review the condition was determined to reportable on April 27, 2023. | ML23177A232 | 0 | good
Brunswick Steam Electric Plant (BSEP) | Unit 2 | Two Main Steam Line Safety Relief Valves Inoperable | 08-31-2023 | On May 23, 2023, BSEP received test results for the eleven main steam line safety relief valves (SRVs) removed from Unit 2 during the spring 2023 refuel outage (RFO). Two of the eleven valves were found to have as found pilot valve lift setpoints outside the +/-3 percent tolerance required by Technical Specification (TS) 3.4.3, which requires ten of the eleven installed SRVs to be operable. All eleven of the SRV pilot valves were replaced with certified spares before Unit 2 startup from the spring 2023 RFO. At the time the test results were received, Unit 2 was operating in Mode 1 at approximately 100% power. Corrosion bonding of the SRV pilot disc to the pilot seat likely caused one of the out of tolerance as-found lift setpoints. The other out of tolerance lift setpoint was likely a result of a combination of degraded pilot valve assembly sub-components. Since less than ten SRVs were operable and the failure modes likely arose over a period of time during Unit 2 operation, this event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant’s TS. There was no impact on the health and safety of the public or plant personnel. (See Page 2 for required number of digits/characters for each block) (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION (03-14-2023) LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME  050  052 2. DOCKET NUMBER 3. LER NUMBER Brunswick Steam Electric Plant (BSEP), Unit 2 00324 YEAR SEQUENTIAL NUMBER REV NO. 2023 - 001 - 00 | Not Found | ML23199A224 | 1 | ok
Browns Ferry Nuclear Plant | Unit 1 | Full Reactor Scram due to an Oscillation Power Range Monitor Confirmation Density Algorithm Trip | 07-19-2023 | On May 20, 2023, at 0315 Central Daylight Time (CDT), while performing quarterly turbine control valve (TCV) testing at 80 percent reactor thermal power (RTP) and 70 percent core flow, Unit 1 automatically scrammed due to an Oscillation Power Range Monitor (OPRM) Confirmation Density Algorithm (CDA) trip. The plant responded to the reactor scram as expected and there were no human performance challenges during the turbine control valve testing or subsequent plant shutdown. The root cause of the event was determined to be that the sensitivity of the CDA trip during off-normal plant conditions was not embedded into processes or procedures, thus preventing development of appropriate risk elimination or mitigation actions. The Corrective Actions to Prevent Recurrence are to revise Surveillance Requirements for the Turbine Control Valve Fast Closure on Turbine Trip and RPT Initiate Logic to specify the appropriate power level and associated valve position for performing the test to ensure no control valve oscillations and that conditions remain outside of the OPRM trip enabled region when possible; revise Technical Instructions for the Reactivity Control Plan Development and Implementation to increase awareness of entry into the OPRM trip enabled region due to the risk of spurious scrams from the CDA instability detection method; revise Design Criteria for the Turbine Electro Hydraulic Control System (EHC) systems to add details with regards to the interrelationship between EHC and OPRM; and revise Design Criteria for Neutron Monitoring Systems to add details on OPRM Algorithms. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (03-14-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME ☒ 2. DOCKET NUMBER 3. LER NUMBER 050 SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 1 ☐ 00259 NUMBER NO. 052 2023 - 002 - 00 | I. Plant Operating Conditions before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN) Unit 1 was in Mode 1 at approximately 80 percent power. II. Description of Event A. Event Summary On May 20, 2023, at 0315 Central Daylight Time (CDT), while performing quarterly turbine control valve (TCV) testing at 80 percent Reactor Thermal Power (RTP) and 70 percent core flow, Unit 1 automatically scrammed due to an Oscillating Power Range Monitor (OPRM) Confirmation Density Algorithm (CDA) trip. The plant responded to the reactor scram as expected and there were no human performance challenges during the TCV testing or subsequent plant shutdown. The Tennessee Valley Authority (TVA) is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(iv)(A), as any event or condition that resulted in a manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B), including: the reactor protection system (RPS) [EIIS: JC] which includes a reactor scram or a reactor trip, and general containment isolation signals affecting containment isolation valves in more than one system. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML23200A238 | 0 | good
Browns Ferry Nuclear Plant | Unit 3 | Pressure Boundary Leak on Residual Heat Removal System Low Pressure Coolant Injection Test Line due to Fatigue Failure | 07-31-2023 | On December 2, 2022, at 2330 Central Standard Time (CST), during a drywell entry for leak identification, BFN Engineering personnel discovered a through-wall piping leak on a test line between the two Residual Heat Removal Shutdown Cooling test line isolation valves. On December 3, 2022, at 1000, it was determined that this test line was classified as American Society of Mechanical Engineers Code Class 1 piping and constitutes part of the BFN, Unit 3 Reactor Coolant System pressure boundary. Operations personnel maintained BFN, Unit 3 in Mode 4 or 5 until the leak was repaired. On December 3, 2022, at 1205 CST, eight-hour Event Notification 56257 was made to the NRC. The test line was cut and capped. The POE for this event determined that the LPCI mode of the BFN, Unit 3 RHR system can still meet the required LPCI flow to the reactor pressure vessel in the worse-case scenario of a small break LOCA for the duration of the mission time. During this time the HPCI system, both loops of the Core Spray system, and all ADS valves remained operable when required, aside from periods of planned maintenance and testing, and were available to provide coolant flow to the core during an emergency. The root cause of this event was that the small bore piping was not analyzed for vulnerability of fatigue failure due to operational or resonance vibration. Corrective actions are to implement Engineering Changes that will result in bounded life cycles for all levels of vibrational stress that the piping will experience; and to implement additional actions, for U3 systems where failure of small bore branch piping would cause a unit shutdown or loss of RCS boundary, to either modify operating ranges of the system and/or to modify the piping assembly. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 12/31/2023 (01-10-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ☒ 050 SEQUENTIAL REV YEAR NUMBER NO. Browns Ferry Nuclear Plant, Unit 3 00296 ☐ 052 2022 - 003 - 01 | I. Plant Operating Conditions before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN) Unit 3 was in Mode 4 at approximately zero percent power. II. Description of Event A. Event Summary On December 2, 2022, at 2330 Central Standard Time (CST), during a drywell entry for leak identification, BFN Engineering personnel discovered a through-wall piping leak on a test line [PSF] between the two Residual Heat Removal (RHR)[BO] Shutdown Cooling (SDC) test line isolation valves [SHV]. On December 3, 2022, at 1000, it was determined that this test line was classified as American Society of Mechanical Engineers (ASME) Code Class 1 piping and the identified leak location was identified as part of the BFN, Unit 3 Reactor Coolant System (RCS) [AC] pressure boundary. Operations personnel maintained BFN, Unit 3 in Mode 4 or 5 until the leak was repaired. On December 3, 2022, at 1205 CST, eight-hour Event Notification (EN) 56257 was made to the NRC. The test line was cut and capped. The TVA is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant’s Technical Specifications (TS); and 10 CFR 50.73(a)(2)(ii)(A), as any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML23212B015 | 0 | good
Browns Ferry Nuclear Plant | Unit 2 | Main Steam Relief Valves Lift Settings Outside of Technical Specifications Required Setpoints | 08-04-2023 | On June 5, 2023, the Tennessee Valley Authority was notified of as-found testing results that four (4) Main Steam Relief Valves (MSRVs) from Browns Ferry Nuclear Pant (BFN), Unit 2 were outside of their Surveillance Requirement limits for an indeterminate amount of time. These affected valves remained capable of maintaining reactor pressure within the American Society of Mechanical Engineers code limits and were still able to perform their safety function. It was determined that one MSRV failed due to corrosion bonding to the valve seats and non-quantifiable leakage known as simmering. Three MSRVs failed below their setpoints due to relaxed setpoint springs. All thirteen of the MSRV pilot valves were replaced during the Unit 2 Spring 2023 refueling outage. The Boiling Water Reactor Owners' Group is continuing to work toward a solution to improve the quality and adhesion of the platinum coating on the discs. BFN will take additional actions to verify that the springs associated with each low failure passes Spring Rate testing or is replaced. /'~ ' .... ?/' ~ □ □ □ I □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ ~ □ □ □ □ □ □ □ I I I I I I I I I I I I I I I I I I I I ~ ID I NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION (01-10-2023) LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) APPROVED BY OMB: NO. 3150-0104 EXPIRES: 12/31/2023 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME ☒ 050 2. DOCKET NUMBER 3. LER NUMBER Browns Ferry Nuclear Plant, Unit 2 00260 YEAR SEQUENTIAL NUMBER REV NO. ☐ 052 2023 - 002 - 00 | Not Found | ML23216A176 | 1 | ok
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Reactor Protection System Electric Power Monitoring System Trip Caused Primary Containment Isolation | 08-14-2023 | On April 14, 2023, at 05:11, James A. FitzPatrick Nuclear Power Plant (JAF) received indication of a half-scram on the “B” side Reactor Protection System (RPS). The cause was determined to be an overvoltage condition that tripped the Electrical Protection Assembly (EPA) for the “B” RPS Motor Generator (MG) Set. The same condition occurred on May 25, 2023, at 23.59. These events caused invalid primary containment isolation signals in multiple systems, reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). The cause was corrosion buildup in the voltage adjust potentiometer which led to the overvoltage trip of the EPA. Corrective actions included replacing the voltage adjust potentiometer. NRC FORM 366 (08-2020) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (03-14-2023) Estimated burden per response to comply with this mandatory collection request: 80 LICENSEE EVENT REPORT (LER) hours. Reported lessons learned are incorporated into the licensing process and fed CONTINUATION SHEET back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 YEAR SEQUENTIAL REV NUMBER NO. James A. FitzPatrick Nuclear Power Plant 05000333  052 2023 – 002 – 01 | Background Reactor Protection System (RPS) [EIIS: JE] Electric Power Monitoring System is provided to isolate the RPS bus from the motor generator (MG) set or an alternate power supply in the event of overvoltage, undervoltage, or underfrequency. This system protects the loads connected to the RPS bus against unacceptable voltage and frequency conditions and forms an important part of the primary success path of the essential safety circuits. Some of the essential equipment powered from the RPS buses includes the RPS logic, scram pilot valve solenoids, and various valve isolation logic. RPS electric power monitoring assembly will detect any abnormal high or low voltage or low frequency condition in the outputs of the two MG sets or the alternate power supply and will de-energize its respective RPS bus, thereby causing all safety functions normally powered by this bus to de-energize. (Safety functions powered by the RPS buses deenergize to actuate.) Two redundant Class IE circuit breakers are connected in series between each RPS bus and its MG set, and between each RPS bus and its alternate power supply. Each of these circuit breakers has an associated independent set of Class IE overvoltage, undervoltage, and under frequency sensing logic. Together, a circuit breaker and its sensing logic constitute an electric power monitoring assembly. If the output of the inservice MG set or alternate power supply exceeds predetermined limits of overvoltage, undervoltage, or underfrequency, a trip coil driven by this logic circuitry opens the circuit breaker, which removes the associated power supply from service. Event Description On April 14, 2023, at 05:11 when James A. FitzPatrick Nuclear Power Plant (JAF) was at 100% power, the station received indication of a half-scram on “B” side RPS. AOP-60, Loss of RPS Bus B Power, was entered and the cause was determined to be a trip of the “B” RPS MG set due to an overvoltage condition. The direct cause of the output breaker tripping was due to an Electric Power Monitoring System overvoltage trip on 71EPA-RPS1B1G, Electrical Protection Assembly (EPA). On May 25, 2023, at 23:59, when JAF was at 100% power, the station received indication of a half-scram on the “B” side RPS. AOP-60 was entered and the cause was determined to be a trip of the “B” RPS MG set due to an overvoltage condition. The direct cause of the output breaker tripping was due to an Electric Power Monitoring System overvoltage trip on 71EPA-RPS1B1G, EPA. In both events, the RPS bus power was restored when it was placed on the alternate power supply. Both events resulted in invalid system actuations of "B" side half scram and Primary Containment Isolation System (PCIS) [JM] isolations. The following systems isolated as a result of the loss of “B” RPS bus: Reactor Water Cleanup [CE], Reactor Building ventilation [NG], “B” Containment Atmosphere Dilution [BB], Torus Vent and Purge, Drywell Equipment and Floor Drain Sumps [WK], “B” Drywell Containment Atmospheric Monitors [IP], Recirculation System Sample Line, and Main Steam Line Drains [SB]. “B” Standby Gas Treatment System [BH] started as designed. These system actuations were not initiated by signals in response to actual plant conditions or parameters satisfying the requirements for initiation of the system. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). Page 2 of 4 | ML23226A139 | 0 | good
River Bend Station | Unit 1 | Not Found | 08-17-2023 | On March 24, 2023, River Bend Station was in Mode 4 during Refuel Outage 22 when testing revealed leakage rates from Division 1 of the Standby Service Water system that could have previously rendered the Ultimate Heat Sink inoperable. On May 6, 2023, testing on Division 2 of the Standby Service Water system also resulted in leakage rates that could have previously rendered the Ultimate Heat Sink inoperable. These discoveries were made when River Bend Station was not in a required Mode of Applicability for the Ultimate Heat Sink. Corrective actions to restore compliance with the allowed design basis leakage were completed for both of the conditions described above prior to the completion of the refuel outage. These events are being reported in accordance with 10 CFR 50.73(a)(2)(v)(B) as an event that could have prevented fulfillment of the safety function provided by the Ultimate Heat Sink and 10 CFR 50. 73(a)(2)(i)(B) as an operation or condition prohibited by Technical Specifications. The events are being reported in a single Licensee Event Report per guidance contained in NUREG-1022, Revision 3. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (03-14-2023) Esl1ma1ed burden per response 10 comply wilh tills mandalory co1 ec11on requesl 80 houn; Reported LICENSEE EVENT REPORT (LEA) lessons learned are incorpo<ated into the l1cens1ng p,ocess and led back to 1nduslry Send commenls regarding burden esIImaIe 10 lhe FOIA, Library. and lntormason Collec110n Branch !T-6 A10M). US CONTINUATION SHEET Nuclear Regula1ory Commission Washington. OC 20555-0001. or by e-mai 10 lnlocollects.Resou,ce@nrc.gov, and the 0MB reV1ewer al 0MB Olf1ce of lnforma11on and Regulalory Affairs. 13150-0104). Alln: Desk Officer for the Nuclear Regulalory Commission 725 171h S1ree1 NW, Wasrnngton, OC 20503 e-ma� �;,·rJ?;-� •;ii,., The NRC may not conduc1 or (See NUREG-1022, R.3 lor instruction and guidance for completing this lorm sponsor and a person Is nol required lo respond 10, a collecllon of mforma11on unless the documenl http://www.nrc.gov/reading-rm/doc-c0Uect1ons/nuregs/staff/sr1022/r3/l requesting or reqU1nng lhe collection d splays a currendy val d OMS conlrof number ■ 1. FACILITY NAME 2. DOCKET NUMBER 3.LERNM3ER 050 River Bend Station, Unit 1 458 YEAR SE N Q U U M E B N E T R IA L R N E O V . 2023 -002 - -01 - 0 052 | EVENT DESCRIPTION On March 24, 2023, River Bend Station (RBS) was in Mode 4 during Refuel Outage 22 (RF22) when testing revealed leakage from the Standby Service Water (SSW) [Bl] system that could have previously rendered the Ultimate Heat Sink (UHS) [BS] in-operable. The condition was discovered when a seat leakage test of SWP-MOV57A [ISV], Service Water Normal Supply Header A Inlet Isolation Valve resulted in a leak rate of approximately 30 gallons per minute (gpm). On May 6, 2023, while RBS was still in Mode 4 during RF22, a seat leakage test performed on SWP-MOV57B [ISV], Service Water Normal Supply Header B Inlet Isolation Valve resulted in a leak rate of 15.5 gpm. Design Basis calculations only allow a leakage rate of 6.9 gpm. SSW and the UHS are required by Technical Specification (TS) 3.7.1 to be operable in Modes 1, 2, and 3. The UHS consists of one 200% cooling tower and one 100% capacity water storage basin. The UHS basin capacity is required by Reg Guide 1.27 and Updated Safety Analysis Report (USAA) 9.2.5 to maintain a minimum 30-day inventory to mitigate the consequences of a Design Basis Accident (OBA) without replenishment. SWP-MOV57A was repaired by replacing the valve seat seals and adjusting the closing torque. SWP-MOV57B was repaired by adjusting the closing torque. Satisfactory post maintenance testing was completed for both valves. This event is being reported in accordance with 10 CFR 50.7 3(a)(2)(v)(B) as an event that could have prevented fulfillment of the safety function provided by the Ultimate Heat Sink because the amount of leakage through SWP­ MOV57 A and SWP-MOV57B would not allow the UHS to fulfill the required 30-day mission time. The event is also being reported in accordance with 10 CFR 50. 73(a)(2)(i)(B) as an operation or condition prohibited by Technical Specifications based on the past-operability review. Although this was a first-time performance of the SWP-MOV57A and SWP­ MOV57B seat leakage test, the assumption is that the leakage existed prior to RF22 and TS 3.7.1 would have been applicable. EVENT CAUSE The direct cause of this event was excessive seat leakage past SWP-MOV57A and SWP-MOV57B. The Root Cause of this event is that RBS did not challenge an assumption regarding the applicability of double isolation on the supply header of SSW. Because of these assumptions, SWP-MOV57A and SWP-MOV57B were not properly characterized by the In-Service Testing program and credit was taken for the isolation capability of check valves in-line with SWP-MOV57 A and SWP-MOV57B. SAFETY ASSESSMENT A risk assessment was completed using assumptions of the worst-case ambient temperature and minimum initial water level in the UHS. The assessment concluded that although the UHS would not require replenishment until at least 22 days into an event, there is negligible severe accident risk associated with total leakage of 45.5 gpm (both trains combined) past SWP-MOV57A and SWP-MOV57B since the UHS would require replenishment prior to the 30-day mission time. Additionally, risk would be further reduced by consideration of actual annual temperature cycles which would significantly reduce evaporative loss from the UHS as well as proceduralized replenishment capabilities. There were no actual Nuclear or Radiological safety consequences due to this event since the OBA did not occur. This event was of minimal significance to the health and safety of the public. NRC Form 366A (03-14 20231 Page _2_ of __3 | ML23229A121 | 1 | ok
River Bend Station | Unit 1 | Division I and II Diesel Generators Inoperable due to Exceeding Load Sequence Times | 09-13-2023 | On February 12, 2023, with River Bend Station (RBS) in Mode 4 during Refueling Outage 22, testing of the Division II Emergency Core Cooling System (ECCS) revealed that both Division II Control Building Chillers (HVK-CHL1B and HVK- CHL1D) failed to sequence onto the emergency bus within the Technical Specification (TS) required time. Investigation of the issue revealed that the same condition was present for the Division I Control Building Chillers (HVK-CHL1A and HVK- CHL1C). The condition described above was caused by a modification that replaced the Control Building Chiller controllers. The preliminary root cause identified that when the controllers were replaced, a delay was introduced in the start logic. Corrective actions to restore TS compliance were completed prior to the next mode of applicability. This condition resulted in the inability to comply with a Surveillance Requirement of TS 3.8.1. At the time of discovery, TS 3.8.1 was not applicable. An evaluation determined that the TS 3.8.1 Surveillance Requirement was not met prior to time of discovery and Required Actions were not taken within the associated allowed Completion Times in accordance with TS 3.8.1 - AC Sources – Operating. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 09/30/2023 (09-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  River Bend Station, Unit 1 050 YEAR SEQUENTIAL REV NUMBER NO. 458 ☐ 2023 - 002 - 01 052 | EVENT DESCRIPTION On February 12, 2023, RBS performed STP-309-0602, DIVISION II ECCS TEST. During the performance of Section 7.4, ECCS/LOP/LOCA Test Initiation, HVK-CHL1B [KM] did not load sequence within the required time. Load sequence time was 237.1 seconds with acceptance criteria of 180.9 to 221.1 seconds. During performance of Section 7.25, ECCS/LOP Test Initiation, HVK-CHL1D [KM] did not load sequence within the required time. Load sequence time was 241 seconds with acceptance criteria of 180.9 to 221.1 seconds. Condition Reports were generated for both issues. On May 2, 2023, the station determined that the Division I and Division II Diesel Generators [EK] had been inoperable as a result of the chiller controller modification. HVK-CHL1C [KM] and HVK-CHL1D modifications were completed in 2014. HVK-CHL1A [KM] and HVK-CHL1B modifications were completed in 2020. The discovery date was determined to be February 12, 2023. The event is reportable as an Operation or Condition Prohibited by Technical Specifications per 10 CFR 50.73(a)(2)(i)(B) and an Event or Condition that Could Have Prevented Fulfillment of a Safety Function per 10 CFR 50.73(a)(2)(v)(A) and (D). EVENT CAUSE This event was caused by an error that was introduced during a modification to the HVK-CHL1(A)(B)(C)(D) control logic. Beginning in 2014, the analog control logic was modified to digital control logic. A bypass timer in the analog logic was not replicated in the new digital logic. The bypass timer blocked a low chiller condenser water flow signal for a short duration during the chiller start sequence. If received, the low water flow signal causes the chiller start sequence to reset. Because the signal was no longer blocked in the digital control logic, the low chiller condenser flow signal was capable of causing the chiller start sequence to reset resulting in an extended chiller start sequence. SAFETY ASSESSMENT The Division I and II Diesel Generators were declared inoperable based on load sequence time of the HVK Chillers exceeding TS SR 3.8.1.18 requirements. The following engineering analysis provided evidence that the delay had no effect on the generator loading sequence. Calculation E-192, STANDBY DIESEL GENERATOR LOADING CALCULATION, evaluates the loading of the standby diesel generators during the worst-case loading conditions (LOP concurrent with LOCA). The calculation verifies that the maximum magnitude for the load blocks is within the tested values of loading established by the vendor. HVK-CHL1B/D are in the 1.5-10-minute load block for the Division II Diesel Generator. The chiller is the last component in the load block to start with a listed start time of 211 seconds from the LOP. The next component to start is at the 10-minute mark. HVK- CHL1A/C are in the 1.5-10-minute load block for the Division I Diesel Generator. The chiller is the last component to start in the 1.5-10-minute load block with a start time of 241 seconds. Even with the additional 40 second delay, the chiller will remain in the 1.5-10-minute load block and there will be at least 5 minutes between a chiller start and the start of the next component. Therefore, the delay has no effect on the generator loading sequence. NRC Form 366A (09-01-2023) Page 2 of 3 . | ML23256A200 | 0 | good
Fermi 2 | Unknown Unit | Technical Specification Completion Time Exceeded Due to Repairs on the MDCT Fan D. | 09-15-2023 | 12. Licensee Contact for this LER Licensee Contact Phone Number (Include area code) Eric Frank-Manager, Nuclear Licensing 734-586-4 772 13. Complete One Line for each Component Failure Described in this Report Cause System Component Manufacturer Reportable to IRIS Cause System Component Manufacturer Reportable to IRIS B cc SPT X999 y B cc VB M085 y 14, Supplemental Report Expected Month Day Year 1S. Expected Submission Date IZ] No □ Yes (If yes, complete 15. Expected Submission Date) 16, Abst.ract (Limit to 1326 spaces, i,e,, approximately 13 singl~spaced typewritten lines) At 0424 Eastern Daylight Time (EDD on July 18, 2023, the Division II Mechanical Draft Cooling Tower (MDCT) fan "D" was declared inoperable due to a trip of the fan motor while running at high speed. The MDCT fans are required to support operability of the Ultimate Heat Sink (UHS). The UHS is required to support operability of the Division II Emergency Equipment Cooling Water (EECW) system and the Emergency Equipment Service Water (EESW) system. The cause of the event was either the degraded mounting hardware between the gear reducer and the pedestal, and/or the degraded bushings on the driveshaft coupling to the gear reducer. The necessary repairs extended beyond the end of the 72-hour completion time prescribed by Technical Specification (TS) 3.7.2. A Notice of Enforcement Discretion (NOED) was approved by the NRC on July 20th, 2023, expiring at 2324 on July 25, 2023. This event is being reported under 10 CFR 50 .73(a)(2)(i)(B) for operation or condition prohibited by TS. Repairs were completed on the degraded mounting hardware and the degraded bushings, and the Division II MDCT fan "D" was declared operable at 1557 on July 22, 2023. There were no radiological releases associated with this event. At no time during this event was there a potential for endangering the public health and safety. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 09/30/2023 (00-01-2023) Estimated bLXden per response to comply with this mandalQl'Y collection request 80 hours. Reported lessons learned are incorporated into the licensing process and fed back lo industry. Send corrments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and lnfonnation Collections Branch (T-6 A10M), U. S. Nuclear Reguafory Commission, Washington, DC 20555-0001, or by email lo CONTINUATION SHEET lnfocollecls.Resource@nrc.gov, and the 0MB reviewer at 0MB Office of Information and RegulatOl'Y Affairs, (3150--0104), Attn: Desk Officer for the Nuclear Regula!Ol'Y Commission, 7'lf, 17th Street NW, Washington, DC 20503; email: oira submission@omb.eop.gov. The NRG may not condlrl or {See NUREG-1022, R3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http:/fwww.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/l requesting er requiring the cdleclion displays a rurrenHy valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV IFermi I I ~ □ -I NUMBER 1-0 N O. 2 052 0~1 002 | INITIAL PLANT CONDITIONS Mode-1 Reactor Power - 100 There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT At 0424 Eastern Daylight Time (EDT) on July 18, 2023, the Division II Residual Heat Removal Service Water (RHRSW) [Bl] Mechanical Draft Cooling Tower (MDCT)[CTW] Fan "D" [FAN], was declared inoperable due to a trip of the fan motor while running at high speed. The MDCT fans are required to support operability of the Ultimate Heat Sink (UHS) [BS]. The UHS reservoir is divided into two, one-half capacity reservoirs, corresponding to Division I and Division II. A two-cell MDCT is located above each of the one-half capacity reservoirs. Each cell is equipped with a MDCT fan. Two MDCT fans above each one-half capacity reservoir are required for it to be considered operable. Each reservoir is the cooling source for that division's service water subsystem (e.g., the Emergency Diesel Generators (EDGs) [DG] cooling water [LG], Emergency Equipment Cooling Water (EECW) system [CC], Emergency Equipment Service Water (EESW}, RHR [BO] system, Core Spray [BG] system). The Division II EECW system cools the High-Pressure Coolant Injection (HPCI) [BJ] system room cooler [CLR]. Typically, when Division II UHS is declared inoperable, then the high-pressure coolant injection (HPCI) system is declared inoperable; however, an Engineering analysis has been performed for HPCI operability which determined that there is reasonable assurance that HPCI would have performed its design function for its given mission time and remained operable. Investigation found that the cause of the trip was due to high vibrations caused by either the degraded mounting bolt (one of three) of the gear reducer to the pedestal [SPT] and/or the degraded bushings [VB] (Manufacturer Marley Company, Part# 69-29-02.) on the driveshaft coupling to the gear reducer. Further analysis is being done to determine the cause of the degradation on those parts. Based on the equipment history of the MDCT fans and the cause of the failure, there is no firm evidence to identify that the failure would have existed previously. Based on NUREG-1022 Section 3.2.2 guidance, the failure is assumed to have occurred at the time of discovery. The necessary repairs extended beyond the end of the 72-hour completion time prescribed by REQUIRED ACTION A.1 of Technical Specification (TS) 3.7.2.(Emergency Equipment Cooling Water (EECW}, Emergency Equipment Service Water (EESW) and Ultimate Heat Sink (UHS)- one reservoir inoperable). A Notice of Enforcement Discretion (NOED) was approved by the NRC on July 20, 2023, effective from 0424 EDT on July 21, 2023, to 2324 EDT on July 25, 2023. The enforcement discretion provided authorization for temporary non-compliance with TS 3.7.2 CONDITION A as described above. In addition, the following TS were also exceeded, TS 3.8.7 CONDITION A (Distribution Systems Operating, one or more required AC Electrical Distribution subsystems inoperable), and CONDITION B (one or more required DC Electrical Distribution subsystems inoperable}, TS 3.8.4 CONDITION B (DC sources operating, one DC Electrical Power Subsystem inoperable) and TS 3.8.1 CONDITION B (AC Sources Operating, both EDGs in one division inoperable). Following the degraded bushing replacement and removal and regrouting of the gearbox foundation bolts, the MDCT Fan "D" was declared operable at 1557 EDT on July 22, 2023. | ML23258A067 | 0 | good
Browns Ferry Nuclear Plant | Unit 2 | Pressure Boundary Leak on Recirculation Pump Discharge Isolation Valve Drain Line Due to Fatigue Failure | 09-18-2023 | On February 17, 2023, during a drywell entry for leak identification, Browns Ferry Nuclear Plant (BFN) personnel discovered a cracked weld on the 2A Recirculation Pump discharge isolation valve drain line. On February 18, 2023, at 0439 Central Standard Time (CST), it was determined that this drain line was classified as American Society of Mechanical Engineers Code Class I piping and constitutes part of the BFN, Unit 2 Reactor Coolant System (RCS) pressure boundary. On February 18, 2023, at 1025 CST, eight-hour Event Notification 56371 was made to the NRC. On March 19, 2023, work was completed to remove and replace the drain line. The root cause of this event was that small bore piping was not analyzed for vulnerability of fatigue failure due to operational or resonance vibration. Corrective actions are to implement changes that will result in bounded life cycles for all levels of vibrational stress that the piping will experience; and to implement additional actions, for Unit 2 systems where failure of small bore branch piping would cause a unit shutdown or loss of RCS boundary, to modify the operating ranges of the system and/or the piping assembly. TVA has concluded that sufficient systems were available to provide the required safety functions needed to protect the health and safety of the public. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 12/31/2023 (01-10-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1.FACILITY NAME 2.DOCKET NUMBER 3. LER NUMBER (cid:1800) 050 SEQUENTIAL REV YEAR NUMBER NO. Browns Ferry Nuclear Plant, Unit 2 00260 (cid:1798) 052 2023 - 001 - 01 | I. Plant Operating Conditions before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN) Unit 2 was in Mode 4 at approximately zero percent power. II. Description of Event A. Event Summary On February 17, 2023, during a drywell entry for leak identification, BFN personnel discovered a cracked weld on the 2A Recirculation Pump [AD] discharge isolation valve [ISV] drain line [PSF]. On February 18, 2023, at 0439 Central Standard Time (CST), it was determined that this drain line was classified as American Society of Mechanical Engineers (ASME) Code Class I piping and constitutes part of the BFN, Unit 2 Reactor Coolant System (RCS) pressure boundary. Operations personnel maintained BFN, Unit 2 in Mode 4 or 5 until the leak was repaired. On February 18, 2023, at 1025 CST, eight-hour Event Notification 56371 was made to the NRC. On March 19, 2023, work was completed to remove and replace the drain line. The TVA is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant’s Technical Specifications (TS); and 10 CFR 50.73(a)(2)(ii)(A), as any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML23261C399 | 0 | good
Hope Creek Generating Station | Unknown Unit | Technical Specification Required Shutdown due to Declaring the Suppression Chamber and Primary Containment Inoperable | 09-25-2023 | On April 30, 2023, Hope Creek Generating Station (HCGS) completed a technical specification (TS) required shutdown because limiting condition for operation (LCO) 3.6.1.1, Primary Containment Integrity, was not met. LCO 3.6.1.1 was not met because drywell-to-torus differential pressure could not be established to perform surveillance requirement (SR) 4.6.2.1.f, and LCO 3.6.2.1, SUPPRESSION CHAMBER, could not be met. HCGS demonstrated containment Operability and returned to power operation. This licensee event report (LER) supplement provides the results of a root cause evaluation (RCE). The direct cause was mechanical interference that prevented seating of one torus-to-drywell vacuum breaker and the root cause was failure to adequately assess and manage risk associated with torus-to- drywell vacuum breaker maintenance. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 09/30/2023 (09-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments f ~ ~ c,J>P. t REG ? t,(,.>O . LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to ~ CONTINUATION SHEET ~ ,i Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory ..;.+-, ••11t•• +O' Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ~ 050 YEAR SEQUENTIAL REV I □ NUMBER NO. Hope Creek Generating Station 354 D □ 052 I 2023 - I 001 I - 02 | IDENTIFICATION OF OCCURRENCE Event Date: April 30, 2023 Discovery Date: April 30, 2023 The root cause evaluation (RCE) determined the condition was first identified and misdiagnosed on October 18, 2022. Hope Creek entered an OPERATIONAL CONDITION (OPCON) that was applicable for the limiting conditions for operation (LCO) on October 28, 2022. CONDITIONS PRIOR TO OCCURRENCE OPCON 1, POWER OPERATION. No other structures, systems or components that could have contributed to the event were inoperable during the event. HCGS was in OPCON 1, POWER OPERATION, when drywell-to-torus bypass leakage was acceptable on September 28, 2022, as shown by successfully completing surveillance requirement (SR) 4.6.2.1.f. HCGS subsequently shutdown to complete a refueling outage. Preventative maintenance was performed on three of the eight torus-to-drywell vacuum breakers during the refueling outage. HCGS entered OPCON 2 and raised reactor coolant temperature above 200 degrees Fahrenheit on October 28, 2022. HCGS declared primary containment inoperable while in OPCON 1, POWER OPERATION at 100 percent rated thermal power on April 30, 2023 because Operators could not establish test conditions required to complete SR 4.6.2.1.f. DESCRIPTION OF OCCURRENCE On April 30, 2023, HCGS attempted to perform surveillance requirement (SR) 4.6.2.1.f but could not establish the initial test conditions (drywell-to-torus differential pressure). HCGS declared SUPPRESSION CHAMBER and PRIMARY CONTAINMENT INTEGRITY inoperable and completed a plant shutdown in accordance with TS. Event notification (EN) 56495 reported the technical specification required shutdown per 10 CFR 50.72(b)(2)(i) and this LER is required by 10 CFR 50.73(a)(2)(i)(A). EN 56494 reported a seriously degraded principal safety barrier per 10 CFR 50.72(b)(3)(ii)(A) and a condition that could prevent fulfillment of a safety function per 10 CFR 50.72(b)(3)(v)(D). Subsequent engineering analysis demonstrates that principal safety barriers were not seriously degraded. Therefore, a LER is not required by 10 CFR 50.73(a)(2)(ii). The engineering analysis also demonstrates that the primary containment safety function would be fulfilled if called upon. However, this LER is required by 10 CFR 50.73(a)(2)(v)(D) because primary containment is a single train system that was declared inoperable based on the inability to establish test conditions. | ML23269A205 | 0 | good
i | Unknown Unit | : | 09-28-2023 | On August 10, 2023, at 0039, with the reactor in Mode 1 and 100% rated thermal power, an automatic Scram occurred caused by the loss of both Reactor Protection System (RPS) busses while transferring the power supply on RPS B bus from Alternate B to Normal. This also caused an isolation signal to all the Main Steam Isolation Valves (MSIVs). High Pressure Core Spray (HPCS) and Reactor Core Isolation Cooling (RCIC) systems automatically initiated, due to lowering water level in the reactor vessel, to restore and control water level in the reactor vessel. Reactor vessel pressure control was accomplished by cycling the Safety Relief Valves (SRVs). The RPS Power Transfer Switch was replaced, and the reactor was restarted on August 15, 2023. The direct cause of the reactor trip was inadvertent overtravel of the RPS power transfer switch, which interrupted power to both RPS busses. The root cause of the reactor trip is attributed to a failure to implement a design change for the RPS power transfer switch to prevent recurrence of a plant scram due to a known design vulnerability. The RPS Power Transfer Switch was replaced with a like-for-like switch as an immediate corrective action, and a planned corrective action is to upgrade the switch to remove the known design vulnerability. This event is reportable due to the actuation of RPS, including a reactor scram, isolation of the MS IVs, and the actuation of Emergency Core Cooling Systems (ECCS) under 10 CFR 50.73(a)(2)(iv)(A). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (03-14-2023) Eslimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) r C e o g m ar m di i n s g s io b n u , r d W en a s e h s in ti g m to a n te , D to C t h 2 e 0 5 In 5 f 5 o - r 0 m 0 a 0 t 1 io , n o r S e b r y v i e c - e m s a B il ra to n c ln h fo (T co -6 lle A c 1 t s O .R M e ). s o U u .S rc . e N @ u n cl r e c a .g r o R v, e g .m ula to th r e y CONTINUATION SHEET 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required (See NUREG-1022, R.3 for instruction and guidance for completing this form to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/ displays a currently valid 0MB control number. 2.DOCKETNUMBER !----,r-3_-~LE~R~NU~M~B~E~R;._ __- --t 1. FACILITY NAME 181 050 YEAR SE N Q U U M E B N E T R IA L R N E O V . Perry Nuclear Power Plant 00440 2023 003 00 □ 052 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. EVENT DESCRIPTION: On August 10, 2023, at 0039, with the plant operating in Mode 1 and approximately 100 percent power, a reactor scram occurred during the transfer of the Reactor Protection System (RPS) [JC] B power supply [JX] from the alternate power supply to the normal power supply. During the transfer, a loss of both RPS A and B busses [BU] occurred, causing the Main Steam Isolation Valves (MSIVs) [ISV] to isolate, and a reactor scram. Safety Relief Valves (SRVs) [RV] automatically opened to lower and maintain pressure in the reactor vessel [RCT], due to the loss of the Condenser [COND] resulting from the MSIV closures. Water level in the reactor vessel dropped to Level 2 (130 inches above the reactor core), and High Pressure Core Spray (HPCS) [BG] and Reactor Core Isolation Cooling (RCIC) [BN] automatically initiated to restore and maintain water level in the reactor vessel. The plant responded to the unexpected RPS actuation and reactor scram as designed. The Control Room Operator was transferring the RPS B power supply from the B alternate feed transformer [XFMR] to the normal B motor-generator [MG] set, in accordance with the operating procedure, following restoration from RPS breaker maintenance. The transfer of RPS power is a non-paralleling "break before make" transfer, causing the RPS bus loads to be momentarily de-energized. A Division 2 half-scram is expected during the transfer. However, an unexpected break in power to the RPS A bus also occurred, providing the second half scram signal and a full RPS actuation. The RPS power switch operation was suspect and was subsequently replaced. The reactor was restarted on August 15, 2023. To perform a transfer from the B alternate transformer to the normal B MG set, the RPS power transfer switch [JS] is rotated from the 45-degree position (ALT 8) to the 0-degree position (NORM). Similarly, to transfer the RPS bus A power supply from the normal A MG set to the A alternate transformer, the power transfer switch is rotated from the 0-degree position (NORM) to the 315-degree position (ALT A). The operating procedure contains a caution statement that reads, "Movement of the MG SET TRANSFER switch 1C71-S1 shall be performed in a slow and steady motion. When placing it in NORM, 3 to 5 degrees of over-travel may cause loss of RPS bus A." This caution statement was added due to a similar incident that occurred in 1988. INVESTIGATION: As part of the root cause investigation, vendor testing was performed on the removed switch and did not identify any functionality issues. It was determined that the RPS A or B bus power break occurs when the power transfer switch over travels by approximately 10 degrees from the NORM position, in either direction. A review of internal operating experience identified that the RPS power transfer switch has a latent design error that allows for overtravel of the switch and subsequent de-energization of both RPS busses. The switch design places operators in an error likely situation by not eliminating the human factor from the switch manipulation. Overtravel of the RPS power transfer switch is possible and has resulted in a previous plant scram (1988). Page 2 of 4 | ML23271A026 | 0 | good
Donald C. Cook Nuclear Plant | Unit 1 | Two Trains of Fuel Handling Area Exhaust Ventilation Inoperable | 09-28-2023 | On July 25, 2023, with Donald C. Cook Nuclear Plant Units 1 and 2 operating at 100 percent power, Operators identified the Fuel Handling Area Exhaust Ventilation (FHAEV) System filter unit difference in pressure (DP) readings were below administrative limits. Subsequently, irradiated fuel movement occurred in the spent fuel pool on July 31, 2023 and August 1 , 2003. Later inspection of each train FHAEV System backdraft damper on August 2, 2023 identified degraded conditions that rendered each FHAEV train inoperable back to July 23, 2023. Technical Specifications require one train of the FHAEV System to be operable during movement of irradiated fuel assemblies in the auxiliary building. There were two occurrences of irradiated fuel movement in the auxiliary building during the time period when both FHAEV trains were inoperable. The event is reportable per 10 CFR 50.73(a)(2)(i)(B) "Operation or Condition Prohibited by Technical Specifications", 10 CFR 50.73(a)(2)(v)(D) "Event or Condition that Could Have Prevented Fulfillment of a Safety Function", and 10 CFR 50.73(a)(2)(vii) "Common Cause Inoperability of Independent Trains or Channels" ,_ - -- ,,. NRC FORM 366A (09-01-2023) LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) EXPIRES: 09/30/2023 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to lnfocollects.Resource@nrc.gov, and the OMB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Ann: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oita submission@omb.eop.g0¥. The NRC may not conduct or sponsor, and a person is not required lo respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 1. FACILITY NAME al ------------. □ | 050 052 2. DOCKET NUMBER I 00315 3. LER NUMBER I YEAR SEQUENTIAL REV [~]] use l=el « Hal Donald C. Cook Nuclear Plant Unit 1 Event Description On July 25, 2023, the Donald C. Cook Nuclear Plant Units 1 and 2 were operating at 100 percent power. Operators identified the Fuel Handling Area Exhaust Ventilation (FHAEV) System [VL] high efficiency particulate air filter (HEPA) and activated charcoal adsorber section difference in pressure (DP) readings were below administrative limits and commenced troubleshooting activities. Operators observed later during a system walkdown that with 12-HV-AFX-2, "Auxiliary Building Ventilation Fuel Handling Area Exhaust Fan #2" [VLJ[FAN] operating, there was reverse flow sufficient to cause "windmilling" of the opposite train fan 12-HV-AFX-1 "Auxiliary Building Ventilation Fuel Handling Area Exhaust Fan #1" [VLJ[FAN] while in standby. Similar symptoms of reverse flow were observed on 12-HV-AFX-2 when idle, while 12-HV-AFX-1 was operating. Internal inspections of each train FHAEV System backdraft damper assemblies 12-HV-BD-AFX-1, "Auxiliary Building Ventilation Fuel Handling Area Exhaust Fan HV-AFX-1 Discharge Backdraft Damper'' [VL][UDMP] and 12-HV-BD-AFX-2, "Auxiliary Building Ventilation Fuel Handling Area Exhaust Fan HV-AFX-2 Discharge Backdraft Damper'' [VL][UDMP] identified both damper mechanisms were partially stuck open and degraded which caused reduced system airflow. The identified conditions rendered each FHAEV System train inoperable. An engineering review of air flow data from 1-VFR-315 "Unit Vent Stack Flow Recorder Transmitter" [VL][FT] indicated system air flow was less than the operability range following a swap from 12-HV-AFX-1 to 12-HV-AFX-2, on July 23, 2023. No symptoms of degraded conditions were detected prior to that time. Repairs to the backdraft dampers were completed and required surveillance testing restored the FHAEV System to an operable status on August 5, 2023. Subsequently, during the time period between July 23, 2023 and August 5, 2023, when the FHAEV System was inoperable, irradiated fuel was moved in the auxiliary building on July 31, 2023 and August 1, 2023. Technical Specification Limiting Condition for Operation (LCO) 3.7.13 "Fuel Handling Area Exhaust Ventilation (FHAEV) System" requires "One FHAEV train shall be OPERABLE and in operation" and is applicable "During movement of irradiated fuel assemblies in the auxiliary building." LCO 3.7.13 requires the FHAEV system to be capable of removing airborne activity originating from a failed fuel assembly any time irradiated fuel is being moved. The mission time of the system is 30 days, which includes the radiological consequences analysis of record for a fuel handling accident in the auxiliary building, which credits the FHAEV System to filter the release through the unit vent. This filtered pathway is credited for the entire analyzed release duration. In order to accomplish the filtration safety function, the Bases for LCO 3. 7 .13 specifies for each FHAEV train, that ductwork, valves, and dampers are operable, and air flow can be maintained. Therefore, the event is reportable under 10 CFR 50.73(a)(2)(i)(B) "Operation or Condition Prohibited by Technical Specifications" due to irradiated fuel being moved when the FHAEV System was incapable of performing its safety function, contrary to LCO 3. 7.13 licensing basis requirements; 10 CFR 50.73(a)(2)(v)(D) "Event or Condition that Could Have Prevented Fulfillment of a Safety Function" due to neither train of the FHAEV being capable of performing the filtration safety function during movement of irradiated fuel; and, 10 CFR 50.73(a)(2)(vii) "Common Cause lnoperability of Independent Trains or Channels", when two independent trains (backdraft dampers) of the single system (FHAEV) were inoperable and would have impacted the ability to mitigate the consequences of an accident. " " _ " = | ML23271A098 | 0 | good
Browns Ferry Nuclear Plant | Unit 1 | High Pressure Coolant Injection System Declared Inoperable Due to a Corroded Actuator | 10-12-2023 | On July 12, 2022, during a routine surveillance test, the Browns Ferry Nuclear Plant (BFN), Unit 1, high pressure coolant injection (HPCI) turbine control (governor) valve did not open as expected. Upon investigation, it was discovered that the electro-governor remote hydraulic actuator (EGR) had internal corrosion, which resulted in binding of the pilot plunger and associated pilot bushing and a subsequent failure to supply the hydraulic oil needed to open the governor valve. The resulting inoperability of the single-train HPCI system would have prevented HPCI from fulfilling its safety function to mitigate the consequences of an accident if demanded. The event was caused by inadequate procedural guidance which led to failing to identify corrosion which led to the valve failure. Additionally, BFN’s maintenance strategy was not aligned with industry best practices and was insufficient for making risk-based decisions related to the reliability of the U1 HPCI EGR. The EGR and remote servo were promptly replaced. As corrective actions to prevent recurrence, BFN revised maintenance procedures to include enhanced acceptance criteria (both wording and images) and now requires photographing inspection results. HPCI / Reactor Core Isolation Cooling (RCIC) moisture content limits, action levels and recovery actions were revised to reflect the new recommended levels. The HPCI Auxiliary Lube Oil Pump is now placed in service on a biweekly basis to recoat the EGR internals and provide real-time validation of anticipated governor valve response. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 12/31/2023 (01-10-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME (cid:1409) 050 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 1 05000-259 NUMBER NO. (cid:1407) 052 2022 - 002 - 01 | I. Plant Operating Conditions before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN) Unit 1 was in Mode 1 at approximately 97 percent power. II. Description of Event A. Event Summary On July 12, 2022, when assistant unit operators (AUOs) locally started the high pressure coolant injection (HPCI) [BJ] auxiliary oil pump [P], HPCI control valve 1-FCV-073-0019 (governor valve) [FCV] did not open as expected during the prerequisite startup checks for BFN, Unit 1 HPCI Flowrate surveillance test 1-SR-3.5.1.7. Subsequent troubleshooting identified that with the turbine at rest, and the auxiliary oil pump running, the electro-governor remote hydraulic actuator (EGR) [SM] did not immediately supply the hydraulic oil needed to open the governor valve. Operations personnel declared HPCI inoperable and entered Technical Specification (TS) 3.5.1, "Emergency Core Cooling System (ECCS) - Operating," Condition C and verified that reactor core isolation cooling (RCIC) [BN] was operable as required. Troubleshooting confirmed that the EGR had failed due to mechanical binding as a result of accumulated corrosion product around the pilot plunger which reduced critical clearances needed for component operation. The resulting inoperability of the single-train HPCI system would have prevented HPCI from fulfilling its safety function that would be needed to mitigate the consequences of an accident. HPCI was returned to standby readiness and was declared operable on July 15, 2022, at 0915 CDT, thus exiting TS 3.5.1 Condition C. The Tennessee Valley Authority (TVA) is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(v)(D), as any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML23285A192 | 0 | good
Fermi2 | Unknown Unit | Not Found | 10-18-2023 | On 8/20/2023 at 1600 Eastern Daylight Time (EDT), a Reactor Coolant System (RCS) pressure boundary leak (approximately 2 gpm) was identified at the socket weld on a Reactor Recirculation Sample Line. The small-bore piping experienced vibration stresses at the header location which contributed to the fatigue failure at the socket weld connection. The leak was repaired, and the unit returned to power operation on 9/9/2023. The corrective action plan addressed the causal factors associated with this event. Corrective actions completed or planned include I) repairing the leak, 2) evaluated if the repair would perfonn its design function until the next refueling outage in 2024 (RF22), and 3) design change to add adequate supports to alleviate vibration to be installed in RF22. This event had no effect on the public health and safety. The event was reported to the Nuclear Regulatory Commission on 8/20/2023, via Event Notification 56685. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response 10 comply with this mandatory collection request: 80 hOUJS. Reported lessons learned are incorporated into the licensing process and led bad( to indlstry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and ln101m8tion Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Convrission, Washington, OC 20555-0001, or by email to CONTINUATION SHEET lnlooollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Offioe ol lnlonnation and Regulatory Affairs, (3150.0104), Attn: Desk Officer for the Nuclear Regwitory Commission, 725 17th Slreet NW, Washington, DC 20503; ema~: oira submission@omb.eop.gov. The NRC may not conciJct or {See NUREG-1022, R.3 for Instruction and guidance for oompleting this form sponsor, and a person is not requi"ed lo respond lo, a coHection of information unless the dooJment http·/twww nrc gov/reading-rm/doc-colleclions/nuregs/staff/sr1022/r3/\ requesting or requiring the collection displays a cwenUy valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 I YEAR SEQUENTIAL REV I □ NUMBER 1-NO0. 1Ferml2 052 00341 □ -1 003 | INITIAL PLANT CONDITIONS MODE - 3 (Hot shutdown) Reactor Power - O There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT On 8/20/2023 at 1600 Eastern Daylight Time (EDT) during plant walkdowns in the Drywell while in MODE 3 to identify a cause of increasing unidentified leakage rate, a Reactor Coolant System (RCS) pressure boundary leak (approximately 2 gallons per minute (gpm)) was identified at the socket weld on the 3/4-inch Reactor Recirculation (RR)[AD] Sample Line [PSP] (6DI-B31-7255-1) at the RR header, CT-831 L018. The RR system consists of the two pump loops external to the Reactor Pressure Vessel (RPV)[RPV]. These loops provide the piping path for the driving flow of water to the RPV jet pumps (located in the RPV). The RR system loops are part of the nuclear system process barrier and are located inside the primary containment structure. The recirculated coolant consists of saturated water from the steam separators and dryers that has been subcooled by incoming feedwater. This water passes down the annulus between the RPV wall and the core shroud. A portion of the coolant flows from the RPV, through the two external RR loops and becomes the driving flow for the jet pumps. Each of the two external RR loops discharges high pressure flow into an external manifold.f rom which individual recirculation inlet lines are routed to the jet pump risers within the RPV. The process sampling test line 6Dl-831-7255-1 for chemical tap runs between the manifold header connection and the RPV penetration X-29A. Restraints for the recirculation system piping are the GE cable-type restraints. The steam and recirculation piping are designed in accordance with the 1969 American National Standards Institute (ANSI) 831.7 Nuclear Power Piping Code, Class 1, including addenda ANSI B31.7b-1971. The RR System circulates the required coolant through the reactor core to maintain fuel temperature within the specified design margins for normal and abnormal operating conditions, and transients. The RR system has the following Safety Functions: 1. Ensure adequate margins for fuel temperature during postulated transients, 2. Maintain pressure integrity during adverse combinations of loadings and forces _which occur during abnormal, accident, and special event conditions, and 3. Maintain the ability of the reactor pressure vessel (RPV) to provide a floodable volume after a pipe break accident. The RR system meets the following power generation design bases: a. RR system shall provide sufficient flow to remove heat from the fuel, and b. System design shall minimize maintenance situations that would require core disassembly and fuel removal. The extent of leaking will result in loss of design function of the pipe, pipe supports, and the equipment attached to the piping. In addition to this, the unit enters a Limiting Condition for Operation (LCO) 3.4.4, which states RCS operational LEAKAGE shall be limited to (a) No pressure boundary LEAKAGE (b) </= 5 gpm unidentified leakage (c) </= 25 gpm total LEAKAGE averaged over the previous 24-hour period; and (d) </= 2 gpm increase in unidentified LEAKAGE within the previous 24-hour period in MODE 1. Technical Specification (TS) 3.4.4 is applicable in MODES 1, 2, and 3. Since the leakage location was identified, this required entry into LCO 3.4.4 "RCS Operational LEAKAGE" CONDITION C - a Identification of pressure boundary leakage with REQUIRED ACTION to be in MODE 3 in 12 hours and MODE 4 in 36 hours. At 1630, a TS-required shutdown to MODE 4 - Cold Shutdown was initiated. The plant was in MODE 4 at 0310 on 8/21/2023. The plant was placed in MODE 5 on 8/30/2023 to support the repair of the leak and the unit returned to power operation on 9/9/2023. Although the source of the RCS LEAKAGE was identified on 8/20/2023, there was indication that the leak began around 6/10/2022 when RCS UNIDENTIFIED LEAKAGE increased and was recorded in the corrective action program under CARD 22-27022. From 6/10/2022 until 8/20/2023, the UNIDENTIFIED LEAKAGE was within the bounds permitted by | ML23291A358 | 1 | ok
Hope Creek Generating Station | Unknown Unit | Shutdown Margin Less than Expected Resulting in a Condition Prohibited by Technical Specifications | 10-20-2023 | On May 4, 2023, during reactor start-up following a maintenance outage, nuclear instrumentation readings (Source Range Monitor (SRM)) were observed to be rapidly rising during withdrawal of a control rod blade (CRB). The Reactor Operator was directed to re-insert the CRB. Nuclear instrumentation readings stabilized and began to lower when the CRB was re-inserted. The Operating Crew subsequently performed a reactor shutdown by fully inserting all CRBs. The start-up was re-commenced on May 5, 2023 with an adjusted start-up sequence. The start-up was successfully completed with normal responses from nuclear instrumentation. Subsequent collection of data determined that there had been a loss of reactivity worth in two CRBs. On August 21, 2023, Hope Creek Generating Station received the results of a Shutdown Margin (SDM) Analysis performed by Global Nuclear Fuel (GNF). The analysis determined that with the reduced reactivity worth of the two CRBs, the calculated SDM for the current fuel cycle was lower than expected, and less than required by Technical Specification 3.1.1, Shutdown Margin, during the early portion of the fuel cycle. This condition is reportable under 10 CFR 50.73(a)(2)(i)(B). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and (See NUREG-1022, R.3 for instruction and guidance for completing this form a person is not required to respond to, a collection of information unless the document requesting or requiring http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3.LER NUMBER Hope Creek Generating Station X 050 SEQUENTIAL REV YEAR NUMBER NO. 00354 2023 - 002 - 00 052 | IDENTIFICATION OF OCCURRENCE Event Date: May 4, 2023 Discovery Date: August 21, 2023 CONDITIONS PRIOR TO OCCURRENCE At the time of the unexpected increase in SRM readings, May 4, 2023, Hope Creek was in Operational Condition (OPCON) 2, Start-up, 0 percent power, with the reactor subcritical. No other structures, systems or components that could have contributed to the event were inoperable at the time of the event. When the analysis from Global Nuclear Fuel (GNF) was accepted, August 21, 2023, Hope Creek was in OPCON 1, Power Operation, at 100 percent rated thermal power. DESCRIPTION OF OCCURRENCE During reactor start-up following a maintenance outage, nuclear instrumentation readings (Source Range Monitor (SRM)) were observed by the Reactor Operator to be rapidly rising during continuous withdrawal of a CRB. The Reactor Operator was directed to re-insert the CRB. Nuclear instrumentation readings stabilized and began to lower when the CRB was re-inserted. The Operating Crew subsequently performed a reactor shutdown by fully inserting all CRBs. An initial investigation did not reveal any errors in sequence development, Estimated Critical Positions (ECP), or CRB reactivity worth calculations. These items were independently checked by the fuel vendor. However, the start-up sequence was revised and a second start-up proceeded without any issue. Evaluation of Local Power Range Monitor (LPRM) responses and Traversing Incore Probe (TIP) data later determined that there was a loss of reactivity worth in two CRBs. Initially four CRBs were inserted to ensure shutdown margin requirements were met. After a calculation performed by GNF, three of the CRBs were withdrawn, leaving one inserted. GNF was engaged to perform a Shutdown Margin (SDM) analysis of the Cycle 25 reactor core. The analysis concluded that the minimum SDM at Beginning of Cycle (BOC) 25 was below the Technical Specification limit of 0.38% delta k/k. Cycle 25 began on October 28, 2022 with reactor start-up from refuel outage R24. This condition existed until core average exposure reached approximately 500 Megawatt-Days per Short Ton (MWD/ST) on November 21, 2022. At that time, the SDM was determined to have been greater than 0.38% delta k/k and therefore compliance with Technical Specifications was restored. CAUSE OF EVENT A Root Cause Evaluation (RCE) was conducted. The Direct Cause of the event was determined to be a reduction of boron-10 in two (2) CRBs, reducing the reactivity worth of these two CRBs. The Root Cause was determined to be that established procedural and administrative criteria for CRB management was ineffective at identifying mechanical end of life. As part of the Extent of Condition review, PSEG identified indications of reduced reactivity worth for two CRBs discharged during the last refueling outage, R24. This was documented in the Corrective Action Program. Visual inspection of the two CRBs was completed and assessment is on-going as part of the Corrective Actions for this event. | ML23293A002 | 0 | good
Nine Mile Point | Unit 2 | Automatic Reactor SCRAM on low Level Due to Partial Loss of Feedwater | 10-27-2023 | On 9/2/2023 at 0632 EDT, with Nine Mile Point Nuclear Station operating at 100% power, a Feedwater transient occurred resulting in a Reactor Protection System {RPS) Automatic Reactor Scram on Low Level (level 3, 159.3"). Follow_ing the scram, reactor water level dropped below Level 2 (108.8") resulting in a Group 2 Recirc Sample System Isolation, Group 3 Traversing lncore Probe (TIP) Isolation Valve Isolation, Group 6 and 7 Reactor Water Cleanup Isolation, and Group 9 Containment Purge Isolations. All control rods inserted as expected. High Pressure Core Spray and Reactor Core Isolation Cooling initiated (RCIC) and injected as expected. Emergency Core Cooling Systems (ECCS) and RCIC were secured and normal reactor pressure and level control was established for hot shutdown. This event is reportable in accordance with 10 CFR 50. 73(a){2)(iv)(A). N~C FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03131/2024 (10-01-2023) Estimated burden per respoose to oomply wilh lllis mandatory collection request 80 hours. Reported lessons learned are incorporated into !he licensing process and fed back lo indusuy Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate lo the FOIA. Library .. and l11fOll!laoon Collecllons Branch fT·6 Al OM). U. S. Nuclear Regulatory Commission. Washington. DC 20555-0001, or by email to CONTINUATION SHEET lnfocoitects.Resource@nrc.gov, and tha 0MB reviewer al: 0MB Office of lnfo!lllllfion and Regulaloiy Affairs. (3!50-0104), Attn: Desk Officer for the Nuclear Regulatory Commission. 725 17111 Street NW Washington. DC 20503; email: fl!rn. &Jbm~o11@qm!1,sl0ll-JO~. The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor. and a parson is not required to respond !o. a collection of information un!ess !he documenl http:/lwww.nrc.gov/reading-rm/doc-colk,ctlonsfnl.lreqs[staff/sJ'LQ22/rM requesting or requiring the colleclion <lispfays a currently valid 0MB control number 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 I YEAR SEQUENTIAL REV ~□- I NUMBER 1-NO0. !Nine Mlle Point Unit 2 50-410 I 052 001 | .THE ENERGY INDUSTRY IDENTIFICATION SYSTEM (EIIS) COMPONENT FUNCTION IDENTIFIED AND SYSTEM NAME OF EACH COMPONENT OR SYSTEM REFERRED TO IN THIS LER ARE ENCLOSED WITHIN [BRACKETS] I. DESCRIPTION OF EVENT A. PRE-EVENT PLANT CONDITIONS: Prior to the event, NMP2 was in Mode 1 (Power Operation) at 100% power. B. EVENT: On 9/2/2023 at 0632 EDT, with Nine Mile Point Nuclear Station operating at 100% power, a Feedwater [SJ] transient occurred resulting in an RPS Automatic Reactor Scram on Low Level (Level 3, 159.3"). Following the Scram, reactor water level dropped below Low Low Level (Level 2, 108.8") resulting in a Group 2 Recirc Sample System Isolation [AD], Group 3 TIP Isolation Valve Isolation. Group 6 and 7 Reactor Water Cleanup Isolation [CE}. and Group 9 Containment Purge Isolations [BBJ. All control rods inserted as expected. High Pressure Core Spray [BGJ and Reactor Core Isolation Cooling [BNJ initiated and injected as expected. ECCS Systems and RCIC were secured and normal reactor pressure and level control was established for hot shutdown. This event is reportable in accordance with 10 CFR 50.73(a){2)(iv){A). C. INOPERABLE SYSTEMS, STRUCTURES, OR COMPONENTS THAT CONTRIBUTED TO THE EVENT: None. Any non-safety related equipment that contributed to the event will be provided in the supplement. D. DATES AND APPROXIMATE TIMES OF MAJOR OCCURENCES AND OPERATOR ACTIONS: The dates, times, major occurrences, and operator actions for this event are as follows. September 2, 2023: 0632-A sudden reduction in Feedwater flow causes level lowering to Low Level (Level 3, 159"), resulting in an RPS Automatic Reactor Scram. 0632-Shortly following the scram, Low Low Level (Level 2, 108.8") is reached, resulting in Group 2, 3, 6, 7, 8, and 9 isolations. Recirculating Pumps trip, and High Pressure Core Spray (HPCS) and Reactor Core Isolation Cooling (RCIC) automatically initiate. 0635 - Turbine tripped on reverse power. None. Additional dates and times of major occurrences and operator actions may be provided in the supplement when the evaluation is complete. | ML23306A048 | 0 | good
Peach Bottom Atomic Power Station | Unit 3 | Standby Liquid Control Pump Inoperable for Greater than LCO Window due to Gas Intrusion | 11-07-2023 | On September 9, 2023, during performance of a functional test, the Unit 3 ‘B’ Standby Liquid Control Pump did not produce discharge pressure. The pump was declared inoperable and Technical Specification Limiting Condition for Operation (LCO) 3.1.7 Condition B was entered. Troubleshooting identified that the pump and part of the discharge piping was not sufficiently filled with water. The most likely source of gas intrusion was the nitrogen filled accumulator located on the discharge piping between the pump and the discharge check valve. The piping was refilled and the accumulator was replaced, after which the pump was run successfully. The system was restored to operable and the LCO was exited on September 12, 2023. The gas leakage rate was slow and therefore, the system was likely inoperable longer than the LCO-allowed outage time (i.e., 7 days). Therefore, the condition is being reported under 10CFR 50.73(a)(2)(i)(B). There were no other systems which were inoperable during this identified condition that contributed to this event. There were no actual safety consequences as a result of this event. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 SEQUENTIAL REV YEAR NUMBER NO. Peach Bottom Atomic Power Station, Unit 3 00278  052 2023 - 001 - 00 | Event Description On September 9, 2023, during performance of a functional test, the Unit 3 ‘B’ Standby Liquid Control (SLC, EIIS: BR) Pump (EIIS: P) did not produce discharge pressure. The pump was declared inoperable and Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.1.7 Condition B was entered at 20:32 hours. Troubleshooting identified that the pump and part of the discharge piping was not sufficiently filled with water. The most likely source of gas intrusion was a leaking bladder inside the pneumatic-hydraulic accumulator (EIIS: ACC). The device is installed on the piping near the SLC pump discharge relief valve to dampen pulsations from the pumps to protect the system piping. Nominal accumulator pressure is between 325 psig and 450 psig. The accumulator bladder was replaced, after which the pump and discharge piping were filled and the pump was run successfully. The system was restored to operable and the LCO was exited on September 12, 2023 at 17:39 hours. At the time of discovery, Unit 3 was operating in MODE 1 at approximately 91% power, due to end-of-cycle coast down. Peach Bottom TS LCO 3.1.7 Required Action B.1 requires that a SLC subsystem be restored to operable status within 7 days or in accordance with the Risk Informed Completion Time Program. If this action is not met, the plant is required to be in MODE 3 within 12 hours and MODE 4 within 36 hours. The most likely cause of the condition is gas leakage through the accumulator bladder. The estimated leak rate was small, because no visible sources of leakage were found on the accumulator bladder and the rate of pressure decay within the accumulator was slow. Failure analysis is being performed on the bladder, but at this time, the exact cause of the leakage is unknown. The 3B SLC subsystem was last run successfully on May 29, 2023. Trending of available accumulator pressure data did not provide a conclusive time of failure. Due to the slow nature of the leakage and the volume of gas intrusion present, it is highly likely that the condition existed longer than the LCO-allowed outage time. Since the 3B train of SLC was likely inoperable for greater than the LCO-allowed outage time, this condition is being reported under 10CFR 50.73(a)(2)(i)(B). The Energy Industry Identification System component function identifier and name of each component or system: EIIS: Standby Liquid Control System, BR 3BT076, Standby Liquid Control N2 Accumulator Manufacturer: Greer Hydraulics, Inc Model: A68514-200 Safety Consequences The SLC System is designed to provide the capability of bringing the reactor, at any time in a fuel cycle, from full power and minimum control rod inventory (which is at the peak of the xenon transient) to a subcritical condition with the reactor in the most reactive, xenon free state without taking credit for control rod movement. The SLC System satisfies the requirements of 10 CFR 50.62 on anticipated transient without scram using highly enriched boron. The SLC System is also used to maintain suppression pool pH at or above 7 following | ML23311A061 | 0 | good
Susquehanna Steam Electric Station (SSES) | Unit 1 | D Diesel Generator Inoperable due to Clogged Fuel Injectors | 11-09-2023 | On September 12, 2023, at approximately 05:01, during the performance of surveillance testing, the D Diesel Generator (DG) failed to reach the required frequency within the acceptance criteria specified in Surveillance Requirement (SR) 3.8.1.7. Operators declared SR 3.8.1.7 failed and entered Technical Specification (TS) Limiting Condition of Operation (LCO) 3.8.1, Condition B, on both Susquehanna Steam Electric Station Unit 1 and 2 for the inoperable D DG. The other three DGs (A, B, and C) were verified to be OPERABLE and operators substituted the E DG in for the D DG. After completion of the E DG substitution, LCO 3.8.1, Condition B, was exited on September 12, 2023, at approximately 22:52. The failure to reach the required frequency within the acceptance criteria was the result of clogged fuel injectors. The condition of the inoperable D DG was determined to likely have existed for longer than allowed by TS, and ~he event was determined to be reportable in accordance with 10 CFR 50. 73(a)(2)(i)(B) as a condition prohibited by TS. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-202,,3,,), ...... Estimaled burden per response lo comply with this mandatory collection request: 80 hours. Reported ,~;-, lessons learned are incorporated into the licensing process and fed back to induslry. Send comments • "' t LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Ubrary, and lnfonmation Collections Branch (T-6A10M), U.S. \ ':/.I .,.,. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory (See NUREG-1022, R.3 for instruction and guidance for completing this form Affairs, (3150-0104), Attn: Oesk Officer for the Nuclear Regulatory Commission, 72517th Street NW https://www.nrc.gov/readinq-nm/doc-collections/nuregs/stafflsr1022/r30 Washington, DC 20503; email: oira submlssion@omb.eop.gov. The NRC may nol conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 181 050 YEAR SEQUENTIAL REV NUMBER NO. Susquehanna Steam Electric Station (SSES) D 052 05000387 2023 - 003 - 00 Unit 1 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, approximately 100 percent Rated Thermal Power (RTP) Unit 2 - Mode 1, approximately 93 percent RTP There were no structures, systems, or components that were inoperable at the start of the event and contributed to the event. EVENT DESCRIPTION On September 12, 2023, at approximately 05:01, operators started the D Diesel Generator (DG) [EIIS Code/Component Code: EK/DG] in accordance with the applicable surveillance procedure. The D DG reached the required frequency at a time of 12.6 seconds, which exceeds the acceptance criteria of 10 seconds specified in Surveillance Requirement (SR) 3.8.1.7. Operators declared SR 3.8.1.7 failed and entered Technical Specification (TS) Limiting Condition of Operation (LCO) 3.8.1, Condition B, on both Susquehanna Steam Electric Station (SSES) Unit 1 and 2 for the inoperable D DG. The other three DGs (A, B, and C) were verified to be OPERABLE and operators substituted the E DG in for the D DG. After completion of the E DG substitution, LCO 3.8.1, Condition B, was exited on September 12, 2023, at approximately 22:52. The condition of the inoperable D DG was determined to likely have existed for longer than allowed by TS, and the event was determined to be reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. The following is a timeline of events: February 2023 to August 2023 - The D DG has higher than normal accumulated low load run time, which was considered as a possible contributor to the clogged injectors. However, start times were acceptable after the low load operation, and there was not an increasing trend in start time. 08/17/2023 - D DG monthly surveillance start time was 8.65 seconds. 09/12/2023 - D DG monthly surveillance start time was 12.6 seconds. LCO 3.8.1, Condition B, was entered at approximately 05:01 due to the D DG being inoperable. The E DG was substituted for the D DG and LCO 3.8.1, Condition B, was exited at approximately 22:52. 09/21/2023 - Troubleshooting identified fuel injectors had excessive carbon buildup. The fuel injectors were cleaned. 09/22/2023 - D DG monthly surveillance was performed successfully with a start time of 7.95 seconds. D DG was substituted back in for the E DG and the D DG was declared operable at approximately 02: 10 on 09/23/2023. SSES TS LCO 3.8.1 requires, in part, that four DGs are OPERABLE in MODES 1, 2, and 3. Condition B requires that an inoperable DG be restored to OPERABLE status within 72 hours or that each unit be shut down to MODE 3 in 12 hours and MODE 4 in 36 hours. Based on the identified cause of the D DG slow start, this condition likely existed for longer than allowed by TS. As a result, this condition was determined to be reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. Page .l_ of.]_ NRG FORM 366A (10-01-2023) NRG FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported <,)I-'' ... , lessons learned are incorporated into the licensing process and fed back to industry. Send comments (~) LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. •1,,• CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory (See NUREG-1022, R.3 for instruction and guidance for completing this form Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW https:/lwww.nrc.gov/readinq-rm/doc-collections/nureqs/staff/sr1022/r3D Washington, DC 20503; email: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER [gJ 050 YEAR SEQUENTIAL REV • NUMBER NO. Susquehanna Steam Electric Station (SSES) D 052 05000387 2023 - 003 - 00 Unit 1 NARRATIVE CAUSE OF EVENT The cause of the slow start was clogged fuel injectors. ANALYSIS/SAFETY SIGNIFICANCE As described in Section 8.3 of the Susquehanna Updated Final Safety Analysis Report (UFSAR), and required by 10 CFR 50, Appendix A, General Design Criterion 17, a single failure of a DG will not prevent safe shutdown of the units in the event of a design basis accident. While the D DG was inoperable, the three remaining DGs (A, B, and C) were aligned and operable. Therefore, the slow start of the D DG did not prevent the DGs from fulfilling their safety function. The safety function of the DGs is to provide power to equipment as assumed in the safety analyses described in Chapter 15 of the Susquehanna UFSAR. In this case, the safety analyses assume the DGs will start in 25.1 seconds of a valid start signal. Additionally, the loading analysis for the DGs assume the Residual Heat Removal motors are loaded at 13 seconds to ensure the DG can handle the load of the large motors. The start time of 12.6 seconds observed during the September 12, 2023, surveillance test was within that assumed in the accident analyses. Therefore, the D DG was able to perform its safety function. Based on engineering analysis, this event will not be counted as a safety system functional failure under the NRC Reactor Oversight Process Performance Indicator. CORRECTIVE ACTIONS Key corrective actions included all D DG fuel injectors being cleaned. Although the station had implemented vendor guidance for low load run time on the DG, Susquehanna is also taking additional actions to refine guidance on low load run times for the DGs. COMPONENT FAILURE INFORMATION Component Name - Diesel Generator 'D' Component Identification - 0G501 D Manufacturer - Cooper Energy Services PREVIOUS OCCURRENCES None. NRG FORM 366A (10-01-2023) Page .1. of .1. | ML23313A196 | 0 | good
Monticello Nuclear Generating Plant | Unknown Unit | Reactor Scram and Containment Isolation due to Valve Responses during Main Turbine Control Valve Testing | 11-13-2023 | On September 27, 2023 at 1041 CDT, with Monticello Nuclear Generating Plant in Mode 1 at approximately 75 percent power for the semiannual Turbine Control Valve (CV) test, an unplanned Reactor Scram, Group I Primary Containment Isolation, and Group II Primary Containment Isolation occurred. The cause of the Reactor Scram was exceeding the Reactor Pressure Vessel (RPV) high pressure scram setpoint during CV testing. CV-1, CV-2 and CV-3 percentage open did not increase enough when CV-4 was closed for testing. The reduction in steam flow caused the RPV pressure to exceed the scram setpoint. Subsequently, an expected low RPV level caused the Group II Primary Containment Isolation. The cause of the Group I Primary Containment Isolation was a transient in the steam line high flow instrumentation sensing lines for the C Main Steam Line. Corrective actions included inspection and adjustment of the four CVs to within manufacturer's specifications. Channel calibration and functional tests were performed to verify that all C Main Steam Line flow instruments met requirements. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME ■ 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV NUMBER NO. Monticello Nuclear Generating Plant 263 052 2023 - 002 - 00 | EVENT DESCRIPTION On September 27, 2023 Monticello Nuclear Generating Plant (MNGP) was operating in Mode 1 and approximately 75 percent power for the semiannual Turbine-Generator Operational Tests. At 1041 Central Daylight Time (CDT), while cycling closed the Turbine Control Valve 4 (CV-4) per the Turbine CV Test, an unplanned Reactor Scram, Group I Primary Containment Isolation, and Group II Primary Containment Isolation occurred. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) for an event or condition that resulted in the automatic actuation of the Reactor Protection System (RPS) [EIIS CODE: JC] including reactor scram and containment isolation signals affecting containment isolation valves in more than one system and multiple Main Steam Isolation Valves (MSIVs) [EIIS CODE: ISV]. EVENT ANALYSIS The Turbine Control Valves (CVs) [EIIS CODE: FCV] are a part of the MNGP Main Turbine System [EIIS CODE: TA]. The CVs control reactor pressure, in conjunction with the turbine bypass valves, by adjusting position to control steam flow. During the semiannual Turbine-Generator Operational Tests, reactor power is reduced to approximately 75 percent to allow for testing of each of the four CVs. While one CV is stroked closed, the other three CVs are expected to increase percent open to compensate for the increased reactor pressure. While stroking CV-4 closed per the procedure, the percent open of CV-1 and CV-2 initially increased then stalled and CV-3 percent open did not change. In turn, total steam flow through the CVs lowered and the reactor pressure exceeded the (RPV) high pressure scram setpoint, resulting in an automatic Reactor Scram. The RPV water level lowered to below the Group II isolation setpoint as expected, resulting in a Group II Primary Containment Isolation. Additionally, a Main Steam Line high flow condition was sensed in C Main Steam Line, resulting in a Group I Primary Containment Isolation and closure of the Main Steam Isolation Valves. There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. ASSESSMENT OF SAFETY CONSEQUENCES All safety systems functioned properly during the transient. All control rods fully inserted during the scram. The High Pressure Coolant Injection (HPCI) system was placed in service to control RPV pressure, but HPCI did not inject into the RPV and was not needed to control RPV water level. There were no radiological, environmental, or industrial impacts associated with this event. The health and safety of the public and site personnel were not impacted during this event. | ML23317A359 | 0 | good
River Bend Station | Unit 1 | Drywell Atmosphere Radiation Monitor Particulate and Gaseous Channels Inoperable due to Out of Tolerance Conversion Factors | 11-15-2023 | On August 29, 2023, with River Bend Station (RBS) operating at 100% power, personnel recognized that the Drywell Atmosphere Radiation Monitor (RMS-RE 112) particulate and gaseous channel conversion factors were out of tolerance. The monitor was declared inoperable and the appropriate Technical Specification (TS) Condition was entered. This event was caused by configuration controls that were inadequate to prevent human performance errors in development of radiation detector digital parameters and transfer of parameters into the detector's database at initial setup. The RMS-RE112 conversion factors have been corrected and the monitor was declared operable on September 7, 2023. This condition is being reported as an Operation or Condition Prohibited by Technical Specifications per 10 CFR 50. 73( a)(2)(i)(B). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensmg process and fed back to industry. Send comments regarding burden estimate to the FOIA Library. and Information Colleclion Branch (T-6 A10MJ US. CONTINUATION SHEET Nuclear Regulatory Commission. Washington. DC 20555-0001. or by e-mail to lnfocollects Resourceilnrc gov. and the OMS reviewer at OMS Office of Information and Regulatory Attairs. (3150-0104). Attn: Desk Officer for the Nuclear Regulatory Commission. 725 17th Street NW Washington. DC 20503. e-mail • _ : • . _ - _ . The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor. and a person is not required to respond to a collection of information unless the document stafts:10:22:3 requesting or requiring the collection displays a currently valid 0MB control number 1. FACILITY NAME ■ 2. DOCKET NUMBER 3. LER NUMBER River Bend Station, Unit 1 050 YEAR SEQUENTIAL REV NUMBER NO. 458 □ 2023 - 003 - 01 052 | EVENT DESCRIPTION On August 29, 2023, River Bend Station (RBS) personnel recognized that the Drywell Atmosphere Radiation Monitor (RMS-RE112) [IL] [MON] particulate and gaseous channel conversion factors were out of tolerance. The monitor was declared inoperable and Technical Specification (TS) Limiting Condition of Operation 3.4.7, Reactor Coolant System Leakage Detection Instrumentation, Condition B was entered. The RMS-RE112 conversion factors were corrected, and the monitor was declared operable on September 7, 2023. The discrepancy was identified as part of an extent of condition review performed due to the Notice of Violation (ML23201A 132) issued to RBS on August 15, 2023, for failing to maintain reliable and accurate indications on five effluent radiation monitors. On July 17, 2023, a condition report was initiated requesting a work order to review and validate the RMS-RE112 conversion factors. On August 29, 2023, RBS personnel recognized that information had been available to determine that the conversion factors were out of tolerance since the condition report was initiated on July 17. Therefore, the date of discovery is July 17, 2023. The conversion factors have been out of tolerance for the life of the plant. Therefore, this event is being reported as an Operation or Condition Prohibited by Technical Specifications per 10 CFR 50.73(a)(2)(i)(B). EVENT CAUSE This event was caused by configuration controls that were inadequate to prevent human performance errors in development of radiation detector digital parameters and transfer of parameters into the detector's database at initial setup. SAFETY ASSESSMENT Limits on leakage from the Reactor Coolant Pressure Boundary (RCPB) are required so that appropriate action can be taken before the integrity of the RCPB is impaired. Leakage detection systems for the Reactor Coolant System (RCS) are provided to alert operators when leakage rates above normal background levels are detected and to supply quantitative measurement of rates. RMS-RE112 comprises one of three RCS leakage detection instrumentation systems required by RBS TS 3.4.7. At least one of the two remaining RCS leakage detection instrumentation systems of TS 3.4.7 remained operable during the 3-year LER past operability period. RMS-RE112 is not used to recognize and properly classify emergency conditions and is not classified as Equipment Important to Emergency Response (EITER). This event was of minimal significance to the health and safety of the public. CORRECTIVE ACTIONS Completed: The RMS-RE112 conversion factors were corrected and the monitor was declared operable on September 7, 2023. NRC Form 366A (10-01-2023) Page _2_ of _3_ | ML23319A429 | 0 | good
River Bend Station | Unit 1 | High Pressure Core Spray Inoperable due to Transformer Failure 8. Other Facilities Involved | 11-15-2023 | At 0132 CDT on September 19, 2022, River Bend Station (RBS) was operating at 100% power when the High Pressure Core Spray System (HPCS) was declared inoperable due to a transformer fault that occurred during Division Ill Standby Diesel Generator monthly surveillance testing. RBS entered Technical Specification 3.8.9, Condition E and declared HPCS and Standby Service Water System Pump 2C (SWP-P2C) inoperable. Reactor Core Isolation Cooling (RCIC) was verified operable. HPCS is a single train system at RBS, therefore an 8-hour report was submitted in accordance with 10 CFR 50.72(b)(3)(v)(D) as an event or condition that could have prevented the fulfilment of a safety function (EN 56116). This event is also being reported in accordance with 10 CFR 50. 73(a)(2)(v)(D) as an event or condition that could have prevented the fulfilment of a safety function. The condition was corrected by replacing the transformer on September 30, 2022. HPCS and SWP-P2C were restored to operable at 0921 CDT on September 30, 2022. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comp� wrth this mandatory collection request. 80 hours Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry Send comments regarding burden estimate to the FOIA Library. and lnfomnation Colleclion Branch (T-6 A10M). US CONTINUATION SHEET Nuclear Regulatory Commission. Washington. DC 20555-0001. or by e-mail to lnfocollects Resource il nrc.gov. and the 0MB reviewer at: 0MB Office of lnfomnation and Regulatory Affairs. (3150-0104). Attn. Desk Officer for the Nuclear Regulatory Comm,ssion. 725 17th Street NW. Washington. DC 20503: e-mail The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor. and a person is not required to respond to a collection of information unless the document htto \','.'✓W .. r1r:rfQ:i_§tc{f�srJ02_ 2 r3 requesting or requiring the collection displays a current� valid 0MB control number 1. FACILITY NAME ■ 2. DOCKET NUMBER 3. LER NUMBER River Bend Station, Unit 1 050 YEAR SEQUENTIAL REV NUMBER NO. 458 □ 2022 - 004 - 01 052 | EVENT DESCRIPTION At 0132 CDT on September 19, 2022, River Bend Station (RBS) was operating at 100% power. There were no other inoperable structures, systems, or components (SSCs) that contributed to this event. The Division Ill Diesel Generator [DG] was started per STP-309-0203, DIVISION Ill DIESEL GENERATOR OPERABILITY TEST. Approximately 5 seconds later the Main Control Room received multiple alarms on Division 3 components. The field operator performed a visual inspection of the Division Ill switchgear and discovered that the E22-S003, HPCS TRANSFORMER [XFMR] was damaged. The Division Ill Diesel Generator was secured and placed in maintenance mode. The transformer failure caused a loss of power to E22-S002, Division Ill 480 VAC switchgear [SWGR]. E22-S002, Division Ill 480 VAC switchgear supplies power to HPCS motor operated valves that are required to align flow to the reactor pressure vessel following system initiation. RBS entered Technical Specification (TS) 3.8.9, Condition E and immediately declared the High Pressure Core Spray System (HPCS) [BG] and Standby Service Water System Pump 2C (SWP-P2C) [Pl inoperable. This also placed RBS in a 14-day TS LCO shutdown action statement due to the inoperability of HPCS. Reactor Core Isolation Cooling (RCIC) [BN] was verified operable. On June 21, 2022, Preventive Work Order 53003640 was performed on the transformer. No signs of degradation were noted, and all acceptance criteria were met satisfactory. Following the completion of the preventive work and prior to the transformer fault, STP-309-0203, DIVISION Ill DIESEL GENERATOR OPERABILITY TEST was successfully completed on July 25, 2022, and again on August 22, 2022. Prior to this event HPCS and the Division 3 Transformer power source were operable. At time of discovery, the HPCS lost its initiation capability because the E22-S002, Division Ill 480 VAC switchgear would not have been powered from the Division Ill Standby Diesel Generator on any HPCS initiation signal. HPCS was inoperable and incapable of performing its design function during this event. RBS is reporting the event in accordance with 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfilment of a safety function. SAFETY ASSESMENT The RBS UFSAR states that in the event of a HPCS system failure such that HPCS cannot maintain reactor water level, the Automatic Depressurization System (ADS), which is independent of any other Emergency Core Cooling System (ECCS), reduces the reactor pressure so that flow from Low Pressure Coolant Injection (LPCI) [BO] and Low Pressure Core Spray (LPCS) [BM] systems enters the reactor vessel in time to cool the core and limit fuel cladding temperature. Additionally, high pressure makeup was available from RCIC. Two of three divisions of ECCS are required for the RBS loss of coolant accident analysis. While HPCS was out of service, Division 1 ECCS and Division 2 ECCS systems and ADS were operable and would have met the ECCS performance criteria of 1 0CFR50.46. The out of service time was maintained within the limits of RBS Technical Specifications. There were no actual Nuclear or Radiological safety consequences due to this event. This event was of minimal significance to the health and safety of the public. NRC Form 366A (10-01-2023) Page _2_ of _3_ | ML23319A436 | 0 | good
Grand Gulf Nuclear Station | Unit 1 | Valve Closure Test Failure Resulting in Condition Prohibited by Technical Specification | 11-30-2023 | On June 13, 2023, while trending as found periodic data from motor operated valve diagnostic test on 1 E61 F003B Drywell Purge Inlet Isolation Valve, it was identified that the butterfly valve disc was traveling past the valve seat, resulting in 1 E61 F003B and Division 2 of the drywell purge and initial vacuum relief subsystem being declared inoperable. 1 E61 F003A Division 1 drywell purge and initial vacuum relief subsystem was operable during this time. Per Grand Gulf Technical Specifications, two drywell post-Loss-of-Coolant Accident and two drywell purge vacuum relief subsystems shall be operable in MODES 1, 2 and 3. Division 2 drywell purge and vacuum relief subsystem was determined to have been inoperable since October 26, 2017. There were no consequences to the general safety of the public, nuclear safety, industrial safety or radiological safety. No radiological releases occurred due to this event. This report is made pursuant to 10 CFR 50.73 (a)(2)(i)(B), any operation or condition which was prohibited by the plant's Technical Specifications. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request 80 hours Reported LICENSEE EVENT REPORT (LER) lessons leamed are il<:orporated ilto the licensilg process and fed back to industry Send comments regardi1g burden estvnate to the FOIA. Library, and Information Colection Branch (T-6 A10M). US. CONTINUATION SHEET Nuclear Regulatory Convnission, Washr,gton, OC 20555-0001, or by e-mai to fnfocoUects Resource@nrc gov, and the 0MB reviewer at: 0MB Office of lnfoITT1Btion and Regulatory Affairs, (3150-0104), Atln: Oesk Officer for the Nuclear Regulatory Coornission, 725 17th Street NW, Washington. DC 20503; e-mail: o,ra subm1ss10n@omb eop gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of infoITT1Btion unless the doeument http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requimg the collection displays a currently valid 0MB control number 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Grand Gulf Nuclear Station, Unit 1 ■ 050 YEAR SE N Q U U M E B N E T R IA L R N E O V . 416 2023 - 001 - 01 □ 052 | Plant Conditions: Mode 1, 98 percent power Description of Event: On October 26, 2017, while performing surveillance for Division 2 post- Loss-of-Coolant Accident (LOCA) Drywell Vacuum Breaker operability, the operator did not observe any movements from the stem of the valve 1 E61 F003B Drywell Purge Inlet Isolation Valve upon initiation. The control room indications were indicating that the valve was opened and closed. Movements of the stem are required for Technical Specification Acceptance Criteria. Thus, the surveillance was completed unsatisfactory. The valve 1 E61 F003B and Division 2 Drywell Purge/Initial Vacuum Relief was declared inoperable. Upon inspection, the spline adapter of valve 1 E61 F003B was found slipping down the valve stem, causing the disengagement between the valve stem and the drive sleeve. Thus, the actuator was moving and indicating opened/closed. However, the valve didn't move. On October 27, 2017, the spline adapter was reinstalled per a work order and surveillance was re-performed satisfactorily. This included a current and switches only diagnostic test which was the current test standard for limit controlled soft seated butterfly valves. On January 24, 2019, it was identified that the diagnostic testing on motor operated valve (MOV) butterfly valves did not currently meet the requirements of GL 96-05/JOG program. This was due to not using a strain gauge to measure valve stem torque. The preventative maintenance requirements (PMRQs) and model work orders (MWOs) were updated for all applicable butterfly valves to reflect that the diagnostic testing required measuring the valve stem torque. On June 6, 2023, the periodic 1 E61 F003B MOV diagnostic test was performed with strain gauge on the stem per work order. The test data was within the criteria in the motor operator valve data record. On June 13, 2023, while trending as found periodic data from the MOV diagnostic test on 1 E61 F003B, it was identified that the butterfly valve's disc is traveling past the valve seat, resulting in valve 1 E61 F003B and Division 2 Drywell Purge/Initial Vacuum Relief being declared inoperable. The test data indicates that the valve is contacting the seat at 40 secs of the full 60 sec stroke time. After contacting the seat, the seating torque decreases (relaxes) and the valve continues to travel for 20 secs past the seat. This MOV design has a full travel of 90 degrees. With the actuator in the full open position, the valve disk is 60 degrees open. Conversely with the actuator in the full closed position, the valve disk is 30 degrees open. This valve has no torque switch in the circuit and is seated using the limit switches. On June 16, 2023, the actuator/valve assembly was adjusted to the proper required position per work order. This was followed by a satisfactory as left diagnostic test using strain gauge to measure valve stem torque. The diagnostic test indicated that the valve disk is now going to full closed position when the actuator is stroked to the full close position. NRC Form 366A (10-01-2023) Page _2_ of __3 _ | ML23334A051 | 0 | good
Quad Cities Nuclear Generating Station | Unit 2 | Turbine Trip and Automatic Reactor Scram due to High Moisture Separator Level | 11-30-2023 | On August 11, 2023, at 0329, Quad Cities Unit 2 had an automatic scram from full power due to a trip of the main turbine. A fault in the Essential Service System (ESS) caused a feedwater heater (FWH) system transient. The drain valve for the 2A Moisture Separator Drain Tank (MSDT) did not open rapidly enough to prevent water level in the moisture separators from reaching the established turbine trip setpoints. The Unit 2 Main Turbine tripped as designed and generated an automatic reactor scram. All control rods inserted and the scram was uncomplicated. Containment isolation valves actuated closed in multiple systems on a valid Group II signal. The cause of the event is an improperly tuned Level Controller for the 2A MSDT allowing the high level turbine trip to be reached following a FWH transient. Completed corrective action was a component recalibration. Planned actions are procedure changes and training. This report is being submitted per 10 CFR 50.73(a)(2)(iv)(A) for an event that resulted in manual or automatic actuation of the reactor protection system including a reactor scram. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Litrary, and Information CoDections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of lnfonnation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclea.< Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of infonnalion unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3Q requesting or requiring the collection displays a currently vaUd 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 00 050 SEQUENTIAL REV YEAR NUMBER NO. Quad Cities Nuclear Generating Station Unit 2 05000-265 0 052 2023 - 001 01 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in text as [XX]. EVENT IDENTIFICATION Turbine Trip and Automatic Reactor Scram due to High Moisture Separator Level CONDITION PRIOR TO EVENT Unit: 2 Event Date: August 11, 2023 Event Time: 0329 CDT Reactor Mode: 1 Mode Name: Power Operation Power Level: 100% No structures, components, or systems that were inoperable at the start of the event that contributed to the event. A. DESCRIPTION OF EVENT On August 11th, 2023, at 0329, Quad Cities Unit 2 had an automatic scram from full power due to a trip of the main turbine [TRB]. A fault in the Essential Service System (ESS)[UJX] caused a feedwater heater (FWH)[HX] system transient. The drain valve [LC] for the 2A Moisture Separator Drain Tank (MSDT)[SN][TK] did not open rapidly enough to prevent water level in the moisture separators [MSR] from reaching the established turbine trip setpoints. The Unit 2 Main Turbine tripped as designed and generated an automatic reactor scram. All control rods were inserted and the scram was uncomplicated. Containment isolation valves actuated closed in multiple systems on a valid Group II signal. B. CAUSES OF EVENT The cause of the scram was an improperly tuned emergency level control valve (LCV) for a MSDT. Tuning was performed by a utility technician based on knowledge of the component and their understanding of plant response without adequate work instructions. There was no evidence of time pressure during this evolution. The controller's [LCO] setpoints were configured to provide a slower response than was appropriate for responding to a FWH level transient. In this case, the valve did not respond rapidly enough to prevent overfilling the associated MSDT and eventually tripping the turbine on high level in the moisture separators. C. SAFETY ANALYSIS SYSTEM DESIGN Moisture Separator Drain Tank Level Controller High pressure turbine exhaust steam is routed to four moisture separators prior to entering the low-pressure turbines. Steam passes through chevron separator elements to remove water droplets which drain to two MSDTs. On a High Level in the MSDT, the MSDT emergency drain valve opens and the normal MSDT LCV | ML23334A076 | 0 | good
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Misaligned Spacer Prevented Tie Breaker Closing Coil Armature Operation on a Magne-Blast for EDG A Subsystem | 12-01-2023 | On April 12, 2023, with James FitzPatrick Nuclear Power Plant (JAF) was at 100% power the Emergency Diesel Generator (EDG) “A” and “C” tie breaker (71-10504) did not close during a performance of monthly full load surveillance test (ST-9BA). This was caused by binding of the closing coil armature of the breaker due to a misaligned spacer installed in June 2021. The cause of this condition is inadequate procedural guidance to ensure proper orientation/alignment of the close coil sleeve and spacers. Tie breaker failure to close rendered the “A” Emergency Diesel Generator (EDG) subsystem inoperable. It was determined that this deficiency began after the last successful test/actuation on March 13, 2023. This condition was prohibited by Technical Specifications (TS), which is reportable per 10 CFR 50.73(a)(2)(i)(B) and 10 CFR 50.73(a)(2)(v)(A). The condition was corrected when the 71-10504 Tie Breaker was replaced on April 13, 2023. A corrective action was completed to revise MP-054.01 and MP-054.03 to improve spacer installation process and ensure proper breaker actuation. NRC FORM 366 (10-01-2023) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 LICENSEE EVENT REPORT (LER) hours. Reported lessons learned are incorporated into the licensing process and fed CONTINUATION SHEET back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory (See NUREG-1022, R.3 for instruction and guidance for completing this form Commission, 725 17th Street NW, Washington, DC 20503; email: http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 YEAR SEQUENTIAL REV NUMBER NO. James A. FitzPatrick Nuclear Power Plant 05000333  052 2023 – 004 – 00 | Background The Emergency Onsite Power Supply System [EIIS identifier: EK] consists of two redundant Emergency Diesel Generator (EDG) subsystems. Each EDG subsystem consists of two EDG units. The capability of the two units in the subsystem to start, force parallel, and attain rated voltage and frequency together within 10 seconds, and run the necessary engineered safeguard loads, meets the requirements for the Emergency AC Power System. The EDG logic system utilizes a force parallel design. This allows two EDG units to parallel onto the respective Emergency AC bus together to provide a combined load. The “A” subsystem tie breaker (71-10504) force parallels the “A” and “C” EDG units. Event Description On April 12, 2023, with James FitzPatrick Nuclear Power Plant (JAF) at 100% power the EDG “A” and “C” tie breaker (71-10504) did not close during a performance of monthly full load surveillance test (ST-9BA). The “B” EDG subsystem was verified to be operable. Troubleshooting identified that the issue was internal to the breaker. On April 13, the 71-10504 Magne-Blast circuit breaker was replaced and at 23:00 the “A” EDG subsystem was restored to service. Total out of service time was approximately 43 hours. Event Analysis The removed Magne-Blast circuit breaker was sent to General Electric (GE) for evaluation. The GE investigation identified that intermittent binding of the close coil armature occurred, which prevented the full stroke required to close the circuit breaker. The binding was repeated multiple times during the investigation. Visual inspection confirmed the closing coil appeared to be askew in the assembly and the spacers were not aligned correctly. The misaligned spacer did not allow the closing coil sleeve to seat properly in the cutout of the support. This decreased the clearance required for the closing coil armature to move freely inside the full length of the assembly. The decreased clearance caused the armature to bind against the spacer and the inside of the sleeve. The armature does not experience binding in all positions of the armature. The armature was rotated and then it was identified that it only became bound in certain positions. A properly installed coil assembly will not become loose, and closing coil will be able to operate without binding. It was determined that the misaligned spacer was installed in June 2021 when 71-10504 was replaced. All subsequent surveillance tests were successful from June 2021 until the failure on April 12, 2023. On October 19, 2023, JAF performed tests of the removed breaker closing coil armature to demonstrate how the armature rotates during each breaker actuation. It rotates at a regular fix quantity during each actuation; therefore, the specific position which caused binding was rotated to that position during the last test on March 13, 2023. Based on this evaluation, the “A” EDG subsystem tie breaker 71-10504 would not have closed between March 13 and April 12, a condition which would have caused the “A” EDG subsystem to be inoperable. Page 2 of 4 | ML23335A068 | 0 | good
i | Unknown Unit | Turbine Stop Valve Limit Switch Failure due to Lubricant Degradation | 12-04-2023 | On 9/7/2023 during surveillances of the turbine stop valves (TSV), limit switch 1 C71-N006G failed. The component was sent offsite for failure analysis. Component failure analysis was complete on 10/18/2023 and determined that the cause was attributed to degradation of switch lubricant which established firm evidence that a past inoperability condition existed. The component 1C 71-N006G is the TSV-4 closure Reactor Protection System (RPS) channel A2 scram limit switch. This device is required by technical specifications to support LCO 3.3.1.1 function 8 (RPS) and LCO 3.3.4.1 (End of Cycle - Recirculation Pump Trip or EOC-RPT). Each TSV position is monitored by two limit switches (for TSV-4, A2 and 82 channels). This condition results in the TSV-4 input to RPS A2 as well as one channel of the EOC-RPT trip being INOPERABLE. The appropriate LCO Conditions and Required Actions were entered and tracked. The RPS and EOC RPT functions were maintained due to the redundant channels remaining OPERABLE. There were no reportability thresholds applicable to this issue at the time of the event, and there was no loss of safety function. The condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) for operation or condition prohibited by Technical Specifications. Immediate corrective actions were taken to replace the component and restore the associated channel to OPERABLE. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send conments regarding burden estimate to the FOIA, Library, and lnfonnation Collections Branch (T-6 A10M), U.S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mai to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Slreet NW, Washington, DC 20503; e-mal: oira submiss1on@omb.eop.gov. The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document h Hp://www.nrc.gov/reading-rm/d oc-co Il ections/nuregs/staff/ sr1 022/r3/) requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Ix] 050 YEAR SEQUENTIAL REV LaSalle County Station, Unit 1 (cid:143) 00373 2023 - 002 00 052 | Plant and System Identification LaSalle Country Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the main turbine system. The affected component was the turbine stop valve (TSV) limit switch 1C71-N006G. This is the limit switch for the TSV number 4 Closure Reactor Protection System (RPS) A2 channel. Condition Prior to Event Unit(s): 1 Date: October 18, 2023 Time: 00:00 CDT Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 100 percent Description On 09/07/2023 the limit switch on Unit 1 TSV-4 failed to actuate during surveillance testing. The limit switch is normally held in the actuated position during unit operation and only allowed to return to the relaxed, shelf state position, upon closure of the turbine stop valve. The failed limit switch, 1C71-N006G, was replaced and sent offsite for component testing and failure analysis. The component failure analysis (documented in report dated October 18, 2023) verified the limit switch malfunction and determined the cause was attributed to degradation of switch lubricant. Cause Analysis attributed the failure to the switch shaft and shaft bearing degraded lubrication causing the shaft to bind in the actuated (Turbine Stop Valve open) position. The cause of the limit switch lubricant degradation was elevated temperatures due to a steam leak in close proximity. This steam leak has circumvented previous corrective actions such as use of high temperature switches and limit switch housing modifications. Reportability and Safety Analysis The component 1C71-N006G is the TSV-4 Closure RPS channel A2 scram limit switch. This device is required to be OPERABLE per LCO 3.3.1.1 Function 8 (RPS) and LCO 3.3.4.1 (EOC-RPT). TSV-4 was fully closed during the surveillance, which should have resulted in the 1C 71-N006G switch being open. Each TSV position is monitored by two limit switches (for TSV-4, A2 and B2 channels). This condition results in the TSV-4 input to RPS A2 as well as one channel of the EOC-RPT trip being INOPERABLE. The appropriate LCO Conditions and Required Actions were entered and tracked. The RPS and EOC-RPT functions were maintained due to the redundant channels remaining OPERABLE. There were no reportability thresholds applicable to this issue at the time of the event, and there was no loss of safety function. Upon receipt of the failure analysis on October 18, 2023, the station was made aware that a past inoperability period existed from the test failure that occurred on September 7, 2023. The inoperability period was greater than allowed by TS LCO 3.3.1.1 and 3.3.4.1, as indicated below. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's TS. • LCO 3.3.1.1 requires that the RPS instrumentation for each function is OPERABLE, and Condition A applies to one or more required channels being inoperable requires that the channel or its associated trip system is placed in trip within 12 hours. In this case, the station had exceeded the completion time of 12 hours, when the | ML23338A183 | 0 | good
Monticello Nuclear Generating Plant | Unknown Unit | Condition Prohibited by Technical Specifications due to Inoperable Main Steam Line Low Pressure Isolation Switch | 12-04-2023 | On October 10, 2023 at 0826, with Monticello Nuclear Generating Plant in Mode 1 at 100 percent power, calibration commenced for PS-2-134B, the B1 Channel Main Steam Line Low Pressure Isolation switch. The calibration is required for the Low Main Steam Line Pressure Isolation function for Technical Specification 3.3.6.1, Primary Containment Isolation Instrumentation. The B1 Channel switch was found out of tolerance low. On October 7, 2023 at 0228, while at 10 percent power, the plant entered Mode 1, which is the Mode of Applicability for this Technical Specification 3.3.6.1 function. The condition of inoperability of the B1 Channel was not known upon entering Mode 1 and the required technical specification actions to place this Channel in trip were not taken. This event is reportable under 10CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by TS 3.3.6.1. The cause of the inoperability was instrument drift. The B1 Channel switch was brought within tolerance prior to completion of the B1 channel calibration procedure on October 10, 2023 at 0901. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported r;»•"fOt,<., lessons learned are incorporated into the licensing process and fed back to industry. Send comments l~\ LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. = : Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET \ .r Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory ., •it••·♦ Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME ■ 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV I I~ I I □ NUMBER NO. Monticello Nuclear Generating Plant 263 D 052 2023 - I 003 - 00 I | EVENT DESCRIPTION On October 10, 2023 at 0826, with Monticello Nuclear Generating Plant in Mode 1 at 100 percent power, testing commenced for PS-2-134B [EIIS CODE: JM], the B1 Channel Main Steam Line Low Pressure Isolation switch, per the quarterly Technical Specification (TS) Surveillance Requirement (SR) 3.3.6.1.4 channel calibration procedure for function 1.b. Function 1.b is the Low Main Steam Line (MSL) Pressure Isolation function for TS 3.3.6.1, Primary Containment Isolation Instrumentation. The B1 Channel switch was found out of tolerance at 641.6 psig compared to the TS allowable value of greater than or equal to 815 psig. The B1 Channel switch was brought into tolerance prior to completion of the B1 Channel switch SR 3.3.6.1.4 channel calibration procedure on October 10, 2023 at 0901. On October 24, 2023, a review of past Operability was completed for the B1 Channel switch. The B1 Channel switch as- found and as-left values were acceptable during the previous SR 3.3.6.1.4 channel calibration procedure on July 3, 2023. Based on review of the plant process computer MSL pressure data, the B1 Channel switch acceptably tripped at greater than the TS allowable value during the September 27, 2023 Scram. However, when the plant was starting up, in Mode 2, at 4 percent power on October 7, 2023 at 0047, the data showed the B1 Channel switch reset prior to 686.7 psig. Since this switch is designed to reset at a higher pressure than the trip pressure, this was the first indication that the B1 Channel switch was below the allowable value. Since the plant mode switch was in Startup, the MSL low pressure Containment Isolation signal was bypassed. On October 7, 2023 at 0228 while at 10 percent power, the plant entered Mode 1, which is the Mode of Applicability for Technical Specification 3.3.6.1 function 1.b. The condition of inoperability of the B1 Channel was not known upon entering Mode 1 and the required technical specification actions to place this Channel in trip were not taken. The Primary Containment Isolation system receives inputs from four channels for the MSL Low Pressure trip function. The trip function, active only during Mode 1, uses a one-out-of-two taken twice logic to initiate isolation of all Main Steam Isolation valves (MSIVs), MSL drain valves, and recirculation sample isolation valves. One of the two A channels and one of the two B channels must trip to initiate the Primary Containment Isolation. In Mode 1, with one channel inoperable, TS 3.3.6.1 Condition A requires placing that channel in trip within 24 hours. When Condition A is not met, Condition E, as directed by Condition C and Table 3.3.6.1-1 requires entry to Mode 2 within 6 hours. This event is reportable under 10 CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by TS 3.3.6.1. DATES AND APPROXIMATE TIMES OF MAJOR OCCURANCES • July 3, 2023 at 0850: The B1 Channel switch as-found and as-left values were acceptable per the SR 3.3.6.1.4 channel calibration procedure. • September 27, 2023 at 1041: During Reactor Scram and Group 1 isolation on C channel MSL high flow, the B1 Channel switch tripped at 925.5 psig, which is acceptably greater than the TS minimum allowable value. • October 7, 2023 at 0047: During plant startup, the B1 Channel switch reset prior to 686.7 psig, which is less than the TS minimum allowable value. • October 7, 2023 at 0228: Event Date. Plant mode switch was placed in run and the plant entered Mode 1. • October 8, 2023 at 0228: The required completion time to place the B1 Channel in trip based on TS 3.3.6.1 Condition A for “One or more required channels inoperable.” • October 8, 2023 at 0828: The required completion time to be in Mode 2 due to TS 3.3.6.1 Condition E, as directed by Condition C and Table 3.3.6.1-1. | ML23338A184 | 0 | good
Peach Bottom Atomic Power Station | Unit 3 | Main Steam Isolation Valves Stroke Times Exceed Technical Specification Limit | 12-14-2023 | On October 16, 2023, during performance of a surveillance test while beginning a refueling outage, the stroke times of Main Steam Isolation Valves (MSIVs) exceeded the Technical Specifications limit of five (5) seconds. The apparent causes attributed to two (2) of the MSIVs had the potential to exist during the previous operating cycle. Therefore, the two (2) MSIVs are being reported under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications because the apparent causes had the potential to have existed longer than allowed by Technical Specifications. The condition was corrected and the valves were returned to satisfactory performance by adjusting the dashpots and exhaust restrictors as needed. There were no safety consequences associated with this condition, as the valve stroke times did not exceed the times considered in the safety analysis. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 SEQUENTIAL REV YEAR NUMBER NO. Peach Bottom Atomic Power Station, Unit 3 00278  052 2023 - 002 - 00 | Event Description On October 16, 2023, during performance of a surveillance test, the stroke time of the ‘A’ Outboard Main Steam Isolation Valve (MSIV) exceeded the Technical Specifications limit of five (5) seconds. The valve stroke time was 6.2 seconds. This test was performed in Mode 3 (hot shutdown) while the unit was being shut down for a refueling outage. Transition to Mode 4 (cold shutdown) was made shortly after completion of the test, and the mode of applicability was exited. The cause of the slow stroke time was attributed to drift in the valve dashpot. Follow-up testing was performed during the outage and adjustments were made as needed. The stroke time was verified to be satisfactory before the unit was restarted from the refueling outage. Additionally, the ‘B’ Inboard MSIV also exhibited a slow stroke time of 5.1 seconds. The cause of this condition was attributed to delayed actuation, likely due to debris or contamination in the solenoid valve. The ‘B’ Outboard MSIV stroked in 5.5 seconds, however this could not be replicated in subsequent testing. The stroke times for these valves were adjusted accordingly and were verified to be satisfactory before the unit was restarted from the refueling outage. The remaining valves stroked within specified Technical Specifications limits. There are two (2) MSIVs welded in a horizontal run of each of the four (4) main steam lines, with one (1) valve as close as possible to the primary containment barrier inside, and the other just outside the barrier. The valves, when closed, form part of the nuclear system process barrier. The MSIVs are operated by pneumatic pressure and by the action of compressed springs. The upper end of the valve stem is attached to a combination air cylinder and hydraulic dashpot that are used for opening and closing the valve and for speed control, respectively. Speed is adjusted by a valve in the hydraulic return line alongside the dashpot. Verifying that the isolation times of each MSIV is within the specified Technical Specifications limits is required to demonstrate operability. The isolation time test ensures that the MSIVs will isolate in a time period that does not exceed the times assumed in the design basis accident analyses. In all cases, the times in the accident analysis were not exceeded because the analysis is performed assuming at least 10 seconds for the MSIV closure time. This report is being made under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. Although there was no evidence of degradation during the prior refueling outage or operating cycle, the condition associated with the ‘A’ Outboard MSIV likely existed for longer than allowed by Technical Specifications. Similarly, there was no evidence of degradation for the MSIVs on the ‘B’ main steam line. The time frame associated with the condition which caused the ‘B’ Inboard MSIV to exhibit a slow stroke time cannot be determined, but the valve is conservatively being included in this report. The ‘B’ Outboard MSIV stroke time that was not repeatable has no firm evidence of existing prior to the time of discovery and is not included within the reportable scope of this LER. The performance of the valves has been entered into the Corrective Action Process for further evaluation of the test performance and evaluation methodology. There were no other systems, structures or components that were inoperable that contributed to the event. | ML23348A260 | 0 | good
edwin i. hatch | Unknown Unit | Manual Reactor Trip Due To Loss of Feedwater 5. Evant Data I. LER Number 7. Report Data 8. Other FacllltlH Involved Month Day Year y.., lle N q u u m e b n e ll r a l Rev N i o s . i on Month Day y.., Faclllly Name □ 050 Dockal Number - - 11 01 2023 2023 003 00 12 19 r 2023 Faclllly Nam• □ 052 Dockal Number 9. Operating Mode 0. Po-r Laval 1 056 11. This Report Is Submitted Pursuant to the Requirements of 10 CFR §: (Check all that apply) 10 CFR Part 20 □ 20.2203(a)(2)(vl) 10 CFR Part 50 □ 50.73(a)(2)(11)(A) □ 50.73(a)(2)(vlll)(A) □ 73.1200(8) □ 20.2201(b) □ 20.2203(8)(3)(1) □ 50.36(c)(1 )(l)(A) □ 50. 73(8)(2)(11)(8) □ 50.73(a)(2)(vlll)(B) □ 73.1200(b) □ 20.2201(d) □ 20.2203(8)(3)(11) □ 50.36(c)(1 )(ll)(A) □ 50. 73(8)(2)(111) □ 50. 73(a)(2)(Ix)(A) □ 73.1200(c) □ 20.2203(8)(1) □ 20.2203(8)(4) □ 50.36(c )(2) ~ 50. 73(a)(2)(Iv)(A) □ 50.73(a)(2)(x) □ 73.1200(d) □ 20.2203(a)(2)(I) 10 CFR Part 21 □ 50.46(8)(3)(11) □ 50.7 3(a)(2)(v)(A) 10 CFR Part 73 □ 73.1200(e) □ 20.2203(8)(2)(11) □ 21.2(c) □ 50.69(g) □ 50. 73(a)(2)(v)(B) □ 73.77(8)(1) □ 73.1200(f) □ 20.2203(8)(2)(111) □ 50.73(a)(2)(I)(A) □ 50. 73(8)(2)(v)(C) □ 73. 77(8)(2)(1) □ 73.1200(g) □ 20.2203(a)(2)(Iv) □ 50. 73(8)(2)(1)(8) □ 50. 73(8)(2)(v)(D) □ 73. n(a)(2)(11) □ 73.1200(h) □ 20.2203(a)(2)(v) □ 50.73(a)(2)(I)(C) □ 50.7 3(a)(2)(vll) □ OTHER (Specify here, in abstract, or NRC 366A). 12. Licensee Contact for this LER Llcanaaa Contact Phone Number (Include area coda) Jimmv Collins - Licensina Manaaer 9124532342 13. Complete One Line for each Component Failure Described In this Report Cau■a System Component Manufacturer Reportable to IRIS Cause System Component Manufacturer Reportable to IRIS X SJ p 8580 y 14. Supplemental Report Expected Month Day Year 15. Expected SubmlAlon Data ~ No □ Yes (If yes, complete 15. Expected Submission Date) 11. Abatract (Limit to 1326 spaces, i.e., approximalely 13 single-spaced typewritten lines) On November 1, 2023, reactor power was being lowered on Unit 2 to support removal of the 'A' Reactor Feed Pump (RFP} from service due to a suction pipe drain line leak. The 'A' RFP was removed from service and isolated at 0642 EDT. During this evolution, water from the leak on the drain line of the 'A' RFP entered various electrical cabinets and components related to the 'B' RFP, causing the 'B' RFP to trip at 0648 EDT. The trip of the 'B' RFP resulted in a loss of feedwater and lowering of reactor water level. Due to the lowering reactor water level, operators manually inserted a reactor trip in anticipation of water level dropping to the automatic reactor protection system (RPS} trip setpoint. The Reactor Core Isolation Cooling (RCIC) and High Pressure Coolant Injection (HPCI) pumps were used to restore reactor water level. All safety system responded as required. The cause of the leak from the 'A' RFP suction drain line was a pipe shear due to excessive stresses from thermal cycling and flow induced vibration. This was corrected by implementing a design change that cut and capped that portion of piping. The cause of the 'B' RFP trip was electrical grounding due to water intrusion from the 'A' RFP leak resulting in an invalid low suction pressure trip on the 'B' RFP. NRC FORM 388A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Ellllmatad burden per l8Sp0IIS8 to comply with this mandaby collection requell: 80 hours. Reported lessons learned ara lncorporatad Into the lk:enslng process and fed back to lnduatly. Send comments LICENSEE EVENT REPORT (LER) regardng burden estimate to the FOIA, Library, and lnfonnallon Collections Bnlnch (T-8 A10M), U. S. CONTINUATION SHEET Nuclear Regulatory Commlulon, Watlqton, DC 20566-0001, or by email to lnfoc:alledl.Resoun:e@nre.gov, and the 0MB r9¥1eMr at 0MB Offlce of Information and Regulaloly AffallB, (3150-0104), Altn: Delk Officer for the Nuclear Regufaby Commlalion, 725 17th Slreel NW, (See NUREG-1022, R.3 for Instruction and guidance for completing this fonn Washington, DC 20503; ernall: oira submlssicn@omb 80J) gov. The NRC may not conduct or htto·/fwww.nrc.gov/reading-rm/doe:collections/nuregs/staff/s.l1022lQLl sponsor, and a pe!S011 la not required to respond to, a c:olledion of lnfonnatlon unless the d0a1ment requesting or requiring the c:ollection displays a cum,ntly valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV IEdwin I. Halch, Unit 2 00366 _□t5- I NUMBER 1-NO0. I 052 003 NARRATIVE EVENT DESCRIPTION On November 1, 2023, reactor power was being lowered on Unit 2 to support removal of the 'A' Reactor Feed Pump (RFP) [EIIS Code: SJ] from service due to a leak on a drain line connected to the suction piping of the pump. At 0642 EDT with the reactor at approximately 56% rated thermal power, the 'A' RFP was removed from service and isolated. While removing the 'A' RFP from service, water from the leak on the drain line of the 'A' RFP entered various electrical cabinets and components related to the 'B' RFP, causing the 'B' RFP to trip at 0648 EDT. The trip of the 'B' RFP resulted in a loss of feedwater and reactor water level lowering. Due to the lowering reactor water level, operators manually inserted a reactor trip in anticipation of water level dropping to the automatic trip setpoint. The Reactor Core Isolation Cooling (RCIC) [EIIS Code: BN] and High Pressure Coolant Injection (HPCI) [EIIS Code: BJ] pumps automatically started and were used to restore reactor water level. Secondary containment isolated and Standby Gas Treatment (SBGT) [EIIS Code: BH] autostarted, and Group 2 and Group 5 primary containment isolation valves [EIIS Code: JM] isolated as expected when their setpoints were reached. There was no safety related equipment inoperable at this time and no other nonfunctional, non-safety equipment that contributed to this event. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual actuation of the reactor protection system and automatic actuation of general containment isolation signals affecting containment isolation valves in more than one system. Additionally, HPCI and RCIC automatically started when their reactor water level setpoints were reached. EVENT CAUSE ANALYSIS A root cause analysis was performed and determined that the direct cause of the leak from the 'A' RFP suction drain line was a pipe shear due to excessive stresses from thermal cycling and flow induced vibration. The cause of the 'B' RFP trip was electrical grounding due to water intrusion from the 'A' RFP leak resulting in an Invalid low suction pressure trip on the 'B'RFP. SAFETY ASSESSMENT There were no safety consequences as a result of this event. All safety related systems functioned as designed during this event. The operating crew responded correctly to the event. The applicable abnormal/emergency operating procedures were entered. The event was within the analysis of the Updated Final Safety Analysis Report (UFSAR) Chapter 15. No radiological release occurred due to this event. CORRECTIVE ACTION The leak from the 'A' RFP suction piping drain line was corrected by implementing a design change that cut and capped that portion of piping. The cause of the 'B' RFP trip was electrical grounding due to water intrusion from the 'A' RFP leak resulting in an invalid low suction pressure trip on the 'B' RFP. All electrical components related to the 'B' RFP were investigated. Impacted components were dried out or replaced as required. PREVIOUS SIMILAR EVENTS None. NRC FORM 386A (1~1-2023) Page 2 of 2 | 12-19-2023 | 12. Licensee Contact for this LER Llcanaaa Contact Phone Number (Include area coda) Jimmv Collins - Licensina Manaaer 9124532342 13. Complete One Line for each Component Failure Described In this Report Cau■a System Component Manufacturer Reportable to IRIS Cause System Component Manufacturer Reportable to IRIS X SJ p 8580 y 14. Supplemental Report Expected Month Day Year 15. Expected SubmlAlon Data ~ No □ Yes (If yes, complete 15. Expected Submission Date) 11. Abatract (Limit to 1326 spaces, i.e., approximalely 13 single-spaced typewritten lines) On November 1, 2023, reactor power was being lowered on Unit 2 to support removal of the 'A' Reactor Feed Pump (RFP} from service due to a suction pipe drain line leak. The 'A' RFP was removed from service and isolated at 0642 EDT. During this evolution, water from the leak on the drain line of the 'A' RFP entered various electrical cabinets and components related to the 'B' RFP, causing the 'B' RFP to trip at 0648 EDT. The trip of the 'B' RFP resulted in a loss of feedwater and lowering of reactor water level. Due to the lowering reactor water level, operators manually inserted a reactor trip in anticipation of water level dropping to the automatic reactor protection system (RPS} trip setpoint. The Reactor Core Isolation Cooling (RCIC) and High Pressure Coolant Injection (HPCI) pumps were used to restore reactor water level. All safety system responded as required. The cause of the leak from the 'A' RFP suction drain line was a pipe shear due to excessive stresses from thermal cycling and flow induced vibration. This was corrected by implementing a design change that cut and capped that portion of piping. The cause of the 'B' RFP trip was electrical grounding due to water intrusion from the 'A' RFP leak resulting in an invalid low suction pressure trip on the 'B' RFP. NRC FORM 388A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Ellllmatad burden per l8Sp0IIS8 to comply with this mandaby collection requell: 80 hours. Reported lessons learned ara lncorporatad Into the lk:enslng process and fed back to lnduatly. Send comments LICENSEE EVENT REPORT (LER) regardng burden estimate to the FOIA, Library, and lnfonnallon Collections Bnlnch (T-8 A10M), U. S. CONTINUATION SHEET Nuclear Regulatory Commlulon, Watlqton, DC 20566-0001, or by email to lnfoc:alledl.Resoun:e@nre.gov, and the 0MB r9¥1eMr at 0MB Offlce of Information and Regulaloly AffallB, (3150-0104), Altn: Delk Officer for the Nuclear Regufaby Commlalion, 725 17th Slreel NW, (See NUREG-1022, R.3 for Instruction and guidance for completing this fonn Washington, DC 20503; ernall: oira submlssicn@omb 80J) gov. The NRC may not conduct or htto·/fwww.nrc.gov/reading-rm/doe:collections/nuregs/staff/s.l1022lQLl sponsor, and a pe!S011 la not required to respond to, a c:olledion of lnfonnatlon unless the d0a1ment requesting or requiring the c:ollection displays a cum,ntly valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV IEdwin I. Halch, Unit 2 00366 _□t5- I NUMBER 1-NO0. I 052 003 | EVENT DESCRIPTION On November 1, 2023, reactor power was being lowered on Unit 2 to support removal of the 'A' Reactor Feed Pump (RFP) [EIIS Code: SJ] from service due to a leak on a drain line connected to the suction piping of the pump. At 0642 EDT with the reactor at approximately 56% rated thermal power, the 'A' RFP was removed from service and isolated. While removing the 'A' RFP from service, water from the leak on the drain line of the 'A' RFP entered various electrical cabinets and components related to the 'B' RFP, causing the 'B' RFP to trip at 0648 EDT. The trip of the 'B' RFP resulted in a loss of feedwater and reactor water level lowering. Due to the lowering reactor water level, operators manually inserted a reactor trip in anticipation of water level dropping to the automatic trip setpoint. The Reactor Core Isolation Cooling (RCIC) [EIIS Code: BN] and High Pressure Coolant Injection (HPCI) [EIIS Code: BJ] pumps automatically started and were used to restore reactor water level. Secondary containment isolated and Standby Gas Treatment (SBGT) [EIIS Code: BH] autostarted, and Group 2 and Group 5 primary containment isolation valves [EIIS Code: JM] isolated as expected when their setpoints were reached. There was no safety related equipment inoperable at this time and no other nonfunctional, non-safety equipment that contributed to this event. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual actuation of the reactor protection system and automatic actuation of general containment isolation signals affecting containment isolation valves in more than one system. Additionally, HPCI and RCIC automatically started when their reactor water level setpoints were reached. EVENT CAUSE ANALYSIS A root cause analysis was performed and determined that the direct cause of the leak from the 'A' RFP suction drain line was a pipe shear due to excessive stresses from thermal cycling and flow induced vibration. The cause of the 'B' RFP trip was electrical grounding due to water intrusion from the 'A' RFP leak resulting in an Invalid low suction pressure trip on the 'B'RFP. SAFETY ASSESSMENT There were no safety consequences as a result of this event. All safety related systems functioned as designed during this event. The operating crew responded correctly to the event. The applicable abnormal/emergency operating procedures were entered. The event was within the analysis of the Updated Final Safety Analysis Report (UFSAR) Chapter 15. No radiological release occurred due to this event. CORRECTIVE ACTION The leak from the 'A' RFP suction piping drain line was corrected by implementing a design change that cut and capped that portion of piping. The cause of the 'B' RFP trip was electrical grounding due to water intrusion from the 'A' RFP leak resulting in an invalid low suction pressure trip on the 'B' RFP. All electrical components related to the 'B' RFP were investigated. Impacted components were dried out or replaced as required. PREVIOUS SIMILAR EVENTS None. NRC FORM 386A (1~1-2023) Page 2 of 2 | ML23353A109 | 0 | good
River Bend Station | Unit 1 | Not Found | 12-28-2023 | On November 2, 2023, with River Bend Station in Mode 4 and 0% power, personnel discovered an unrecognized surveillance failure for the Division I Drywall Post Accident Radiation Monitor (RMS-RE20A). The monitor was declared Inoperable and the appropriate Technical Specification Condition was entered. The surveillance was reperformed on RMS-RE20A and the monitor was declared Operable on November 12, 2023. The surveillance failure was due to human performance error. This condition is being reported as an Operation or Condition Prohibited by Technical Specifications per 10 CFR 50.7 3(a)(2)(i)(B). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, OC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW. Washington. DC 20503; e·mail: :)l(a Jubr:11ss1on '¢.:on�o eo:J Q0'1. The NRG may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document (See NUREG-1022, R.3 for instruction and guidance for completing this form requesting or requiring the collection displays a currently valid 0MB control number. http://www. nrc. gov/ reading-rm/doc-collections/nu reas/staff /sr 1 022/r3;; 1. FACILITY NAME ■ 2. DOCKET NUMBER 3. LER NUMBER River Bend Station, Unit 1 050 YEAR SEQUENTIAL REV NUMBER NO. 458 □ 2023 004 00 052 | EVENT DESCRIPTION River Bend Station (RBS) Technical Specification (TS) Limiting Condition of Operation (LCO) 3.3.3.1, Post Accident Monitoring (PAM) Instrumentation requires both Division I and Division II Drywall Post Accident Radiation Monitors to be Operable in Modes 1 and 2. If one Drywall Post Accident Radiation Monitor is declared Inoperable, LCO 3.3.3.1 Condition A is entered, and the monitor must be restored to Operable in 30 days. On November 2, 2023, with RBS in Mode 4 and 0% power, personnel discovered an unrecognized surveillance failure (STP-511-4289 RMS-Primary Drywall Area Radiation Monitor, Channel Calibration RMS-RE20A) for the Division I Drywall Post Accident Radiation Monitor (RMS-RE20A) [IL] [MON] during a review of a previously performed work package. The monitor was declared Inoperable and LCO 3.3.3.1 Condition A was entered. The surveillance was performed with satisfactory results on November 2, 2023, and the monitor was declared Operable on November 12, 2023. The unrecognized surveillance failure was identified during a review of the last performance of STP-511-4289 which was performed on February 28, 2023. It was determined that RMS-RE20A was left in an out of tolerance state and did not meet the requirements of the surveillance. Therefore, RMS-RE20A is considered Inoperable from February 28, 2023, until November 12, 2023. LCO 3.3.3.1 is applicable in Modes 1 and 2. RBS was in Mode 4 on February 28, 2023, and did not exit Mode 4 until entering Mode 2 on June 15, 2023. RBS then went from Mode 2 to Mode 1 on June 16, 2023, and remained in Mode 1 until entering Mode 3 on October 29, 2023, for a planned outage. RBS did not enter an applicable Mode again until November 13, 2023, when Mode 2 was entered for start up to exit the planned outage. Therefore, RBS was Operating in a manner prohibited by TS from June 15, 2023, until October 29, 2023. Prior to February 28, 2023, STP-511-4289 was last performed on March 11, 2021, with satisfactory results. Therefore, RMS-RE20A was Operable until the failed surveillance performed on February 28, 2023. EVENT CAUSE The casual evaluation investigation has determined that the event was caused by a human performance error while performing the surveillance on February 28, 2023. The RBS technician performing the surveillance did not identify and correct a parameter that was found out of tolerance. SAFETY ASSESSMENT The primary purpose of the PAM instrumentation is to display plant variables that provide information required by the control room operators during accident situations. This information provides the necessary support for the operator to take the manual actions for which no automatic control is provided and that are required for safety systems to accomplish their safety functions for Design Basis Events. RMS-RE20B provides redundant function capability to RMS­ RE20A and was Operable from February 28, 2023, to November 12, 2023. Therefore, safety function was maintained throughout the time RMS-RE20A was Inoperable and this event was of minimal significance to the health and safety of the public. NRC Form 366A (10-01-2023) Page _2_ of _3_ | ML23362A034 | 1 | ok
Nine Mile Point | Unit 1 | Average Power Range Monitors Declared Inoperable Due to Trip of Reactor Recirculation Pump 12 | 12-15-2023 | On October 21, 2023, at 2048 EDT, Reactor Recirculation Pump #12 (RRP 12) tripped. Following the RRP trip, the Average Power Range Monitors (APRMs) flow bias trips were inoperable due to reverse flow through the RRP. The APRMS were restored to operable on October 21, 2023, at 2058 EDT, the RRP 12 discharge blocking valve was closed, eliminating the reverse flow condition, and returning the APRMs to operable. This event is reportable under 10 CFR 50. 73(a)(2)(v)(A) as any event or condition that could have prevented the fulfillment of a safety function of structures or systems that are needed to shut down the reactor and maintain it in a safe shutdown condition. The cause of the RRP 12 trip is a failed coupling on the tachometer generator. Corrective actions included restoring the tachometer to functional. The event described in this LER is documented in the plant's corrective action program report 04711520. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (03-14-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A1 0M), U. S Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington. DC 20503: email: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor. and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nureqs/staff/sr1022/r3D requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 SEQUENTIAL REV YEAR NUMBER NO. Nine Mile Point Unit 1 50-220 □ 052 2023 - 002 - 00 | THE ENERGY INDUSTRY IDENTIFICATION SYSTEM (EIIS) COMPONENT FUNCTION IDENTIFIED AND SYSTEM NAME OF EACH COMPONENT OR SYSTEM REFERRED TO IN THIS LER ARE ENCLOSED WITHIN [BRACKETS] I. DESCRIPTION OF EVENT A. PRE-EVENT PLANT CONDITIONS: Prior to the event, NMP1 was in Mode 1 (Power Operation) at 100% power. B. EVENT: On October 21, 2023, at 2048 EDT, with Nine Mile Point Nuclear Station Unit 1 operating at 100% power, Reactor Recirculation Pump (RRP) [AD] 12 tripped due to a loss of coupling in the tachometer generator, and reactor power lowered to 88%. This trip also resulted in a reverse flow condition through RRP 12. This reverse flow condition results in an unconservative total flow input to the Average Power Range Monitor (APRM) [IG] logic resulting in the APRM flow biased trip set point being higher than the allowable Technical Specification value. As a result, Operations declared the APRMs inoperable. At 2058 EDT, operators stopped reverse flow through RRP 12 by closing the discharge blocking valve, and all APRMs were returned to operable. Control room operators subsequently made an 8-hour report (EN-56810) under 10 CFR 50. 72(b)(3)(v)(A). This event is reportable in accordance with 10 CFR 50. 73(a)(2)(v)(A). C. INOPERABLE SYSTEMS, STRUCTURES, OR COMPONENTS THAT CONTRIBUTED TO THE EVENT: None. D. DATES AND APPROXIMATE TIMES OF MAJOR OCCURENCES AND OPERATOR ACTIONS: The dates, times, major occurrences, and operator actions for this event are as follows. October 21, 2023: 2048 - RRP 12 trips due to loss of tachometer generator coupling, resulting in a reverse flow condition through the pump. APRMs are inoperable due to the reverse flow condition. 2058 - Operators close the RRP 12 discharge blocking valve, arresting the reverse flow condition. APRMs are operable. E. METHOD OF DISCOVERY: This event was self-revealed when reactor recirc pump 12 tripped and control room operators received annunciators for Recirculation Motor Generator Set 12. F. SAFETY SYSTEM RESPONSES: | ML23363A151 | 0 | good
Not Found | Unknown Unit | Not Found | 01-22-2024 | Not Found | Not Found | ML24022A224 | 4 | ok
Browns Ferry Nuclear Plant | Unit 1 | Standby Liquid Control Inoperable due to Demineralized Water In-leakage | 01-29-2024 | A past operability evaluation determined that for a period of time from January 18 to January 19, 2023, the Standby Liquid Control (SLC) system tank sodium pentaborate (SPB) concentration dropped below the requirements of Technical Specification (TS) Surveillance Requirement 3.1.7.3 which requires the SPB solution to be greater than or equal to 8.0% by weight. The cause of this event was leakage past valve 1-SHV-002-1208, “SLC Demin Water Supply Shutoff Valve,” that allowed demineralized water to dilute the SPB solution in the SLC tank. The past operability evaluation performed by engineering concluded that although SPB concentration dropped below the TS minimum requirements, sufficient SPB solution was available to provide the required pH buffering function; therefore, the safety function of the SLC system was maintained. An engineering change to physically separate the SLC tank from the demineralized water system has been implemented to prevent leakage into the SLC tank. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME (cid:1409) 050 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 1 00259 NUMBER NO. (cid:1407) 052 2023 - 003 - 00 | I. Plant Operating Conditions before the Event At the time of this event, Browns Ferry Nuclear Plant (BFN) Unit 1 was in Mode 1 at approximately 100 percent power. II. Description of Event A. Event Summary On January 19, 2023, engineering noted that the Standby Liquid Control (SLC) system [BR] tank level had increased greater than 1 inch. The SLC tank level was validated by Chemistry per dipstick method and discovered to have risen approximately 2 inches. The cause of the SLC tank level increase was determined to be demineralized water [KC] leaking past valve 1-SHV-002-1208, “SLC Demin Water Supply Shutoff Valve.” The valve was adjusted to stop the leakage of demineralized water into the SLC tank. Chemistry added sodium pentaborate (SPB) to the tank and then analyzed the SLC tank contents to ensure proper limits were met. Following a similar event in November 2023, the operability of the SLC system between the start of the water intrusion and the addition of SPB by Chemistry was questioned for both events. Past operability evaluations were requested for these events on November 14, 2023. Past operability evaluations were performed by engineering on the two events. On November 30, 2023, it was determined that on January 18, 2023, the SLC tank SPB concentration dropped below the requirements of Technical Specification (TS) Surveillance Requirement (SR) 3.1.7.3 which requires the SPB solution to be greater than or equal to 8.0% by weight. Failure to meet TS SR 3.1.7.3 resulted in the SLC system being inoperable. Because the SLC tank is common to both SLC subsystems, the Tennessee Valley Authority (TVA) is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(v)(C) & (D), as any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material; or mitigate the consequences of an accident. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML24029A241 | 0 | good
River Bend Station | Unit 1 | Automatic Reactor Scram Due to a Turbine Trip Following a Disconnect Failure at Switchyard | 02-08-2024 | On December 13, 2023, at 01 :02 CST, with River Bend Station, Unit 1, operating in Mode 1 at 100% power, a turbine trip signal resulted in an automatic reactor scram. All control rods fully inserted and there were no complications. All systems responded as designed. The turbine trip signal was caused by a switchyard disconnect that was not properly seated in the saddle of the disconnect fingers, which resulted in an open circuit condition on the output of the main generator. Following a trip of the Reactor Feedwater System due to a Reactor Feedwater Heating isolation, Reactor Core Isolation Cooling was utilized to maintain reactor vessel inventory. The Reactor Feedwater System was restarted once the Reactor Feedwater Heating isolation signal was reset. Reactor water level control was transitioned back to the Reactor Feedwater System. This report is made pursuant to 10 CFR 50. 73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of the Reactor Protection System. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply wnh this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington. DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Ottice of Information and Regulatory Affairs. (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW. Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.n re. gov/reading-rm/doc-collections/nu regs/staff /sr1 022/r3/) requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER River Bend Station, Unit 1 ■ 050 YEAR SEQUENTIAL REV NUMBER NO, 458 2023 006 00 □ 052 | EVENT DESCRIPTION On December 13, 2023, at 01 :02 CST, River Bend Station (RBS), Unit 1, was operating in Mode 1 at 100% power when a turbine trip signal resulted in an automatic reactor scram. All control rods fully inserted and there were no complications. All systems responded as designed. Following the scram, the Reactor Feedwater System (FWS) [SJ] tripped on low suction pressure caused by isolations to both trains of Reactor Feedwater Heating [SJ]. At 01 :08 CST, reactor water level control was transitioned to the Reactor Core Isolation Cooling (RCIC) [BN] system to maintain inventory of the reactor vessel. At 01 :10 CST, Reactor Feedwater System Pump B (FWS-P1 B) [SJ] was restarted. At 01 :14 CST, reactor water level control was transitioned back to FWS and RCIC was secured. Reactor pressure was maintained by the Turbine Bypass Valves (JI). This event was reported under 10 CFR 50.72(b)(2)(iv)(B), as any event or condition that results in actuation of the Reactor Protection System (RPS) when the reactor is critical and 10 CFR 50.72(b)(3)(iv)(A) Specified System Actuation as result of Group 3 isolations (EN 56887). This report is made pursuant to 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of the Reactor Protection System. EVENT CAUSE The cause of the turbine trip signal was due to a Generator Side Disconnect [DISC] switch failing as a result of not being fully seated in the saddle of the disconnect fingers. This created a hotspot that melted the pads to the point where the cable connections faulted between the disconnect and the triad jumper cable to the next length of bus work. The damaged disconnects resulted in an open circuit condition on the output of the Main Generator. After further investigation, it was determined that the disconnects were not properly seated in the saddle of the disconnect fingers because of personnel error. During the closing of the disconnects following maintenance activities, the disconnects were locked in a partially closed position. The movable members were closed, but not all the way to their mechanical stops. SAFETY ASSESSMENT There were no actual Nuclear or Radiological safety consequences due to this event. Thus, this event was of minimal significance to the health and safety of the public. The plant response to this event was bounded by the Updated Safety Analysis Report analysis of a Main Turbine Trip with Steam Bypass Valves/Pressure Regulators in service. NRC form 366A (10-01-2023) Page _2_ of _3_ | ML24039A130 | 0 | good
Not Found | Unknown Unit | Reactor Scram Due to Generator Stator Fault to Ground | 02-13-2024 | On December 16, 2023, Grand Gulf Nuclear Station was operating at 81 percent power following a planned sequence exchange and no critical work activities were in progress. At 0346, all three in service main generator protective relays measured an increase in voltage across the secondary of the neutral grounding transformer which resulted in a main generator lockout and subsequent main turbine trip and automatic reactor scram. The direct cause of the main generator lockout was a generator stator fault to ground. A root cause was not identified. Actions have been created to ensure the generator bushings are clean and the solenoid contactors are replaced. All control rods fully inserted, there were no complications and all plant systems responded as designed. No radiological releases occurred due to this event. There were no consequences to the safety of the public, nuclear safety, industrial safety, or radiological safety. This report is made in accordance with 10 CFR 50.73{a)(2)(iv)(A), for any event or condition that resulted in manual or automatic actuation of the Reactor Protection System. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U S. Nuclear Regulatory Comnission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: Q!liLlvbmi~SIO!l@Qmb ~_p.gQ.y. The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document t!l!R:llwww nrc.aov/reading-rm/doc-collect1ons/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid 0MB control number. ~1. FA-CIL-ITY- NA-ME ----------. ~ 2. DOCKET NUMBER 3. LER NUMBER 050 REV I NO. 1-0 Grand Gulf Nuclear Station, Unit 1 416 052 □ | PLANT CONDITIONS During the event, Grand Gulf Nuclear Station (GGNS) was in Mode 1, 81 percent power following a planned sequence exchange. There were no critical work activities in progress, and there were no inoperable safety-related systems at the time of the event. DESCRIPTION OF EVENTS On December 16, 2023, GGNS was operating at 81 percent power following a planned sequence exchange and no critical work activities were in progress. At 0346, all three in service main generator protective relays measured an increase in voltage across the secondary of the neutral grounding transformer. This voltage increased to approximately 30V (3240V primary) which was above the 59N (90 percent Stator Ground Fault) function trip setpoint of 8.566V (928.6V primary). All relays tripped after a built-in three second delay which initiated a main generator lockout and subsequent main turbine trip and reactor scram. All control rods fully inserted, and all plant systems responded as designed. Reactor water level was maintained by main feedwater and condensate. Reactor pressure was maintained by the main turbine bypass valves. No radiological releases occurred. REPORTA BILITY The automatic Reactor Protection System (RPS) actuation was initially reported to the NRC as a 4-hour report per 10 CFR 50.72(b)(2)(iv)(B) on December 16, 2023 (EN 56894). This report is made in accordance with 10 CFR 50.73(a)(2)(iv)(A) for any event or condition that resulted in manual or automatic actuation of any system listed in paragraph 10 CFR 50.7 3(a)(2)(iv)(B). CAUSE The Direct Cause of the RPS actuation was Generator Stator fault to ground resulting in a main generator lockout and reactor scram. A root cause was not identified. CORRECTIVE ACTIONS Immediately following the event, a turbine and generator cooldown was performed to allow testing of the generator stator windings, the isophase bus and the neutral grounding transformer. Additionally, all components associated with the main generator terminal voltages were tested for insulation resistance to ensure no ground is present. Corrective actions are being enacted to ensure that preventative maintenance is in place to clean the main generator bushings and replace the seal oil drain regulator tank solenoid contactors. SAFETY SIGNIFICANCE The reactor trip system responded as expected to the automatic trip signal. There was no failure of any function that would have prevented fulfillment of actions necessary to shutdown the reactor and maintain it in a safe shutdown condition, remove residual heat, control the release of radioactive material, or mitigate the consequences of an accident. All systems required to bring the plant to MODE 3 responded correctly. All safety related emergency core cooling systems were operable and available during the SCRAM. There was no loss of safety function for this event. There were no safety consequences impacting plant or public safety because of this event. PREVIOUSLY SIMILAR EVENTS LER 2020-003: On May 25,2020, at 0433, GGNS experienced an automatic reactor scram due to a main turbine trip. | ML24044A193 | 1 | ok
Edwin I. Hatch Nuclear Plant | Unit 2 | Unit 2 High Pressure Coolant Injection (HPCI) System Inoperable | 02-14-2024 | At 0223 EST on 12/18/2023, while Unit 2 was at 100% power in MODE 1, the High Pressure Coolant Injection (HPCI) outboard steam isolation valve received a spurious close signal resulting in the HPCI system being isolated and unavailable to automatically start. Consequently, HPCI was declared inoperable. The cause of HPCI isolating was electronic noise stemming from the age-related failure of a Reactor Core Isolation Cooling (RCIC) Analog Transmitter Trip System (ATTS) card. The manner in which the RCIC ATTS card failed did not adversely affect the operability of RCIC. However, due to the proximity of the RCIC ATTS card and the HPCI ATTS card (both located on the same instrument rack), the electronic noise caused the HPCI ATTS card to introduce a spurious signal to isolate the HPCI system. The RCIC System and the low pressure Emergency Core Cooling Systems (ECCS) were operable and available during this event. Subsequently, the failed RCIC A TTS card was replaced and operability of the HPCI System was restored at 0512 EST on 12/18/2023 by resetting the isolation signal and returning the system to standby line up. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ~ 050 I SEQUENTIAL REV YEAR NUMBER NO. Edwin I. Hatch Nuclear Plant Unit 2 00366 • 120241 -I 1-G □ 052 I 001 | EVENT DESCRIPTION At 0223 EST on 12/18/2023, while Unit 2 was at 100% power in MODE 1, the High Pressure Coolant Injection (HPCI) (EIIS: BJ) outboard steam isolation valve received a spurious close signal resulting in the HPCI system being isolated and unavailable to automatically start. Consequently, HPCI was declared inoperable. The spurious HPCI isolation was due to electronic noise stemming from a failed Reactor Core Isolation Cooling (RCIC) (EIIS: BN) Analog Transmitter Trip System (ATTS) card (EIIS: TIS). The RCIC ATTS card was replaced and HPCI was restored to operable status at 0512 EST on 12/18/2023. The RCIC System and the low pressure Emergency Core Cooling Systems (ECCS) were operable and available during this event. FAILED COMPONENTS INFORMATION: Master Parts List Number: 2E51 N666B Manufacturer: General Electric Model Number: GE P/N 184C5988G201 Type: Analog Transmitter Trip System (ATTS) EVENT CAUSE ANALYSIS The cause of HPCI isolating was electronic noise stemming from the age-related failure of a RCIC ATTS card. The manner in which the RCIC ATTS card failed did not adversely affect the operability of RCIC. However, due to the proximity of the RCIC ATTS card and the HPCI ATTS card (both located on the same instrument rack), the electronic noise caused the HPCI ATTS card to introduce a spurious signal to isolate the HPCI system. SAFETY ASSESSMENT Even though HPCI lost its ability to automatically start, the RCIC System and the low pressure ECCS were operable and available during this event. However, because HPCI does not have a redundant system the isolation of the HPCI System and loss of its automatic functions represents a condition that could have prevented the fulfillment of the HPCI safety function to mitigate the consequences of an accident and is reportable per 50.73(a)(2)(v)(D). There were no actual safety consequences as a result of this event. The event was within the analysis of the UFSAR Chapter 15. CORRECTIVE ACTIONS The failed RCIC ATTS card was successfully replaced and operability for the HPCI System was restored at 0512 EST on 12/18/2023 by resetting the isolation signal and returning the system to standby line up. An extent of condition is being performed to identify other ATTS cards located in the same panels that could potentially be susceptilble to failure due to electronic noise. Additionally, preventative maintenance strategies are being created to replace ATTS cards prior to age-related failure. PREVIOUS SIMILAR EVENTS On March 28, 2023, with Unit 1 at 100% rated thermal power, an operability review concluded that the High Pressure Coolant Injection (HPCI) pump would not have automatically started during a 22 minute period on March 18, 2023 when an invalid high suppression pool water level signal was received and before the signal was reset. Causal analysis determined that the failure of an unrelated instrument card, located on the same instrument rack as the instrument card monitoring Unit 1 suppression pool water level, caused a momentary voltage perturbation on the rack, likely leading to an invalid suppression pool water level high signal from the suppression pool water level instrument card. This high-level signal caused the Unit 1 HPCI system trip solenoid to actuate. There was no actual high level in the Unit 1 suppression pool. Corrective actions included resetting the invalid suppression pool level high signal and replacing the failed instrument card. | ML24045A152 | 0 | good
Catawba Nuclear Station | Unit 2 | Condition Prohibited by Technical Specifications and Loss of Safety Function due to Failed Damper Controller for the 2A 1 Emergency Diesel Generator Room Ventilation Fan | 03-04-2024 | On January 2, 2024, the 2A Emergency Diesel Generator (DG) was unloaded and secured prior to the completion of a periodic 5-hour run due to rising temperatures and air quality conditions in the 2A DG room. It was determined that the 2A1 Emergency Ventilation Fan Damper Controller was failed and did not allow the normal amount of outside air to circulate into the room. Additionally, the 2A2 Emergency Ventilation Fan was out of service in support of maintenance activities. As a result, 2A DG room temperatures increased to an off-normal level less than the alarm setpoint. The 2A DG was declared inoperable until the degraded damper controller was repaired. Further investigation revealed Catawba Nuclear Station had evidence the condition of the failed 2A 1 Damper Controller, combined with the out of service 2A2 Ventilation Fan, had existed since December 5, 2023. A review performed for the timeframe between December 5, 2023, and January 2, 2024, identified the 2A DG VD system was non-functional during this time, resulting in the 2A DG being inoperable. This resulted in instances which represented conditions prohibited by Technical Specifications, and instances of a loss of safety function. There was no impact to the health and safety of the public. NRC FORM 366A (10-01-2023) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nureqs/staff/sr1022/r3/) 1. FACILITY NAME Catawba Nuclear Station, Units 1 and 2 | BACKGROUND ■ 050 □ 052 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A 10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001 , or by email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Offcer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 2. DOCKET NUMBER YEAR 00413, 00414 2024 - 3. LER NUMBER SEQUENTIAL NUMBER 001 REV NO. 00 The following information is provided to assist readers in understanding the event described in this LER. Applicable Energy Industry Identification System [EIIS] and component codes are enclosed within brackets. Catawba's unique system and component identifiers are contained within parentheses. !This event is being reported under 10 CFR 50. 73(a)(2)(i)(B) for condition prohibited by Technical Specifications (TS) and 10 CFR 50. 73(a)(2)(v)(A), (B), and (D) for an event or condition that could have prevented the fulfillment of a Safety Function. The onsite standby power source for each 4160 volt Engineered Safety Features (ESF) bus at Catawba is a dedicated Diesel Generator (DG)[EK]. For each unit, DGs A and Bare dedicated to ESF buses ETA and ETB, respectively. Each DG starts automatically on a Safety Injection (SI) signal (i.e., low pressurizer pressure or high containment pressure) or on an ESF bus degraded voltage or undervoltage signal. After the DG has started, it will automatically tie to its respective bus after offsite power is tripped as a consequence of ESF bus undervoltage or degraded voltage, independent of or coincident with an SI signal. The DGs will also start and operate in the standby mode without tying to the ESF bus on an SI signal alone. Following the trip of offsite power, a sequencer strips loads from the ESF bus. When the DG is tied to the ESF bus, loads are then sequentially connected to its respective ESF bus by the automatic load sequencer. In the event of a loss of preferred power, the ESF electrical loads are automatically connected to the DGs in sufficient time to provide for safe reactor shutdown and to mitigate the consequences of a Design Basis Accident such as a Loss of Coolant Accident (LOCA). There are also provisions to accommodate the connecting of the Emergency Supplemental Power Source (ESPS) ~o one train of either unit's Class 1 E AC Distribution System (ESF). The ESPS consists of two 50% capacity non- safety related commercial grade DGs. Manual actions are required to align the ESPS to the station and only one of the station's four onsite Class 1 E Distribution System trains can be supplied by the ESPS at any given time. The ESPS is made available to support extended Completion Times in the event of an inoperable DG as well as a defense-in-depth source of AC power to mitigate a station blackout event. The ESPS would remain disconnected rom the Class 1 E AC Distribution System unless required for supplemental power to one of the four 4.16 kV ESF buses. The primary purpose of the Diesel Building Ventilation System (VD)[VJ] is to maintain the temperature within ~he minimum and maximum limits for operation of equipment and personnel access for inspection, testing, and maintenance. The ESF Actuation System actuates the Diesel Building Ventilation System to maintain proper ventilation of the Diesel Building for equipment operation. The Diesel Generator Emergency Ventilation portion of the VD System is required to maintain the Diesel Building temperature between 60 and 120-degrees Fahrenheit during any Design Basis Event (such as a LOCA) coincident with a Loss of Offsite Power (LOOP). Emergency Ventilation Fans 2A 1 and 2A2 automatically start when the 2A DG starts. NRG FORM 366A (10-01-2023) Page_2_ of _5_ | ML24064A190 | 0 | good
Cooper Nuclear Station 298 1 of 5 | Unknown Unit | Inoperable Turbine Stop Valve Limit Switch Causes Condition Prohibited by Technical Specifications | 03-04-2024 | During the performance of surveillance testing on January 3, 2024, turbine stop valve (TSV)-1 open limit switch, MS-LMS-SVOS1(1 ), failed to actuate. This failure prevented actuation of the Reactor Protection System (RPS) scram logic for channel A 1. At 0400, Operations declared TSV-1 limit switch inoperable and entered the applicable Technical Specifications (TS) Limiting Condition for Operation (LCO) 12-hour action statement to place the RPS channel in trip and inserting a half-scram. A pre-planned contingency power reduction was initiated to replace the limit switch. When the switch linkage was disassembled for replacement, the arm was found loose and not fully engaged onto the limit switch shaft. The switch was replaced, and Operations exited the TS LCO action statement at 0249 on January 4, 2024. The cause of the failure was due to looseness in the limit switch linkage that attached to the limit switch cam. This prevented proper engagement to actuate the limit switch when it was exercised for testing. There were no safety consequences as a result of this event. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process LICENSEE EVENT REPORT (LER) and fed back to industry. Send comments regarding burden estimate to the FOIA, CONTINUATION SHEET Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: (See NUREG-1022, R.3 for instruction and guidance for completing this form oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a http://www.nrc.gov/reading-rm/doc-collections/nureqs/staff/sr1022/r3/) person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Cooper Nuclear Station 05000-298 NUMBER NO. 2024 001 00 | PLANT STATUS Cooper Nuclear Station (CNS) was in Mode 1, Power Operation, at 100 percent power at the time of the event on January 3, 2024. BACKGROUND The Reactor Protection System (RPS) [El IS:JC] provides timely protection against the onset and consequences of conditions that threaten the integrity of the fuel barrier and the reactor coolant pressure boundary. The RPS limits the uncontrolled release of radioactive material from the fuel and reactor coolant pressure boundary by terminating excessive temperature and pressure increases through the initiation of an automatic scram. The RPS includes sensors, relays [EIIS:RL Y], bypass circuits, and switches that are necessary to cause initiation of a reactor [EIIS:RPV] scram. The input parameters to the scram logic are from instrumentation that monitors reactor vessel water level, reactor vessel pressure, neutron flux, main steam line isolation valve position, turbine control valve fast closure, turbine stop valve (TSV) position, drywell pressure, and scram discharge volume water level. The RPS is arranged as two separately powered trip systems (trip system A and trip system 8). Each trip system has three logics. Two of the logics (A 1, A2; 81, 82) are used to produce automatic trip signals. The input parameters mentioned above are represented by at least one input to each of these logic channels. The remaining logic is used for a manual trip signal. The outputs of the automatic logic channels in a trip system are combined in a "one-out-of-two" logic so that either channel can trip the associated trip system. The tripping of both systems will produce a reactor scram. The operability of RPS is dependent on the operability of individual instrumentation channel functions specified in Technical Specifications 3.3.1.1, RPS Instrumentation, Table 3.3.1.1-1. For the Turbine Stop Valve-Closure Function (Table 3.3.1.1-1, Function 8), each RPS trip system receives two Turbine Stop Valve-Closure channel inputs from a TSV, each consisting of one position (i.e., limit) switch [EIIS:33] assembly with two contacts, each inputting to a relay. The relays provide a parallel logic input to an RPS trip logic channel. The logic for the Turbine Stop Valve-Closure Function is such that both TSVs must be closed to produce a reactor scram. Single TSV closure will produce a half scram. Four channels of Turbine Stop Valve-Closure Function, with two channels in each trip system, are required to be operable. EVENT DESCRIPTION On January 3, 2024, TSV-1 limit switch MS-LMS-SVOS1 (1 ), failed to actuate during surveillance testing. Testing of the limit switch function is required to meet Technical Specifications (TS) Surveillance Requirement 3.3.1.1.9 for Table 3.3.1.1-1, Function 8 - TSV Closure. Failure of limit switch MS-LMS-SVOS1 (1) to actuate revented makin u the RPS scram lo ic for channel A1. The other TSV-1 limit switch, MS-LMS-SVOS1 2 , | ML24064A252 | 0 | good
cooper nuclear station | Unknown Unit | Technical Specifications Prohibited Condition for Inoperable Service Water Booster Pump | 03-04-2024 | On August 27, 2022, Residual Heat Removal Service Water Booster pump 'D' (SW-P-BPD) outboard pump bearing temperature reached the high warning temperature alarm. Upon investigation of the alarm, a three drops per minute oil leak was observed on the pump inboard, radial bearing. At 2120 hours, Operations declared SW-P-BPD inoperable and entered the applicable Technical Specification Limiting Condition for Operation. The pump bearing oil leakage was repaired and both inboard and outboard booster pump bearings replaced. SW-P-BPD was declared operable at 1614 on September 1, 2022. The cause of the pump inboard bearing oil leakage was a fabrication issue by the original pump manufacturer. The cause of the pump thrust bearing elevated temperature was that the maintenance procedure used for the previous pump rebuild in July 2022 was not as detailed in accordance with the original manufacturer's recommendations with respect to installation of the pump thrust bearing. There were no safety consequences as a result of this event. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process LICENSEE EVENT REPORT (LER) and fed back to industry. Send comments regarding burden estimate to the FOIA, CONTINUATION SHEET Library, and Information Collections Branch (T-6 A 1O M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: (See NUREG-1022, R.3 for instruction and guidance for completing this form oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a http://www.nrc.gov/readinq-rm/doc-collections/nureqs/staff/sr1022/r3/) person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Cooper Nuclear Station 05000-298 YEAR SEQUENTIAL REV NUMBER NO. 2024 002 00 | PLANT STATUS At the time of the event on August 27, 2022, Cooper Nuclear Station (CNS) was in Mode 1, Power Operation, at 81 percent power for end-of-cycle power coast down. BACKGROUND The Residual Heat Removal [EIIS:BO] Service Water Booster (RHRSWB) system is designed to provide cooling water for the Residual Heat Removal system (RHR) heat exchangers [EIIS:HX], required for a safe reactor shutdown following a Design Basis Accident or transient. The RHRSWB system is operated whenever the RHR heat exchangers are required to operate in the shutdown cooling or suppression pool cooling mode. The system is initiated manually from the Control Room. If operating during a loss of coolant accident (LOCA), the system is automatically tripped to allow the diesel generators [EIIS:DG] to automatically power only that equipment necessary to reflood the core. The RHRSWB system removes heat from the suppression pool via the RHR system to limit the suppression pool temperature and primary containment [EIIS:NH] pressure following a LOCA. This ensures that the primary containment can perform its function of limiting the release of radioactive materials to the environment following a LOCA. The RHRSWB system consists of two independent and redundant subsystems. Each subsystem is made up of a header, two pumps [EIIS:P], a suction source, valves, piping, heat exchanger, and associated instrumentation. Two RHRSWB pumps per subsystem are required to be operable to satisfy the requirements of Technical Specifications (TS), Limiting Condition for Operation (LCO) 3.7.1. EVENT DESCRIPTION RHRSWB pump 'D' (SW-P-BPD) was removed from service at 0202 ~ours on July 27, 2022, and was replaced as part of routine preventive maintenance. SW-P-BPD was restored to operable status after this replacement at 0333 hours on July 29, 2022. On August 27, 2022, at approximately 1330 hours, SW-P-BPD was placed in service to support SW chemical injection to control zebra mussels within the SW system. At approximately 1942 hours, a high thrust bearing temperature alarm was received on the Plant Management Information System (PMIS). While investigating the condition, a separate oil leak of three drops per minute (dpm) was observed on the pump inboard radial bearing, and a one dpm oil leak observed on the pump outboard thrust bearing. Due to the excessive oil leakage of the pump inboard bearing and pump outboard bearing high temperature, Operations declared SW-P-BPD inoperable at 2120 hours and entered TS LCO 3.7.1, Condition A, Required Action A.1, to restore SW-P-BPD to operable status within 30 da s. | ML24064A255 | 0 | good
Hope Creek Generating Station | Unknown Unit | Inadvertent Main Turbine Control Valve Closure Caused Reactor Scram | 03-19-2024 | On December 14, 2023, at 1939 EST, while attempting to manually close a failed open #4 turbine control valve (TCV), the #4 TCV closed rapidly. This caused a scram on average power range monitor (APRM) high neutron flux due to a rise in reactor pressure. Hope Creek Generating Station (HCGS) repaired the #4 TCV by replacing the servo valve. In addition, the fast-acting solenoid (FAS) valve and the shutoff valve were replaced. HCGS synchronized the Main Generator to the grid on December 17, 2023, at 1537 EST. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments ~c,J>P.REGt,(,.>O f~t?. LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to ~ CONTINUATION SHEET ~ ,i Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory ..;.+-, ••11t•• +O' Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ~ 050 YEAR SEQUENTIAL REV I □ NUMBER D NO. Hope Creek Generating Station 00354 2023 I □ 052 I - 003 I - 01 | ABSTRACT (continued) A Root Cause Evaluation (RCE) was performed. The root cause of this event was inadequate adherence to applicable administrative tools and processes. Corrective actions include procedure revisions and reinforcement of expectations regarding procedure adherence. HCGS reported this per 10 CFR 50.72(b)(2)(iv)(B) as event notification 56889 and now reports this event per 10 CFR 50.73(a)(2)(iv)(A). PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor (BWR/4) Turbine Control Valve/ Electro-Hydraulic Control System (EHC) - TG IDENTIFICATION OF OCCURRENCE Event Date: December 14, 2023 Discovery Date: December 14, 2023 CONDITIONS PRIOR TO OCCURRENCE OPCON 1, POWER OPERATION. Reactor power was at 88 percent. No other structures, systems or components that could have contributed to the event were inoperable during the event. DESCRIPTION OF OCCURRENCE On December 11, 2023, an EHC leak was discovered on the #4 turbine control valve (TCV). Reactor power was reduced to 90 percent, the #4 TCV was closed, and EHC was isolated to stop the leak while the plant was at 90 percent power. HCGS further lowered power to 70% to facilitate conditions for repairs. On December 14, 2023, HCGS was at 88 percent power after #4 TCV FAS oil supply tubing repairs. During restoration, foreign material that entered and damaged the servo o-rings during the leak repair caused the #4 TCV to go full open despite having a closed demand signal. While taking action to manually close the #4 TCV, the valve unexpectedly closed in approximately one second causing an automatic actuation of the reactor protection system (RPS) due to high average power range monitor (APRM) high neutron flux. All control rods fully inserted into the core. All safety systems responded as designed and expected. There were no emergency core cooling system actuations during the event. | ML24079A283 | 0 | good
Peach Bottom Atomic Power Station | Unit 2 | Automatic Reactor Scram due to an Invalid Generator Lockout | 03-31-2024 | On 01/29/2024 at 1202 hours, Unit 2 experienced a Generator lockout, Turbine trip and automatic Reactor Scram. All control rods inserted, and all safety systems responded as designed. Reactor level was initially maintained by Feedwater and pressure controlled with bypass valves. During the scram response, condenser vacuum degraded due to the loss of Turbine steam seals, resulting in level and pressure control being transferred to Reactor Core Isolation Cooling (RCIC) and High Pressure Coolant Injection (HPCI), respectively. The cause of the Generator lockout is under investigation, with the suspected cause being a spurious trip of the Audio Tone system. The system has been removed from service with a redundant system providing the protective function. The Audio Tone system is scheduled for replacement in the 2024 refueling outage. This event is reportable under 10CFR50.73(a)(2)(iv)(A) due to manual or automatic actuation of systems listed in 10CFR50.73(a)(2)(iv)(B) including the Reactor Protection System, containment isolation signals, actuation of an emergency core cooling system and Reactor Core Isolation Cooling. An ENS notification was made within 4 hours of the event and was updated within 8 hours, reference ENS 56936. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 SEQUENTIAL REV YEAR NUMBER NO. Peach Bottom Atomic Power Station, Unit 2 00277  052 2024 - 001 - 00 | Plant Operating Conditions Before the Event Prior to the event, Peach Bottom Atomic Power Station, Unit 2 was operating at approximately 100% power in MODE 1. There were no structures, systems or components (SSC) that were inoperable at the start of the event that contributed to the event. Event Description On 01/29/2024 at 1140 hours, the Main Control Room (MCR) received a Generator Tone Trouble Alarm, which immediately reset once acknowledged. A second Generator Tone Trouble Alarm was received, which remained locked in for a short period of time (approximately 15 seconds) before resetting. At 1202 hours, Unit 2 experienced a Generator lockout, Turbine trip and automatic Reactor Scram. Turbine control valves (EIIS: TA) closed as expected. Safety relief valves (EIIS: SB) were used to control the expected pressure increase and were not reopened after the initial transient. Primary Containment Group II and III Isolations (EIIS: JM) occurred as expected. Reactor vessel level was initially controlled by Feedwater (EIIS: SJ). Condenser vacuum slowly degraded due to an issue with the turbine steam seal system (EIIS: TC) and, therefore, after approximately 20 minutes level control was transferred to the Reactor Core Isolation Cooling (RCIC) system (EIIS: BN). Pressure control was maintained by turbine bypass valves (EIIS: SO) and the High Pressure Coolant Injection (HPCI) system (EIIS: BJ), which was only used for pressure control and not injection. Steam seals were restored and condenser vacuum was re-established. Vessel level control was transferred to Condensate (EIIS: SD) and the unit was safely transitioned to a cold shutdown condition. A review of the plant event logs confirmed that a generator lockout and power-load unbalance occurred. The 2-50F-386A, Main Transformer Over Head Line Protection Lock Out Relay was the first actuating device. The ‘TTR-1’ Audio Tone drawers indicated that a trip signal was transmitted from the Audio Tone drawers in the Cable Spreading Room to the drawers in the substation. The substation drawers opened the CB-225 and CB- 215 breakers (EIIS: EL) upon receipt of the trip signal. At this time, the cause of the Generator lockout is still under investigation by a Root Cause analysis. The most probable cause is a failure of the Audio Tone trip system cables which are planned for abandonment in the upcoming 2024 refueling outage as part of a planned system upgrade. Currently, there is no plan to supplement this LER; however, this LER will be supplemented if the conclusions of the Root Cause analysis substantially change the information presented in this LER. An investigation was performed and the cause of the loss of condenser vacuum is attributed to the setting of the sealing steam header pressure control valve. This resulted in the valve not opening to admit steam to the sealing steam header following the trip of the main turbine, which provided a path for air in-leakage and degraded condenser vacuum. Unit 3 was unaffected by this event. Unit 2 start up was commenced at 2028 hours on 01/30/2024 and the unit was synchronized to the grid at 1427 hours on 01/31/2024. This event is reportable under 10CFR50.73(a)(2)(iv)(A) due to manual or automatic actuation of systems listed in 10CFR50.73(a)(2)(iv)(B) including RPS, containment isolation signals, actuation of an emergency core | ML24081A121 | 0 | good
Prairie Island Nuclear Generating Plant | Unit 1 | Reactor trip, Auxiliary Feedwater and Emergency Service Water system actuation due to electrical transient in DC control power cables | 03-21-2024 | At 11:10 on October 19, 2023, with Prairie Island Nuclear Generating Plant Unit 1 operating at 100 percent power in Mode 1, power operations, multiple substation breakers unexpectedly opened and multiple grounds were detected on DC control power cabling from the plant to the substation control house. This resulted in a Unit 1 Turbine Trip and subsequent Reactor Trip with a loss of all non-safety related busses and the actuation of Auxiliary Feedwater and Emergency Service Water. Operators responded to the event in accordance with approved procedures and safely placed the plant in Mode 3. Horizontal directional drilling in progress at the site damaged DC control cables resulting in the identified plant response. This was caused by weakness in the Excavation Permit approval process as well as inadequate oversight of the personnel performing the work. DC cable replacement has been completed and multiple procedure changes have been initiated to address the identified gaps and prevent recurrence of this event. There were no radiological impacts from the event. The health and safety of the public and site personnel were not impacted during this event. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) due to a Reactor Trip, a valid Auxiliary Feedwater actuation of Emergency Service Water system. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 YEAR SEQUENTIAL REV NUMBER NO. Prairie Island Nuclear Generating Plant, Unit 1 -282 2023 052 - 001 - 01 | Plant Operating Conditions Prior to the Event: Unit 1 - Mode 1, 100 percent Power Unit 2 - Defueled EVENT DESCRIPTION At 11:10 on October 19, 2023, with Prairie Island Nuclear Generating Plant (PINGP) Unit 1 operating at 100 percent power and Unit 2 defueled in a scheduled refueling outage, multiple substation breakers, including the Unit 1 generator output breaker, unexpectedly opened causing a Unit 1 Turbine [TA] Trip and subsequent Reactor Trip. In addition, multiple grounds were detected on DC control cabling for both Units from the plant to the substation control house. The Turbine Trip caused 1M Main Transformer to become deenergized, which is the normal power supply to non-safety related (NSR) busses on Unit 1. 1R Auxiliary Transformer was also deenergized as a result of the event and therefore was not available for a Fast Bus Transfer, which resulted in a loss of all NSR busses on both Units. The reactor trip resulted in Steam Generator Water Level (SGWL) in both Steam Generators rapidly shrinking to below the setpoint for an automatic start of both Auxiliary Feedwater (AFW)[BA] pumps. These pumps ensure that at least one Steam Generator contains enough water to serve as the heat sink for reactor decay heat and sensible heat removal following a reactor trip. Both the 11 Turbine Driven AFW Pump and 12 Motor Driven AFW Pump actuated upon reaching the automatic start setpoint for low SGWL. The 121 Motor Driven Cooling Water Pump (MDCLP) auto started on low header pressure due to the loss of the NSR 11 Cooling Water (CL) Pump. The 121 MDCLP is designed to start automatically if CL header pressure drops to 80 pounds per square inch gauge (psig). The 121 MDCLP is a part of the PINGP Cooling Water (CL) System [BI]. The CL system is a ring header which is shared by Units 1 and 2 that provides a heat sink for the removal of process and operational heat from safety-related components during a design basis accident or transient. At 14:15 on October 19, 2023, Event Notification (EN) # 56803 was reported to the NRC as a 4-hour Non-Emergency report under 10 CFR 50.72(b)(2)(iv)(B) actuation of the reactor protection system and 8-Hr Non-Emergency report under 10 CFR 50.72(b)(3)(iv)(A) for an Auxiliary Feedwater Actuation. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) due to a trip of the Unit 1 reactor, a valid Pressurized Water Reactor (PWR) Auxiliary Feedwater actuation for Unit 1 and actuation of Emergency Service Water system (121 MDCLP for Unit 1 and Unit 2). ASSESSMENT OF SAFETY CONSEQUENCES All control rods were fully inserted into the core following the trip. All safety functions operated as designed. This event does not represent a safety system functional failure for Unit 1 or Unit 2. AFW actuated as expected. The AFW System automatically supplied feedwater to the Steam Generators to remove decay heat from the Reactor Coolant System when SGWL shrunk after the reactor trip. Decay heat was removed by the Steam Generators through the Steam Generator Power Operated Relief Valves. The auto start of 121 MDCLP did not challenge nuclear safety as the Cooling Water system responded as designed. | ML24081A153 | 0 | good
grand gulf nuclear station | Unknown Unit | Not Found | 03-27-2024 | 12.Licensee Contact for this LER JLieceffn sHeea rCdoynt act Phone Nu8m0b2e-r3 (I8n0cl-u5d1e 2ar4ea code) 13. Complete One Line for each Component Failure Described in this Report Cause System Component Manufacturer Reportable to IRIS Cause System Component Manufacturer Reportable to IRIS N/A N/A N/A N/A N/A N/A N/A N/A N/A N/A Month Day Year □ 14. Supplemental Report Expected � No Yes (If yes, complete 15. Expected Submission Date) 15. Expected Submission Date 1O6. nA Jbastnraucat r(Lyim 2it9 to, 1230226 4sp, aGcersa, in.ed., aGppurlofx imNautecllye 1a3r s iSngtalet-sipoance wd tyapse owrpitteenr alinteins)g at 100 percent power, and all safety systems were operable. At 1005 CT, during surveillance testing of the High Pressure Core Spray (HPCS) system, the HPCS minimum flow valve went from full open indication to dual indication and failed to close as expected. The cause of the valve's failure to close was a sheared actuator motor pinion key. The actuator motor pinion key was replaced using updated work instructions. Although HPCS was declared inoperable during the event, an engineering evaluation concluded that HPCS system remained able to perform its safety functions to maintain thermal limits and address pressurized and depressurized conditions in the reactor pressure vessel. Therefore, there were no actual safety consequences to the event. This report is being made in accordance with 10 CFR 50.73(a)(2)(v)(D), for any event or condition that could have prevented the fulfillment of the safety function of systems that are needed to mitigate the consequences of an accident. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A1 0M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: ~ - The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document bttp·//www ore gov/reading-rm/doc-collections/nuregs/staff/sr10221r3/) requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME r-, 2. DOCKET NUMBER 3. LER NUMBER ..-------------, ~ 050 YEAR SEQUENTIAL REV I ~□- I NUMBER 1-NGO. Grand Gulf Nuclear Station, Unit 1 I 416 □ 052 001 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. DESCRIPTION On January 29, 2024, Grand Gulf Nuclear Station (GGNS) was operating at 100 percent power, and all safety systems were operable. At 0950 CT, the site began Technical Specification 3.5.1, ECCS Operating surveillance testing on the High Pressure Core Spray (HPCS) [BG] system. At 1005 CT, during the surveillance, HPCS minimum flow valve went from full open indication to dual indication and failed to close as expected. At 1620 CT, the HPCS minimum flow valve was manually closed. REPORTA BILITY The HPCS minimum flow valve failure to close was initially reported to the NRC as an 8-hour report per 10 CFR 50.72(b) (3)(v)(D) on January 29, 2024 (EN 56938). This report is made in accordance with 10 CFR 50.73(a)(2)(v)(D) for any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. Although HPCS was declared inoperable during the event, an engineering evaluation concluded that HPCS system remained able to perform its safety functions to maintain thermal limits and address pressurized and depressurized conditions in the reactor pressure vessel. Therefore, in accordance with NEI 99-02, Regulatory Assessment Performance Indicator Guideline, Section 2.2, Mitigating Systems Cornerstone, Sub-Section, Safety System Functional Failures, this event will not be counted against the Reactor Oversight Process Safety System Functional Failure Performance Indicator. CAUSE Trouble shooting was initiated and it was determined that the actuator motor pinion key had sheared off preventing the valve from actuating. Further investigation determined that the pinion key had not been correctly staked due to inadequate procedure instructions when the actuator motor was replaced in 2010. CORRECTIVE ACTIONS Immediately following the event, the HPCS minimum flow valve was manually closed. A new motor pinion key was installed using updated work instructions. Extent of condition actions are being developed to inspect motor pinion keys on similar valves. SAFETY SIGNIFICANCE There were no actual safety consequences associated with the condition described in this report. The HPCS system provides and maintains an adequate coolant inventory inside the reactor vessel to limit the fuel cladding temperatures in the event of breaks in the reactor coolant pressure boundary. The system is initiated by either high pressure in the drywell or low water level in the reactor vessel. Though the as-found HPCS minimum flow valve position rendered the system inoperable throughout the time period, the HPCS system was able to perform its safety functions for maintaining thermal limits. The HPCS system was able to address pressurized as well as depressurized (LOCA) conditions in the reactor pressure vessel. PREVIOUS SIMILAR EVENTS None | ML24087A196 | 1 | ok
Monticello Nuclear Generating Plant | Unknown Unit | Reactor Scram, Containment Isolation, and Cooldown Rate outside of limits following technician adjustment of wrong component | 04-25-2024 | On February 28, 2024 at 0839 CST, with Monticello Nuclear Generating Plant in Mode 1 at 100 percent power, an inadvertent Anticipated Transient Without Scram (A TWS) system initiation resulted in trip of both Reactor Recirculation pumps, venting of the Scram Air Header, and Control Rod insertion. Control Room Operators inserted a manual Reactor Scram. Containment Isolation valves actuated and closed on a valid Group 2 signal post Reactor Scram. On March 08, 2024 at 1400 CST it was identified that within an hour following the Reactor Scram, the bottom head of the Reactor Pressure Vessel exceeded the Pressure and Temperature Limit cooldown rate of less than or equal to 100 degrees Fahrenheit per hour. The event was caused when a technician did not perform verification that the physical component matched the Surveillance Procedure step. The technician adjusted the potentiometer in the C module rather than the A module while the A channel was in trip which made up the required two trip signals and actuated the ATWS system. The Surveillance Procedure will be updated in a planned procedure change to improve human performance factors and to remove the steps to adjust the potentiometers in the A and C modules. An analytical evaluation determining the effects of the out-of-limit condition on the structural integrity of the Reactor Coolant System will be submitted to the Nuclear Regulatory Commission for review and approval per 10 CFR 50.55a(b)(2)(xliii). NRG FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects. Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-col1ections/nuregs/staff/sr1022/r3/) displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ~ 050 I IG SEQUENTIAL REV NUMBER NO. Monticello Nuclear Generating Plant 263 0 □ 052 -I 001 - I | EVENT DESCRIPTION On February 28, 2024 at 0839 CST, with Monticello Nuclear Generating Plant (MNGP) in Mode 1 at 100 percent power, an inadvertent Anticipated Transient Without Scram (ATWS) [EIIS CODE: JC] system initiation resulted in trip of both Reactor Recirculation [EIIS CODE: AD] pumps, venting of the Scram Air Header, and Control Rod insertion. Control Room Operators inserted a manual Reactor Scram. Containment Isolation [EIIS CODE: JM] valves actuated and closed on a valid Group 2 signal post Reactor Scram. On March 08, 2024 at 1400 CST it was identified that within an hour following the Reactor Scram, the bottom head of the Reactor Pressure Vessel [EIIS CODE: SB] exceeded the Pressure and Temperature Limit cooldown rate of less than or equal to 100 degrees Fahrenheit per hour. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) for an event or condition that resulted in the manual actuation of the Reactor Protection System (RPS) [EIIS CODE: JC] including Reactor Scram and automatic actuation of Containment Isolation signals affecting Containment Isolation valves in more than one system. This event is reportable under 10 CFR 50.73(a)(2)(i)(B) for an operation or condition which was prohibited by Technical Specification Limiting Condition of Operation (LCO) 3.4.9, Reactor Coolant System (RCS) Pressure and Temperature (PIT) Limits, specifically the requirement to determine the RCS is acceptable for continued operation within 72 hours of not meeting the Pressure and Temperature limit cooldown rate per required action A.2. EVENT ANALYSIS The function of the ATWS system is to mitigate the consequences of a failure of the RPS to achieve reactor shutdown when required. The A TWS system consists of two separately powered trip systems, Division I and Division II, each made up of two sub-channels: A and C for Division I and B and D for Division II. Each sub-channel receives an input from an independent sensor monitoring each of the A TWS trip parameters. A trip occurring in both sub-channels of logic Division I or a trip occurring in both sub-channels of logic Division II will cause an ATWS trip which opens both 11 and 12 Recirculation MG set generator field breakers and causes Control Rod insertion by venting the Scram Air Header. During performance of the quarterly Technical Specification Surveillance Procedure, ATWS - Recirc Trip for Reactor Pressure and Level Trip Unit Test and Calibration, a human performance error occurred. There were no systems, structures, or components that were inoperable at the start of the event that contributed to the event. During the first quarter of each year during the quarterly Surveillance Requirement 3.3.4.1.6 performance of the logic system functional test on A sub-channel ATWS RCP Trip Reactor Pressure relay, the Surveillance Procedure directs the MNGP Instrumentation and Control Technician to adjust the module's trip adjusting potentiometer. This step is done in accordance with an obsolete manufacturer's recommendation in order to preclude potential equipment degradation. The Technician successfully performed the functional test on A sub-channel and then, with A sub-channel remaining in trip, obtained a different tool to perform the potentiometer adjustment. The Technician did not verify the physical component to the procedural step and incorrectly adjusted the potentiometer of the adjacent C module, which is located in the same panel as the intended A module, which cause the trip of the C sub-channel. As both A sub-channel and C sub-channel were in trip, the Division I A TWS system actuated. The inadvertent ATWS system initiation resulted in trip of both Reactor Recirculation pumps, venting of the Scram Air Header, and Control Rod insertion. Control Room Operators inserted a manual Reactor Scram. Containment Isolation valves actuated and closed on a valid Group 2 signal post Reactor Scram. NRG FORM 366A (04-02-2024) Page 2 of 3 | ML24116A117 | 0 | good
LaSalle County Station | Unit 1 | Core Operating Limits Report Thermal Limits Exceeded | 04-26-2024 | On February 21, 2024, while performing the water rod inspection of fuel bundle GGJ319 during a planned refueling outage, it was identified that several fuel spacers had propagated up within the bundle toward the upper tie plate. It was determined through analysis that spacer positioning had a direct effect on the Minimum Critical Power Ratio (MCPR). On March 4, 2024, an analysis of the operating conditions by Global Nuclear Fuel (GNF) of fuel bundle GGJ319 was reviewed and accepted by the station. The report confirmed that during the previous cycle, the Operating Limit MCPR exceeded limits set by Technical Specifications (TS) 3.2.2. Since the Operating Limit MCPR was exceeded for longer than allowed by TS Limiting Condition for Operation (LCO) 3.2.2, this event is reportable as a condition prohibited by TS per 10 CFR 50.73(a)(2)(i)(B). The fuel bundle spacers shifted out of position over the previous operating cycle. This condition was identified during the process of inspections in response to GNF 10 CFR Part 21 communication SC 22-04. This fuel bundle has been removed from the reactor core, is currently located in the spent fuel pool, and will not be re-loaded into the core. There was no impact to the health and safety of the public or plant personnel because the Safety Limit MCPR was not exceeded in the previous cycle operation. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported : ~ - - ¥ ~ ,.· . " ' . . . lessons learned are inco!J)Orated into the licensing process and fed back to industry. Send comments . LICENSEE EVENT REPORT (LER) regarding burden estimate lo the FOIA, library, and Information Collections Branch (T-6 A10M), U. S. ; ~. . . ~ Nuclear Regulatory Commission, Washington, DC 20555-0001, or by emai lo \ ..... .,,J CONTINUATION SHEET lnfooollecls.Resource@nrc.gov, and the 0MB reviewer al: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Corrrnission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required lo (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of infonnation unless lhe document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nu regs/staff/ sr1022/r3D displays a currently valid 0MB control number. 1. FACILITY NAME (cid:127) 2. DOCKET NUMBER 3. LER NUMBER 050 SEQUENTIAL REV YEAR NUMBER NO. LaSalle County Station, Unit 1 00373 0 052 2024 - 001 00 | Plant and System Identification LaSalle Country Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the reactor core system. The affected component was the GNF3 fuel bundle GGJ319. Condition Prior to Event Unit(s): 1 Date: March 4, 2024 Time: 00:00 CDT Reactor Mode(s): 4 Mode(s) Name: Cold Shutdown Power Level: 0 percent Description On February 21, 2024, during planned in-core fuel inspections for misoriented water rods of susceptible GNF3 fuel bundles in response to GNF 10 CFR Part 21 communication SC 22-04, an unexpected condition for fuel bundle GGJ319 was discovered where spacers 6, 7, and 8 were found near the top of the bundle upper tie plate. After initial discovery, subsequent inspection revealed that spacers 4 and 5 had also moved upward to the top of the fuel assembly. Fuel spacers 1 through 3 had not moved from their expected position. Fuel bundle GGJ319 was permanently discharged to the spent fuel pool. Fuel vender GNF evaluated the impact of this condition for the previous operating cycle. The evaluation conservatively assumed the spacers were displaced for the entirety of the previous cycle, since it could not be determined when the spacers had moved. The evaluation was reviewed and accepted by the station on March 4, 2024. The evaluation report determined that • there were no penalties or adjustments associated with Linear Heat Generation Rate (LHGR) and Average Planar Linear Heat Generation Rate (APLHGR) and no discernable impact to thermal limits and margins. • there was no discernable impact to thermal limits and margins for co-resident fuel in the Unit 1 reactor core during the previous cycle of operation. • the Operating Limit MCPR exceeded limits set by TS 3.2.2 for the previous cycle. • the Safety Limit MCPR requirements set by TS 2.1.1.2 were never violated for the previous cycle. Cause The apparent cause of the spacer relocation was determined to be the misoriented water rod in fuel bundle GGJ319. The misorientation of the water rod would have occurred during fuel bundle fabrication. The misorientation caused the spacers to not be locked into position, causing them to propagate up the bundle due to hydraulic force during normal operation. Reportability and Safety Analysis Fuel bundle GGJ319 must satisfy the requirements of TS 3.2.1, AVERAGE PLANAR HEAT GENERATION RATE (APLHGR); TS 3.2.2, MINIMUM CRITICAL POWER RATIO (MCPR); TS 3.2.3, LINEAR HEAT GENERATION RATE (LHGR); AND T.S. 2.1.1.2, SAFETY LIMITS. The report determined that the requirements of TS 3.2.1 for APLHGR and TS 3.2.3 for LHGR were met for the previous cycle operation. The report confirmed the requirements of TS 2.1.1.2 for the Safety Limit MCPR was never violated for the previous cycle operation. | ML24117A127 | 0 | good
Calvert Cliffs Nuclear Power Plant | Unit 1 | Emergency Diesel Generators Automatic Start due to Loss of a 13kV Bus | 04-29-2024 | On February 28, 2024, with Calvert Cliffs Unit 1 in Mode 5 (Cold Shutdown) and Unit 2 in Mode 1 (Power Operation), a 13kV Service Electric Bus de-energized when a breaker tripped open due to a protective relay contact inadvertently closing. The loss of the electric bus resulted in the loss of 4kV unit service transformers and 4kV busses. The 1A and 2A emergency diesel generators automatically started as designed, when the 4kV busses were lost. The cause of the loss of the number 13kV Bus was due to mechanical agitation of a relay mounted on a breaker cabinet door in the Electrical Distribution Reliability Improvement Project (EDRIP) building. The relay contact inadvertently closed due to mechanical agitation during clearance and tagging activities. The relay was subsequently replaced. Operations restricted access to the EDRIP building, restricted operation of the associated circuit breakers, and added cautions to Operations Procedures. Planned corrective actions include relocating the relays from the EDRIP switchgear doors to a location better suited for these type relays. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 SEQUENTIAL REV YEAR NUMBER NO. Calvert Cliffs Nuclear Power Plant, Unit 1 05000317  052 2024 - 002 - 00 | PLANT AND SYSTEM IDENTIFICATION Calvert Cliffs Nuclear Power Plant, Units 1 and 2, are Combustion Engineering Pressurized Water Reactors each with a licensed maximum power level of 2737 megawatts thermal. The Energy Industry Identification System code used in the text is identified as [EA]. A. CONDITION PRIOR TO EVENT Unit: 1 Date: February 28, 2024 Power level: 0 Mode: Unit 1 was in Mode 5 when the event occurred. Unit: 2 Date: February 28, 2024 Power level: 65 Mode: Unit 2 was in Mode 1 when the event occurred. B. DESCRIPTION OF EVENT At 13:50 on February 28, 2024, with Calvert Cliffs Unit 1 in Mode 5 (Cold Shutdown), and Unit 2 in Mode 1 (Power Operation), the number 11 13kV Service Electric Bus de-energized when a breaker tripped open due to a protective relay contact inadvertently closing. The loss of 11 13kV Bus resulted in the loss of 4kV unit service transformers U-4000-11 and U-4000-12, and the 11 4kV and 21 4kV busses were deenergized. The Unit 1 1A emergency diesel generator (EDG) automatically started when the 11 4kV bus was deenergized and the Unit 2 2A EDG automatically started when the 21 4kV bus was deenergized. There were no safety consequences as a result of the event based on all safety systems functioning and operating as designed. C. DATES AND APPROXIMATE TIMES OF MAJOR OCCURRENCES February 28, 2024: 13:50: The number 11 13kV Service Electric Bus deenergized. The Unit Service Transformers U-4000-11, U-4000-12 and U-4000-13 were lost. The Unit 1 11 4kV bus deenergized. 1A EDG automatically started. The Unit 2 21 4kV bus deenergized. 2A EDG automatically started. February 28, 2024: 16:32: The Unit 1 11 4kV bus was powered from its alternate feeder breaker and the 1A EDG was separated from the bus and secured in accordance with normal operating procedures. February 28, 2024: 18:00: The Unit 2 21 4kV bus was powered from its alternate feeder breaker and the 2A EDG was separated from the bus and secured in accordance with normal operating procedures. | ML24121A002 | 0 | good
Comanche Peak Nuclear Power Plant | Unknown Unit | Potential Loss of Safety Function Due to the lnoperability of Both Trains of the Un interruptible Power Supply Heating, Ventilation, and Air Conditioning (UPS HVAC) | 05-06-2024 | On March 05, 2024, Units 1 and 2 were operating at 100% power. At 0720 the Uninterrupted Power Supply, Heating, Ventilation, and Air Conditioning (UPS HVAC) X-02 automatically shutdown, which caused the station to determine that there was a potential loss of safety function for the equipment in the UPS and Distribution Rooms, due to losing the ability to control the temperature during a postulated emergency condition. This meets the safety system functional failure criteria. This was due to the failure of the UPS HVAC X-02 unit, concurrent with the UPS HVAC X-01 unit and the Emergency Fan Coil Units (EFCUs) being out of service for maintenance. The immediate corrective actions were for the station to start the EFCUs at 0729 which restored cooling to three of the four UPS and Distribution Rooms. This restored the safety function after approximately nine minutes. The station then restored operability to the UPS HVAC X-01 system by switching the cooling system to the other unit (Unit 2, Train A) approximately 41 minutes after the UPS HVAC X-02 trip, which restored the temperature control to all four UPS and Distribution Rooms. The root cause of this event was the station exhibiting a less than adequate conservative bias to the unique operability concerns associated with the UPS HVAC Cooling System when performing off-normal maintenance. NRG FORM 3668 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported ~(,,._,,v,AA£11u,,.,, lessons learned are incorporated into the licensing process and fed back to industry. Send comments .f • ' :.0~ .t LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to ~ ~ ,.,,., ~o,e, ~ , (FAILURE CONTINUATION) lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory ........ Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17~ Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection httR://www.nre.gov/read ing-rm/doc-co llections/n u regs/staff/ sr1 022/r3/) displays a currently valid 0MB control number. 1. FACILITY NAME 0 050 2. DOCKET NUMBER S 3 E . Q LE U R E N N U T M IA B L E R REV 10 NUMBER NO. Comanche Peak Nuclear Power Plant □ 052 I 445 -I 001 1- 1 00 I 13. COMPLETE ONE LINE FOR EACH COMPONENT FAILURE DESCRIBED IN THIS REPORT CAUSE SYSTEM COMPONENT MANUFACTURER REPORTABLE TO IRIS D EF COND GMC N NRC FORM 3668 (04-02-2024) Page 2 of 6 NRG FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimale to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email lo CONTINUATION SHEET lnfocollecls.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to http://www. nrc.g ov/reading-rm/doc-collections/nu reqs/staff/sr1 022/r3/) respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 0YE AR SEQUENTIAL REV I NUMBER NO. Comanche Peak Nuclear Power Plant ~- I 1-0 445 □ 052 I 001 | I. DESCRIPTION OF REPORTABLE EVENT On March 05, 2024, Units 1 and 2 were operating at 100% power. At 0720 the Uninterrupted Power Supply, Heating, Ventilation, and Air Conditioning (UPS HVAC) X-02 unit tripped, which caused the station to potentially lose a safety function. Specifically, the station lost the ability to properly control the temperature of the UPS and Distribution Rooms during a postulated emergency condition. The other factors leading to this were the Emergency Fan Coil Units (EFCUs) being off, which renders them inoperable, and UPS HVAC X-01 being inoperable, due to the support system, Component Cooling Water (CCW) Unit 1, Train A (1-A), being inoperable . The station restored the safety function after approximately nine minutes, by starting all of the EFCUs at 0729, which restored cooling to three of the four UPS and Distribution Rooms (EFCU 1-A was only functional, due to the support system CCW 1-A being inoperable, however forced air circulation was returned). The station then connected UPS HVAC X-01 to CCW Train 2-A approximately 41 minutes after the event, which restored temperature control to all four UPS and Distribution Rooms. A REPORTABLE EVENT CLASSIFICATION This event is reportable under 1 0CFR50.73(a)(2)(v)(D), "Any event or condition that could have prevented the fulfillment of the safety function of the structures or systems that are needed to ... Mitigate the consequences of an accident." This is based on the station losing both trains that provide temperature control to the UPS and Distribution Rooms, during a postulated Large-Break Loss of Cooling Accident (LBLOCA), or a similar postulated event which causes a high containment pressure, Hl-3, signal (18.0 psig). This is due to losing all three cooling systems in the UPS and Distribution Rooms, specifically: 1) The cooling system supporting UPS HVAC X-01, CCW Train 1-A, being inoperable for planned maintenance on the heat exchanger (Hx). Even-though CCW is cross-connected to the 1-B train for all alternative conditions, a Hl-3 signal would cause CCW to isolate Train 1-A from Train 1-B to support containment spray. 2) The four EFCUs being turned off at the time of the event, based on procedural allowance, which renders them inoperable due to no auto-start mechanism. 3) UPS HVAC X-02 being inoperable due to a failure of the evaporator blower motor, causing the system to shutdown. B. PLANT CONDITION PRIOR TO EVENT On March 05, 2024, prior to the event, both Units 1 and 2 were operating at approximately 100% power. C. STATUS OF STRUCTURES, SYSTEMS, OR COMPONENTS THAT WERE INOPERABLE AT THE START OF THE EVENT AND CONTRIBUTED TO THE EVENT The event caused the station to immediately lose UPS HVAC X-02, due to the motor shutdown The EFCUs in the UPS and Distribution Rooms were inoperable prior to the event, due to being turned off, based on maintenance personnel working in UPS and Distribution Room associated with Train 1-A. UPS HVAC X-01 was inoperable prior to the event, based on the CCW Train 1-A Hx maintenance. D. NARRATIVE SUMMARY OF THE EVENT, INCLUDING DAYS AND APPROXIMATE TIMES On March 05, 2024, Units 1 and 2 were operating at 100% power. At 0720 a failure occurred for UPS HVAC X-02 [EIIS: (EF)(ACU)], specifically, the evaporator blower motor [EIIS: (EF)(MO)] had a immediate failure. This event, coupled with the EFCUs [EIIS: (EF)(FCU)] being inoperable and the support system for UPS HVAC X-01 being inoperable, CCW Train 1-A Hx [EIIS (CW)(Hx)], resulted in the station losing all trains of UPS HVAC, and hence potentially losing the safety function to mitigate consequences of a postulated accident by losing the ability to control the temperature of the UPS and Distribution Rooms during an accident. | ML24127A155 | 0 | good
Edwin I. Hatch Nuclear Plant | Unit 1 | Unit 1 Manual Reactor Trip Due to Loss of Feedwater | 05-09-2024 | At 1338 EDT on 3/11/2024, while Unit 1 was in MODE 1 at 35% power and performing power ascension activities, the reactor was manually tripped due to reactor water level decreasing following the trip of the 'A' Reactor Feed Pump (RFP) on low suction pressure. Due to the power level at the time, the 'B' RFP had not been placed in service. Closure of Containment Isolation Valves (CIV's) in multiple systems and actuation of High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) pumps occurred as a result of reaching the respective actuation setpoints on reactor water level as designed. The 'B' RFP was placed in service to control water level at 1340 EDT on 3/11/2024. The cause of the 'A' RFP trip was the use of the incorrect procedure section for isolation of a condensate pump while the main condenser was under vacuum. This allowed air leakage into the system which resulted in the low suction pressure trip of the 'A' RFP. The Condensate & Feedwater System procedure has been revised to clearly direct the performer to the appropriate section. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and lnfonmation Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of lnfonmation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRG may not conduct or sponsor, and a person is not required to respond to, a collection of infonmation unless the document requesting or requiring the collection http://www,nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/l displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV Edwin I. Hatch Nuclear Plant Unit 1 321 ~ NUMBER NO. ~-I 1-0 □ 052 002 I I | EVENT DESCRIPTION At 1338 EDT on 3/11/2024, while Unit 1 was in MODE 1 at 35% power and performing power ascension activities, the reactor was manually tripped due to reactor water level decreasing following the trip of the 'A' Reactor Feed Pump (RFP)(EIIS Code: P) on low suction pressure. Due to the power level at the time, the 'B' RFP had not been placed in service. Closure of Containment Isolation Valves (CIVs)(EIIS Code: ISV) in multiple systems and actuation of High Pressure Coolant Injection (HPCl)(EIIS Code: BJ) and Reactor Core Isolation Cooling (RCIC)(EIIS Code: BN) pumps occurred as a result of reaching the respective actuation setpoints on reactor water level as designed. The 'B' RFP was placed in service to control water level at 1340 EDT on 3/11/2024. Once the 'B' RFP was placed in service, HPCI and RCIC were secured at 1340 EDT and 1342 EDT respectively. EVENT CAUSE ANALYSIS Based on causal analysis, the cause of the 'A' RFP trip was the use of the incorrect procedure section for isolation of a condensate pump while the main condenser was under vacuum. This allowed air leakage into the system which resulted in the low suction pressure trip of the 'A' RFP. SAFETY ASSESSMENT AND REPORTABILITY There were no actual safety consequences as a result of this event. All safety related systems functioned as designed during this event. The operating crew responded correctly to the event. The applicable abnormal/emergency operating procedures were entered. The event was within the analysis of the Updated Final Safety Analysis Report (UFSAR) Chapter 15. This event is reportable per 10 CFR 50.7 3(a)(2)(iv)(A), as any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section. Systems that actuated during this event that are listed in (a)(2)(iv)(B) include; the Reactor Protection System (RPS)(EIIS Code: IG), general Containment Isolation Valves (CIV) in more than one system, ECCS including the HPCI system, and the RCIC system. CORRECTIVE ACTIONS The Condensate & Feedwater System procedure has been revised to clearly direct the performer to the appropriate section for isolating a condensate pump when the main condenser is under vacuum. PREVIOUS SIMILAR EVENTS On 09/29/2000 at 1357 EDT, Unit 1 was in the Run mode at a power level of approximately 1520 CMWT (55 percent rated thermal power). At that time, the reactor was scrammed manually following a trip of the operating Reactor Feedwater Pump (RFP) and a decrease in water level. Personnel inserted the scram in anticipation of an automatic scram on low water level. A RFP was placed into service to maintain level. This event was caused by component failure. During the implementation of a clearance to isolate a condensate pump, air was introduced into the condensate pump suction header through a leaking pump suction isolation valve. The presence of air led to the trip of the operating RFP on low suction pressure. LER 2000-011-00. | ML24130A268 | 0 | good
Cooper Nuclear Station 298 1 of 4 | Unknown Unit | Main Turbine Stop Valve Position Switches Do Not Meet Channel Independence Criteria Results In Two Channels Being Declared Inoperable And A Condition Prohibited bv Technical Specifications | 05-09-2024 | On March 11, 2024, a question was raised concerning the mechanical separation criteria of the Reactor Protection System Turbine Stop Valve (TSV) closure function position switches as the position switches on each TSV are connected together with all-thread for actuation. On March 29, 2024, it was determined that the two position switches for each TSV do not have channel independence and one position switch for each TSV was declared inoperable because the switches are mechanically linked together. The direct cause of the failure to meet the requirement of channel separation comes from the position switches not being mechanically separated due to sharing a common linkage. A causal factor for this was the initial assumption was incorrect that the plant is constructed consistently with the design basis. The channel independence issue will be resolved by the engineering change process. A seminar will be presented to engineering personnel to address the assumption the plant was constructed consistent with the licensing basis. There were no safety consequences as a result of this event. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process LICENSEE EVENT REPORT (LER) and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC (See NUREG-1022, R.3 for instruction and guidance for completing this form may not conduct or sponsor, and a person is not required to respond to, a collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/} of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Cooper Nuclear Station 05000-298 NUMBER NO. 2024 004 00 | PLANT STATUS At the time of the event on March 11, 2024, Cooper Nuclear Station (CNS) was in Mode 1, Power Operation, at 100 percent steady-state power. BACKGROUND The Reactor Protection System (RPS) [EIIS:JC] initiates a reactor [EIIS:RPV] scram when one or more monitored parameters exceed their specified limits to preserve the integrity of the fuel cladding and the reactor coolant pressure boundary and minimize the energy that must be absorbed following a loss of coolant accident. This can be accomplished either automatically or manually. RPS is arranged as two separately powered trip systems. Each trip system has three logics. Two of the logics are used to produce automatic trip signals. The remaining logic is used for a manual trip signal. Each of the two logics used for automatic trip signals receives input signals from at least one channel for each monitored variable. Thus, two channels are required for each monitored variable to provide independent inputs to the logics of one trip system. At least four channels for each monitored variable are required for the logics of both trip systems. Closure of the Turbine Stop Valves (TSV) results in the loss of a heat sink that produces reactor pressure, neutron flux, and heat flux transients. A reactor scram is initiated at the start of TSV closure in anticipation of the transients that would result from the closure of these valves. TSV closure signals are initiated from position switches (also referred to as limit switches) [EIIS:33] located on each of the two TSVs. Two independent position switches are associated with each stop valve. Both of the switches from one TSV provide input to RPS trip system A; the two switches from the other TSV provide input to RPS trip system B. Thus, each RPS trip system receives two TSV closure channel inputs from a TSV, each consisting of one position switch assembly with two contacts, each inputting to a relay [EIIS:RL Y]. The relays provide a parallel logic input to an RPS trip logic channel. The logic for the TSV closure function is such that both TSVs must be closed to produce a scram. Single valve closure will produce a half scram. This function must be enabled at thermal power greater than or equal to 29.5 percent reactor thermal power as measured by turbine supply pressure. Four channels of TSV closure function, with two channels in each trip system, are required to be operable for Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.3.1.1 to ensure that no single instrument failure will preclude a scram from this function if both TSVs should close. | ML24131A023 | 0 | good
Cooper Nuclear Station 298 1 of 4 | Unknown Unit | Not Found | 05-13-2024 | On March 13, 2024, while performing planned maintenance on High Pressure Coolant Injection Pressure Switch 2787 (HPCI-PS-2787), the pressure switch setpoint was found to be outside of calibration tolerance. A new pressure switch, that passed calibration tolerance during bench testing, was subsequently installed and found to be out of tolerance. Further investigation revealed that the pressure switch had not been installed per the seismic test report. As such, the pressure switch was removed and reinstalled per the seismic test report and passed calibration testing. Guidance documents directing installation of the pressure switch will be revised to include installation requirements. Event Notification 57041 was submitted on March 21, 2024, for this condition. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: BO hours. Reported lessons learned are incorporated into the licensing process LICENSEE EVENT REPORT (LER) and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC (See NUREG-1022, R.3 for instruction and guidance for completing this form may not conduct or sponsor, and a person is not required to respond to, a collection http://www.nrc.gov/readlng-rmldoc-collections/nuregs/staff/sr1022/r3/l of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Cooper Nuclear Station 05000-298 NUMBER NO. 2024 005 00 | PLANT STATUS At the time of the event on March 13, 2024, Cooper Nuclear Station (CNS) was in Mode 1, Power Operation, at 100 percent steady-state power. BACKGROUND The High Pressure Coolant Injection (HPCI) system [EIIS:BJ] provides protection to the core in case of a small break in the reactor coolant pressure boundary which does not result in a rapid depressurization of the reactor vessel [EIIS:RPV]. The HPCI system permits the nuclear plant to be shutdown while maintaining sufficient reactor vessel water inventory until the reactor vessel is depressurized. HPCI continues to operate until reactor vessel pressure is below the pressure at which Low Pressure Coolant Injection system [EIIS:BO] operation or Core Spray system [EIIS:BM] operation can be used to maintain core cooling. HPCI consists of a steam turbine assembly [EIIS:TRB] driving a multi-stage booster and main pump assembly [EIIS:P] and system piping, valves, controls and instrumentation. The HPCI turbine is driven by steam from the reactor which is generated by decay and residual heat. The function of the HPCI Pressure Switch (PS) is to operate the auxiliary oil pump. It senses oil pressure at the turbine driven oil pump discharge. HPCI-PS-2787 opens when the turbine driven oil pump pressure is greater than or equal to 85 psig, stopping the auxiliary oil pump. HPCI-PS-2787 closes when the turbine driven oil pump pressure is greater than or equal to 20 psig, thus starting the auxiliary oil pump at a shutdown speed. HPCI-PS-2787 was installed as an Equipment Qualification pressure switch as part of original station equipment. On March 26, 2009, HPCI-PS-2787 was replaced with the same model of pressure switch. This replacement was the last remaining spare Model 9012-ACW-22. This model switch is obsolete and no longer available. In 2012, the vendor manual for the switch was updated and included installation torque values for the new 9012G model. In July 2014, an equivalent change (EC) was approved to replace HPCI-PS-2787, Model 9012-ACW-22, with a new Model 9012G. The EC did not include discussion on mounting requirements for this new model. A test report was issued for Model 9012G on August 30, 2016, and included mounting requirements for Model 9012G. In 2023, HPCI-PS-2787, Model 9012-ACW-22, was replaced with Model 9012G. The work documents for this replacement did not specify a torque value for the mounting screws. | ML24134A267 | 1 | ok
Nine Mile Point | Unit 2 | LER 2024-001-00, Automatic Reactor Scram on Turbine Trip due to Low Condenser Vacuum | 05-01-2024 | On 3/3/24 at 1942 while performing a plant shutdown in preparation for a refuel outage, Nine Mile Point Unit 2 experienced a Reactor Scram due to a Main Turbine trip on low condenser vacuum. The plant was at ~ 55% power at the time of the Reactor Scram. Following the scram, a Low RPV Level scram and containment isolation signal on Level 3 was received, as expected. The containment isolation signal impacted RHR Shutdown Cooling, RHR letdown to radwaste, and RHR sampling. All impacted valves were in the closed position at the time the isolation occurred. All control rods were fully inserted. Plant response was as expected. Post scram the Main Turbine Bypass Valves were used to control decay heat and normal post scram level control via the feed/ condensate system. The event notification (EN 57004) was made pursuant to 10 CFR 50.72(b)(2)(iv)(B) RPS Actuation and 10 CFR 50.72(b)(3)(iv)(A) Specified System Actuation and is reportable pursuant to 1O CFR 50.73(a)(2)(iv)(A). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to http://www. nrc.q ov/reading-rm/doc-collecti ons/nuregs/s taff/sr1 022/r30 respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 YEAR SEQUENTIAL REV Nine Mile Point Unit 2 410 NUMBER NO. □ 052 2024 - 001 - 00 | THE ENERGY INDUSTRY IDENTIFICATION SYSTEM (EIIS) COMPONENT FUNCTION IDENTIFIED AND SYSTEM NAME OF EACH COMPONENT OR SYSTEM REFERRED TO IN THIS LER ARE ENCLOSED WITHIN [BRACKETS] I. DESCRIPTION OF EVENT A. PRE-EVENT PLANT CONDITIONS: Prior to the event, NMP2 was in Mode 1 (Power Operation) at 55% power. B. EVENT: At 19:15 on March 3, 2024, NMP2 was continuing with a downpower in preparation for a refueling outage with normal gland sealing steam [TC] in service. As expected around 55% reactor power, the extraction steam [SB] pressure lowered to the 50 psig setpoint causing the extraction steam valve (2ESS-STV104 REBOILERS 1A &1 B EXTR SUPPLY ISOL VLV) to Clean Steam Reboiler A (CSR 'A') [RBLR] to close. By design, a main steam [SB] valve (2ASS-STV112 REBOILERS 1A & 1 B MAIN STM TRIP VLV) is intended to open as soon as the extraction steam valve closes, raising pressure to 95 psig. Upon closure of 2ESS-STV104, 2ASS-STV112 failed to open automatically. Operators attempted to open the valve manually by taking the control switch to the open position, however the valve indicated on the main control board that it remained closed and steam pressure to the CSR 'A' began to lower rapidly. To restore pressure, operators re-opened 2ESS-STV104 to re-establish the extraction steam source. CSR 'A' outlet pressure remained adequate to supply turbine seal glands, however pressure was lowering slowly consistent with extraction steam pressure. Without operator action, 2ASS-STV112 opened approximately 6 minutes later causing CSR 'A' inlet pressure to rise rapidly. Within 40 seconds, the CSR 'A' drain tank [TK] reached the high-level alarm and the hi-hi level trip was reached 6 seconds later sending a signal to isolate the inlet steam (2ASS-MOV3A REBOILER 1A STM INLET VLV) [ISV] to the CSR. The hi-hi level cleared and recurred six additional times. During this time operators attempted to reopen 2ASS-MOV3A to CSR 'A', however it auto isolated each time. When regulated turbine gland seal pressure dropped below the 6.3 psig setpoint for the Emergency Gland Sealing [SB] steam line, the system was unavailable to support turbine glands as it had been isolated due to failures occurring during the September 2023 forced outage. While Auxiliary Boilers [SA] were at normal pressure and temperature, valve 2ASS-AOV145 (AUX BLR STM INLET VLV) to the clean steam reboilers was gagged closed and not readily available to the operators As a result of degrading CSR pressure and unavailability of redundant Emergency Gland Sealing steam supply, gland sealing steam pressure was lost at 19:38 and condenser [COND) vacuum rapidly degraded. Operators stopped actions to restore the CSR to brief on a manual reactor trip. Prior to initiating the manual trip an automatic trip (JC] occurred at 19:42 at an indicated condenser vacuum of 24.5". At 19:59, CSR 'A' was restored to service by opening 2ASS-MOV3A. No additional hi-hi level conditions occurred. Operators requested maintenance support to close 2ASS-STV112 because it has an interlock that prevents 2ASS AOV145 from being opened unless 2ASS-STV112 is closed. Once closed, the gagging device on 2ASS-AOV145 was removed and steam was supplied to the CSR from the Auxiliary boilers. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). | ML24136A202 | 0 | good
fermi 2 | Unknown Unit | Automatic RPS SCRAM on High RPV Pressure While Attempting to Lower Generator Output During RF-22 | 05-15-2024 | Not Found | INITIAL PLANT CONDITIONS Mode -1 Reactor Power - 023 There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT At 0004 Eastern Daylight Time (EDT) on March 23, 2024, with the unit in Mode 1 at 23-percent power, the reactor automatically scrammed due to high Reactor Pressure Vessel (RPV) pressure when the turbine bypass valves [PCV] (which were being opened per Fermi procedure 22.000.04 "Plant Shutdown from 25-percent Power") unexpectedly closed while attempting to lower Generator [GEN] output to 55 MWe to support shutdown for a refueling outage. The SCRAM was not complex, with systems responding normally post-scram, with the exception of the pressure control system. The transient occurred while lowering Turbine Speed/Load Demand which caused arise in pressure/power until the Reactor Pressure System (RPS) [JD] Set point for Reactor Pressure High was exceeded and resulted in an Automatic Reactor Scram. Reactor water level was maintained at normal level following expected post-scram feedwater level response. Decay heat was removed by the Main Steam System [SB] to the main condenser using manual operation of turbine bypass valves. All Control Rods were inserted into the core. DESCRIPTION OF THE SYSTEM The Main Turbine Bypass System [JI] and Moisture Separator Reheater (MSR) [RHTR] are designed to control steam pressure when reactor steam generation exceeds turbine requirements during unit startup, sudden load reduction, and cool down. It allows excess steam flow from the reactor to the condenser without going through the turbine. The bypass capacity of the Main Turbine Bypass System and Moisture Separator Reheater is 30-percent of the Nuclear Steam Supply System [SB] rated steam flow. Sudden load reductions within the capacity of the steam bypass can be accommodated without reactor SCRAM. The Main Turbine Bypass System consists of two valves connected to a 52-inch manifold, which is between the main steam isolation valves and the turbine stop valves. Each of these valves is operated by a separate hydraulic unitized actuator. The bypass valves are controlled by the Main Turbine Pressure Regulator Control System [JI], as discussed in the Updated Final Safety Analysis Report (UFSAR), Section 7.7.1.4. The bypass valves are normally closed, and the pressure regulator controls the turbine control valves that direct all steam flow to the turbine. If the turbine speed controls or the load limiter restricts steam flow to the turbine, the pressure regulator controls the system pressure by opening the bypass valves. When the bypass valves open, the steam flows from the 52-inch manifold through connecting piping to the condenser. The reheating steam flow path to the moisture separator reheater provides an additional steam volume that mitigates a rapid pressure increase (e.g., from a generator load reduction). NRCFORM366A(04-02-2024) Page 2 Of 3 | ML24136A211 | 1 | ok
Fermi 2 | Unknown Unit | Primary Containment Isolation Valve Declared Inoperable for a Period Prohibited by Technical Specifications | 05-16-2024 | At 1718 EDT on March 17, 2024, it was identified that E4150-F042, HPCI Booster Pump Suction from Suppression Pool Inboard Iso MOV, was not fully closing without holding down the pushbutton in the Main Control Room. The Primary Containment Isolation function (PCIV) of E4150-F042 was declared inoperable. This condition did not challenge the ability of Primary Containment to perform its overall safety function. On March 19th, actions were taken to replace the associated Closed Auxiliary Seal-in contact block and restore the PCIV function of E4150-F042. A Past Operability evaluation was conducted, which determined that upon a HPCI System steam line isolation signal from the HPCI control logic, E4150-F042 would not fully close. The PCIV function of E4150-F042 was declared inoperable for a period exceeding that which is allowable per TS 3.6.1.3. This condition is being reported under 10CFR50.73(a)(2)(i)(B), operation or condition which is prohibited by plant technical specifications. There were no safety consequences or radiological releases associated with this event. The cause of the E4150-F042 not fully closing is due to the Closed Auxiliary Seal-in Contact failing to keep the close contactor coil energized due to high resistance across the electrical contacts. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments f ~ ~ c,J>P. t REG ? t,<,.>O . LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to ~ CONTINUATION SHEET ~ ,i Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory ..;.+-, ••11t•• +O' Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ~ 050 YEAR SEQUENTIAL REV I □ NUMBER NO. Fermi 2 00341 D □ 052 I 2024 - I 002 I - 00 | INITIAL PLANT CONDITIONS Mode – 1 Reactor Power – 099 There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT At 1718 (EDT) on March 17, 2024, it was identified that E4150-F042, High-Pressure Coolant Injection (HPCI) [BJ] Booster Pump Suction from Suppression Pool Inboard Isolation [ISV] Motor Operated Valve (MOV) (Manufacturer Powell Co., Model 3023WE), was not fully closing without holding down the pushbutton in the Main Control Room (MCR). The Primary Containment Isolation function (PCIV) [BD] of the E4150-F042 was declared inoperable. This condition did not challenge the ability of Primary Containment [JM] to perform its safety function as containment integrity would have been maintained by the redundant water seal and by E4150-F041, HPCI Booster Pump Suction from Suppression Pool Outboard Isolation MOV. This condition also did not challenge the ability of E4150-F042 to automatically open when required, therefore the High-Pressure Coolant Injection (HPCI) system remained operable. This condition was first identified in Fermi 2 condition report (CR) 2023-30437 (05/23/2023) and again in CR 2024-36518 (02/25/2024). Both earlier CRs drew the same inaccurate operability conclusion that the manual seal-in contact via the open pushbutton is not used when E4150-F042 is closed due to a containment isolation signal. Due to this inaccurate operability conclusion in those 2 CRs, a past operability and reportability review were not conducted (action in CR 2024-36518 to understand the inaccurate operability conclusions). During a pre-refueling outage (RF22) review of Main Control Room Deficiency work orders, a DTE Electrician generated CR 2024-36970 (03/17/2024) to review the associated information with E4150-F042. The operability determination with that CR placed the PCIV function of E4150-F042 inoperable. Operations entered Limiting Condition for Operation (LCO) 2024-0087 on 03/17/2024 at 2345 with an expiration date of 03/20/2024 at 2345 to isolate the affected flow path and align Emergency Core Cooling System operations and instrumentation per TS 3.6.1.3, TS 3.5.1, and TS 3.3.5.1. Those actions were completed and LCO 2024-0087 was exited on 03/18/2024 at 0851. At that time operations moved to revised LCO 2024-0087B with an expiration date of 04/01/2024 at 0851 to support the necessary repairs per TS 3.5.1 and TS 3.3.5.1. LCO 2024-0087B was exited on 03/19/2024 at 1039 when repairs were made and the PCIV function of E4150-F042 was restored to operable status. Based on the past operability review, the time period used to declare the PCIV function of E4150-F042 inoperable is from when the condition was first identified in CR 2023-30437 on 05/23/2023, until the appropriate repairs were made on 03/19/2024. Per Technical Specification (TS) 3.6.1.3 Primary Containment Isolation Valves (PCIV), each PCIV shall be operable in MODES 1, 2 and 3. CONDITION E states that if any required action and associated completion time of CONDITION A, B, C or D are not met, ACTION E.1 requires the plant to be in MODE 3 in 12 hours, and ACTION E.2 requires the plant to be in MODE 4 in 36 hours. Immediate troubleshooting was conducted on E4150-F042 failing to fully close. It was determined that E4150-F042 Closed Auxiliary Seal-in contact was intermittently failing to keep the close contactor coil energized due to high resistance across the electrical contacts. This resulted in E4150-F042 failing to fully stroke closed during required surveillances without holding the pushbutton closed in the Main Control Room. | ML24137A008 | 0 | good
LaSalle County Station | Unit 1 | Reactor Protection System Half Scram due to Motor Generator Set Electric Power Monitoring Assembly Output Breaker Trip | 05-17-2024 | On March 25, 2024, LaSalle Unit 1 was operating at 100 percent power, when the 1B reactor protection system (RPS) motor- generator (MG) set electric power monitoring assembly (EPMA) output breaker tripped due to an underfrequency condition, which resulted in the loss of the 1B RPS bus. The loss of power to this bus created a half-scram condition and initiated closure of isolation valves in multiple systems. The condition was an invalid actuation because it was not the result of actual plant conditions and not an intentional manual action. Actuations and isolations that occurred performed as designed. The cause of the MG set EPMA output breaker trip was the EPMA trip card for the output breaker being out of range high for the underfrequency setpoint which caused the trip on underfrequency. The loss of the 1B RPS bus resulted in general containment isolation signals that affected containment isolation valves in more than one system while the unit was critical. Therefore, the condition is reportable in accordance with 10 CFR 50. 73(a)(2)(iv)(A). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA. Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission. Washington. DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104). Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRG may not conduct or sponsor. and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection http://www. n re.gov/read ing-rm/doc-collections/nuregs/staff/sr1 022lr3D displays a currently valid 0MB control number. 1. FACILITY NAME (cid:127) 2. DOCKET NUMBER 3. LER NUMBER 050 SEQUENTIAL REV YEAR NUMBER NO. LaSalle County Station, Unit 1 (cid:143) 00373 052 2024 - 002 00 | Plant and System Identification LaSalle Country Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was "8" reactor protection system (RPS) logic and associate isolation functions. The affected component is the 18 electric power monitoring assembly (EPMA) output breaker. Condition Prior to Event Unit(s): 1 Date: March 25, 2024 Time: 04:04 CDT Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 100 percent Description On March 25, 2024, the main control room (MCR) received a "B" RPS half scram due to a loss of power to the Unit 1 "B" (1 B) RPS bus. Operations entered the applicable abnormal operation procedures for the loss of the 18 RPS bus. Field operators determined that the 18 RPS motor-generator (MG) set EPMA output breaker had tripped. The loss of power to the 1B RPS bus resulted in a half-scram condition and closure of isolation valves in multiple systems. The condition was considered an invalid actuation because it was not the result of a valid input signal to the RPS and was not an intentional manual action. Troubleshooting identified the frequency supplied by the MG set was approximately 60 Hz, as expected. All actuations and isolations performed as designed. The loss of the 18 RPS bus resulted in isolations of the reactor water cleanup system, main steam line drains, reactor coolant system sampling, instrument nitrogen system, reactor recirculation hydraulic power units, and containment monitoring system. The loss of the 18 RPS bus also resulted in the loss of power to portions of the average power range monitor, local power range monitor, oscillation power range monitor, and control rod block systems; as well as portions of the radiation monitoring for the main steam lines, reactor building vent, and fuel pool vent. Appropriate actuations and primary containment isolations occurred as designed. After the loss of power to the 18 RPS bus, the applicable Technical Specification (TS) timeclocks and actions were entered. Power was restored to the 18 bus by transferring the bus to the alternate power supply in accordance with plant procedures. The half-scram and isolations were reset, and the equipment was returned to operable status. All applicable TS timeclocks and actions were exited. Cause The 1B RPS MG set EPMA output breaker tripped due to an underfrequency trip signal from the EPMA trip card. The EPMA trip card was out of range high for the underfrequency setpoint which caused the 1B RPS MG set EPMA output breaker to trip due to underfrequency, even if there was no underfrequency condition present. Reportability and Safety Analysis The loss of a RPS bus and associated RPS actuation is considered an invalid actuation because it was not the result of a valid signal and not an intentional manual action. TS Surveillance Requirement (SR) 3.3.8.2.2 requires that the EPMA to have a frequency setpoint of greater than or equal to 57.3 Hz. The EPMA trip card underfrequency setpoint was discovered to be out of range high, therefore the EPMA output breaker trip is considered conservative and in compliance with SR 3.3.8.2.2. The loss of the RPS bus resulted in general containment isolation signals that actuated containment isolation valves in more than one system or multiple main steam isolation valves while the unit was critical. Therefore, the loss of the RPS bus is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). NRG FORM 366A (04-02-2024) Page_2_ of _3_ | ML24138A030 | 0 | good
Grand Gulf Nuclear Station | Unknown Unit | Automatic Actuation of Reactor Protection System | 05-28-2024 | On March 26, 2024 at 1115 CDT, Grand Gulf Nuclear Station experienced an automatic actuation' of the reactor protection system (RPS) due to high reactor coolant system (RCS) pressure while performing in-service leak testing. The plant was in Mode 4 at zero percent power with all control rods inserted at the time of the RPS actuation. The RPS actuation occurred due to a valid high RCS pressure signal and all plant systems responded as designed. The high pressure condition occurred due to inadvertent isolation of the blowdown discharge flow path. There were no safety consequences impacting the plant or public as a result of this event. The reactor was shutdown and subcritical at the time of the actuation. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request. 80 hours Reported lessons learned are incorporated into the licensing process and fed back to Industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M). U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104). Attn: Desk Officer for the Nuclear Regulatory ComrT11ss10n 725 17th Street NW. (See NUREG-1022, R_3 for instruction and guidance for completing this form Washington, DC 20503. The NRG may not conduct or sponsor, and a person is not required to IJi!R 1/\/'f::!:IW nrc gov/reading-rrn/doc-collect1on!.!/nuregs/staff/sr1022/r~/) respond to, a collection of information unless the document requesting or requinng the collecton displays a currently valid 0MB control number. 1. FACILITY NAME 00 050 2. DOCKET NUMBER 18 3. LER NUMBER SEQUENTIAL REV NUMBER NO. Grand Gulf Nuclear Station 416 1- 0 I -I □ 052 002 | PLANT CONDITIONS At the time of the event, Grand Gulf Nuclear Station (GGNS) was in Mode 4 (Cold Shutdown) with all control rods inserted at 0% reactor power. The station was performing in-service leak testing with reactor coolant system (RCS) pressure at approximately 1025 psig. DESCRIPTION OF EVENT During the performance of in-service leak testing, RCS pressure was being maintained with control rod drive (CRD) flow and reactor water cleanup (RWCU) blowdown to the main condenser. The Control Room was transferring RWCU blowdown to the radwaste system when RCS pressure began to rise. Reactor operators took action to reduce CRD flow, but RCS pressure did not reduce rapidly. The reactor protection system actuated as designed on high RCS pressure. Operators responded per the off-normal event procedure and the RPS was reset. REPORTA BILITY The automatic RPS actuation was initially reported to the NRC as a 4-hour report per 10 CFR 50.72(b)(2)(iv)(B) on March 26, 2024. This report is made in accordance with 10 CFR 50. 73(a)(2)(iv)(A) for any event or condition that resulted in manual or automatic actuation of any system listed in paragraph 1O CFR 50. 73(a)(2)(iv)(B). CAUSE The cause of the event was RWCU blowdown discharge flow path was isolated with the RCS at high pressure. Operators believed that the RWCU blowdown flow path to the main condenser could be isolated before aligning a discharge flow path to the radwaste system. CORRECTIVE ACTIONS Completed actions: • The RWCU discharge flow path was re-established. • The RPS was reset. Planned action: • Revise integrated operating instruction procedure 03-1-01-6 "Reactor Vessel In-Service Leak Test" to add specific guidance for swapping RWCU discharge flow paths. SAFETY SIGNIFICANCE There were no safety consequences, real or potential, resulting from the event. The reactor was sub-critical with all rods inserted at the time of the event and all systems responded as designed. PREVIOUS SIMILAR EVENTS None | ML24149A159 | 0 | good
River Bend Station | Unit 1 | Manual Reactor Scram Due to Lowering Feedwater Temperature Following an Automatic Isolation of Feedwater Heater String | 06-04-2024 | On November 17, 2023, at 22:15 CST, with River Bend Station, Unit 1, operating in Mode 1 at 30% power, an isolation of Low-Pressure Feedwater Heater String ‘A’ occurred. Operators entered the applicable Abnormal Operating Procedure (AOP) and reduced power to mitigate the lowering feedwater temperature. Reactor power was lowered to 24% and a manual reactor scram was inserted at 23:55 CST. All control rods fully inserted and there were no complications. All systems responded as designed. A direct cause of the Heater String isolation cannot be determined. This report is made pursuant to 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of the Reactor Protection System. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported ~c; , ,>A AEG<,l ..> LICENSEE EVENT REPORT (LER) l r e e s g s a o r n d s in g le a b r u n r e d d e n a r e e s t i i n m c a o t r e p o to ra t t h e e d F in O to IA t , h e L ib lic ra e r n y s , in a g n d p r In o f c o e r s m s a a ti n o d n f C e o d l l b e a c c ti k o n to s B in r d a u n s c t h ry ( . T S -6 e n A d 1 c 0 o M m ), m U e . n S ts . !~o\ .: Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to ~ ~ . 0 CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory '(,..., *••·· 0~ Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid OMB control number. 1. FACILITY NAME ■ 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV I I~ I I □ NUMBER NO. River Bend Station, Unit 1 00458 D 2023 052 - I 005 - 01 I | Event Description On November 17, 2023, at 22:15 CST, River Bend Station (RBS), Unit 1, was operating at 30% power while performing plant startup activities when an isolation of Low-Pressure Feedwater Heater String ‘A’ [SJ] occurred. Main Control Room Operators entered Abnormal Operating Procedure – Loss of Feedwater Heating (AOP-0007) for transients involving lowering feedwater temperature. AOP-0007, Attachment 1 (Feedwater Temperature vs Core Thermal Power Graph), provides guidance for power operations with reduced feedwater temperature from 100% reactor power to 25% reactor power. In accordance with AOP-0007, Attachment 1, operators began to manually insert control rods using the Control Rod Drive System [AA] to exit the restricted region for power operations at the lower feedwater temperature. Control rod insertion lowered power to 24%, which placed the unit below the graph start point of AOP-0007, Attachment 1. At 23:55 CST, while RBS was operating at 24% power, a manual reactor scram was inserted due to operation below the graph start point of AOP-0007, Attachment 1, caused by continued lowering of feedwater temperature. All control rods fully inserted and there were no complications. All systems responded as designed. AOP-0007, Attachment 1, contains a graph of feedwater temperature versus core thermal power; however, no information is provided for power levels below 25.7% of rated power. With reactor power lowering to 24%, the operators were not able to determine if the unit was operating in an acceptable region. Therefore, the conservative decision was made to manually scram the reactor. Following the initial investigation, engineering input from calculations performed as part of an engineering change has provided new information for operating at power levels below 25.7%. This event was reported under 10 CFR 50.72(b)(2)(iv)(B), as any event or condition that results in actuation of the Reactor Protection System (RPS) when the reactor is critical and 10 CFR 50.72(b)(3)(iv)(A) Specified System Actuation as result of Group 3 isolations (EN 56863). This report is made pursuant to 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of the Reactor Protection System. Event Cause There is insufficient evidence to determine a direct causal factor for the Low-Pressure Feedwater Heater String isolation event. An independent third-party review of this incident has determined the most probable cause of the isolation was a level switch actuation due to steam backflow from the drain receiver tank volume flashing as a result of a rapid pressure transient event. Safety Assessment The actual consequence was the initiation of a manual scram. Following the scram, reactor pressure was maintained by the Turbine Steam Drains [TF] and reactor water level was maintained by the Feedwater [SJ] system. The RBS power to flow map continued to meet the licensing acceptance criteria parameters. There were no actual consequences to general safety of the public, nuclear safety, industrial safety, and radiological safety for this event. | ML24156A040 | 0 | good
Cooper Nuclear Station 298 1 of 5 | Unknown Unit | Secondary Containment Differential Pressure Perturbation Exceeds Technical Specifications | 06-06-2024 | On October 22, 2023, Reactor Building pressure exceeded the Technical Specifications limit of -0.25 inches of water gauge (wg) resulting in Secondary Containment being declared inoperable. Operations personnel walked down the ventilation systems and found that the first discharge duct hatch for EF-R-1 B was open. The hatch was subsequently closed, and Secondary Containment pressure returned to the normal operating set point of -0.33 inches wg. The cause of the event was the opened first discharge duct hatch for EF-R-1 B. The cause of the open hatch has been determined to be looseness of the latching mechanism likely due to normal vibrations from system operations. There was no impact on nuclear safety, plant reliability, radiological safety, or industrial safety. Event Notification 56811 was submitted on October 22, 2023, due to the unplanned inoperability of Secondary Containment. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process LICENSEE EVENT REPORT (LER) and fed back to industry. Send comments regarding burden estimate to the FOIA, CONTINUATION SHEET Library, and Information Collections Branch (T-6 A 1O M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC (See NUREG-1022, R.3 for instruction and guidance for completing this form may not conduct or sponsor, and a person is not required to respond to, a collection http://www. nrc.g ov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Cooper Nuclear Station 05000-298 NUMBER NO. 2023 002 01 | PLANT STATUS Cooper Nuclear Station was in Mode 1, Power Operation, at 100 percent power at the time of the event on October 22, 2023. Both Standby Gas Treatment (SGT) [EIIS: BH] trains were in normal standby lineup. Reactor Building Heating and Ventilation (RB HV) [EIIS: VA] was controlling Secondary Containment pressure. Single exhaust fan EF-R-1 B was in service, with an indicated exhaust flow rate of 35,000 standard cubic feet per minute, for cold weather operation. BACKGROUND Secondary Containment serves as a barrier to confine and monitor potential releases during fuel handling operations and is a system that limits the release of radioactive materials to the environment and consists of four subsystems. One of the subsystems is the Reactor Building [EIIS: NG], which encloses the Reactor Pressure Vessel [EIIS: RPV] and Primary Containment [EIIS: NH]. The Secondary Containment area (most of the Reactor Building) has supply and exhaust ventilating systems. The supply system furnishes filtered 100% outdoor air to all floors of the building through ductwork. The supply unit has an operating and standby (100% capacity) fan, each with vortex dampers [EIIS: COMP], which deliver supply air at a rate proportional to a static pneumatic signal set manually by operations personnel. The exhaust air is induced from the ventilated areas to a common plenum connected to the two exhaust fans, each of 100% capacity. The air is then exhausted to the atmosphere. During normal plant operation, a minimum average negative pressure (vacuum) of 0.25 inches of water gauge (wg) is maintained by differential pressure (DP) controllers which receive signals proportional to the pressure difference between outside air and the Secondary Containment atmosphere, and control the position of the exhaust fan vortex dampers. The DP is detected by four separate probes, with one on each side of the Reactor Building. Control action is initiated from the average value of the four sensor probes. If a Loss of Coolant Accident should occur, all ventilation systems of the Primary Containment area and Secondary Containment area will trip, Secondary Containment is isolated automatically, and the SGT system will be automatically initiated. Each exhaust fan has a transition piece between the round fan barrel and the following rectangular duct work. Each exhaust fan has an air operated discharge damper installed in the duct work immediately downstream of the transition piece. On each exhaust fan discharge duct, there is a duct hatch on the upstream side of the | ML24158A065 | 0 | good
Limerick Generating Station | Unit 1 | Core Operating Limits Report Thermal Limit Exceeded for Unit 1 Fuel Bundle GGK123 | 06-18-2024 | On April 12, 2024, while performing a water rod inspection of fuel bundle GGK123 during a planned refuel outage, it was(cid:3) identified that several fuel spacers had propagated up within the bundle toward the upper tie plate. It was determined through(cid:3) analysis that spacer positioning had a direct effect on the Minimum Critical Power Ratio (MCPR). On April 22, 2024, an(cid:3) analysis of the operating conditions by Global Nuclear Fuel (GNF) of fuel bundle GGK123 was reviewed and accepted by the(cid:3) station. The report confirmed that, during the previous cycle, the Operating Limit MCPR exceeded limits set by Technical(cid:3) Specifications (TS) 3.2.3. Since the Operating Limit MCPR was exceeded for longer than allowed by TS Limiting Condition for(cid:3) Operation (LCO) 3.2.3, this event is reportable as a condition prohibited by TS per 10 CFR 50.73(a)(2)(i)(B). The fuel bundle spacers shifted out of position over the previous operating cycle. This condition was identified during the(cid:3) inspections in response to GNF 10 CFR Part 21 communication SC 22-04, GNF3 Raised Water Rod. This fuel bundle has(cid:3) been removed from the reactor core, is currently located in the spent fuel pool, and will not be re-loaded into the core. There(cid:3) was no impact to the health and safety of the public or plant personnel because the Safety Limit MCPR was not exceeded in(cid:3) the previous cycle operation(cid:17) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments ~¥' LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. ; i CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to ..... Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory <--+_, ~o' Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 •YEAR SEQUENTIAL REV I I~ I NUMBER NO. Limerick Generating Station Unit 1 352 I D 052 2024 - I 003 - 00 I | Condition Prior to Event On April 22, 2024, prior to the determination that fuel bundle GGK123 had exceeded a thermal limit, Limerick Generating Station Unit 1 was in Operational Condition (OPCON) 4 (Cold Shutdown) with reactor coolant temperature of 132 degrees Fahrenheit. Event Description On April 12, 2024, during planned in-core fuel inspections for mis-oriented water rods of susceptible GNF3 fuel bundles [EIIS System AC] in response to GNF 10 CFR Part 21 communication SC 22-04, an unexpected condition for fuel bundle GGK123 was discovered where four spacers visibly collocated below the upper tie plate. The four spacers located in the bottom portion of the fuel bundle were found at their expected (installed) axial locations. Fuel bundle GGK123 was permanently discharged to the spent fuel pool. Fuel vendor GNF evaluated the impact of this condition for the previous operating cycle. The evaluation conservatively assumed the spacers were displaced for all but the first week of the cycle. The inspection results showed the spacer contact marks indicated prolonged contact with the fuel indicating the spacers did not move early in the cycle. On April 22, 2024, the station completed the evaluation for fuel bundle GGK123. Analysis of the Event The evaluation report determined that: (cid:118) There were no penalties or adjustments associated with Linear Heat Generation Rate (LHGR) and Average Planar(cid:3)Linear Heat Generation Rate (APLHGR) and no (cid:71)(cid:76)(cid:86)(cid:70)(cid:72)(cid:85)(cid:81)(cid:76)(cid:69)(cid:79)(cid:72) impact to thermal limits and margins. (cid:118) There was no discernible impact to thermal limits and margins for co-resident fuel in the Unit 1 reactor core during the(cid:3)previous cycle of operation. (cid:118) The Operating Limit Minimum Critical Power Ratio (MCPR) exceeded limits set by TS 3.2.3 for the previous cycle. (cid:118) The Safety Limit MCPR requirements set by TS 2.1.2 were never violated for the previous cycle. The report determined that the requirements of TS LCO 3.2.3 MCPR were not met for Unit 1 Cycle 20. TS LCO 3.2.3 requires all MCPR values to be greater than or equal to the MCPR operating limits specified in the Core Operating Limits Report (COLR). If the MCPR value is less than the MCPR value in the COLR, TS LCO 3.2.3 Action b requires corrective actions to be initiated within 15 minutes and the MCPR value restored to within the required limits within two-hours or reduce thermal power to less than 25 percent within the next 4 hours. Since the station conservatively assumed the condition existed for most of the operating cycle, the station exceeded the two-hour requirement to restore MCPR within limits and did not reduce thermal power to less than 25 percent within the next 4 hours. Therefore, this event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant’s TS. Safety Consequences There were no actual safety consequences to this condition. The MCPR Safety Limit was not exceeded and there was no breach of fuel cladding for fuel bundle GGK123. | ML24170A772 | 0 | good
Joseph M. Farley Nuclear Plant | Unit 2 | Manual Reactor Trip due to Loss of Power to the 2A 125 Volt DC Distribution Panel | 06-19-2024 | On February 16, 2024, at 00:48 CDT while in Mode 1 and at 100% power, Farley Nuclear Plant (FNP) operators manually tripped Unit 2 following a loss of control of critical air-operated valves due to a partial loss of A-train DC power. LA08-2, the feeder breaker to the 2A 125VDC Distribution Panel, was found tripped open. This event resulted in a loss of letdown and the reactor makeup system. With volume control tank (VCT) makeup capability lost, operators made the decision to trip the reactor prior to charging pump suction rollover to the refueling water storage tank (RWST). The cause of the breaker opening was due to a short between wires on the A phase current transformer (CT)/ sensor wiring harness in breaker LA08-2 because of poor workmanship. Immediate corrective action included replacing breaker LA08-2 with a spare breaker to restore plant equipment to operation and stabilize the plant. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) due to the automatic actuation of multiple systems listed in 10 CFR 50.73(a)(2)(iv)(B). FNP Unit 1 was not affected during this event. However, the 10 CFR 21 notification does apply to Unit 1. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid 0MB control number. .1. -FA-CIL-ITY- NA-ME- ----------, ~ 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV Joseph M. Farley Nuclear Plant, Unit 2 364 □ NUMBER NO. ~- I 1-0 □ 052 I I 002 | EVENT DESCRIPTION: On February 16, 2024, at 00:48 CDT, with reactor power at 100% and in Mode 1, Farley Nuclear Plant (FNP) operators manually tripped Unit 2 following a partial loss of A-train 125V DC power which affected critical air-operated valves. Breaker LA08-2 [EIIS: EJ/BKR] the supply breaker to the 2A 125VDC Distribution Panel, was found tripped open. Loss of power to the 2A 125VDC Distribution Panel resulted in a loss of letdown and the reactor makeup system. With the volume control tank (VCT) [EIIS: CB / TK] makeup capability lost operators made the decision to trip the reactor prior to the charging pump suction rollover to the refueling water storage tank (RWST). Operating events and actions occurred in the following timeline on February 16, 2024: 00:35 Multiple Main Control Room Alarms are received. 00:35 Breaker LA08-02 Tripped (Entry into TS 3.8.9) 00:35 Entry into Abnormal Operating Procedure for CVCS Malfunction 00:36 Entry into Abnormal Operating Procedure of Loss of Instrument Air 00:36 Letdown confirmed isolated and loss of makeup capability. 00:48 Operators Manually Trip Reactor based on VCT level. 01 :42 Reactor Coolant Pump 2B secured due to low seal leak off. 01 :45 Pressurizer (PZR) level rises to Technical Specification (TS) high value of 63.5%. (Entry into TS 3.4.9) 02:09 Instrument Air realigned to Containment. 03:08 Commenced Reactor Coolant System (RCS) Cooldown 04:20 Following troubleshooting and breaker replacement, closed Breaker LA08-02 and restored Letdown (Exit TS 3.8.9) 04:34 NRC notified per 10 CFR 50. 72 (EN# 56971) 04:54 PZR level restored (Exit TS 3.4.9) Following the reactor trip, main feedwater [EIIS: JB] continued to be available. An actuation of the Auxiliary Feedwater System [EIIS: BA] occurred following the manual reactor trip as designed due to low level in the steam generators [EIIS: SB/SG]. BASIS FOR REPORTABILITY AND SAFETY ASSESSMENT: The safety consequences of this event were low. Although the component failure had downstream interrelation system effects on letdown and makeup, the operating crew appropriately mitigated the transient with abnormal and emergency operating procedures. Additionally, all TS required actions were met and parameters restored well within required action times. The operating crew responded appropriately to the event. This event was within the analysis of the UFSAR Chapter 15. This event is reportable per 10 CFR 50. 73(a)(2)(iv)(A) due to the automatic actuation of the Reactor Protection System [EIIS: AA] and AFW system as listed in 10 CFR 50.73(a)(2)(iv)(B). FNP Unit 1 was not affected during this event. CAUSE: The 125 Volt DC AKW breaker was built by Siemens and equipped with SIGMATRIP DC Analog Trip Unit built by SURE-TRIP. Framatome was the vendor used to qualify the safety related breakers and trip units. The analysis determined that the vendor QA/QC program was not sufficient to identify poor practices when interfacing with third party products. It was determined that during installation of the SIGMAT RIP DC Analog Trip Unit that the stranded wires that were terminated in the harness protruded in such a manner they were able to short to an adjacent wire in the harness. The short occurred in breaker LA08-2 (Serial Number R-300950258102B-001) on the A phase current transformer (CT)/sensor harness. For the SIGMATRIP DC Analog Trip Unit, Siemens and Framatome do not currently have a verification step/QA/QC check or any instruction for inspecting the wires connected in the wiring harnesses mounted to the CTs/sensors or the trip uniUlogic box. | ML24171A018 | 0 | good
i | Unknown Unit | : | 06-20-2024 | From March 25, 2024 to March 31, 2024, in Mode 1 at 100% power, Residual Heat Removal (RHR) loops B and C were not configured to the dedicated waterleg pump, a condition prohibited by Technical Specifications (TS). This condition, and an unanalyzed condition of the alternate keepfill configuration, were determined April 25, 2024. Based on the Cause Investigation: Cause 1 was a series of human performance errors processing an improper operating procedure revision; Cause 2 was ineffective communication between Operations and Engineering; a Contributing Cause was that past evaluations of the requested procedure change had missed the opportunity to clearly state in the procedure that the change did not support single active component failure licensing basis requirements The RHR procedure was revised to reflect the licensing basis. Planned corrective actions include: implementing an operations procedure department’s guidance document; authoring a new Training case study about communications; revising RHR and inservice testing program procedures to explain why alternate keep fill configuration causes RHR loop inoperability. The March 2024 RHR operational configurations are being reported as a condition prohibited by TS under 10 CFR 50.73(a)(2)(i)(B), and as an unanalyzed condition under 10 CFR 50.73(a)(2)(ii)(B). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Services Branch (T-6 A10M), U. S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ~ 050 YEAR SEQUENTIAL REV NUMBER NO. Perry Nuclear Power Plant 00440 2024 - 001 - 00 □ 052 | Energy Industry Identification System and Component (EIIS) codes are identified in the text as [XX]. System Description The Perry Residual Heat Removal (RHR) System [BO] is part of the Emergency Core Cooling System (ECCS) that is designed to provide cooling water (the RHR’s Low Pressure Coolant Injection (LPCI) function) to the reactor vessel [RPV] as protection against postulated loss-of-coolant accidents (LOCA). The RHR System has three loops (A, B, C), each with its own injection pump [P], which differ from the waterleg pumps. The licensing basis, as stated in the Updated Safety Analysis Report (USAR), requires that RHR cooling water flow from the Suppression Pool [BT] to the reactor vessel be initiated rapidly when the RHR System is called on to perform its function. The lag between the signal to start an RHR pump and the initiation of flow can be minimized by keeping the pumps’ discharge lines full. The licensing basis credits only the specific safety related, seismically qualified RHR waterleg pumps to automatically provide water to the RHR loops, downstream of each loop’s main RHR pump, to maintain the loops water solid. One waterleg pump supplies water to the RHR A loop, and another waterleg pump supplies water to both the RHR B and RHR C loops. An alternate keep fill configuration, relying upon water from non-safety related, non-seismically qualified, and non-essentially powered Condensate Transfer and Storage System [KA] piping, can be used to provide initial filling of the RHR discharge lines. The Condensate Transfer and Storage System piping water enters, via the alternate keep fill lineup, at each RHR loop’s piping downstream of where each loop would receive the waterleg pump’s water. At the interface of RHR and Condensate Transfer and Storage piping, each RHR loop has a single 8-inch safety-related check valve [V]. This alternate keep fill configuration is not a licensing basis credited method of keeping the RHR discharge lines water solid. Perry Technical Specification (TS) 3.5.1 is "ECCS - Operating." Limiting Condition for Operation (LCO) 3.5.1 requires each ECCS injection/spray subsystem be Operable in Modes 1, 2, and 3. With one low pressure ECCS injection/spray subsystem inoperable, TS LCO 3.5.1 Required Action A.1 requires the subsystem be restored to Operable status in 7 days. With two ECCS injection subsystems inoperable, Required Action C.1 requires one subsystem be restored to Operable status in 72 hours. If the C.1 Required Action and associated Completion Time are not performed and met, Required Action D.1 requires the unit be in Mode 3 Hot Shutdown in 12 hours, and Required Action D.2 requires the unit be in Mode 4 Cold Shutdown in 36 hours. DESCRIPTION OF EVENT 1. Operation in a condition prohibited by Technical Specifications. On February 22, 2024, operating procedure SOI-E12 Revision 79, “Residual Heat Removal System,” had been updated to Revision 80. The main purpose of that revision had been to delete revision 79’s directives pertaining to waterleg pump and alternate keep fill operation. Revision 79 reflected the licensing basis by stating as a Precaution and Limitation (P&L) that “If RHR A, B, or C are placed on alternate keep fill or the respective Waterleg pump is shutdown the affected RHR loop will be inoperable,” and by directing as a procedure step to “DECLARE the affected RHR loop inoperable.” Revision 80 of SOI-E12 deleted directives to declare an RHR loop inoperable, whenever that RHR loop has an inoperable waterleg pump or is in alternate keep fill configuration. Revision 80 directed in a new Precaution and Limitation that “If RHR A, B, OR C are placed on alternate keep fill AND the RHR PUMP A(B,C) DISCHARGE PRESSURE HI/LO. . . is received the RHR loop will be inoperable,” thereby allowing the system to be considered operable otherwise. | ML24172A162 | 0 | good
Browns Ferry Nuclear Plant | Unit 1 | Reactor Scram due to Generator Step-Up Transformer Failure | 06-24-2024 | On April 24, 2024, at 2215 Central Daylight Savings Time, while Unit 1 was at 100 percent rated thermal power, Browns Ferry Nuclear Plant Unit 1 experienced an automatic reactor scram due to a fault within the 1B Main Transformer. All plant equipment responded as expected, and Unit 1 was transitioned to Mode 4. The cause of the transformer failure is currently under investigation. The root cause of the transformer failure will not be known until a forensic tear down is complete. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), as an automatic actuation of the Reactor Protection System, Primary Containment Isolation System, the High-Pressure Coolant Injection System, and the Reactor Core Isolation Cooling System. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ☒ 050 SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 1 00259 NUMBER NO. ☐ 052 2024 - 002 - 00 | I. Plant Operating Conditions before the Event At the time of discovery of this event on April 24, 2024, Browns Ferry Nuclear Plant (BFN) Unit 1 was in Mode 1 at approximately 100 percent Rated Thermal Power (RTP). II. Description of Event A. Event Summary On April 24, 2024, at 2215 Central Daylight Savings Time (CDT), while Unit 1 was at 100 percent RTP, Browns Ferry Nuclear Plant (BFN) Unit 1 experienced an automatic reactor scram from a turbine control valve (TCV) [XCV] fast closure signal due to a fault within the 1B Main Transformer [XFMR]. All plant equipment responded as expected, and Browns Ferry Unit 1 was transitioned to Mode 4. Primary Containment Isolation Systems (PCIS) [JM] Groups 2, 3, 6, and 8 isolation signal reactor water level (RWL) Level 3 (+2”) was received. Upon receipt of this signal, all components actuated as required. Following the reactor scram, due to reactor water level reaching Level 2 (-45”), reactor recirculation pumps tripped as expected and both High Pressure Coolant Injection (HPCI)[BJ] and Reactor Core Isolation Cooling (RCIC) [BN] initiation signals were received, and both systems initiated as designed. All safety systems operated as expected. At no time was public health and safety at risk. The Tennessee Valley Authority (TVA) is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(iv)(A), as an automatic actuation of the Reactor Protection System (RPS) [JC], the Primary Containment Isolation System (PCIS) [JM], the High-Pressure Coolant Injection (HPCI) [BJ] System, and the Reactor Core Isolation Cooling (RCIC) [BN] System. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML24176A102 | 0 | good
Browns Ferry Nuclear Plant | Unit 1 | Inoperability of Unit 3 Diesel Generator due to Relay Failure | 07-03-2024 | On February 14, 2024, while performing Surveillance Procedure 3-SR-3.8.1.9(3D OL), “Diesel Generator 3D Emergency Load Acceptance Test with Unit 3 Operating,” the Unit 3 D Emergency Diesel Generator (DG) did not start on an undervoltage condition on its associated safety bus as expected. BFN-3-RLY-082-D/SUDR (Single Unit Defeat Relay) contacts 3 and 4 are designed as normally closed but were found electrically open in the normal state causing the Diesel fast start circuit to not be made up. The apparent cause of the misalignment of the SUDR relay contacts was the lack of effective Preventative Maintenance (PM). Improved PM Strategy to provide more detailed relay inspections /testing requirements for DG starting logic relays that have critical functions will be implemented. During this event, the 3D DG would have continued to support the safety function of starting on the receipt of an accident signal as designed. Although the 3D DG would not have automatically started during a loss of offsite power, operators are directed to immediately ensure DGs are started and tied to their respective safety busses. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME ☒ 050 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 1 00259 NUMBER NO. ☐ 052 2024 - 001 - 01 | I. Plant Operating Conditions before the Event At the time of this event on December 14, 2022, Browns Ferry Nuclear Plant (BFN) Unit 1 was in Mode 1 at approximately 100 percent power, Unit 2 was in Mode 1 at approximately 100 percent power, and Unit 3 was in Mode 1 at approximately 96 percent power. II. Description of Event A. Event Summary On February 14, 2024, while performing Surveillance Procedure 3-SR-3.8.1.9(3D OL), “Diesel Generator 3D Emergency Load Acceptance Test with Unit 3 Operating,” the Unit 3 D Emergency Diesel Generator (DG) [EK] did not start on an undervoltage condition on its associated safety bus [EB] as expected. Troubleshooting identified that the DG did not start due to a failure (open circuit) of Single Unit Defeat Relay (SUDR) [RLY] normally closed contacts (3-4). The relay was repaired and the surveillance test was reperformed satisfactorily on February 15, 2024. A past operability evaluation was performed by engineering that determined that the relay had been inoperable since December 14, 2022 when the 3D EDG started slower than expected during the performance of Surveillance Procedure 3-SR-3.8.1.1(3D), “Diesel Generator 3D Monthly Operability Test.” It was not originally recognized that the slower than expected DG start time could be an indication of the inability of the DG to start on a loss of voltage signal. Unit 3 Technical Specifications (TS) 3.8.1, “AC Sources - Operating,” and 3.8.2, “AC Sources - Shutdown,” requires the Unit 3 DGs to be operable in MODES 1, 2, 3, 4 and 5, and during movement of irradiated fuel assemblies in the secondary containment. Units 1 and 2 TSs 3.8.1 and 3.8.2 require the Unit 3 DGs associated with AC Boards needed to support equipment required for Units 1 and 2 to be Operable in Modes 1, 2, 3, 4, and 5, and during movement of irradiated fuel assemblies in the secondary containment. Because the 3D DG was inoperable from December 14, 2022, until February 15, 2024, the associated TS Actions were not complied with. Additionally, Mode changes were made with the 3D DG inoperable which is prohibited by TS 3.0.4. The Tennessee Valley Authority (TVA) is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant’s TSs. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML24185A151 | 0 | good
Edwin I. Hatch Nuclear Plant | Unit 2 | Incorrectly Installed Temporary Modification Results in Multiple Conditions Prohibited by Plant Technical Specifications | 04-30-2027 | At 1301 EST on 2/27/2024 while Unit 2 was at 100% power in MODE 1 and Unit 1 was at 0% power in MODE 4, it was discovered that a temporary Plant Service Water (PSW) modification was incorrectly installed on the Bravo condensing unit (CDU) of the Main Control Room Air Conditioning (MCRAC) subsystem. This temporary modification was installed on 1/30/2024 and then removed on 2/28/2024. For the time period that the incorrectly installed temporary PSW modification was in place, a past operability review (POR) was performed. The POR confirmed that the temporary PSW modification was installed incorrectly, rendering the Bravo MCRAC subsystem inoperable for a period of 29 days. Additionally, it was determined that the Alpha MCRAC subsystem was inoperable due to low refrigerant between 1/25/2024 and 2/8/2024. Due to these inoperabilities, several conditions prohibited by Technical Specifications (TS) were experienced as discussed below. With the removal of the temporary PSW modification on 2/28/2024 the operability of the Bravo MCRAC subsystem was restored. The Alpha MCRAC subsystem was repaired by adding refrigerant on 2/8/2024. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid 0MB control number. .1. -FA-CIL-ITY- NA-ME- ----------, ~ 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV Edwin I. Hatch Nuclear Plant Unit 2 00366 □ NUMBER NO. ~- I 1-0 □ 052 I I 002 | EVENT DESCRIPTION At 1301 EST on 2/27/2024 while Unit 2 was at 100% power in MODE 1 and Unit 1 was at 0% power in MODE 4, it was discovered that a temporary Plant Service Water (PSW) (EIIS Code: Bl) modification was incorrectly installed on the Bravo condensing unit (CDU) of the Main Control Room Air Conditioning (MCRAC) subsystem (EIIS Code: VI). This temporary modification was installed on 1/30/2024 @ 1020 and then restored on 2/28/2024 @ 1441. For the time period that the incorrectly installed temporary PSW modification was in place, a past operability review (POR) was performed. The POR confirmed that the temporary PSW modification was installed incorrectly, rendering the Bravo MC RAC subsystem inoperable for a period of 29 days, between 1/30/2024 @ 1020 and 2/28/2024 @ 1441. Additionally, it was determined that the Alpha MCRAC subsystem was inoperable due to low refrigerant between 1/25/2024@ 0416 - 2/8/2024@0410. Due to these inoperabilities, twelve conditions prohibited by Technical Specifications (TS) were experienced as discussed below. For reference, Unit 1 and Unit 2 share MCRAC and Main Control Room Environmental Control (MCREC) subsystems and have a common refueling floor. Unit 2 was in MODE 1 throughout the duration of these events. Unit 1 was in MODE 1 until 2/4/2024 @ 0008 when it entered MODE 3. Unit 1 was cooled down to MODE 4 on 2/4/2024 @ 0653 and then entered MODE 5 on 2/5/2024 @ 1211. Unit 1 transitioned back to MODE 4 on 2/23/2024 @ 1850. Prohibited Condition 1 & 2: Unit 1 & Unit 2 were not brought to MODE 3 in 12 hours as required by TS 3.7.4.E The design of the MCREC system requires one operable MCRAC subsystem per MCREC subsystem. With the Bravo MCRAC subsystem inoperable, the other two subsystems (Alpha and Charlie) have to be in-service to meet the requirements of the MCREC TS condition 3.7.4. The POR revealed that this condition was not continuously met. From 2/1/2024@ 0824 until 2/1/2024@ 2147 all three MCRAC units were inoperable_ Alpha and Bravo were inoperable for reasons discussed above and Charlie was inoperable due to a cooling water tagout. This condition, which resulted in both MCREC trains being rendered inoperable, existed in excess of the Unit 1 & Unit 2 TS condition 3.7.4.E (two MCREC subsystems inoperable) completion time of 12 hours to be in MODE 3. Prohibited Conditions 3 & 4: Unit 2 was not brought to MODE 3 in 12 hours as required by TSs 3.7.4.C and 3.7.5.D Once the Bravo MCRAC unit was rendered inoperable due to the PSW modification, concurrent with the Alpha MCRAC inoperability, one of the MCREC subsystems was rendered inoperable. The required actions for Unit 2 TS conditions 3.7.4.A (one MCREC inoperable) and 3.7.5.B (two MCRAC subsystems inoperable) each have a 7 day completion time. These completion times began on 1/30/2024 @ 1020 and expired on 2/6/2024 @ 1020 requiring entry into TS conditions 3.7.4.C and 3.7.5.D, each with a 12 hour completion time to be in MODE 3. These completion times expired on 2/6/2024@ 2220, but Unit 2 was not brought into MODE 3. Prohibited Condition 5: Unit 2 was not brought to MODE 3 in 12 hours as required by TS 3.7.4.E From 2/6/2024 @ 2350 until 2/8/2024 @ 0410, all three MCRAC units were inoperable (Note: Unit 1 was not in a MODE of applicability specified in TS 3.7.4.E during this time). Alpha and Bravo were inoperable for reasons discussed above and Charlie was inoperable due to an electrical bus tagout. This condition, which resulted in both MCREC trains being rendered inoperable, existed in excess of the Unit 2 TS condition 3.7.4.E (two MCREC subsystems inoperable) completion time of 12 hours to be in MODE 3. | ML24185A259 | 0 | good
Edwin I. Hatch Nuclear Plant | Unit 1 | Reactor Core Isolation Cooling (RCIC) System Inoperable Due to Mispositioned Link | 07-03-2024 | At 1133 EDT on 5/8/2024, with Unit 1 operating at 99. 7% power in MODE 1, maintenance was performing a surveillance on Reactor Core Isolation Cooling (RCIC) and identified an open electrical link that should have been in the closed position. This link being open defeated the RCIC High Reactor Water Level trip function. The High Reactor Water Level trip is a Technical Specification (TS) required function, without which RCIC is inoperable. At 1725 on 5/8/2024 the link was closed, restoring the High Reactor Water Level trip function and RCIC operability. Causal analysis determined that, due to a gap in the usage of human performance (HU) tools, the link was inadvertantly left open after restoration of a tagout on 3/8/2024 during the refueling outage. Corrective actions for this event focused on management reinforcement of HU Tool usage. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV Edwin I. Hatch Nuclear Plant Unit 1 00321 □ NUMBER NO. ~- I 1-G □ 052 I I 003 | EVENT DESCRIPTION At 1133 EDT on 5/8/2024, with Unit 1 operating at 99. 7% power in MODE 1, maintenance was performing a surveillance on Reactor Core Isolation Cooling (RCIC)(EIIS: BN) and identified an open electrical link that should have been in the closed position. This link being open defeats the RCIC High Reactor Water Level trip function. The High Reactor Water Level trip is a Technical Specification required function, without which RCIC is inoperable. EVENT CAUSE ANALYSIS The link being inadvertently left open was due to a gap in the usage of HU tools such as task preview, validating assumptions, and having a questioning attitude when manipulating plant equipment. SAFETY ASSESSMENT There were no actual safety consequences as a result of this event. At any time while the link was open, RCIC would have started at its low reactor water level setpoint and injected as required. If vessel level continued to rise during RCIC injection moisture carryover into the main steam lines could, over the course of time, lead to RCIC turbine damage. However, the RCIC mission time is only 8 hours and RCIC can be manually secured at any time if needed. Furthermore, RCIC is not credited in the safety analysis. This event is reportable per 10 CFR 50.73 (a)(2)(i)(B) as a condition prohibited by TS. The RCIC system was inoperable between 3/8/2024 until the link was closed on 5/8/2024. During this time, Unit 1 entered the mode of applicability on 3/10/2024 @ 1150 and then exited the mode of applicability due to cooling down from a reactor scram on 3/11/2024 @ 1903. Then Unit 1 entered the mode of applicability again after the subsequent startup on 3/17/2024 @ 1928. The allowable TS 3.5.3.A (RCIC inoperable) completion time of 14 days plus the TS 3.5.3.B completion time of 12 hours to be in MODE 3 was exceeded on 4/1/2024 @ 0728. Addtionally, the High Pressure Coolant Injection (HPCl)(EIIS: BJ) pump was operable when RCIC was inoperable except from 3/10/2024@ 2331 until 3/11/2024@ 0027 for performance of a surveillance test. This overlapping time of RCIC and HPCI inoperabilities did not exceed the TS 3.5.1.G completion time of 12 hours to bring the unit to MODE 3 when both RCIC and HPCI are inoperable. All low pressure ECCS systems were operable during the time RCIC was inoperable. CORRECTIVE ACTIONS At 1725 on 5/8/2024 the link was closed, restoring the High Reactor Water Level trip function and RCIC operability. Immediate corrective actions for this event focused on management reinforcement of HU Tool usage. Additionally, actions are in progress to conduct oral boards to reinforce the use of HU Tools. PREVIOUS SIMILAR EVENTS None. | ML24185A269 | 0 | good
Browns Ferry Nuclear Plant | Unit 3 | Main Steam Relief Valves Lift Settings Outside of Technical Specifications Required Setpoints | 07-08-2024 | On May 7, 2024, the Tennessee Valley Authority (TVA) was notified of as-found testing results that four (4) Main Steam Relief Valves (MSRVs) from Browns Ferry Nuclear Pant (BFN), Unit 3 were outside of their Surveillance Requirement limits for an indeterminate amount of time. These affected valves remained capable of maintaining reactor pressure within the American Society of Mechanical Engineers code limits and were still able to perform their safety function. It was determined that two MSRVs failed above their setpoints due to corrosion bonding to the valve seats and non-quantifiable leakage known as simmering. Two other MSRVs failed below their setpoints due to relaxed setpoint springs. All thirteen of the MSRV pilot valves were replaced during the Unit 3 Spring 2024 refueling outage. The Boiling Water Reactor Owners' Group is continuing to work toward a solution to improve the quality and adhesion of the platinum coating on the pilot discs. BFN will take additional actions to verify that the springs associated with each low failure passes Spring Rate testing or is replaced. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME ☒ 050 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 3 00296 NUMBER NO. ☐ 052 2024 - 003 - 2024 | I. Plant Operating Conditions before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN) Unit 3 was in Mode 1 at approximately 100 percent power. II. Description of Event A. Event Summary On May 7, 2024, NTS/Element notified TVA with the as-found testing results of the thirteen Main Steam Relief Valves (MSRVs) [RV], which were removed during the Spring 2024 Unit 3 Refueling Outage 21 (U3R21). Four (4) MSRVs (3-PCV-001-0004, 3-PCV-001-0005, 3-PCV-001-0022, and 3-PCV-001-0030) had as-found lift settings which were outside of the +/- 3 percent band of their setpoints required by Technical Specification (TS) 3.4.3, Safety/Relief Valves (S/RVs) for an indeterminate amount of time. Throughout this event, the two stage MSRV pilot valves remained capable of maintaining reactor pressure below 1375 pounds per square inch gauge (psig), which is the American Society of Mechanical Engineers (ASME) code limit of 110 percent of the vessel design pressure. The valves remained capable of performing their required safety function. TVA is submitting this report in accordance with Title 10 of the Code of Federal Regulations 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant’s TS. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML24190A129 | 0 | good
Perry Nuclear Power Plant | Unit 1 | : | 07-15-2024 | While operating in MODE 1 at 100% power on May 23, 2024 at 0000, Perry Nuclear Power Plant (PNPP) operators entered Technical Specification (TS) 3.4.5 due to the unidentified reactor coolant system (RCS) leak rate exceeding 5 gpm. PNPP operators commenced a manual reactor shutdown in accordance with site procedures at 0053 on May 23, 2024. Unable to reduce the unidentified RCS leakage, the shutdown transitioned to a TS required shutdown at 0400 and reported as Event Number 57136. The required safety systems and shutdown equipment performed as expected, resulting in an uncomplicated shutdown. The source of the unidentified RCS leakage was the reactor recirculation loop 'A' suction valve packing leak-off line via a failed sight glass flange. The leak-off line was isolated and sight glass repaired. The root causes were failing to maintain and operate the leak detection system leak-off lines as designed because of unrecognized potential consequences from a failure in inaccessible areas and not prioritizing permanent repairs for long standing equipment degradation during outage scoping. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(A) as completion of a plant shutdown required by the Technical Specifications. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150--0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported ,.r)P·'w.fl~5Gul.t \ . LICENSEE EVENT REPORT (LER) l r e e s g s a o rd n i s n g le a b r u n r e d d e n a r e e s i t n im co a r te p o t r o a t t e h d e in F t O o IA th , e L l i i b ce ra n r s y i , n g a n p d r o In ce fo s r s m a a n ti d o n fe S d e b r a vi c c k e s to B in ra d n u c s h tr y ( . T S -6 e n A d 1 0 c M om ), m U e . n S ts . ; • \ ;. 'I i CONTINUATION SHEET N ln u fo c q le o a ll r e cts R .R e e g s u o la u t r o c r e y @ nr C c o .g m o m v, is a s n io d n t , h e 0 W M a B s h r i e n v g i t e o w n, e r at D : C 0 MB 2 0 O 5 f 5 fic 5 e -0 o 0 f 0 1 In , form o a r tion b y a nd e R - e m g a u il l ator to y ··~·41 Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17'" Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rrn/doc-collections/nureqs/staff/sr1022/r3D displays a curren~y valid 0MB control number. 2. DOCKET NUMBER 3. LER NUMBER 1. FACILITY NAME 181 050 SEQUENTIAL REV YEAR NUMBER NO. Perry Nuclear Power Plant Unit 1 440 □ 052 2024 003 00 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. Background: The Perry Nuclear Power Plant (PNPP) reactor coolant recirculation system [AD] is designed to provide a forced coolant flow through the core to remove heat from the fuel. The pressure containing components of the reactor coolant system (RCS) and the portions of connecting systems out to and including the isolation valves define the reactor coolant pressure boundary (RCPB). During plant life, the joint and valve interfaces can produce varying amounts of reactor coolant leakage through either normal operational wear or mechanical deterioration. Limits on RCS operational leakage are required to ensure appropriate action is taken before the integrity of the RCPB is impaired. The safety significance of leaks from the RCPB varies widely depending on the source, rate, and duration; therefore, detection of leakage in the drywell is necessary. Methods for quickly separating the identified LEAKAGE from the unidentified LEAKAGE are necessary to provide the operators quantitative information to permit them to take corrective action should a leak occur detrimental to the safety of the facility or the public. A limited amount of leakage inside the drywell is expected from auxiliary systems that cannot be made 100% leak tight. Leakage from these systems should be detected and isolated from the drywell atmosphere, if possible, so as not to mask RCS operational LEAKAGE detection. Twenty-one drywell valves, including the reactor coolant recirculation pump suction valves [AD-V], have packing leak-off lines routed to the drywell equipment drain sump [WK]. Leakage directed to the drywell equipment drain sump is considered identified leakage while leakage collected through the floor drains to the floor drain sump is unidentified. Both leakage rates display and alarm in the Control Room. Each valve packing leak-off line has a temperature transmitter [AD-TT] that provides an alarm in the Control Room on high temperature in the line. A manually operated solenoid valve [AD-TSV] can then be closed from the Control Room to isolate the line. Located in the drywell and inaccessible while at power, the leak- off lines have a manual isolation valve [AD-ISV] upstream and a sight glass [AD-FG] downstream of the solenoid valves. Technical Specifications: PNPP Technical Specification (TS) Limiting Condition for Operation (LCO) 3.4.5, "RCS Operational LEAKAGE" applies in MODES 1, 2, and 3 and requires: no pressure boundary LEAKAGE; less than or equal to 5 gpm unidentified LEAKAGE; less than or equal to 30 gpm total LEAKAGE over the previous 24 hour period; and less than or equal to 2 gpm increase in unidentified LEAKAGE within the previous 24 hour period in MODE 1. When unidentified or total leakage is not within the limits, TS 3.4.5 Action B.1 requires the leakage to be within limits in 4 hours, and Action C.1 requires verification that the unidentified LEAKAGE increase is not service sensitive austenitic material within 4 hours. If the required actions and associated completion times are not met, TS 3.4.5 Action D.1 requires the plant to be placed in MODE 3 within 12 hours, and Action D.2 requires the plant to be placed in MODE 4 within 36 hours. DESCRIPTION OF EVENT: With PNPP operating in MODE 1 and 100 percent power, the drywell unidentified rate of change high alarm was received at 0000 on May 23, 2024. The drywell floor drain sump rate indicated 7.7 gpm. Condition B of TS 3.4.5 was entered to reduce the unidentified leakage to less than or equal to 5 gpm within 4 hours and lowering reactor power to achieve MODE 3 was started, in accordance with site procedures. Subsequently, the operations crew received the valve stem leak-off temperature alarm, indicating at least one of the 21 drywell valve leak-off line temperatures were greater than or equal to180 degrees F. Four lines were identified as potential sources. Simple troubleshooting found none of the four manually operated solenoid valves functioned. At 0400 on Page iof ! | ML24198A025 | 0 | good
LaSalle County Station | Unit 1 | Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.1.3 Completion Time Exceeded | 07-31-2024 | On April 9, 2024, while preparing for the Unit 1 traversing in-core probe (TIP) system shear valve actuating cartridge operability test to meet Technical Specification (TS) Surveillance Requirement (SR) 3.6.1.3.9, it was identified that three of the five installed shear valve squib cartridges had expired in October 2023. The Bases for SR 3.6.1.3.9 requires that the controls that limit shelf life and operating life of the explosive charge be followed, as applicable. Since the five-year expiration date was exceeded for the three identified TIP shear valves, the Bases requirements of SR 3.6.1.3.9 were not met and rendered the three TIP shear valves INOPERABLE. Due to SR 3.6.1.3.9 Bases not being met, TS Limiting Condition for Operation (LCO) 3.6.1.3 is required to be entered. The station exceeded the completion time for TS LCO 3.6.1.3; therefore, this this event is reportable as a condition prohibited by TS per 10 CFR 50.73(a)(2)(i)(B). Since three TIP shear valves were inoperable simultaneously due to the same cause, this event is also reportable per 10 CFR 50.73(a)(2)(vii) as a common cause inoperability of independent trains or channels. There was no impact to the health and safety of the public or plant personnel because all five squib cartridges were removed and tested successfully. The successful completion of the test demonstrated that the TIP shear valves with the expired squib cartridges were still capable of performing their function with the expired squib cartridges installed. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported ......... ~"( "'> lessons learned are incorporated into the licensing process and fed back to industry. Send comments f~V~' \ LICENSEE EVENT REPORT (LER) regarding burden estimate lo the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. . Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to \~...Y..✓ .i CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection http:l/www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D displays a currently valid 0MB control number. 1. FACILITY NAME (cid:127) 2. DOCKET NUMBER 3. LER NUMBER 050 SEQUENTIAL REV YEAR NUMBER NO. LaSalle County Station, Unit 1 (cid:143) 00373 052 2024 - 003 01 | Plant and System Identification LaSalle Country Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the traversing in-core probe (TIP) system. The affected components are the 1C 51- J004A/D/E TIP system shear valves. Condition Prior to Event Unit(s): 1 Date: April 9, 2024 Time: 18:30 CDT Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 100 percent Description On April 9, 2024, while preparing for the Unit 1 traversing in-core probe (TIP) system shear valve actuating cartridge operability test, it was identified that squib cartridges installed in three out of the five Unit 1 TIP shear valves had expired ('A', 'D', and 'E' trains). The squib cartridges have an expiration date of five years from the time the charge is packed into the firing mechanism. The five-year expiration date is based on the manufacturer's operating experience of squib charges not reliably firing after five years. The previous performance of this test on October 18, 2021, replaced and tested the squib cartridge from the 'B' train TIP shear valve while noting the other four squib cartridges were set to expire in October 2023, prior to the next performance of the test. A separate surveillance performed on January 31, 2023, replaced, and tested the squib cartridge from the 'C' train TIP shear valve. Upon identification, all applicable Technical Specification (TS) timeclocks were entered, and actions were taken to isolate the affected penetration flow path. The operability test was performed on April 10, 2024, and all five squib charges were replaced, and the removed charges were actuated successfully. The TIP shear valves were declared operable and all applicable TS timeclocks were exited. The successful completion of the test demonstrated that the TIP shear valves with the expired squib cartridges were still capable of performing their function. Cause The cause of the event is that the test surveillance did not factor in the expiration date of the squib cartridges for future surveillance test performances. Instead, an alternative tracking method was used to ensure the squib cartridges did not expire prior to the next performance of the operability test, which was ineffective. Additionally, during the last performance of the operability test, the expiration dates of the squib cartridges were not documented in the Corrective Action Program (CAP) to ensure expiration dates were not exceeded. Reportability and Safety Analysis The TIP valve assembly contains both a ball valve and a shear valve. When the TIP system is in standby, the system is retracted, and the ball valves are closed to maintain primary containment integrity. When the TIP system is operating and the detectors are in the core, the ball valve is open. In the event of a primary containment isolation signal, the TIP system is automatically withdrawn from the core and the ball valves are closed to maintain containment integrity. The shear valve is only used if a leak occurs when the TIP is beyond the ball valve and the power to the TIP system fails. The shear valve is actuated manually and can cut through and close off the tubing to preserve primary containment integrity. Therefore, both the ball valve and the shear valve are primary containment isolation valves (PCIVs) and must meet the requirements of TS Limiting Condition for Operation (LCO) 3.6.1.3, each PCIV shall be OPERABLE. | ML24213A022 | 0 | good
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | EDG Lube Oil Check Valve Bonnet Cap Leak due to Failed Gasket | 04-30-2027 | On April 24, 2024, at 1948, with James A. FitzPatrick Nuclear Power Plant at 100% power, the “B” Emergency Diesel Generator (EDG) was being operated for surveillance testing when lube oil leaked from the bonnet cap of check valve 93EDG-57B. The leak originated when a gasket between the body-to-bonnet connection failed. The gasket was installed on October 11, 2023. The cause of the gasket failure was uneven compression during installation when the bonnet cap was over tightened and yielded the thread root. Work planning instruction and the technical evaluation did not identify a change to the metal-to-metal tightening standard when installing a gasket as a corrective action on October 11, 2023. This deficiency would have prevented the fulfillment of the “B” EDG subsystem safety function due to not meeting the lube oil inventory requirement. The other 3 EDG units were not affected by this deficiency, no gaskets were installed. This condition was prohibited by Technical Specifications (TS), which is reportable per 10 CFR 50.73(a)(2)(i)(B). In addition, during this period, when “A” EDG subsystem was inoperable for planned maintenance, both subsystems were inoperable, a condition reportable per 10 CFR 50.73(a)(2)(v)(A). The condition was corrected by replacing the check valve on April 25, 2024. A case study will be developed and shared. NRC FORM 366 (04-02-2024) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 LICENSEE EVENT REPORT (LER) hours. Reported lessons learned are incorporated into the licensing process and fed CONTINUATION SHEET back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory (See NUREG-1022, R.3 for instruction and guidance for completing this form Commission, 725 17th Street NW, Washington, DC 20503; email: http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 YEAR SEQUENTIAL REV NUMBER NO. James A. FitzPatrick Nuclear Power Plant 05000333  052 2024 – 001 – 01 | Background The Emergency Onsite Power Supply System [EIIS identifier: EK] consists of two redundant Emergency Diesel Generator (EDG) subsystems. Each EDG subsystem consists of two EDG units. The capability of the two units in the subsystem to start, force parallel, and attain rated voltage and frequency together within 10 seconds, and run the necessary engineered safeguard loads, meets the requirements for the Emergency AC Power System. The EDG lubrication system [LA] is designed to provide sufficient lubrication (lube oil) to permit proper operation by circulating the lube oil to the diesel engine working surfaces and to remove excess heat generated by friction during operation. The lube oil inventory volume required to ensure 7 days continuous operation is 168 gallons based on the manufacturer's consumption values and without reaching the recommended minimum level. In standby, the system circulates warmed oil through the EDG engines to promote successful quick starts. This is accomplished by a 5/8-inch line with a swing check valve (93EDG-57B for “B” EDG unit), which closes during EDG operation to prevent bypassing flow. The check valve has a bonnet cap to access internals for preventive maintenance. Event Description On April 24, 2024, with James A. FitzPatrick Nuclear Power Plant (JAF) at 100% power, a surveillance test was started at 1912, involving an operational test of the “B” EDG subsystem. Operators were monitoring the performance when they discovered lube oil spraying from the top of check valve 93EDG-57B. At 1948, the “B” EDG unit was declared inoperable. Operators secured the EDG as well as the circulating and turbocharger lube oil pumps. The leak originated from the bonnet cap. With the engine in standby, the leak rate was approximately 60 drops per minute (dpm). A leak rate could not be observed with the system pressurized during the event; however, it was estimated that 11.5 gallons of lube oil was lost due to the leak. The operations staff estimated that the engine was running for approximately 5 minutes with the leak before the engine was secured. Therefore, the leak rate was approximately 2.3 gallons per minute (gpm), or 138 gallons per hour (gph). The magnitude of the lube oil leak would have exhausted the lube oil supply and this deficiency would have prevented the function of “B” EDG unit to fulfill its mission time. The A, C, and D check valves did not have any similar leaking condition. The “A” EDG subsystem remained Operable and the “D” EDG unit remained available during this event. The check valve 93EDG-57B was replaced on April 25 by 1300. There was no leakage following the repair. The Post Maintenance Testing was completed satisfactory restoring the “B” EDG subsystem to Operable. Page 2 of 4 | ML24234A140 | 0 | good
i | Unknown Unit | Emergency Diesel Generator Auto-Start and Load due to Loss of System Auxiliary Transformer 6. Evant Data 6. LER Number 7. Report Data 8. Other Facilities Involved Month Day Year Year S N eq u u m e b n e ti r a l Re N vi o s . io n Month Day Year F N a A cll ltyName (cid:143) 050 N Do A ck et Number 04 20 2024 2024 - 004 - 01 08 22 2024 N Fa A cil ity Name (cid:143) 052 D N o A ck et Number 9. Operating Mode 10. Power Laval 1 100 percent 11. This Report Is Submitted Pursuant to the Requirements of 10 CFR §: (Check all that apply) (cid:143) D D D (cid:143) 10 CFR Part 20 20.2203(a)(2)(vl) (cid:143) 10 CFR Part 60 SO. 73(a)(2)(11)(A) SO. 73(a)(2)(vlll)(A) (cid:143) 73.1200(a) D 0 D 20.2201(b) 20.2203(a)(3)(I) 50.36(c)(1)(I)(A) so. 73(a)(2)(11)(B) SO. 73(a)(2)(vlll)(B) 73.1200(b) (cid:143) 0 D D 0 D 20.2201(d) 20.2203(a)(3)(11) 50.36(c)(1)(11)(A) SO. 73(a)(2)(111) SO. 73(a)(2)(Ix)(A) 73.1200(c) (cid:143) D D D D 20.2203(a)(1) 20.2203(a)(4) 50.36(c)(2) ~ SO. 73(a)(2)(Iv)(A) SO. 73(a)(2)(x) 73.1200(d) D 20.2203(a)(2)(I) 10 CFR Part 21 D S0.46(a)(3)(11) D so. 73(a)(2)(v)(A) 10 CFR Part 73 D 73.1200(e) (cid:143) (cid:143) D D D D 20.2203(a)(2)(11) 21.2(c) 50.69(g) so. 73(a)(2)(v)(B) 73.77(a)(1) 73.1200(f) (cid:143) (cid:143) D D D 20.2203(a)(2)(111) 50. 73(a)(2)(I)(A) so. 73(a)(2)(v)(C) 73. 77(a)(2)(I) 73.1200(g) (cid:143) 0 D D D 20.2203(a)(2)(Iv) SO. 73(a)(2)(I)(B) 50.73(a)(2)(v)(D) 73. 77(a)(2)(11) 73.1200(h) (cid:143) D D 20.2203(a)(2)(v) SO. 73(a)(2)(I)(C) SO.7 3(a)(2)(vll) 0 OTHER (Specify here, in abstract, or NRG 366A). 12. Licensee Contact for this LER licensee Contact Phone Number (Include area coda) Joseph Reda, Operations Director (815) 415-2200 13. Complete One Line for each Component Failure Described In this Report Cause System Component Manufacturer Reportable to IRIS Cause System Component Manufacturer Reportable to IRIS X FK BKR W120 y X EB BKR 1005 y 14. Supplemental Report Expected Month Day Year [8J No I D Yes (If yes, complete 15. Expected Submission Dale) 16. Expected Submission Date I 16. Abstract (Limit to 1326 spaces, i.e .• approximately 13 single-spaced typewritten lines) On April 20, 2024, with LaSalle Unit 1 operating at 100 percent power and gas circuit breaker (GCB) 11-13 open to support transmission system operator testing of power line L0104 relays, oil circuit breaker (OCB) 1-13 tripped open on differential current resulting in the loss of the Unit 1 system auxiliary transformer (SAT). Bus 141 Y (Division 1) , normally supplied by the I Unit 1 SAT, failed to fast transfer to the Unit 1 unit auxiliary transformer (UAT), resulting in the Division 1 emergency diesel generator (EDG) to automatically start and load onto the 141Y bus, causing a load shed of the 141Y bus and momentary loss of power to the 141Y bus. The loss of the Unit 1 SAT also caused the Division 3 EDG to automatically start and load, as designed, onto bus 143 (Division 3). The load shed on bus 141Y caused power to be lost to the Unit 1 "A" (1A) reactor protection system (RPS) bus, resulting in a "A" RPS half-scram condition and closure of isolation valves in multiple systems. All actuations and isolations performed as designed. During the fast transfer of Division 2 from the Unit 1 SAT to UAT, the Unit 1 reactor building ventilation system (VR) 'B' supply isolation damper and "A' exhaust isolation damper went shut unexpectedly causing a loss of Unit 1 VR. These events are reportable in accordance with 10 CFR 50.7 3(a)(2)(iv)(A). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) r ......, Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments f:I.J.i LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to i~..... / CONTINUATION SHEET lnfocollec1S.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 72517th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection http://www. nrc.g o v/readinq-rm/doc-col leclions/nuregs/staff/sr1 022/r3Q displays a currently valid 0MB control number. 1. FACILITY NAME (cid:127) 2. DOCKET NUMBER 3. LER NUMBER 050 SEQUENTIAL REV YEAR NUMBER NO. LaSalle County Station, Unit 1 (cid:143) 00373 052 2024 - 004 01 NARRATIVE Plant and System Identification LaSalle Country Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the alternating current (AC) power system. The affected component is 345 kV oil circuit breaker (OCB) 1-13, the mechanism operated contacts (MOC) 15 and 16 of air circuit breaker (ACB) 1412, and the TSC switch contacts on ACB 1415. Condition Prior to Event Unit(s): 1 Date: April 20, 2024 Time: 07:04 CDT Reactor Mode( s): 1 Mode(s) Name: Power Operation Power Level: 100 percent Description Emergency Diesel Generator (EOG) Actuation and Load On April 20, 2024, with gas service breaker (GCB) 11-13 open to support transmission system operator (TSO) testing of power line L0104 relays, OCB 1-13 tripped open on differential current resulting in the loss of the Unit 1 system auxiliary transformer (SAT). Bus 141Y (engineered safety feature (ESF) Division 1), which is normally supplied by the Unit 1 SAT, failed to fast transfer to the Unit 1 unit auxiliary transformer (UAT), resulting in the Division 1 EOG to automatically start and load onto the 141Y bus, causing a load shed of the 141Y bus and a momentary loss of power to the 141Y bus. The loss of the Unit 1 SAT also caused the Division 3 EOG to automatically start and load, as designed, onto bus 143 (ESF Division 3), which is normally supplied by the Unit 1 SAT. Bus 142Y (ESF Division 2) fast transferred to the Unit 1 UAT, as expected, resulting in no requirement for the Division 2 EOG to automatically start. The automatic starting of the Division 1 and Division 3 EDGs is considered a valid actuation due to the loss of power to ESF buses. During the fast transfer of ESF Division 2 from the Unit 1 SAT to UAT, the Unit 1 reactor building ventilation system (VR) 'B' supply isolation damper and "A' exhaust isolation damper went shut unexpectedly causing a loss of Unit 1 VR. This resulted in a main steam tunnel high temperature condition which was bypassed per station procedure. The dampers were reopened, and Unit 1 VR was restored. Reactor Protection System (RPS) Unit 1 "A" Half-Scram As a result of the load shed on bus 141Y, power was lost to the Unit 1 "A" (1A) RPS bus, resulting in a "A" RPS half-scram condition and closure of isolation valves in multiple systems. The condition was considered an invalid actuation because it was the result of losing power to the bus and not the result of a valid input signal to the RPS or intentional manual action. All actuations and isolations performed as designed. The loss of the 1A RPS bus resulted in isolations of the reactor water cleanup system, main steam line drains, reactor coolant system sampling, instrument nitrogen system, reactor recirculation hydraulic power units, and containment monitoring system. The loss of the 1A RPS bus also resulted in the loss of power to portions of the average power range monitor, local power range monitor, oscillation power range monitor, and control rod block systems; as well as portions of the radiation monitoring for the main steam lines, reactor building vent, and fuel pool vent. Appropriate actuations and primary containment isolations occurred as designed. After the loss of power to the 1A RPS bus, the applicable Technical Specification (TS) timeclocks and actions were entered. Power was restored to the 1A bus by transferring the bus to the alternate power supply in accordance with plant NRC FORM 366A (04-02-2024) Page_2_ of _s_ NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and lnfonnation Collections Branch (T-6A10M), U.S. Nuclear Regulatory Commission, Washington, DC 2055!>-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of lnfonnation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of infonnation unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-colleclions/nuregs/stafflsr1022/r3D displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER (cid:127) 050 SEQUENTIAL REV YEAR NUMBER NO. LaSalle County Station, Unit 1 (cid:143) 052 00373 2024 - 004 - 01 NARRATIVE procedures. The half-scram and isolations were reset, and the equipment was returned to operable status. All applicable TS timeclocks and actions were exited. Cause EOG Actuation and Load The root cause of OCB 1-13 tripping open was an absence of procedural guidance requiring the switchyard owner to provide the details of their modification testing plan, including work instructions, and the required performance of a quality station review of testing plan / work instructions. Causal factors that were identified with the root cause are the following: 1. Placement of dispatched grounds by the switchyard owner with the presence of induced voltage on power line L0104. 2. Failure of LaSalle County Station personnel to recognize the possibility of induced voltage being present on the out-of-service 345 kV power line L0104 after switching, caused by the in-service 345 kV power line L0103 that runs parallel with power line L0104, flowing to ground via the bus 13-dispatched ground when GCB 11-13 was moved to the closed position. Contributing causes to the event that were identified in the root cause are the following: 1. The TSC switch for ACB 1415 was not closed as expected. 2. Failure to follow the maintenance strategy template recommendation to verify contact resistance or cycle the MOC switch on a regular interval. Troubleshooting determined the cause of the fast transfer failure of bus 141 Y from the Unit 1 SAT to the Unit 1 UAT was increased resistance across MOC 15 and 16 of ACB 1412, and the TSC switch contacts were open on ACB 1415, Unit 1 UAT feed breaker to bus 141Y, even though they were verified to be closed the last time the breaker was racked in during refueling outage L 1R 20 earlier in 2024. RPS Unit 1A Half-Scram The cause of the RPS Unit 1A loss of power and half scram was the momentary loss of power from the 141Y bus due to the load shed caused by the fast transfer failure. The loss of power from the 141 Y bus resulted in a loss of power to the 1A RPS motor-generator set that normally powers the 1A RPS. Reportability and Safety Analysis EOG Actuation and Load The loss of the Unit 1 SAT and actuation of the Division 1 and Division 3 emergency diesel generators was initially reported as an 8-hour notification (ENS 57083) in accordance with 10 CFR 50. 72(b)(3)(iv)(A) for a valid actuation of the emergency AC electrical power systems. This event is also required to be reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that results in the valid actuation of the emergency AC electrical power systems. NRC FORM 366A (04-02-2024) Page_3_ of _s_ NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2,0,2,4,) /1.¥.....~... Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments s i LICENSEE EVENT REPORT (LER) N re u g c a l r e d a in r g b R ur e d g e u n l a e to s r ti y m ate C o to m t m he is s F i O on IA , , Li W bra a r s y h , in a g n t d o n ln , fonn D a C t ion 2 C 0 o 5 l 5 le 5 c - t 0 io 0 n 0 s 1 , B ran o c r h (T b - y 6 A10 em M a ). i l U.S to . \ ... ..... ,r- J CONTINUATION SHEET lnfocollecls.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of lnfonnation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, OC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of infonnation unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D displays a currently valid 0MB control number. 1. FACILITY NAME (cid:127) 2. DOCKET NUMBER 3. LER NUMBER 050 SEQUENTIAL REV YEAR NUMBER NO. LaSalle County Station, Unit 1 (cid:143) 00373 052 2024 - 004 01 NARRATIVE RPS Unit 1A Half-Scram The loss of the Unit 1A RPS bus and associated RPS actuation is considered an invalid actuation because it was not the result of a valid signal and not an intentional manual action. The loss of the RPS bus resulted in general containment isolation signals that actuated containment isolation valves in more than one system or multiple main steam isolation valves while the unit was critical. Therefore, the loss of the RPS bus is reportable in accordance with 10 CFR 50. 73(a)(2)(iv)(A). Safety System Functional Failure Review The system equipment responses do not result in a safety system functional failure (SSFF) as defined in accordance with NEI 99-02, "Regulatory Assessment Performance Indicator Guideline." The EOG and RPS safety systems performed their as-designed safety functions. Corrective Actions Corrective actions taken in response to the conditions were: • Entered the required TS timeclocks and actions and notified the TSO to secure all testing. • Transferred the 1A RPS bus to the alternate power supply, reset the half-scram, and exited applicable TS timeclocks and actions. • Closed OCB 1-13 and reenergized the Unit 1 SAT • Transferred buses 141Y, 142Y, and 143 to the Unit 1 SAT; shutdown the Division 1 and Division 3 EDGs; and exited applicable TS timeclocks and actions. • Transferred the 1A RPS bus back to the normal power supply. • Racked out and then racked in ACB 1415 to close the TSC switch contacts. • Cleaned MOC 15 and 16 on ACB 1412 to decrease the resistance back to acceptable levels. • Develop electrical maintenance procedure to check all 4 kV and 6 kV switchgear breaker contacts to confirm alignment for fast transfer logic. • Update the normal startup procedure to incorporate new electrical maintenance procedure during bus alignment. • Revise the Switchyard Services Agreement procedure to add guidance for the station to perform a quality review for all modification testing instructions when modifications and testing are to be performed in the switchyard. • Update 4 kV and 6 kV breaker inspection and operational test procedures to include preventative maintenance strategies for either verifying resistances or burnishing MOC switch contacts. • Prioritize and expedite the engineering change for the removal of TSC switches. • Remove and send the TSC switch on ACB 1415 for failure analysis. Previous Occurrences There have been no previous occurrences of an EOG actuation in the past 3 years. There have been two occurrences of RPS half-scrams in the past 3 years that were attributed to a loss of power. Unit 1 LER 373-2024-002-00 On March 25, 2024, LaSalle Unit 1 was operating at 100 percent power, when the 1B RPS MG set electric power monitoring assembly (EPMA) output breaker tripped due to an underfrequency condition, which resulted in the loss of the 18 RPS bus. The loss of power to this bus created a half-scram condition and initiated closure of isolation valves in NRG FORM 366A (04-02-2024) Page_4_ of _5_ NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) ,,.,.,..-..., Estimated burden per response to comply with this mandatory colection request 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to indusby. Send comments ;~·) LICENSEE EVENT REPORT (LER) regaiding burden estimate to the FOIA, Library, and lnfonnation Collections Branch (T-6A10M), U.S. Nuclear Regulatory Commission, Washinglon, DC 20555-0001, or by email to \~ ..... / CONTINUATION SHEET lnfoco!ecls.Resoun;e@nrc.gov, and the 0MB reviewer at: 0MB Office of lnfonnation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of infonnation unless the document requesting or requiring the collection http :l/www.nrc.gov/readinq-rm/doc-collections/nuregs/staff/ sr1 022/r3D displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER (cid:127) 050 SEQUENTIAL REV YEAR NUMBER NO. LaSalle County Station, Unit 1 (cid:143) 052 00373 2024 - 004 - 01 NARRATIVE multiple systems. The condition was an invalid actuation because it was not the result of actual plant conditions and not an intentional manual action. The cause of the MG set EPMA output breaker trip was the EPMA trip card for the output breaker being out of range high for the underfrequency setpoint which caused the trip on underfrequency. As a result, the EPMA trip card was replaced, and the system was restored back to its original configuration. Unit 2 LER 374-2021-002-00 On May 31, 2021, LaSalle Unit 2 was operating at 100 percent power, when the 2A RPS motor generator (MG) set output breaker tripped due to an overload condition, which resulted in a loss of 2A RPS bus. Loss of power to this bus created a half-scram and initiated closure of outboard isolation valves in multiple systems. The condition was an invalid actuation because it was not the result of actual plant conditions and not an intentional manual action. The cause of the issue was a degraded voltage adjustment potentiometer (device 1P ) on the 2A RPS MG set, which was causing intermittent resistance readings. The intermittent resistance caused the output voltage of the RPS MG set to fluctuate. As a result, the degraded potentiometer and the voltage regulator were replaced as part of the trouble-shooting efforts, and the system was restored back to its original configuration. Component Failure Data Manufacturer: Westinghouse Electric Company Device: Oil Circuit Breaker, 345 kV Component ID: 0SYOCB1-13, 345 kV Oil Circuit Breaker 1-13 Manufacturer: ITE Circuit Breaker Limited Device: Air Circuit Breaker, 4160 V Component ID: ACB 1412 Bus Feed from SAT 1AP91E (TR 142) Manufacturer: ITE Circuit Breaker Limited Device: Air Circuit Breaker, 4160 V Component ID: ACB 1415 1AP04E / 1AP03E (141Y / 141X) Bus Tie NRC FORM 366A (04-02-2024) Page _L_ of _L_ NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150--0104 EXPIRES: 04/30/2027 (04-02-2024) ............. Estimnd b..-den per response to compi'( will 11~ mandatory collection request 80 ho .... Reportsd lessons !¥1~ LICENSEE EVENT REPORT (LER) lea-nod are inCOIJ)orated i11D the licensing process aid fed bacl< ID industy. Send comments ragning burden estimate ID the FO/A, Librmy, and Information Collections Btaich (T-8 A10M), U. S. Nuclea- Regulatory \. ..... I Commissioo, Washington, DC 20555-0001, or by email to lnfocolleets.Resource@rve.gov, aid Ile OM:I revie- (See Page 2 for required number of digits/characters for each block) at OMS 01llee of Information and Regulaay Affais, (3150-0104), Attn: Desi< Offie" to, the Nuelea-Regulatory (See NUREG-1022, R.3 for instruction and guidance for completing this fom, Commissioo, 725 171h Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person Is httI;r/lwww .nrc.gov/reading-rm/doc-collections/n uregs/staff/ sr1 022/r3D not requred ID respond ID, a coleetion of information unless Ile document requesting or requring the collection displays a e11Tenli'( vale! 0MB contol num~. 1. Facility Name ~ 050 2. Docket Number 3.Page LaSalle County Station, Unit 2 (cid:143) 00374 1 OF 3 052 4. Title Air Circuit Breaker (ACB) Mechanically Operated Contacts (MOC) switch failed to actuate | 08-22-2024 | On April 20, 2024, with LaSalle Unit 1 operating at 100 percent power and gas circuit breaker (GCB) 11-13 open to support transmission system operator testing of power line L0104 relays, oil circuit breaker (OCB) 1-13 tripped open on differential current resulting in the loss of the Unit 1 system auxiliary transformer (SAT). Bus 141 Y (Division 1) , normally supplied by the I Unit 1 SAT, failed to fast transfer to the Unit 1 unit auxiliary transformer (UAT), resulting in the Division 1 emergency diesel generator (EDG) to automatically start and load onto the 141Y bus, causing a load shed of the 141Y bus and momentary loss of power to the 141Y bus. The loss of the Unit 1 SAT also caused the Division 3 EDG to automatically start and load, as designed, onto bus 143 (Division 3). The load shed on bus 141Y caused power to be lost to the Unit 1 "A" (1A) reactor protection system (RPS) bus, resulting in a "A" RPS half-scram condition and closure of isolation valves in multiple systems. All actuations and isolations performed as designed. During the fast transfer of Division 2 from the Unit 1 SAT to UAT, the Unit 1 reactor building ventilation system (VR) 'B' supply isolation damper and "A' exhaust isolation damper went shut unexpectedly causing a loss of Unit 1 VR. These events are reportable in accordance with 10 CFR 50.7 3(a)(2)(iv)(A). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) r ......, Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments f:I.J.i LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to i~..... / CONTINUATION SHEET lnfocollec1S.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 72517th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection http://www. nrc.g o v/readinq-rm/doc-col leclions/nuregs/staff/sr1 022/r3Q displays a currently valid 0MB control number. 1. FACILITY NAME (cid:127) 2. DOCKET NUMBER 3. LER NUMBER 050 SEQUENTIAL REV YEAR NUMBER NO. LaSalle County Station, Unit 1 (cid:143) 00373 052 2024 - 004 01 | Plant and System Identification LaSalle Country Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the alternating current (AC) power system. The affected component is 345 kV oil circuit breaker (OCB) 1-13, the mechanism operated contacts (MOC) 15 and 16 of air circuit breaker (ACB) 1412, and the TSC switch contacts on ACB 1415. Condition Prior to Event Unit(s): 1 Date: April 20, 2024 Time: 07:04 CDT Reactor Mode( s): 1 Mode(s) Name: Power Operation Power Level: 100 percent Description Emergency Diesel Generator (EOG) Actuation and Load On April 20, 2024, with gas service breaker (GCB) 11-13 open to support transmission system operator (TSO) testing of power line L0104 relays, OCB 1-13 tripped open on differential current resulting in the loss of the Unit 1 system auxiliary transformer (SAT). Bus 141Y (engineered safety feature (ESF) Division 1), which is normally supplied by the Unit 1 SAT, failed to fast transfer to the Unit 1 unit auxiliary transformer (UAT), resulting in the Division 1 EOG to automatically start and load onto the 141Y bus, causing a load shed of the 141Y bus and a momentary loss of power to the 141Y bus. The loss of the Unit 1 SAT also caused the Division 3 EOG to automatically start and load, as designed, onto bus 143 (ESF Division 3), which is normally supplied by the Unit 1 SAT. Bus 142Y (ESF Division 2) fast transferred to the Unit 1 UAT, as expected, resulting in no requirement for the Division 2 EOG to automatically start. The automatic starting of the Division 1 and Division 3 EDGs is considered a valid actuation due to the loss of power to ESF buses. During the fast transfer of ESF Division 2 from the Unit 1 SAT to UAT, the Unit 1 reactor building ventilation system (VR) 'B' supply isolation damper and "A' exhaust isolation damper went shut unexpectedly causing a loss of Unit 1 VR. This resulted in a main steam tunnel high temperature condition which was bypassed per station procedure. The dampers were reopened, and Unit 1 VR was restored. Reactor Protection System (RPS) Unit 1 "A" Half-Scram As a result of the load shed on bus 141Y, power was lost to the Unit 1 "A" (1A) RPS bus, resulting in a "A" RPS half-scram condition and closure of isolation valves in multiple systems. The condition was considered an invalid actuation because it was the result of losing power to the bus and not the result of a valid input signal to the RPS or intentional manual action. All actuations and isolations performed as designed. The loss of the 1A RPS bus resulted in isolations of the reactor water cleanup system, main steam line drains, reactor coolant system sampling, instrument nitrogen system, reactor recirculation hydraulic power units, and containment monitoring system. The loss of the 1A RPS bus also resulted in the loss of power to portions of the average power range monitor, local power range monitor, oscillation power range monitor, and control rod block systems; as well as portions of the radiation monitoring for the main steam lines, reactor building vent, and fuel pool vent. Appropriate actuations and primary containment isolations occurred as designed. After the loss of power to the 1A RPS bus, the applicable Technical Specification (TS) timeclocks and actions were entered. Power was restored to the 1A bus by transferring the bus to the alternate power supply in accordance with plant | ML24235A178 | 0 | good
Grand Gulf Nuclear Station | Unit 1 | Feedwater Inlet Check Valve Incorrectly Determined Operable | 04-30-2027 | On April 2, 2022, at 0301 CT, while the plant was in MODE 4 with all control rods inserted during a refuel outage, Grand Gulf Nuclear Station identified a failed post work leakage rate test of Feedwater Inlet Check Valve, 1 B21 F032B. An operability evaluation of the valve was performed, and the valve was inappropriately determined to be operable. The valve was returned to service, and the plant returned to MODE 1 at the end of the refuel outage. On June 27, 2024, NRC inspectors identified a Green finding and associated Non-Cited Violation of Technical Specification 3.6.1.3, "Primary Containment Isolation Valves" (PCIV) for failure to ensure each PCIV was operable. Valve 1 B21 F032B failed the leakage rate test due to degradation and wear of the valve seat. The operator failed to properly evaluate the operability due to a lack of understanding of the Primary Containment Leakage Rate Testing (Appendix J) program requirements. There was no impact on the health and safety of the public or reactor safety. The feedwater isolation shutoff valve 1B 21 F065B would have maintained leakage rates for the containment penetration; therefore, there was no significant risk to containment integrity. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 0 4 / 3 0 / 2 0 2 7 (04-02-2,0.2.4.). ,;\ Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) !~, regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S \~/ Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail lo ···-· CONTINUATION SHEET lnlocollects Resource@nrc gov, and the 0MB reviewer al: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer lor the Nuclear Regulatory Commission, 725 17th Street NW. (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRG may not conduct or sponsor, and a person is not required to respond https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r;m to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER 181 050 YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 NUMBER NO. 416 0 052 2024 003 00 | Plant Conditions: At the time of the event, Grand Gulf Nuclear Station was in MODE 4 (Cold Shutdown) with all control rods inserted at zero percent reactor power. The station was performing a post-work leakage rate test on Feedwater Inlet Check Valve 1821F032B. Description of Event: On April 2, 2022, during the performance of the post work leakage rate test of the Feedwater Inlet Check Valve 1821 F032B, a failing leakage rate of 7650 milliliters per minute was observed. A Condition Report was issued per procedure, and an operability evaluation was performed using the past operability, the technical specification surveillance requirement, and the Primary Containment Leakage Rate Testing (Appendix J) program requirements. An incorrect assumption about the Appendix J requirements was made, and it was determined that the identified leakage was within the allowable leakage rate based on the surveillance requirements. The operability evaluation incorrectly determined that Feedwater Inlet Check Valve 1821 F032B, was operable, and the valve remained in service for the 24- month fuel cycle. On June 27, 2024, as part of the Biennial Problem Identification and Resolution Inspection Report 05000416/2024010, the NRC inspectors identified a Green finding and associated Non-Cited Violation of Technical Specification (TS) 3.6.1.3, "Primary Containment Isolation Valves" (PCIV) for failure to ensure each PCIV was operable following a failed leakage rate test of 1821 F032B during a refueling outage. A violation of TS 3.0.4 was also identified for making a mode change without meeting the requirements to do so as a result of not meeting TS 3.6.1.3. Reportability: This report is made in accordance with 10 CFR 50.73(a)(2)(i)(B) for an operation of condition which was prohibited by the plant's Technical Specifications. TS LCO 3.6.1.3 requires each PCIV to be OPERABLE. Due to incorrect operability evaluation, Required Actions C and E were not taken. Cause(s): The direct cause of the event was degradation and wear of the valve's seat which resulted in the failed leakage rate test. An additional cause of insufficient knowledge of the Appendix J program requirements by the Senior Reactor Operators (SROs) was also identified as the cause of the incorrectly performed operability evaluation. Corrective Actions: Completed Actions: Repairs to the valve seat were made during 2024 refuel outage. Post-work leak rate testing was completed satisfactorily and indicated a leak rate of zero millimeters per minute. Planned Actions: Update Operability Training for SROs with a focus on Code testing requirements. Safety Significance: There was no impact on the health and safety of the public or reactor safety. The feedwater isolation shutoff valve 1821 F065B would have maintained leakage rates for the containment penetration; therefore, there was no significant risk to containment integrity. Previous Similar Events: LEA 2023-001-01 Valve Closure Test Failure Resulting in Condition Prohibited by Technical Specification LER 2021-001-01 Primary Containment Outer Airlock Door Inoperable Due To Unacceptable Leak Rate NRG FORM 366A (04-02-2024) Page 2 of 2 | ML24239A788 | 0 | good
i | Unknown Unit | Manual Reactor Scram Due to Degraded Main Condenser Vacuum | 08-26-2024 | due to degrading Main Condenser vacuum caused by a failed turbine bearing waste water and oil (slop) drain. The event was reported by Event Notification 56846 in accordance with 10 CFR 50. 72(b )(2)(iv)(B) and 10 CFR 50.7 2(b) (3)(iv)(A). This event is also reportable in accordance with 10 CFR 50. 73(a)(2)(iv)(A) as an event that resulted in a manual actuation of the Reactor Protection System (including a reactor scram). Failure of the slop drain was caused by vibration/cyclic fatigue-induced failure of the socket weld on the 1.5" pipe to the 3" x 1.5" pipe reducer inside the Main Condenser. Key corrective action included plugging and welding the failed slop drain and reducing the length of the resulting pipe stub. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www. n re.gov /reading-rm/doc-collection sin u regs/staff/ sr1 022/r3/} displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 r:YE:A:RJ SEQUENTIAL REV Susquehanna Steam Electric Station Unit 1 I 00387 I ~-I NUMBER 1- NO 0 . □ 052 004 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, approximately 100% Rated Thermal Power (RTP) Unit 2 -Mode 1, approximately 100% RTP Vacuum rapidly degraded on the Susquehanna Steam Electric Station (SSES) Unit 1 Main Condenser, which resulted in the need for a manual reactor scram. EVENT DESCRIPTION On November 10, 2023, SSES Unit 1 was manually scrammed due to degraded Main Condenser [EIIS System Code/ Component Code: SG/COND] vacuum caused by a failed turbine bearing waste water and oil (slop) drain [EIIS System Code/Component Code: TF/DRN]. The following is a timeline of significant events associated with the scram: November 10, 2023, at approximately 01 :06 - Unit 1 Main Condenser vacuum was rapidly degrading along with indication of high offgas flow. A Recirculation Limiter 2 runback was inserted to lower reactor power. Main Condenser vacuum continued to degrade following the reduction in reactor power to approximately 70%. November 10, 2023, at approximately 01: 18 -A manual scram was inserted when Main Condenser vacuum reached 6 inches of mercury absolute. Plant response to the scram was per design, Reactor Protection System (RPS) [EIIS System Code: JC] channels all tripped and maintained the scram signal for the required 10 second period. Reactor Water Level lowered to -25" following the scram. Reactor Water Level 3 (+13 inch) containment isolation system signals were received and went to completion. The feedwater system [EIIS System Code: SJ] remained in service as the primary Reactor Pressure Vessel (EIIS System Code/Component Code: AC/RPV] water level control system. There were no Emergency Diesel Generator [EIIS System Code/Component Code: EK/DG] starts or Safety Relief Valve [EIIS System Code/ Component Code: SB/RV] actuations during the event. The event was reported by Event Notification 56846 in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3) (iv)(A). This event is also reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a manual actuation of the RPS (including a reactor scram). CAUSE OF EVENT Failure of the slop drain was caused by vibration/cyclic fatigue-induced failure of the socket weld on the 1.5" pipe to the 3" x 1.5" pipe reducer inside the Main Condenser. This failure was due to the original slop drain capping and piping removal modification in 2002 not being performed in accordance with the associated engineering change. In addition to the slop drain piping, pipe supports that were intended to support the remaining piping were erroneously removed. This allowed a remaining vertically suspended 1.5" diameter pipe stub of approximately 40 inches to vibrate, which eventually caused the weld failure. ANALYSIS/SAFETY SIGNIFICANCE The actual consequences from the drain leaking air into the Unit 1 Main Condenser were degraded Unit 1 Main Condenser vacuum, a forced down power, and subsequent manual scram. Without prompt operator action, an automatic scram would have been initiated. Additionally, High Pressure Coolant Injection (EIIS System Code: BJ) System and Reactor Core Isolation Cooling (EIIS System Code: BN) System could have initiated which would require initiating support systems as well as adding additional heat to the suppression pool. This would have necessitated using the Residual Heat Removal (EIIS System Code: BJ) System in Suppression Pool Cooling mode to transfer the suppression pool heat to the spray pond. NRG FORM 366A (04-02-2024) Page 2 of 3 | ML24239A847 | 0 | good
Byron Station | Unit 1 | Both Trains of Control Room Ventilation Temperature Control System Inoperable | 09-05-2024 | At 1440 CDT on July 7, 2024, the OA and OB trains of the Control Room Ventilation (VC) Temperature Control System were simultaneously inoperable resulting in a condition that could have prevented the fulfillment of a safety function and was reported as an eight-hour, non-emergency notification per 10 CFR 50. 72(b)(3)(v)(D) under ENS 57211 to the NRC. OB Control Room Ventilation (VC) Temperature Control system was restored to operable status at 1634 CDT on 7/7/2024. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA. Library. and Information Collections Branch (T-6 A1 O M). U. S. Nuclear Regulatory Commission. Washington. DC 20555-0001. or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs. (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW. Washington. DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER (cid:127) 050 SEQUENTIAL REV YEAR NUMBER NO. Byron Station, Unit 1 05000454 (cid:143) 052 2024 - 001 00 | A. Plant Operating Conditions Before the Event: Event Date: July 7, 2024 Unit 1 - Mode 1 - Power Operations, Reactor Power 100 percent Unit 2 - Mode 1 - Power Operations, Reactor Power 100 percent Reactor Coolant System (RCS)[AB]: Normal Operating Temperature and Pressure No structures, systems, or components were inoperable at the start of this event that contributed to the event. B. Description of the Event: At 1310 CDT on 7/ 7 /24 the auxiliary building equipment operator (EO) noted the DA Control Room Ventilation (VC) Temperature Control System chiller oil level had dropped from a previous rounds reading of 37 percent to 15 percent. The EO notified the main control room and the operations field supervisor was dispatched to review the condition. The shift manager notified maintenance to request support to add oil to the DA VC chiller. At 1355 CDT, a briefing was held in the control room to perform the crosstie of the service building (VS) chilled water system to the 0A VC chilled water system per procedure BOP VC-20. At 1404 CDT, while the briefing was in progress, the auxiliary building EO notified the main control room that the oil level in the DA VC chiller had further decreased to 0 percent in the sight glass, but that oil was still visible with foam present. Following the briefing, two equipment operators obtained keys to unlock the individual valves needed to perform the crosstie. At approximately 1435 CDT, the operations field supervisor notified the main control room that the oil level in the DA VC chilled water system was no longer visible in the sight glass. At 1440 the DA VC chiller was secured and declared inoperable by Operations and the equipment operators began to perform the procedure steps to establish the VC to VS chilled water crosstie. While attempting to crosstie 0A VC train to the service building (VS) chilled water system, the equipment operators incorrectly operated valves on the OB VC chiller train. This caused the OB VC chiller train to become inoperable. With both trains of control room chillers inoperable, Unit 1 and Unit 2 entered TS 3.7.11 Condition D. Operations personnel returned to the field at 16:34 CDT on 7/7/24 and restored the valve lineup for the OB VC chiller returning the OB VC chiller to operable and exiting Condition D of TS 3.7.11. This event was determined to be a loss of safety function for the control room chilled water system and an 8-hour ENS (57211) was made to the NRC per 10 CFR 50.72(b)(3)(v)(D) at 22:12 CDT on 7/7/24. C. Causes of Event: The root cause of this event was determined to be an inadequate brief performed by the Operations SRO with the Reactor Operator and Equipment Operators. During the brief, the SRO supervisor did not clearly establish that each operator understood their role in the crosstie activity or utilize station prints to clearly establish the intended plant manipulations. As a result, the equipment operators manipulated incorrect valves while establishing the crosstie which resulted in both trains of VC Temperature Control System being declared inoperable. Contributing causes to the event were a lack of system knowledge and experience combined with less than adequate procedural guidance. The equipment operators performing the crosstie did not fully understand the flow path that needed to be established. Additionally, training provided in 2018 when the VS to VC crosstie | ML24249A074 | 0 | good
Peach Bottom Atomic Power Station | Unit 2 | Automatic Reactor Scram Following Main Turbine Trip due to Degraded Condenser Vacuum | 09-05-2024 | While conducting power ascension following a maintenance outage, Peach Bottom Unit 2 began experiencing increasing condensate pump discharge chlorides because of a condenser tube leak. A condenser water box was isolated to facilitate repairs, but due to high river temperatures combined with elevated offgas inleakage, the water box isolation resulted in degrading condenser vacuum. Attempts to restore vacuum were unsuccessful and ultimately required a trip of the main turbine. Because the Reactor Protection System (RPS) input for Turbine Stop Valve (TSV) and Turbine Control Valve fast (TCV) closure was armed, the turbine valve closure generated a scram signal. Group II and III Primary Containment Isolation Valves isolated because reactor water level reached the isolation setpoint. Reactor water level was maintained with feedwater and pressure was maintained with bypass valves. The scram occurred without complication and all systems responded as expected. Unit 3 was not impacted by this event. This event is reportable under 10CFR50.73(a)(2)(iv)(A) due to manual or automatic isolation of systems listed in 10CFR50.73(a)(2)(iv)(B) including RPS and containment isolation signals. An ENS notification was made within 4 hours of the event, reference ENS 57221. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 SEQUENTIAL REV YEAR NUMBER NO. Peach Bottom Atomic Power Station, Unit 2 00277  052 2024 - 003 - 00 | Plant Operating Conditions Before the Event Prior to the event, on July 10, 2024, Peach Bottom Unit 2 was in Mode 1 conducting power ascension following a maintenance outage. It was identified that condensate pump discharge chloride conductivity was increasing, indicative of a condenser (EIIS: SG) tube leak. To facilitate investigation and repair of leaking tubes, a condenser waterbox was isolated with the reactor at approximately 62% power. Waterbox isolation combined with seasonally high river temperatures and elevated offgas (EIIS: WF) inleakage from a degraded valve in the offgas system resulted in degrading condenser vacuum. Although the waterbox was returned to service, condenser vacuum continued to degrade. The operating crew reduced power per station procedures, but condenser vacuum reached the threshold requiring a manual trip of the main turbine (EIIS: TA). Event Description The turbine was manually tripped on July 10, 2024 at 07:28 with the reactor at 25.6% power, which is within the physical capability of bypass valves (EIIS: SO). This is below the power level at which the Reactor Protection System (RPS) input for Turbine Stop Valve (TSV) and Turbine Control Valve (TCV) fast closure (EIIS: TA) is required to be armed per Technical Specifications, but due to conservative instrument setpoints, the input was still armed and the closure of the valves generated a scram signal. The scram occurred without complication. The Reactor Pressure Vessel (RPV) low level setpoint was reached, resulting in isolation of Group II and III Primary Containment Isolation System (PCIS) (EIIS: JM) valves as expected. Water level in the RPV was restored and maintained with Feedwater (EIIS: SJ) and pressure was maintained with bypass valves. This event is reportable under 10CFR50.73(a)(2)(iv)(A) due to manual or automatic isolation of systems listed in 10CFR50.73(a)(2)(iv)(B) including RPS and containment isolation signals. An ENS notification was made within 4 hours of the event, reference ENS 57221. Safety Consequences The reactor Scram occurred as designed and resulted in no safety consequences. All safety systems responded as expected. Use of emergency core cooling systems for level and pressure control was not required. Unit 3 was not impacted by this event. Cause and Corrective Actions The cause of the scram was RPS input from TSV and TCV fast closure due to a manual trip of the Main turbine. Procedures directed tripping the turbine if steam flow was within bypass valve capability but did not warn that the RPS logic may be armed. Actions have been taken to revise procedures from tripping the turbine “if within bypass valve capability” to “if it is known that the Main TCV/TSV closure is bypassed on A or B RPS”. Additionally, the cause of the degraded condenser vacuum condition was investigated. The root cause of this condition is that the station did not recognize and evaluate the cumulative effect of increased offgas air inleakage and isolation of a condenser waterbox with high river temperatures, culminating in a rapid lowering of main condenser vacuum. As a contributor, station models were unable to accurately predict the impact of elevated offgas inleakage on condenser performance. The corrective actions focus on enhancing the station governance for isolating a waterbox. | ML24249A109 | 0 | good
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Reactor Protection System Electric Power Monitoring System Trip Caused Primary Containment Isolation | 09-04-2024 | On July 8, 2024, at 1927, James A. FitzPatrick Nuclear Power Plant (JAF) received annunciators and indication of a half-scram on the “B” side Reactor Protection System (RPS). The cause was determined to be an overvoltage condition that tripped the Electrical Protection Assembly (EPA) for the “B” RPS Motor Generator (MG) Set. This event caused invalid primary containment isolation signals in multiple systems, reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). The investigation into the cause of the event is ongoing. A supplement to this report will be submitted when the investigation is complete. NRC FORM 366 (04-02-2024) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 LICENSEE EVENT REPORT (LER) hours. Reported lessons learned are incorporated into the licensing process and fed CONTINUATION SHEET back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory (See NUREG-1022, R.3 for instruction and guidance for completing this form Commission, 725 17th Street NW, Washington, DC 20503; email: http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 YEAR SEQUENTIAL REV NUMBER NO. James A. FitzPatrick Nuclear Power Plant 05000333  052 2024 – 002 – 00 | Background Reactor Protection System (RPS) [EIIS: JE] Electric Power Monitoring System is provided to isolate the RPS bus from the motor generator (MG) set or an alternate power supply in the event of overvoltage, undervoltage, or underfrequency. This system protects the loads connected to the RPS bus against unacceptable voltage and frequency conditions and forms an important part of the primary success path of the essential safety circuits. Some of the essential equipment powered from the RPS buses includes the RPS logic, scram pilot valve solenoids, and various valve isolation logic. RPS electric power monitoring assembly will detect any abnormal high or low voltage or low frequency condition in the outputs of the two MG sets or the alternate power supply and will de-energize its respective RPS bus, thereby causing all safety functions normally powered by this bus to de-energize. (Safety functions powered by the RPS buses deenergize to actuate.) Two redundant Class IE circuit breakers are connected in series between each RPS bus and its MG set, and between each RPS bus and its alternate power supply. Each of these circuit breakers has an associated independent set of Class IE overvoltage, undervoltage, and under frequency sensing logic. Together, a circuit breaker and its sensing logic constitute an electric power monitoring assembly. If the output of the inservice MG set or alternate power supply exceeds predetermined limits of overvoltage, undervoltage, or underfrequency, a trip coil driven by this logic circuitry opens the circuit breaker, which removes the associated power supply from service. Event Description On July 8, 2024, at 1927 when James A. FitzPatrick Nuclear Power Plant (JAF) at 100% power, annunciators were received with indication of a half-scram on “B” side RPS. AOP-60, Loss of RPS Bus B Power, was entered and the cause was determined to be a trip of the “B” RPS MG set due to an overvoltage condition. The direct cause of the output breaker tripping was due to an Electric Power Monitoring System overvoltage trip on 71EPA-RPS1B1G, Electrical Protection Assembly (EPA). The condition was corrected when the RPS Bus was placed on the alternate power supply. The event resulted in invalid system actuations of "B" side half scram and Primary Containment Isolation System (PCIS) [JM] isolations. The following systems isolated as a result of the loss of “B” RPS bus: Reactor Water Cleanup [CE], Reactor Building ventilation [NG], “B” Containment Atmosphere Dilution [BB], Torus Vent and Purge, Drywell Equipment and Floor Drain Sumps [WK], “B” Drywell Containment Atmospheric Monitors [IP], Recirculation System Sample Line, and Main Steam Line Drains [SB]. “B” Standby Gas Treatment System [BH] started as designed. These system actuations were not initiated by signals in response to actual plant conditions or parameters satisfying the requirements for initiation of the system. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). Page 2 of 3 | ML24249A254 | 0 | good
Calvert Cliffs Nuclear Power Plant | Unit 1 | 1A Diesel Generator Inoperable Due to Potential Transformer Failure | 04-30-2027 | On July 2, 2024, the Main Control Room received alarm “4KV BUS U/V, 480V BUS U/V, 125V DC,” Window AA06. Initial investigation using the Alarm Response Manual (ARM) did not identify any abnormal degraded conditions and the 1A Emergency Diesel Generator (EDG) was immediately determined to be operable. Follow-up investigation and troubleshooting identified a failed potential transformer associated with the 17 4KV bus protective relays, which would result in the 1A EDG output breaker tripping open on overcurrent during load sequencing in an emergency scenario. The 1A EDG was promptly declared inoperable on July 8, 2024, and the station entered Technical Specification Condition 3.8.1.B for Unit 1 and 3.8.1.E for Unit 2. After entering the Technical Specification Conditions the site took all requisite Required Actions. The potential transformer was replaced on July 10, 2024, and following a successful surveillance run, the 1A EDG was declared operable on July 11, 2024. Prior to entering the Technical Specification Conditions and taking the associated requisite Required Actions, in the period between July 2, 2024, and July 8, 2024, the station exceeded the completion time for Technical Specification LCO 3.8.1 for Unit 1 and 3.8.1 for Unit 2; therefore, this event is reportable under 10CFR50.73(a)(2)(i)(B) as an operation or condition which was prohibited by the plant's Technical Specifications. (See Page 2 for required number of digits/characters for each block) (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION (04-02-2024) LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME  050  052 2. DOCKET NUMBER 3. LER NUMBER Calvert Cliffs Nuclear Power Plant, Unit 1 05000317 YEAR 2024 - SEQUENTIAL NUMBER 003 - REV NO. 00 | Not Found | ML24250A179 | 1 | ok
hope creek generating station | Unknown Unit | Not Found | 09-05-2024 | On May 3, 2024, during a refueling outage, Hope Creek Generating Station (HCGS) performed Primary Containment Integrated Leak Rate Testing (ILRT) Type A test as required by Technical Specification 4.6.1.2. The as-found test was not completed successfully because the stabilization criteria was not met, and the test was invalidated. The as-left test was completed successfully prior to plant start-up. This licensee event report (LER) supplement provides the results of a Root Cause Evaluation (RCE). The Direct Cause was inadequate bolt seating torque that led to loss of O-ring seal compression. The Root Cause was identified as inadequate procedural guidance for validating and measuring flange to drywell airlock surface gap. This event was reported to the NRC as an eight-hour, non-emergency per 10 CFR 50.72(b)(3)(ii)(A) in Event Notification number 57103 on May 3, 2024. Subsequently, LER 2024-001-00 was submitted on July 2, 2024, reporting the event per 10 CFR 50.73(a)(2)(ii)(A). This LER supplement also identifies additional reporting criterion, 10 CFR 50.73(a)(2)(v)(C). Tammy Morin (856)-339-2286 ~./;(,-,>" ~£<111,.,,.0._ ! ~ ~ : ~ $ ~+-? ,..,.11•• ._o' 00 □ □ □ I □ [{] □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ [{] □ □ □ □ □ □ □ □ □ □ □ [{] □ NRC FORM 366A (04-02-2024) U.S. NUCLEAR REGULATORY COMMISSION LICENSEE EVENT REPORT (LER) CONTINUATION SHEET APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) | Not Found | ML24253A265 | 2 | ok
Clinton Power Station 00461 1 OF 3 | Unknown Unit | Reactor Core Isolation Cooling System Inoperable Prior to Mode Change | 09-24-2024 | On October 10, 2023, at 23:02 CST, the Reactor Core Isolation Cooling (RCIC) system tripped during performance of Surveillance Requirement (SR) 3.5.3.3. This SR is performed when RCIC steam supply pressure is at the higher operating ranges of the system to verify that the RCIC pump can develop the required flow rate against a system head corresponding to reactor pressure. The system was restored to operable on October 16, 2023, at 02:51 CST following replacement and calibration of the Electric Governor-Remote (EG-R). Engineering personnel suspected that the RCIC system trip was due to a faulty EG-R; however, subsequent failure analysis identified no significant issues with the EG-R. On December 19, 2023, Engineering personnel determined that work performed on August 28, 2023 affected functionality of the EG-R and caused RCIC to be inoperable per Technical Specifications (TS) 3.5.3, "RCIC System." This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS 3.0.4. Specifically, on October 9, 2023, at 05: 14 CST, during unit startup following a refueling outage, the Applicability for TS 3.5.3 was entered (i.e., Mode 2 with reactor steam dome pressure greater than 150 psig) with the RCIC system inoperable. In addition, the unit was taken to Mode 1 on October 10, 2023. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMIS APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection il tto ://wwv1. n re. qov.1r e 81j ina-rm/d oc-collecti ons/nureosist a ffi s r 1 022/ r3/) displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 SEQUENTIAL REV YEAR NUMBER NO. Clinton Power Station 00461 □ 052 2023 - 002 01 | CONDITION PRIOR TO THE EVENT Unit: 1 Event Date: December 19, 2023 Event Time: 0800 CST Mode: 1 Mode Name: Power Operation Reactor Power: 100 EVENT DESCRIPTION On October 8, 2023, Operations commenced reactor startup following a refueling outage. On October 10, 2023, at 23:02 CST, the Reactor Core Isolation Cooling (RCIC) system tripped on low suction pressure during performance of Surveillance Requirement (SR) 3.5.3.3 and the RCIC system was declared inoperable. This SR is performed when RCIC steam supply pressure is at the higher operating ranges of the system to verify that the RCIC pump can develop the required flow rate against a system head corresponding to reactor pressure. Troubleshooting activities commenced to determine the cause of the RCIC system trip. As part of the troubleshooting activities, the RCIC Electric Governor - Remote (EG-R) was replaced and calibrated. Following replacement of the EG-R, SR 3.5.3.3 was re performed satisfactorily and the RCIC system was declared operable at 02:51 CST on October 16, 2023. Based on the successful re-performance of SR 3.5.3.3 following replacement of the EG-R, Engineering personnel suspected that the RCIC system trip on low suction pressure was due to a faulty EG-R. The suspect EG-R was sent offsite for failure analysis. Results from the failure analysis were documented in a failure analysis report that was issued on November 17, 2023. The report stated that the EG-R showed no signs of degradation and that the sharp, rapid changes in the EG-R output that were observed on October 10, 2023, could not be replicated. Efforts continued to determine the cause of the RCIC system low suction pressure trip. On December 19, 2023, a review of Plant Process Computer data revealed an anomaly to the Electric Governor - Magnetic Pickup (EG-M) output that occurred on August 28, 2023. Further investigation determined that on August 28, 2023, with Unit 1 in Mode 1 at 100% power, work associated with a plant modification on the transient test system disturbed electrical connections for the EG-M. Transient Test is a high-speed data acquisition system which monitors and records analog and digital signals from various plant systems. The EG-M is the flow control system component that transmits an electrical signal to the EG-R proportional to the error signal developed between turbine speed demand and actual turbine speed. When the electrical connections were disturbed, EG-M output fell to 0% scale, indicating a loss of functionality of that component. This was unrecognized by station personnel at the time of occurrence. Further investigation has also found that between September 11, 2023 and October 8, 2023, through various maintenance activities performed on the RCIC system, there is a potential for air to have been entrained in the lubricating oil system. Air entrainment in the lubricating oil control subsystem can cause governor speed and ramp control issues. On December 19, 2023, at approximately 08:00 CST, it was determined that the work performed on August 28, 2023, affected functionality of the EG-M and potentially caused the RCIC system to be inoperable per Technical Specifications Section 3.5.3, "RCIC System." Condition A of TS 3.5.3 applies when the RCIC system is inoperable, with a Required Action to restore the RCIC system to operable status within 14 days. The Completion Time for this Required Action was not exceeded because the Applicability for TS 3.5.3 was exited prior to the expiration of the 14-day Completion Time to support the unit shutdown for a planned refueling outage. However, this event is reportable in accordance with 1 O CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS 3.0.4. Specifically, on October 9, 2023, at 05: 14 CST, during unit startup following the refueling outage, the Applicability for TS 3.5.3 was entered (i.e., Mode 2 with reactor steam dome pressure greater than 150 psig) with TS 3.5.3 not met because the RCIC system was inoperable. In addition, the unit was taken to Mode 1 on October 10, 2023. | ML24270A035 | 0 | good
Prairie Island Nuclear Generating Plant | Unit 1 | Auxiliary Building Special Ventilation System Inoperable during movement of irradiated fuel assemblies. | 09-16-2024 | On May 02, 2024, the Prairie Island Nuclear Generating Plant (PINGP) Units 1 and 2 were operating at 100 percent power while performing fuel handling operations. For a 33-minute period between 12:52 and 13:25, radiation monitors 1R-37 and 2R-30 were both out of service while movement of irradiated fuel assemblies was occurring. On July 11, 2024, while completing a review of the design and licensing basis of radiation monitors 1[2]R-37, 1[2]R-30, it was determined that these monitors are required for Auxiliary Building Special Ventilation System (ABSVS) operability during movement of irradiated fuel assemblies per Technical Specification (TS) 3.7.12. Changes to fuel handling procedures have been initiated. TS Bases for the ABSVS were further clarified and communicated to the operating crews. This will ensure compliance with TS going forward when irradiated fuel is being moved. This event is reportable under 10 CFR 50.73(a)(2)(i)(B) for an Operation or Condition Prohibited by Technical Specifications. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 YEAR SEQUENTIAL REV NUMBER NO. Prairie Island Nuclear Generating Plant, Unit 1 -282 2024 052 - 001 - 01 | Plant Operating Conditions Prior to the Event: Unit 1 – Mode 1, 100 percent Power. Unit 2 – Mode 1, 100 percent Power. EVENT DESCRIPTION On May 02, 2024, the Prairie Island Nuclear Generating Plant (PINGP) was performing fuel handling operations in the Spent Fuel Pool area in support of a Cask loading campaign. For a 33-minute period between 12:52 and 13:25, Radiation Monitors [IL] 1R-37 (Unit 1, Train A) and 2R-30 (Unit 2, Train B) were both out of service while movement of irradiated fuel assemblies was occurring. This impacted the Auxiliary Building Special Ventilation System [VF] (ABSVS) and caused both Train A and Train B of the ABSVS to be inoperable during the movement of irradiated fuel assemblies. The implications of this condition were not known at the time. Radiation monitors 1[2]R-37, 1[2]R-30 are vent gas monitors that monitor for potential radiological releases out of the Auxiliary Building Normal Ventilation (ABNV) exhaust stacks. One of the safety functions of these monitors is to send an auto-start signal to the ABSVS upon detecting high radiation. The Unit 1 ABNV exhaust stack is monitored by 1R-37 (Train A) and 1R-30 (Train B) while the Unit 2 ABNV stack is monitored by 2R-37 (Train A) and 2R-30 (Train B). The ABSVS is a single system that serves both Unit 1 and Unit 2. The system consists of two redundant trains: Train A and Train B. Actuation of either train of the ABSVS will isolate the ABNV exhaust stacks on both Units. The high radiation signal from 1[2]R-37 and 1[2]R-30 is the credited ABSVS actuation signal during a Fuel Handling Accident (FHA) event. With 1R-37 out of service (OOS), the A Train ABSVS would not receive this auto-start signal from a release through the Unit 1 ABNV exhaust stack thus making Train A inoperable during the movement of irradiated fuel assemblies. With 2R-30 OOS, the B train ABSVS would not receive this auto-start signal from a release through the Unit 2 ABNV exhaust stack thus making Train B inoperable during the movement of irradiated fuel assemblies. Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.12 Auxiliary Building Special Ventilation System (ABSVS) requires "Two ABSVS trains shall be OPERABLE" and is applicable in MODES 1, 2, 3 and 4 and "During movement of irradiated fuel assemblies”. The radiation monitors only impact the operability of an ABSVS train during movement of irradiated fuel assemblies. There are no conditions in TS 3.7.12 that apply to two Trains of ABSVS being inoperable during movement of irradiated fuel assemblies due to radiation monitors out of service. With no applicable action provided in Tech Spec 3.7.12, LCO 3.0.3 applied since LCO 3.0.3 establishes the actions that must be implemented when an LCO is not met and an associated action is not provided. LCO 3.0.3 states that the unit shall be placed in a MODE or other specified condition in which the LCO is not applicable and delineates the time limits for placing the unit in a safe MODE. However, since the high radiation signal is only required for LCO 3.7.12 during movement of irradiated fuel, a unit shutdown would not provide appropriate remedial measures. The appropriate action in response to two trains of ABSVS being inoperable during movement of irradiated fuel assemblies due to radiation monitors out of service would be to immediately suspend the movement of irradiated fuel assemblies, but that did not happen. This event is reportable under 10 CFR 50.73(a)(2)(i)(B) for an Operation or Condition Prohibited by Technical Specifications. | ML24296B194 | 0 | good
Browns Ferry Nuclear Plant | Unit 2 | Secondary Containment Isolation Valve Inoperable due to Mechanical Failure | 10-28-2024 | On November 18, 2023, at approximately 2038 Central Standard Time, during performance of Surveillance Requirement 3.6.4.2.1, Secondary Containment Isolation Valve (SCIV) Stroke Timing, Reactor Zone Outboard Supply Damper 2-DMP-0064-0013 failed to close upon securing Reactor Zone Supply Fans. Operations personnel declared 2-DMP-064-0013 inoperable for SCIV function and entered Technical Specification Limiting Condition for Operation 3.6.4.2 Condition A. On November 22, 2023, 1515 CST, following corrective maintenance on the damper, Operations personnel declared damper 2-DMP-064-0013 operable for SCIV function and exited TS LCO 3.6.4.2 Condition A. On December 18, 2023, a Past Operability Evaluation determined that the damper had been inoperable for longer than allowed by TS. This condition did not result in any loss of safety function. The apparent cause of this event was a lack of proper guidance in damper maintenance instructions. The corrective actions to reduce the possibility of recurrence for this condition are to replace broken and/or degraded components on the affected valve, and to revise maintenance procedures for the dampers to include an updated Preventative Maintenance plan with Electric Power Research Institute maintenance guidance. Revision 2 to this report includes applicability to BFN Units 1 and 3 which was not previously reported. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME (cid:1409) 050 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 2 00260 NUMBER NO. (cid:1407) 052 2024 - 001 - 02 | I. Plant Operating Conditions before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN) Units 1, 2, and 3 were each in Mode 1 at approximately 100 percent power. II. Description of Event A. Event Summary On November 18, 2023, at approximately 2038 Central Standard Time (CST), during performance of Surveillance Requirement (SR) 3.6.4.2.1, Secondary Containment [JM] Isolation Valve (SCIV) [ISV] Stroke Timing, Reactor Zone Outboard Supply Damper [DMP] 2-DMP-064-0013 failed to close upon securing Reactor Zone Supply Fans [FAN]. Operations personnel declared 2-DMP- 064-0013 inoperable for SCIV function and entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.4.2 Condition A. On November 22, 2023, 1515 CST, following implementation of a Temporary Modification (TMOD) to the damper, Operations personnel declared damper 2-DMP-064-0013 operable for SCIV function and exited TS LCO 3.6.4.2 Condition A. On December 18, 2023, TVA completed a Past Operability Evaluation (POE) which determined that the damper had been inoperable for longer than allowed by TS. The Tennessee Valley Authority is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant’s TS. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML24302A223 | 0 | good
Browns Ferry Nuclear Plant | Unit 1 | Valid Specified System Actuation Caused the Automatic Start of Emergency Diesel Generators | 10-29-2024 | On August 30, 2024, at 1051 Central Daylight Time Breaker 1622 failed to close during the transfer of Shutdown Bus 1 from 4kV Unit Board 1A to 4kV Unit Board 2B. This failure resulted in deenergizing 4kV Shutdown (SD) Boards A and B, and the A and B Emergency Diesel Generators started and tied to their respective 4kV SD Boards in response. The cause of the event was a loose LS-9 appliance lug which resulted in a loss of power on 4kV SD Boards A and B. As corrective action, the lug was repaired. Additional actions to prevent recurrence will include, briefing of operators and maintenance personnel on this event, as well as procedure enhancements to operating instructions. .::.¢1>""£au(.,> f ¥.' '!, l "'+., ,t,d" .. ,.., .. [8] □ I □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ [8] □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ I I I I I I I I I I I I I I I I I I I [8] ID NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION (04-02-2024) LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME ☒ 050 2. DOCKET NUMBER 3. LER NUMBER Browns Ferry Nuclear Plant, Unit 1 00259 YEAR SEQUENTIAL NUMBER REV NO. ☐ 052 2024 - 003 - 00 | Not Found | ML24303A034 | 1 | ok
Quad Cities Nuclear Power Station | Unit 2 | Turbine Trip and Automatic Scram due to Digital EHC Power Supply Intermittent Failure | 10-30-2024 | On May 23, 2024, at 2223 CST, Quad Cities Unit 2 had an automatic scram from 38 percent power due to a trip of the main turbine. A Digital Electro-Hydraulic Control (DEHC) erroneous Speed Difference Trip signal initiated a Turbine Trip signal. The Unit 2 Main Turbine tripped as designed and generated an automatic reactor scram. All control rods inserted and the scram was uncomplicated. Containment isolation valves actuated closed in multiple systems on valid Group II and Group Ill signals as a result of low reactor water level. The cause of the DEHC trip signal was intermittent channel <R1 > core power supply failure, resulting in an erroneous speed demand value being generated. The power supply and several DEHC cards.were replaced with new components. This report is being submitted per 10 CFR 50. 73(a)(2)(iv)(A) for an event that resulted in manual or automatic actuation of the reactor protection system including a reactor scram, and containment isolation signals affecting more than one system. NRC FORM 366A (04-02-2024) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME • 050 Quad Cities Nuclear Power Station, Unit 2 • 052 | PLANT AND SYSTEM IDENTIFICATION Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A 10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Offcer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 2. DOCKET NUMBER YEAR 00265 2024 - 3. LER NUMBER SEQUENTIAL NUMBER 002 REV NO. 01 General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in text as [XX]. EVENT IDENTIFICATION Turbine Trip and Automatic Scram due to Digital EHC Power Supply Intermittent Failure CONDITION PRIOR TO EVENT Unit: 2 Reactor Mode: 1 Event Date: May 23, 2024 Mode Name: Power Operation Event Time: 2223 CST Power Level: 38 percent No structures, systems, or components that were inoperable at the start of the event contributed to the event. A. DESCRIPTION OF EVENT At 2223 CST on May 23, 2024, with Quad Cities Unit 2 at 38 percent power, the reactor automatically scrammed due to a turbine [TRB] trip signal resulting in turbine stop valve closure, creating a valid reactor protection system signal. Reactor vessel level reached the low-level set-point following the scram, resulting in valid Group II and Group Ill containment actuation signals. The trip was not complex with all systems responding as expected post-trip. This report is being submitted per 10 CFR 50. 73(a)(2)(iv)(A) for an event that resulted in manual or automatic actuation of the reactor protection system including a reactor scram, and containment isolation signals affecting more than one system. Prior to the scram, the unit was reducing power for planned transformer maintenance. A turbine speed versus speed demand comparison generated a Speed Difference Trip and turbine trip signal due to an erroneous speed demand signal. B. CAUSES OF EVENT The cause of the event is an intermittent power supply failure that was not recognized as a single point vulnerability due to the diversity of the system. The turbine trip signal was generated by Digital Electro-Hydraulic Control (DEHC) [TG] turbine speed and speed demand mismatch logic. An intermittent failure of the channel <R1 > core power supply [RJX] resulted in an erroneous speed demand value being generated. DEHC initiated a turbine trip due to a 100% actual speed compared to a 0% speed demand, which is larger than the 10% setpoint. While there was known degradation of this power supply, it was not recognized as a single point vulnerability to DEHC due to system redundancies. NRG FORM 366A (04-02-2024) Page _2_ of _4_ | ML24304A856 | 0 | good
Edwin I. Hatch Nuclear Plant | Unit 1 | Manual Reactor Trip During Hurricane Helene Due to Degrading Condenser Vacuum | 11-19-2024 | At 0346 EDT on 9/27/24, with Unit 1 in Mode 1 at approximately 54% power, the reactor was manually tripped due to degrading condenser vacuum. The trip was not complex, with all systems responding normally including the closure of containment isolation valves in multiple systems. The Operating crew responded correctly to the event and the plant was stabilized. The degrading condenser vacuum was caused by debris from Hurricane Helene that accumulated and clogged the circulation water screens of the Unit 1 flume. The circulation water system was shutdown and the debris removed from the Unit 1 circulation water screens. The event is reportable per 10 CFR 50.73(a)(2)(iv)(A) as any event or condition that resulted in the manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section. Systems that actuated during this event that are listed in (a)(2)(iv)(B) include: the Reactor Protection System (RPS) and general Containment Isolation Valves (CIV) in multiple systems. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04--02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA. Library, and Information CoDections Branch (T-6 A10M), U.S. Nudear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrt:.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104). Attn: Desk Officer for lhe Nudear Regulatory Commission, 725 17th Street NW. Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of Information unless the document requesting or requiring the collection bttQ://www.nrc.gov/reading,_rm/doc-collectionsillY.(fillslstaff/sr.1022/r3I) displays a currently valid 0MB control number. 1. FACILITY NAME r-, 2. DOCKET NUMBER 3. LER NUMBER ..-----------------, ~ 050 cY:E:AR7 SEQUENTIAL REV Edwin I. Hatch Nuclear Plant Unit 1 00321 NUMBER NO. ~- I 1-G □ 052 I I 004 | EVENT DESCRIPTION At 0346 EDT on 9/27/24, with Unit 1 in Mode 1 at approximately 54% power, the reactor was manually tripped due to degrading condenser vacuum. The trip was not complex, with all systems responding normally including the closure of containment isolation valves {CIV)(EIIS Code: ISV) in multiple systems. The Operating crew responded correctly to the event and the plant was stabilized. There were no inoperable systems that contributed to this event. EVENT CAUSE ANALYSIS The degrading condenser vacuum was caused by debris from Hurricane Helene that accumulated and clogged the circulation water screens of the Unit 1 flume. SAFETY ASSESSMENT AND REPORTABILITY There were no actual safety consequences as a result of this event. All safety related systems functioned as designed during this event. The Operating crew responded correctly to the event. The applicable abnormal / emergency operating procedures were properly entered and the plant was stabilized. The event was within the analysis of the Updated Final Safety Analysis Report (UFSAR) Chapter 15. The event is reportable per 10 CFR 50.73(a)(2)(iv)(A) as any event or condition that resulted in the manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section. Systems that actuated during this event that are listed in (a)(2)(iv)(B) include: the Reactor Protection System (RPS)(EIIS Code: IG) and general Containment Isolation Valves (CIV) in multiple systems. CORRECTIVE ACTIONS The circulation water system was shutdown and the debris removed from the Unit 1 circulation water screens. PREVIOUS SIMILAR EVENTS None. | ML24324A187 | 0 | good
Grand Gulf Nuclear Station | Unit 1 | High Pressure Core Spray Over Frequency Relay Trip | 11-22-2024 | On September 24, 2024, Grand Gulf Nuclear Station, Unit 1 was operating at 100 percent power with the High Pressure Core Spray (HPCS) offline for testing and all safety systems operable. At 22:04 CT, during planned surveillance testing of HPCS and the Division Ill diesel generator, the HPCS pump breaker unexpectantly tripped after the HPCS diesel generator started and powered the safety bus. The breaker performed its motor protection function and tripped due to an over-frequency indication. This resulted in a potential loss of safety function. Troubleshooting was performed, and the HPCS over-frequency relay was replaced. The system was returned to service. The cause of the trip was determined to be the failure of the over-frequency relay. The over-frequency relay was determined to be non-essential, and actions were created to remove the relay from the system. During the testing of the HPCS system, alternate ECCS systems were available to provide core cooling and injection to the reactor; therefore, there were no actual safety consequences to the event. This report is made in accordance with 10 CFR 50. 73a(2)(v)(D) for an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 0 4 / 3 0 / 2 0 2 7 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: BO hours. Reported rO\ lessons learned are incorporated into the licensing process and led back to industry Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch IT-6 A10M), U.S. \~.....l. j Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnlocollects.Resource@nrc.gov. and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRG may not conduct or sponsor, and a person is not required to respond https://www .nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/QL) to, a collection of information unless the document requesting or requiring the co lecllon displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER 181 050 YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 NUMBER NO. 00416 0 052 2024 004 00 | Plant Conditions: At the time of the event, Grand Gulf Nuclear Station, Unit 1 was in Mode 1 at 100% power. The station was conducting planned surveillance testing on the High Pressure Core Spray (HPCS) Division Ill Emergency Diesel Generator (EDG). Description of Event: On September 24, 2024, while performing a HPCS loss of offsite power surveillance, the Division Ill EDG started and loaded the safety bus as expected, but the HPCS pump breaker immediately tripped which resulted in a potential loss of safety function. Reportability: This report is made in accordance with 10 CFR 50.73a(2)(v)(D) for an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. HPCS is required to be able to inject water during a loss of cooling accident. Cause(s): The direct cause of the event was a failure of the HPCS over-frequency relay. The HPCS original system design included an over-frequency relay that is not required. This feature has existed since construction, and its need was not evaluated after HPCS was built without the Level-8 injection valve isolation bypass signal, per the GE system design criteria. Corrective Actions: Completed Actions: -Electrical Maintenance replaced the HPCS over-frequency relay. -A Failure Modes Analysis and a Root Cause Evaluation were performed to identify and correct the causes of the event. Planned Actions: -Revise current preventative maintenance to include capacitor checks based on EPRI guidance. -Revise over-frequency calibration procedure to state that all installation or reinstallation of the over frequency relay is required to be with a matched capacitor. -Remove the over-frequency relay protection (17 AC-181) from the HPCS motor protection circuit. Safety Significance: There were no actual safety consequences associated with this condition. The HPCS system functions as a part of the Emergency Core Cooling System (ECCS). It functions to provide and maintain an adequate coolant inventory inside the reactor vessel to limit the fuel cladding temperatures in the event of breaks in the reactor coolant pressure boundary. The system is initiated by either high pressure in the drywall or low water level in the reactor vessel. During the testing of the HPCS system, alternate ECCS systems were available to provide core cooling and injection to the reactor. Previous Similar Events: LER 24-001-00 High Pressure Core Spray Inoperable due to Minimum Flow Valve Failure to Close | ML24326A363 | 0 | good
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Turbine Trip and Scram due to Automatic Voltage Regulator Protective Device during a Grid Transient | 11-22-2024 | At 0720 on September 23, 2024, James A. FitzPatrick Nuclear Power Plant (JAF) was at 100% power when an automatic scram occurred as a result of a main turbine trip due to an automatic trip of the generator output breakers. All control rods inserted and a subsequent Reactor Pressure Vessel (RPV) low water level resulted in Group 2 isolation and system initiation of High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC). RCIC did inject but HPCI did not inject as expected based on RPV water level recovery with the Feedwater System. The generator output breakers were tripped because of the energization of the digital Automatic Voltage Regulator (AVR) protective device crowbar circuit due to an overvoltage condition during a grid transient. A corrective action is planned to evaluate and model the event to determine if the min limiter function or software changes to the AVR should be implemented. This event is reportable in accordance with CFR 50.73(a)(2)(iv)(A) as a Reactor Protection System (RPS) actuation, including a general containment Group 2 isolation and HPCI and RCIC system actuation. NRC FORM 366 (04-02-2024) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 LICENSEE EVENT REPORT (LER) hours. Reported lessons learned are incorporated into the licensing process and fed CONTINUATION SHEET back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory (See NUREG-1022, R.3 for instruction and guidance for completing this form Commission, 725 17th Street NW, Washington, DC 20503; email: http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 YEAR SEQUENTIAL REV NUMBER NO. James A. FitzPatrick Nuclear Power Plant 05000333  052 2024 – 003 – 00 | Background The main generator [EIIS identifier:TB] has an Exciter System [TL] to stabilize voltages from the electrical transmission grid. The excitation is controlled by a Digital Automatic Voltage Regulator (AVR). The AVR has two redundant channels. Reactive Power is measured in units of "mega volt-amperes reactive", or MVAR, and is taken into account when designing and operating power systems. The power associated with reactive power does no net work but current must still be supplied by the conductors, transformers and generators. They must be sized to carry the total current, not just the current that does useful work (active power). Insufficient reactive power can depress voltage levels on an electrical grid and, under certain operating conditions, collapse the network (a blackout). Therefore, the purpose of the AVR is to control the exciter based on changes on the grid, including reactive power. AVR may enable control parameters such as over excitation Protective Device Threshold – Trip / Disconnect limiter (OEL) to prevent overheating from excessive current; and an under excitation Limiter Threshold – Controls Parameter limiter (UEL) to prevent de-synchronization from the grid. Besides control parameters, the AVR is designed with protection devices to trip the system to protect components from being damaged. The protective device associated with this event is the crowbar circuit which is Time designed to respond to an overvoltage or surge condition. Event Description On September 23, 2024, at 0720 with James A. FitzPatrick Nuclear Power Plant (JAF) reactor operating at 100 percent power, an automatic reactor shutdown (scram) occurred because of a main turbine trip due to an automatic trip of the generator output breakers. All control rods inserted and a subsequent Reactor Pressure Vessel (RPV) low water level resulted in Group 2 isolation and system initiation of High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC). RCIC did inject but HPCI did not inject as expected based on RPV water level recovery with the Feedwater System. This event was reported at the time of the event by ENS 573331 and is reportable in accordance with CFR 50.73(a)(2)(iv)(A) as a Reactor Protection System (RPS) actuation, including a general containment Group 2 isolation and HPCI and RCIC system actuation. Page 2 of 3 | ML24327A098 | 0 | good
Browns Ferry Nuclear Plant | Unit 2 | High Pressure Coolant Injection Inoperable due to Rupture Disc Failure and Resulting System Isolation | 11-25-2024 | On March 19, 2024, at 1030 Central Daylight Time (CDT), during performance of 2-SR-3.5.1.7, High Pressure Coolant Injection (HPCI) Flowrate at Rated Reactor Pressure, after operating the Unit 2 HPCI system for approximately 37 minutes at rated pressure and flow, BFN Unit 2 received indications of high rupture disc pressure, HPCI Turbine trip, and HPCI isolation. Operations personnel verified HPCI isolated as expected, declared HPCI inoperable, verified BFN Unit 2 Reactor Core Isolation Cooling (RCIC) operability, and entered 2-AOI-64-2B for isolation. On March 19, 2024, at 1719 CDT, Event Notification 57036 was made to the NRC. BFN Unit 2 remained in Technical Specification (TS) Limiting Condition for Operation (LCO) 3.5.1 until the rupture disc was replaced and the HPCI system was declared operable at 1051 CDT on March 25, 2024. The root cause of this event was that the operating ratio of the rupture disc was not used to develop effective operating limits to protect the integrity of the disc. The corrective actions taken to prevent recurrence will be to create or revise a design output document to determine the operating pressure limit for the HPCI and RCIC System turbine exhaust line rupture discs, to revise affected drawings and procedures to specify the operating pressure limit for the rupture discs, and to revise installation and maintenance instructions to include all pertinent operating limits for operating rupture discs on HPCI systems. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION (04-02-2024) LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME ☒ 050 2. DOCKET NUMBER 3. LER NUMBER Browns Ferry Nuclear Plant, Unit 2 00260 YEAR SEQUENTIAL NUMBER REV NO. ☐ 052 2024 - 002 - 01 | Not Found | ML24330A077 | 1 | ok
Cooper Nuclear Station 298 1 of 3 | Unknown Unit | Inoperable Pressure Switch During Mode Change Results in Operation or Condition Prohibited by Technical Specifications | 12-31-2024 | On November 3, 2024, with the Cooper Nuclear Station (CNS) reactor in Mode 1, Power Operation, scheduled surveillance testing of the eight Safety Relief Valves (SRV) was being performed. During this testing, pressure switch (MS-PS-3008) did not actuate when SRV71 B was taken to the OPEN position. As such, Operations personnel declared MS-PS-3008 inoperable. Review of a picture taken in the area of SRV71 B on October 16, 2024, while the reactor was in Mode 5, Refueling, revealed that the flex hose that extends from the SRV tailpipe to the pressure switch may be damaged. This was later confirmed when maintenance personnel found the flex hose on top of the SRV tailpipe and the connection port for MS-PS-3008 damaged. Repairs were made and subsequent testing performed satisfactorily, and Operations personnel declared MS-PS-3008 operable. CNS made the change from Mode 4 to Mode 2 while this condition existed, violating Technical Speciation (TS) Limiting Condition for Operation 3.0.4, and is reporting this event as an operation or condition prohibited by plant TS. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process LICENSEE EVENT REPORT {LER) and fed back to industry. Send comments regarding burden estimate to the CO NTINUATION SHEET FOIA, Library, and Information Collections Branch (T-6 A10M), U. s. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. (See NUREG-1022, R.3 for instruction and guidance for completing this form The NRC may not conduct or sponsor, and a person is not required to respond http://www.nrc.gov/readinq-rm/doc-collections/nuregs/staff/sr1022/r3/) to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Cooper Nuclear Station 05000-298 NUMBER NO. 2024 007 00 | PLANT STATUS Cooper Nuclear Station (CNS) was in Mode 1, Power Operation, at 18 percent power at the time of the event on November 3, 2024. BACKGROUND The pressure relief system includes three American Society of Mechanical Engineers (ASME) code safety valves (SV) [EIIS: SB] and eight safety relief valves (SRV) [EIIS: RV], all of which are located on the main steam lines [EIIS: SB] within the drywell [EIIS: NH], between the reactor vessel [EIIS: RPV] and the first main steam isolation valve [EIIS: ISV]. The SVs provide protection against over pressurization of the nuclear system and discharge directly into the interior space of the drywell. The SRVs discharge to the suppression pool and provide three main functions: overpressure relief operation to limit the pressure rise and prevent safety valve opening, overpressure safety operation to prevent nuclear system over pressurization, and depressurization operation (opened automatically or manually) as part of the emergency core cooling system [EIIS: BJ, BM, BO]. Each SRV is equipped with a pressure switch mounted in its discharge tailpipe. When a SRVs associated discharge pressure switch senses tailpipe pressure of at least 30 psig, the SRV can be determined to be in the OPEN position. When the pressure switch is actuated at 30 psig, an amber indicating light will illuminate in the Control Room and the annunciator for the relief valve will alarm, indicating the SRV is open. EVENT DESCRIPTION On November 3, 2024, while performing scheduled surveillance testing of the eight Safety Relief Valves (SRV) during plant start-up activities from Refueling Outage (RE33), pressure switch (MS-PS-300B) did not actuate when SRV71 B was taken to the OPEN position. SRV71 B tailpipe temperature did immediately rise, however, the temperature was approximately 100 degrees Fahrenheit lower than expected for a fully open SRV and the temperature profile exhibited erratic behavior. The main turbine bypass valve position responded as expected, confirming SRV71 B did fully open. As such, MS-PS-300A was declared inoperable on November 3, 2024. As a result of the low temperatures on the SRV71 B tailpipe, questions arose regarding the possibility of a disconnected flex hose that extends from the SRV71 B tailpipe to MS-PS-300B. SRV71 B was not cycled open prior to RE33 and was not subjected to abnormal operating conditions that would have induced a vibration or fatigue failure of the flex hose. A picture taken near the area of SRV71 B on October 16, 2024, was reviewed and it was discovered that the flex hose may have been inadvertently disconnected. Maintenance personnel were dispatched to SRV71 B and confirmed that the flex hose was disconnected and was laying on top of the SRV71 B tailpipe. The threaded connections of the flex hose and the connection port on the SRV71 B tailpipe were found damaged. | ML24366A126 | 0 | good
Grand Gulf Nuclear Station | Unit 1 | Loss of Seal Steam Controller Power Resulted in Manual Reactor Shutdown | 01-09-2025 | On November 10, 2024, at 0337 CST, Grand Gulf Nuclear Station, Unit 1 was operating at 100 percent power with all safety systems operable. A failed power supply resulted in a loss of seal steam controller power and led to a degraded condenser vacuum which resulted in a manual reactor shutdown. All control rods were fully inserted with no complications. Following initial scram response, a group 1 containment isolation signal resulted in the closure of all main steam isolation valves at 0545 CST. Later, an automatic Reactor Protection System actuation occurred at 0620 CST while in MODE 3 while all control rods were inserted. The cause of the loss of seal steam controller power was determined to be a failed power supply, 1 N21 K602B which had exceeded its expected life. The 1 N21 K602B power supply was replaced, and seal steam control was returned to service. This report is made in accordance with 10 CFR 50.73(a)(2)(iv)(A) for events or conditions that resulted in the manual or automatic actuation of the reactor protection system. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 0 4 / 3 0 / 2 0 2 7 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: BO hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M). U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnlocollects.Resource@nrc.gov, and the 0MB reviewer at. 0MB Office of Information and Regulatory Attairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503 The NRC may not conduct or sponsor, and a person is not required to respond https://www.nrc.gov/reading-rm/doc-colleclions/nuregs/staff/ sr1 022/r3/l to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER 181 050 YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 NUMBER NO. 00416 □ 052 2024 005 00 | Plant Conditions: At the time of the event, Grand Gulf Nuclear Station, Unit 1 was in Mode 1 at 100% power, and all safety systems were operable. Description of Event: On November 10, 2024, at 0337 CST, a power supply failure resulted in a loss of seal steam controller power and led to a degraded condenser vacuum which resulted in a manual reactor shutdown. All control rods fully inserted, and there were no complications. Following initial scram response, a group 1 containment isolation signal resulted in the closure of all main steam isolation valves at 0545 CST. This signal was due to the continued degradation of the condenser vacuum post-trip. An automatic RPS actuation occurred while in MODE 3 with all control rods currently inserted at 0620 CST. Following the second actuation of the reactor protection system (RPS), pressure was controlled by safety relief valves and reactor core isolation cooling was used to maintain water level. Reportability: This report is made in accordance with 10 CFR 50.73(a)(2)(iv)(A) for events or conditions which resulted in the manual or automatic actuation of the RPS. Cause(s): The direct cause of the 1 N21 K602B power supply failure was aged components exceeding their expected life. The root cause of the event was the determination of the life expectancy of the power supplies with electrolytic capacitors was incorrectly designed using the in-service date as the starting criteria; however, electrolytic capacitors begin degrading upon manufactured date. Starting the life expectancy for this power supply from the in-service date as opposed to manufactured date resulted in the power supply being installed with a projected life expectancy of 10 years when the component already had 6 years of shelf life and only 4 years of remaining life expectancy. Corrective Actions: Completed Actions: -The seal steam power supply 1 N21 K602B was replaced, and seal steam control was restored. Planned Actions: -Revise maintenance procedure to include steps which guide actual full age determination and evaluation of power supplies. This will include a signature requirement for Maintenance to contact Supply Chain, and it will require initiating a Condition Report to document and evaluate the power supply age prior to being installed. Safety Significance: There were no actual safety consequences associated with this condition. Plant systems responded as designed and the unit was brought to Mode 3 by Control Room Operators. Previous Similar Events: None identified. NRG FORM 366A (04-02-2024) Page 2 of 2 | ML25009A011 | 0 | good
i | Unknown Unit | Not Found | 01-10-2025 | Nine Mile Point Unit 2 ■ 410 4 Supplement to LER 2024-002-00, Automatic Reactor Scram on Turbine Trip due to failed breaker 09 23 2024 2024 002 01 01 09 2025 Mode 1, Power Operation 100% ✔ Matt Rossi, Site Regulatory Assurance Manager (315)-349-7012 X TL BKR G080 Yes X TL BD GE Yes ✔ On 9/23/2024 failure of the Main Generator Field Circuit Breaker (41M-2EXSX01) [EXC] lead to a Generator Field Loss of Excitation [TL]. This resulted in a Main Generator Lockout which caused a Turbine Trip [TA] and automatic anticipatory RPS actuation [JC] at 07:20. High resistance across Main Generator Field Circuit Breaker (41M-2EXSX01) caused a large voltage drop across the breaker main contacts. The Auto Voltage Regulator (AVR) [90] control system responded to the lower excitation through the feedback and increased output to compensate. The increased output resulted in increased voltage drop, heat at the contacts, a subsequent fire, and Loss of Field Excitation. The resulting Turbine Trip and Turbine Stop and Control Valve closure caused an automatic anticipatory RPS actuation. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). NRC FORM 366A (04-02-2024) U.S. NUCLEAR REGULATORY COMMISSION LICENSEE EVENT REPORT (LER) CONTINUATION SHEET APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) | Not Found | ML25009A027 | 2 | ok
browns ferry nuclear plant | Unknown Unit | Main Steam Relief Valves Lift Settings Outside of Technical Specifications Required Setpoints | 01-10-2025 | On November 12, 2024, the Tennessee Valley Authority (TVA) was notified of as-found testing results that two (2) Main Steam Relief Valves (MSRVs) from Browns Ferry Nuclear Pant (BFN), Unit 1 were outside of their Surveillance Requirement limits for an indeterminate amount of time. These affected valves remained capable of maintaining reactor pressure within the American Society of Mechanical Engineers code limits and were still able to perform their safety function. It was determined that one MSRV failed above its setpoint due to corrosion bonding to the valve seats. The other MSRV failed below its setpoint due to relaxed setpoint springs. All thirteen of the MSRV pilot valves were replaced during the Unit 1 Fall 2024 refueling outage. The Boiling Water Reactor Owners' Group is continuing to work toward a solution to improve the quality and adhesion of the platinum coating on the pilot discs. BFN will continue to verify that the springs pass spring rate testing during their rebuilding and replacing those which do not. /¥,,,, ..... ,.,... E i . . ~ ... ,;.+,, ~d' .. ...... [8] □ I □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ [8] □ □ □ □ □ □ □ I I I I I I I I I I I I I I I I I I I [8] ID NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION (04-02-2024) LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME ☒ 050 2. DOCKET NUMBER 3. LER NUMBER Browns Ferry Nuclear Plant, Unit 1 00259 YEAR SEQUENTIAL NUMBER REV NO. ☐ 052 2024 - 004 - 00 | Not Found | ML25010A346 | 1 | ok
i | Unknown Unit | : | 01-23-2025 | On November 26, 2024, at 1158, with the reactor in Mode 1 and 100 percent rated thermal power, the Division 3 diesel generator (DG) was declared inoperable per Technical Specification (TS} 3.8.1, due to the right bank air start motor not operating properly during a monthly surveillance test. Subsequent troubleshooting found that the right bank air start motor air hoses were improperly connected during maintenance in June of 2024. Satisfactory testing of the DG, following proper air hose connection, resulted in correct operation of the right back air start motor, and the Division 3 DG was declared operable at 1731 on November 27, 2024. The cause was determined to be insufficient use of verification practices and/or use of vendor drawings during the air start motor air hose re-assembly during previous maintenance. Corrective actions include adding an independent verification procedure step to ensure the proper connection of the air start motor air hoses and revisions to maintenance procedures for configuration control. This event was reported on November 26, 2024, as a loss of safety function under 10 CFR 50.72(b)(3)(v)(D), for accident mitigation, due to the Division 3 DG being declared Inoperable. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 0 4130/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A1 0M}, U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond (See NUREG-1022, R.3 for instruction and guidance for completing this form to, a collection of information unless the document requesting or requiring the collection displays a http:// W'NW. n re. gov/reading-rm/doc-co 11 ecti o ns/nu regs/staffl s r1 022/r3/ currently valid 0MB control number. 2. DOCKET NUMBER ..__ ___3 _. _LE_R_N_U_M_B..,E_R_ ___ 1. FACILITY NAME t8l 050 SEQUENTIAL REV YEAR NUMBER NO. Perry Nuclear Power Plant 00440 2024 005 00 □ 052 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. BACKGROUND: The High Pressure Core Spray (HPCS) [BG] system power source, the Division 3 DG [DG], is self-contained, except for access to the preferred source of offsite power through the onsite AC power distribution system and the system actuation signal source. The system is operable as an isolated system independent of electrical connection to any other system by using the Division 3 DG. HPCS provides and maintains an adequate coolant inventory inside the reactor vessel to limit fuel cladding temperatures in the event of breaks in the reactor coolant pressure boundary. The system is initiated by either high pressure in the drywell or low water level in the reactor vessel [RCT). It operates independently of all other systems over the entire range of pressure differences from greater than normal operating pressure to zero. The HPCS cooling decreases vessel pressure to enable the low-pressure cooling systems to function. The HPCS system pump [P] motor [MO] is powered by a diesel generator if auxiliary power is not available; the system may also be used as a backup for the Reactor Core Isolation Cooling (RCIC) [BN] system. DESCRIPTION OF EVENT: On November 26, 2024, at 1158, with the reactor in Mode 1 and 100 percent rated thermal power, during a surveillance test of the Division 3 DG, it was identified that the right bank air start motor was not operating correctly, based on noting a lack of a sufficient pressure drop at the air storage tank. The Division 3 DG was declared Inoperable, but available, and TS 3.8.1, AC Sources - Operating, Condition B, one required DG inoperable, was entered. During troubleshooting, it was discovered that the air hoses to the right bank air start motor were not configured correctly, causing improper operation of the right bank air start motor. The air hoses were determined to have been configured incorrectly during maintenance in June of 2024. The air hoses were returned to the proper configuration and a post-maintenance run of the Division 3 DG was performed, resulting in a normal start using both right and left bank air start motors. On November 27, 2024, at 1731, the Division 3 DG was declared Operable and TS 3.8.1 was met. Although other power sources were available during this period, the inoperable condition of the Division 3 DG is reportable under 10 CFR 50.73(a)(2)(v)(D) for mitigating the consequences of an accident during a loss of offsite power/loss of coolant accident (LOOP/LOCA). Since the air hoses to the right bank air start motor were found to be misconfigured since June of 2024, the Division 3 DG has been inoperable since that time. As such, this is also reportable under 10 CFR 50.73(a)(2)(i)(B). CAUSE OF EVENT: Cause: Insufficient use of verification practices and/or use of vendor drawings to allow for correct re-assembly of the air start motor air hoses. NRG FORM 366A (04-02-2024) Page 2 of 3 | ML25023A193 | 0 | good
Cooper Nuclear Station 298 1 of 5 | Unknown Unit | Not Found | 02-20-2025 | On January 31, 2024, a steam leak was identified near the High Pressure Coolant Injection (HPCI) drain line steam trap. This issue was entered into the work management process. The steam leak was later noted as degraded on February 19, 2024, and during a walkdown on February 22, 2024, to support the work order for repair, a maintenance technician identified steam potentially coming from the piping between the HPCI steam trap and a HPCI downstream valve. As a result of this potential through-wall pipe leak, Operations declared HPCI inoperable at 1718 hours on February 22, 2024, and entered the applicable Technical Specifications Condition. An eight-hour non-emergency event notification (EN 56989) was made to the Nuclear Regulatory Commission. The HPCI trap assembly (steam trap, outlet valve, and piping) was replaced and HPCI was returned to operable status at 2101 on February 24, 2024. A failure analysis on the removed HPCI steam trap assembly revealed internal damage resulting in leak-by, allowing flow accelerated corrosion (FAC) and/or erosion of the piping immediately downstream The root cause is steam trap performance and leak-by events were not thoroughly understood regarding the potential adverse effects of erosion and/or FAC. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process LICENSEE EVENT REPORT (LER) and fed back to industry. Send comments regarding burden estimate to the FOIA, CONTINUATION SHEET Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC (See NUREG-1022, R.3 for instruction and guidance for completing this form may not conduct or sponsor, and a person is not required to respond to, a collection http://www. nrc. gov/ readi nq-rm/d oc-collections/nu regs/staff/ sr1 022/r3/) of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LERNUMBER Cooper Nuclear Station 05000-298 YEAR SEQUENTIAL REV NUMBER NO. 2024 003 01 | PLANT STATUS At the time of the event on January 31, 2024, Cooper Nuclear Station (CNS) was in Mode 1, Power Operation, at 100 percent steady-state power. BACKGROUND The High Pressure Coolant Injection (HPCI) system [EIIS:BJ] provides protection to the core in case of a small break in the reactor coolant pressure boundary which does not result in a rapid depressurization of the reactor vessel [EIIS:RPV]. The HPCI system permits the nuclear plant to be shutdown while maintaining sufficient reactor vessel water inventory until the reactor vessel is depressurized. HPCI continues to operate until reactor vessel pressure is below the pressure at which Low Pressure Coolant Injection system [EIIS:BO] operation or Core Spray system [EIIS:BM] operation can be used to maintain core cooling. HPCI consists of a steam turbine assembly [EIIS:TRB] driving a multi-stage booster and main pump assembly [EIIS:P] and system piping valves, controls and instrumentation. The HPCI turbine is driven by steam from the reactor which is generated by decay and residual heat. The HPCI turbine drain line steam trap, HPCI-TP-S57, provides a drain path for the HPCI steam supply drip leg since the HPCI steam supply block valve is normally closed preventing steam from supplying the turbine. Condensate forms from the steam in the drip leg. HPCI-TP-S57 allows the high pressure condensate to pass through it to the lower pressure drain line to the Main Condenser [EIIS:SG]. The trap is designed to prevent high pressure steam from passing through the drain with the condensate. HPCI-TP-S57 is manufactured by Yarway Corporation, model 515BSWR. HPCI is a single train system and is required to be operable to satisfy the requirements of Technical Specifications (TS) 3.5.1. EVENT DESCRIPTION On January 31, 2024, a station operator identified a steam leak near HPCI-TP-S57. The steam leak could be heard once entering the HPCI room and an approximate six-inch steam plume was visible around HPCI-TP- S57. This issue was entered into the work management process for repair. On February 19, 2024, during a subsequent station operator tour, the steam leak had degraded. Condensation was no longer completely contained in the catch basin; floor troughs and drains had completely captured the remaining condensation. The operability reviews for these conditions assessed the steam leak as coming from the body to bonnet gasket of HPCI-TP-S57 which is not considered American Society of Mechanical Engineers (ASME) code leakage (leakage from mechanical connections is classified as non-code leakage). Based on the leakage being non-code leakage, not impacting surrounding HPCI equipment, and HPCI steam pressure unaffected, HPCI remained operable. | ML25051A147 | 1 | ok
i | Unknown Unit | : | 02-24-2025 | On October 29, 2024, at 1152, with the reactor in Mode 1 and 100 percent rated thermal power, Operations declared the Division 3 diesel generator (DG) Inoperable per Technical Specification (TS) 3.8.1, due to output voltage dropping below the TS acceptance value during a monthly surveillance run. Subsequent troubleshooting found potentiometers on the voltage regulator were oxidized, requiring exercise, which remediated the output voltage issue. Satisfactory testing of the DG, following the troubleshooting, resulted in a proper and steady output voltage, and the Division 3 DG was declared Operable on October 31, 2024, at 0030. This is a supplemental report to LER 2024-004-00 to update the causal investigation and the corrective actions. The cause was determined to be oxidation of the voltage regulator R1 and R3 potentiometers due to high humidity. Corrective actions include exercising potentiometer R1, R3, and R4 on the output voltage regulator to remove oxidation and revising operating procedures to perform cycling the output voltage adjustment monthly. This event was reported on October 29, 2024, as a loss of safety function, due to the loss of the Division 3 DG, under 10 CFR 50.72(b)(3)(v)(D), for accident mitigation. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A1 0M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond (See NUREG-1022, R.3 for instruction and guidance for completing this form to, a collection of information unless the document requesting or requiring the collection displays a http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/ currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER t------.-3_.L _E_R_N_U_M_BE.-R_ __- --1 050 SEQUENTIAL REV YEAR NUMBER NO. Perry Nuclear Power Plant 00440 □ 052 2024 004 01 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. BACKGROUND: The high pressure core spray (HPCS) [BG] system power source, the Division 3 DG [DG], is self-contained, except for access to the preferred source of offsite power through the onsite AC power distribution system and the system actuation signal source. The system is operable as an isolated system independent of electrical connection to any other system by using the Division 3 DG. HPCS provides and maintains an adequate coolant inventory inside the reactor vessel to limit fuel cladding temperatures in the event of breaks in the reactor coolant pressure boundary. The system is initiated by either high pressure in the drywall or low water level in the reactor vessel [RCT]. It operates independently of all other systems over the entire range of pressure differences from greater than normal operating pressure to zero. The HPCS cooling decreases vessel pressure to enable the low-pressure cooling systems to function. The HPCS system pump [P] motor [MO] is powered by a diesel generator if auxiliary power is not available; the system may also be used as a backup for the reactor core isolation cooling (RCIC) [BN] system. DESCRIPTION OF EVENT: On October 29, 2024, at 1152, with the reactor in Mode 1 and 100 percent rated thermal power, during a preventative maintenance run of the Division 3 DG, it was noticed that the generator output voltage had dropped below the Technical Specification (TS) acceptance value of 3994 volts (3900 volts, adjusted for instrument I inaccuracy). The lowest value recorded during the DG run was 3947 volts. The Division 3 DG was declared Inoperable, but available, and TS 3.8.1, AC Sources - Operating, Condition B, one required DG inoperable, was entered. During troubleshooting, it was discovered that an oxidation layer had built up on the R1 potentiometer in the output voltage regulator [RG]. Exercising the potentiometer throughout its range caused the oxidation layer to be removed, thereby eliminating the high resistance point and allowing the voltage regulator to function normally. A post-maintenance run of the Division 3 DG was performed resulting in a normal and steady output voltage. On October 31, 2024, at 0030, the Division 3 DG was declared Operable and TS 3.8.1 was met. Due to the lnoperability of the Division 3 DG, it was determined to be an event or condition that could have prevented fulfillment of a safety function under 10 CFR 50. 72(b )(3)(v)(D) for mitigating the consequences of an accident during a loss of offsite power/loss of coolant accident (LOOP/LOCA). The NRC was notified at 1732, on October 29, 2024, and this was documented on Event Notification 57406. No other failures of the Division 3 DG or the voltage regulator could be found during the previous three-year timeframe. Although outside of the three-year timeframe, a previous similar event was identified and is discussed later in this report. | ML25055A256 | 0 | good
SEQUENTIAL REV | Unknown Unit | Loss of The Control Room Emergency Air Temperature Control System Due to a Chiller Oil Migration | 03-03-2025 | On January 4, 2025 at 0855 EST, with Unit 1 and Unit 2 at 100% rated thermal power, both trains of the Control Room Emergency Air Temperature Control System (CREATCS) were simultaneously inoperable. This condition occurred when the A-A Main Control Room (MCR) chiller experienced an oil migration event and tripped on oil failure while the B train of CREATCS had been previously declared inoperable for a B-B MCR chiller maintenance outage. The A train of CREATCS was later restored at 1408 EST on January 4, 2025 following the addition of MCR chiller oil, adjustment of the chiller’s temperature control valve (TCV) and subsequent observation of stable chiller parameters. Applicable technical specification (TS) limiting conditions for operability (LCO) were entered for less than six hours as a result. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond (See NUREG-1022, R.3 for instruction and guidance for completing this form to, a collection of information unless the document requesting or requiring the collection displays a http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) currently valid OMB control number 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ☒ 050 SEQUENTIAL REV YEAR NUMBER NO. Watts Bar Nuclear Plant, Unit 1 00390 ☐ 052 2025 - 001 - 00 | I. Plant Operating Conditions before the Event Watts Bar Unit 1 and Unit 2 were at 100 percent Rated Thermal Power (RTP) before the event. II. Description of Event A. Event Summary On January 4, 2025 at 0855 EST, with Unit 1 and Unit 2 at 100% rated thermal power, both trains of the Control Room Emergency Air Temperature Control System (CREATCS){EIIS:VI} were simultaneously inoperable. This condition occurred when the A-A Main Control Room (MCR) chiller experienced an oil migration event and tripped on oil failure while the B train of CREATCS had been previously declared inoperable for a B-B MCR chiller maintenance outage. The A train of CREATCS was later restored at 1408 EST on January 4, 2025 following the addition of MCR chiller oil, adjustment of the chiller’s temperature control valve (TCV){EIIS:TCV}, and subsequent observation of stable chiller parameters. Applicable technical specification (TS) limiting conditions for operability (LCO) were entered for less than six hours as a result. This condition is being reported to the Nuclear Regulatory Commission (NRC) in accordance with 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event The B-B MCR chiller had been removed from service for a maintenance outage when the A-A MCR chiller trip occurred. | ML25062A082 | 0 | good
YEAR | Unknown Unit | Not Found | 03-07-2025 | On January 16, 2025, at 1657 CDT, it was discovered that manual Secondary Containment Isolation Valve (SCIV) 2-1279- 21A, 2A Reactor Water Clean Up Filter Demineralizer Rad Waste Drain Valve, was in an Open position. This resulted in discovery of a condition which was prohibited by Technical Specifications (TS). The valve should have been in a Closed position or should have had appropriate administrative controls applied when left in an Open position under the applicable tagout boundary that had been established. The valve was closed on January 16, 2025, at 1801 CDT in accordance with TS 3.6.4.2 Condition A. However, a past functionality review indicated the valve had been open for approximately 86 hours total, which exceeded TS 3.6.4.2 Condition A.1 to isolate the line in 8 hours. The cause of the event was a failure to implement administrative controls for the SCIV left in an open position during tagout boundary dispatch and placement. Immediate action was to close the SCIV. Follow up actions will be to improve SCIV tagout boundaries and valve labels. This report is being submitted under 10 CFR 50. 73(a)(2)(i)(B) for an operation or condition which was prohibited by the plant's Technical Specifications. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regaiding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A1 0M), U. S. Nucleat Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRG may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www. nrc.qov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D displays a currently valid 0MB control number. 1. FACILITY NAME (cid:127) 2. DOCKET NUMBER 3. LER NUMBER 050 SEQUENTIAL REV YEAR NUMBER NO. Quad Cities Nuclear Power Station Unit 1 (cid:143) 00254 052 2025 - 001 00 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Technical Specification 3.6.4.2 Action Not Performed Due to Tagout Boundary Placement Error A. CONDITION PRIOR TO EVENT Unit: 1 Event Date: January 16, 2025 Event Time: 1657 CDT Reactor Mode: 1 Mode Name: Power Operation Power Level: 93% There were no other structures, systems or components (SSC) inoperable during this event time period that could have contributed to this event. B. DESCRIPTION OF EVENT On January 16, 2025, at 1657 CDT, it was discovered that manual secondary containment isolation valve (SCIV)[ISV] 2- 1279-21A, 2A Reactor Water Clean Up [CE] Filter Demineralizer Rad Waste Drain Valve, was in an Open position. Operations discovered this during maintenance activities within the tagout boundary that was to be provided by this valve. The valve was tagged in an Open position using a Caution/Information card to ensure the piping remained drained during the work on an adjacent valve. The 2-1279-21A could have been used as a drain for the volume, under applicable procedural and administrative controls, and then later Closed, although there were no specific instructions in the tagout to close the valve after draining. The tagout did include cautions and procedure references for the 2-1279-21A related to it being a SCIV. When the Open position of the valve was discovered, Technical Specification (TS) 3.6.4.2 Condition A was entered. The 2-1279-21A valve was closed at 1801 CDT, and TS 3.6.4.2 Condition A was exited. A past functionality review indicated that the valve had been left in an Open position from when the tagout was validated at 0409 on January 13, 2025, until it was closed at 1801 CDT on January 16, 2025, for a total of 85 hours and 52 minutes. This exceeds the 8 hour completion time in TS 3.6.4.2 Condition A Action A.1 to isolate the secondary containment flow path. Issue Report 04830292 was generated. A tagout package includes multiple sections, including placement instructions at the front of the package, and card notes at the end, in addition to the actual physical tags, called EPN (Equipment Part Numbers) Tags, that are hung on the equipment. Specific to this tagout, the EPN Tag had a note referring to a governing procedure for SCIV openings, and a note that secondary containment could be violated. These secondary containment impacts were not fully recognized by the operations team hanging the tagout, and the necessary administrative controls were not discussed in detail in a pre job brief. | ML25066A110 | 1 | ok
Donald C. Cook Nuclear Plant | Unit 2 | 2AB Emergency Diesel Generator Inoperable for longer than allowed by Technical Specifications | 03-27-2025 | On May 21, 2024, with Cook Nuclear Plant (CNP) Units 1 and 2 in Mode 1 at 100% power, the 2AB EDG failed to reach the required frequency during the slow speed start surveillance, per the required acceptance criteria range of 59.5 to 60.4 Hz. The failure to reach the required frequency was originally attributed to corroded connections on the Minimum Speed Threshold and Slow Start control relays. On July 23, 2024, the 2AB EOG, once again, failed to reach the required frequency during a surveillance run. The cause of the failure was determined to be an intermittent failure of the Digital Reference Unit (DRU). Due to the similar symptoms between the two failures of the 2AB EOG, it was determined that the 2AB EDG failure on May 21, 2024, was also due to a failure of the DRU. Due to the discovery that both EOG failures were a result of a failure of the DRU, the 2AB EOG was determined to be inoperable from the time the original condition was discovered on 05/21/2024 at 2115, until the time it successfully passed a surveillance after the DRU was replaced on 7/24/2024 at 2300. Therefore, the identified condition is reportable, for both units, in accordance with 10 CFR 50.73(a)(2)(i)(B) as a Condition prohibited by Technical Specifications. Furthermore, during this period of time, there were instances on Unit 2 where concurrent with the 2AB EOG, the 2CD EOG was inoperable, which results in being reportable per 10 CFR 50. 73(a)(2)(v) as an Event or Condition which could have prevented the fulfillment of a Safety Function. The Root Cause for the failure to properly identify and correct the May 21, 2024 EOG surveillance failure was I a lack of proper oversight and proper use of knowledge worker human performance tools during the Failure Investigation Process (FIP). Corrective Actions include formalization and improvements in qualifying FIP team management sponsors and team leaders. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nudear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nudear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nu regs/staff/ sr1 022/r3/) displays a currently valid 0MB control number. ■ 1. . FA - CIL - ITY - NA - ME - ----------, r ~ -, 050 I2. DOCKET NUMBER YEAR 3 S . E L Q E U R E N N U T M IA B L E R REV Donald C. Cook Nuclear Plant Unit 2 00316 I □ NUMBER NO. ~-I 1-0 □ 052 004 | EVENT DESCRIPTION On May 21, 2024, with Cook Nuclear Plant (CNP) Units 1 and 2 in Mode 1 at 100% power, the 2AB Emergency Diesel Generator (EOG) [DG] failed to reach the required frequency during the slow speed start surveillance, per the required acceptance criteria range of 59.5 to 60.4 Hz. The failure to reach the required frequency was originally attributed to corroded connections on the Minimum Speed Threshold and Slow Start control relays. On July 23, 2024, the 2AB EOG, once again, failed to reach the required frequency during a surveillance run. The cause of the failure was determined to be an intermittent failure of the Digital Reference Unit (DRU). Due to the similar symptoms between the two failures of the 2AB EOG, it was determined that the 2AB EDG failure on May 21, 2024, was also due to the failure of the DRU. Unit 2 Limiting Condition of Operation (LCO) 3.8.1 requires two diesel generators (DGs) capable of supplying the onsite Class 1E power distribution subsystem(s) to be OPERABLE in MODE 1. Additionally, Unit 1 LCO 3.8.1 requires the Unit 2 EDG(s) to be capable of supporting the associated equipment required to be OPERABLE by LCO 3.7.8, Essential Service Water (ESW) System [Bl]. If both Unit 1 ESW trains are cross-tied to Unit 2, then the two Unit 2 EDGs are required to be OPERABLE. The maximum COMPLETION TIME allowed to restore an inoperable EOG to OPERABLE status in MODE 1 is 14 days. With this COMPLETION TIME not met, then the affected Unit is required to be in MODE 3 in 6 hours and MODE 5 in 36 hours. Due to the discovery that both EOG failures were a result of a failure of the DRU, the 2AB EOG was determined to be inoperable from the time the original condition was discovered on 05/21/2024 at 2115, until the time it successfully passed a surveillance after the DRU was replaced on 7/24/2024 at 2300. The period of time that the 2AB EOG was determined to be INOPERABLE exceeds the time allowed by LCO 3.8.1. Therefore, the identified condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a Condition prohibited by Technical Specifications, for Units 1 and 2. Additionally, during this period of time, it was determined that the redundant EOG (2CD) was INOPERABLE for surveillance and maintenance activities during the following times: 05/22/2024 21 :08 -05/22/2024 22:33 U2 CD INOPERABLE for U1 ESW surveillance 05/30/2024 07:05 - 05/30/2024 14:50 U2 CD INOPERABLE for maintenance 06/03/2024 20: 15 -06/04/2024 01 :25 U2 CD INOPERABLE for surveillance activities 07/09/2024 19:34 - 07/10/2024 00:15 U2 CD INOPERABLE for surveillance activities 07/10/2024 20:52 - 07/10/2024 21:46 U2 CD INOPERABLE for U2 ESW surveillance Additionally, LCO 3.8.1 contains a Prescribed Action to declare supported systems inoperable upon discovery of the inoperability of redundant required features concurrent with DG inoperability, with a Completion Time of 4 hours. During the time that the 2AB EOG was determined to be inoperable, there were instances where supported systems should have been declared inoperable. Therefore, during these instances, as well as the 5 instances that 2CD EOG was INOPERABLE for surveillance and maintenance activities, the identified condition is reportable per 10 CFR 50.73(a)(2)(v) as an Event or Condition which could have prevented the fulfillment of a Safety Function for Unit 2. COMPONENT 2-DGAB-DRU - 2AB EOG DRU | ML25086A101 | 0 | good
Quad Cities Nuclear Power Station | Unit 1 | Control Room Emergency Ventilation Air Conditioning System Inoperable Due to a Logic Issue | 03-27-2025 | On 01/26/2025 at 14:50, the Control Room Emergency Ventilation (CREV) Air Conditioning (AC) system was declared inoperable due to a trip of the Refrigeration Condensing Unit (RCU) feed breaker. Technical Specification (TS) 3. 7.5 Condition A was entered at that time. Control Room operators discovered that the indicating light for the RCU was not lit. An operator was dispatched and found that the feed breaker had tripped. After post maintenance testing of the breaker, TS 3.7.5 Condition A was exited on 02/07/2025 at 00:30. Initial troubleshooting narrowed down to two potential causes which includes breaker failure and loose breaker wiring. The causal product identified a design vulnerability where a simultaneous failure of a pressure switch and time delay relay could also cause the issue. The first two causes were addressed by breaker inspection and overhaul. The final cause will be addressed by replacement of a time delay relay and low suction pressure switch. This is being reported in accordance with 10 CFR 50. 73(a)(2)(v)(D), any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. NRC FORM 366A (04-02-2024) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 /rllll\oc,<.r,O: f~J·} LICENSEE EVENT REPORT (LER) ,~ CONTINUATION SHEET ..... (See NUREG-1022, R.3 for instruction and guidance for completing this form http:1/www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D 1. FACILITY NAME • 050 Quad Cities Nuclear Power Station Unit 1 • 052 | PLANT AND SYSTEM IDENTIFICATION Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate lo the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to lnfocollecls.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclea,- Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of infom1ation unless the document requesting or requiring the collection displays a currently valid 0MB control number. 2. DOCKET NUMBER YEAR 00254 2024 - 3. LE R NUMBER SEQUENTIAL NUMBER 002 REV NO. 00 General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Control Room Emergency Ventilation Air Conditioning System Inoperable Due to a Logic Issue A. CONDITION PRIOR TO EVENT Unit: 1 Reactor Mode: 1 Event Date: January 26, 2025 Mode Name: Power Operation Event Time: 1450 hours CST Power Level: 91% No systems, structures, or components that were inoperable at the start of the event contributed to the event. B. DESCRIPTION OF EVENT On January 26, 2025, at 14:50, Operations identified that there was no indicating light for the Control Room Emergency Ventilation (CREV)[VI] Refrigeration [RFU] Condensing Unit (RCU) 0-9400-102 on the Main Control Room (MCR)[NA] Panel 912-5. An operator was dispatched and found that local indications also showed the RCU to have no power and the breaker [BKR] in a tripped condition. The station entered Technical Specification (TS) 3.7.5 Condition A for an inoperable CREV Air Conditioning (AC) [ACU] system. ENS Notification #57515 was made in accordance with 10 CFR 50.72(b)(3)(v)(D) for any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. The CREV RCU is known to start with a high inrush of current. This was previously attributed to a "double start" condition where it would start once and then within seconds start again. Between 2009 and 2012, numerous trips of the CREV RCU breaker occurred. To eliminate these events a modification was installed in 2009 to add a time delay relay to the low suction pressure switch. The modification was to eliminate/reduce the number of "double starts" on the compressor and reduce the breaker tripping. In addition, the breaker dial setting was changed in 2012 from 8.1 to 9.4 to provide additional margin in the breaker trip setting. All these previous events and changes to the logic and breaker settings have made the system more robust over time. Between 2012 and 2020, and again after 2020, there were no CREV RCU breaker trip events. Because the CREV AC system is a single train system, this report is submitted in accordance with the requirements of 10 CFR 50.73(a)(2)(v)(D), which requires the reporting of an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. | ML25086A216 | 0 | good
Grand Gulf Nuclear Station | Unit 1 | Manual Scram Due to Degraded Condenser Vacuum | 04-16-2025 | On February 15, 2025, at 2240 CT, Grand Gulf Nuclear Station, Unit 1 operators initiated a manual Reactor Protection System (RPS) actuation due to degrading condenser vacuum which resulted from a loss of seal steam. Rainwater intrusion had entered the enclosure building due to degraded roofing. The water entered a load control center which caused an overcurrent and loss of power in a static inverter. The loss of the static inverter resulted in a loss of seal steam that led to a degraded condenser vacuum. All control rods were fully inserted with no complications. The cause of the event was determined to be water intrusion due to degraded roofing of the enclosure building. This report is being made in accordance with 10 CFR 50.73(a)(2)(iv)(A) for any event that resulted in manual actuation of the RPS system. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Oflicer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond https://www_nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/QL) to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER [8J 050 YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 NUMBER NO. 00416 0 052 2025 001 00 | Plant Conditions: At the time of the event Grand Gulf Nuclear Station (GGNS), Unit 1 was in MODE 1 at 84 percent power. The Division 2 Emergency Diesel Generator was inoperable due to scheduled maintenance, and all other safety systems were operable. Description of Event: On February 15, 2025, rainwater intrusion entered the enclosure building due to degraded roofing. The water entered a load control center which caused an overcurrent and loss of power in a static inverter. At 2237 CT, the loss of power to the static inverter caused a loss of seal steam and degrading condenser vacuum. At 2240 CT, a manual Reactor Protection System (RPS) actuation was initiated due to degrading condenser vacuum. All control rods fully inserted, and there were no complications. Reportability: This report is being made in accordance with 1O CFR 50.73(a)(2)(iv)(A) for any event that resulted in manual actuation of the RPS system. Cause(s): The direct cause of the event was water intrusion due to degraded enclosure building roofing which entered the load control center and caused an overcurrent condition and loss of power to the static inverter. Corrective Actions: Completed Actions: -Restored the function of the enclosure building roof drains. -Replaced damaged Load Center Bus components Planned Actions: -Replace enclosure building roof. -Update preventative maintenance instructions for roof inspections to ensure that degradation is identified. -Review all single power source inverters to identify and correct any single point vulnerabilities. Safety Significance: There were no actual safety consequences associated with this condition. Plant systems responded as designed and the unit was brought to Mode 3 by Control Room Operators. Previous Similar Events: None identified. | ML25106A148 | 0 | good
i | Unknown Unit | Inoperability of Keowee Hydroelectric Unit Due to Legacy Deficiencies in Generator Exciter Speed Switch Calibration Procedure Resulting in a Condition Prohibited by Technical Specifications | 04-21-2025 | On 2/20/2025, Keowee Hydroelectric Station Unit 1 (KHU-1) was determined to be inoperable based on observed generator excitation time exceeding design basis values. Troubleshooting determined that speed switches responsible for automatically initiating generator excitation during KHU startup were not fully calibrated following planned replacement on 2/18/2025 due to a legacy procedure deficiency and the scope of post-maintenance testing (PMT) was inadequate to detect the incomplete calibration. The switches removed on 2/18/2025 were reinstalled, correct excitation response timing verified, and KHU-1 was restored to operable on 2/21/2025. Planned corrective actions include speed switch calibration procedure revisions to correct the procedure deficiencies and PMT scope, reviews for similar deficiencies in other instrument procedures, and reviews for adequacy of PMT scope for other complex hardware configurable electronic devices. This event is reportable under 10 CFR 50.73(a)(2)(i)(B) as an Operation or Condition Prohibited by Technical Specifications. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION (04-02-2024) LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME Oconee Nuclear Station Unit 1 050 2. DOCKET NUMBER 00269 3. LER NUMBER YEAR 2025 SEQUENTIAL NUMBER - 001 REV NO. - 00 052 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. BACKGROUND At Oconee Nuclear Station (ONS), the Keowee Hydroelectric Station (KHS) [EK] serves the emergency power function typically performed by diesel generators [DG] at other nuclear facilities. The KHS consists of two (2) hydroelectric turbine/generator units (KHUs) and associated support equipment and auxiliaries. Each KHU is provided with its own automatic start equipment and both KHUs undergo simultaneous automatic emergency starts during an emergency. Emergency power can be provided to the main feeder buses (MFB)[EB] of any or all three ONS Units from the Keowee Hydroelectric Station via either of two emergency power paths: The Overhead Emergency Power Path, that includes the Unit¶s Start-up Transformer [XFMR] (CT-1, CT-2, or CT-3) on each ONS Unit The Underground Emergency Power Path, that includes Transformer CT-4 [XFMR] and both Standby Buses [EB]. Emergency onsite power may also be provided to the MFB of any or all three ONS Units from a Lee Combustion Turbine (LCT) [EK] on a dedicated 100kV transmission line through Transformer CT-5 [XFMR] via one or both Standby Buses. For any ONS Unit in Modes 1-4, Technical Specification (TS) 3.8.1 specifies that two KHUs be operable with one capable of automatically providing power through the Underground Emergency Power Path to both MFB via the Standby Bus and the other capable of automatically providing power through the Overhead Emergency Power Path to both MFB. An operable KHU and its required emergency power path are required to be able to provide sufficient power within specified limits of voltage and frequency within 23 seconds after an emergency start initiate signal. EVENT DESCRIPTION All times are Eastern Standard Time. On 2/18/2025, ONS Units 1, 2, and 3 were all in Mode 1 operating at approximately 100% full power, KHU-1 aligned as the Overhead KHU, and KHU-2 aligned as the Underground KHU. At 08:14, KHU-1 was removed from service for a planned maintenance outage. An item in the scope of the planned maintenance was planned replacement of speed switches in the KHU-1 generator exciter control circuit. These switches initiate generator field energization during KHU startup once the KHU reaches a preset speed. Following completion of maintenance and operational checks, KHU-1 was declared operable at 22:36. An alignment swap of the KHUs was completed at 23:09, resulting in KHU-1 being aligned as the Underground KHU and KHU- 2 being aligned as the Overhead KHU. During the normal operational check of KHU-1 performed on 2/18/2025 following maintenance, operators noted that KHU-1 generator excitation seemed to take longer than usual. However, no unexpected alarms were received. Operators continued to monitor performance of KHU-1 during normal commercial startups over the next few shifts. On 2/20/2025, Engineering was contacted to evaluate the KHU-1 startup performance. Data review indicated that a delay KHU-1 generator excitation ranged from approximately 50 seconds to as much as approximately 2 minutes during normal, non-emergency starts. Engineering confirmed that the excitation logic was the same for normal and emergency start and that, while KHU-1 continued to be capable of starting and supplying emergency power, the observed additional time delay challenged the ability of KHU-1 to meet the requirement to provide emergency power within 23 seconds of receipt of an emergency start signal. | ML25111A260 | 0 | good
Limerick Generating Station | Unit 1 | Bypass Leakage on the B Train of Standby Gas Treatment System HEPA Filters Exceeded Technical Specification Value | 04-21-2025 | 12.Licensee Contact for this LER Licensee Contact Phone Number (Include area code) Jordan Rajan 610-718-3400 13.Complete One Line for each Component Failure Described in this Report Cause System Component Manufacturer Reportable to IRIS Cause System Component Manufacturer Reportable to IRIS A BH FLT A220 Yes 14. Supplemental Report Expected Month Day Year 15. Expected Submission Date □✔ No □ Yes (If yes, complete 15. Expected Submission Date) 16.(cid:3)Abstract (Limit to 1326 spaces, i.e., approximately 13 single-spaced typewritten lines) On February 19, 2025, at 08:40 the B (cid:85)(cid:83)ain of Standby Gas Treatment System (SGTS) was removed from service to test the charcoal adsorber and High-Efficiency Particulate Air (HEPA) filter banks. The test identified the as-found leakage for the upstream and downstream HEPA filter banks exceeded the Technical Specification (TS) leakage allowance. The HEPA filters were replaced, and the system was satisfactor(cid:74)(cid:77)y retested. This condition was reportable per 10 CFR 50.73(a)(2)(i)(B). The B(cid:1)(cid:85)(cid:83)(cid:66)(cid:74)(cid:79)(cid:1)(cid:80)(cid:71) SGTS was previously tested on March 19, 2020, and the as-found leakage was elevated. Since the leakage was close to the TS acceptance criteria, the issue was entered into the corrective action process. The HEPA filters exceeded the leakage criteria (cid:67)(cid:70)(cid:68)(cid:66)(cid:86)(cid:84)(cid:70)(cid:1)(cid:38)(cid:79)(cid:72)(cid:74)(cid:79)(cid:70)(cid:70)(cid:83)(cid:74)(cid:79)(cid:72)(cid:1)(cid:69)(cid:74)(cid:69)(cid:1)(cid:79)(cid:80)(cid:85)(cid:1)(cid:70)(cid:79)(cid:84)(cid:86)(cid:83)(cid:70)(cid:1)(cid:78)(cid:66)(cid:74)(cid:79)(cid:85)(cid:70)(cid:79)(cid:66)(cid:79)(cid:68)(cid:70)(cid:1)(cid:88)(cid:66)(cid:84)(cid:1)(cid:84)(cid:68)(cid:73)(cid:70)(cid:69)(cid:86)(cid:77)(cid:70)(cid:69)(cid:1)(cid:66)(cid:79)(cid:69)(cid:1)(cid:70)(cid:89)(cid:70)(cid:68)(cid:86)(cid:85)(cid:70)(cid:69)(cid:1)(cid:81)(cid:83)(cid:74)(cid:80)(cid:83)(cid:1)(cid:85)(cid:80)(cid:1)(cid:70)(cid:89)(cid:68)(cid:70)(cid:70)(cid:69)(cid:74)(cid:79)(cid:72)(cid:1)(cid:85)(cid:73)(cid:70)(cid:1)(cid:53)(cid:52)(cid:1) (cid:77)(cid:74)(cid:78)(cid:74)(cid:85). An action to perform post trending analysis will be added to the Surveillance Test package to ensure the filters do not exceed the TS leakage criteria before the next scheduled performance. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported /¥,...,..,.., .,,. ... lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. \ ~ . .i g CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to ....... Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory ......+. . 0~ Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 YEAR SEQUENTIAL REV I I~ I I □ NUMBER NO. Limerick Generating Station Unit 1 352 D 052 2025 - I 001 - 00 I | Unit Condition Prior to the Event Unit 1 was in Operational Condition (OPCON) 1 (Power Operation) at approximately 100% power. Unit 2 was in Operational Condition (OPCON) 1 (Power Operation) at approximately 100% power. There were no other structures, systems or components out of service that contributed to this event. Description of the Event On February 19, 2025, at 08:40 the B (cid:87)rain of Standby Gas Treatment System (SGTS) [EIIS:BH] was removed from service to test the charcoal adsorber and High-Efficiency Particulate Air (HEPA) filter banks. Each SGTS train has two HEPA filter banks and a charcoal adsorber. The upstream HEPA filter bank removes radioactive particulates, while the charcoal adsorber removes gaseous iodine that may be present in the air stream. The downstream HEPA filter bank removes any carbon fines that may become entrained in the air stream after leaving the charcoal adsorber and providing redundant protection against failure of the upstream HEPA filter. (cid:47)(cid:72)(cid:68)(cid:78)(cid:68)(cid:74)(cid:72)(cid:3)(cid:80)(cid:88)(cid:86)(cid:87)(cid:3)(cid:69)(cid:72)(cid:3)(cid:79)(cid:72)(cid:86)(cid:86)(cid:3)(cid:87)(cid:75)(cid:68)(cid:81)(cid:3)(cid:19)(cid:17)(cid:19)(cid:24)(cid:3)(cid:83)(cid:72)(cid:85)(cid:70)(cid:72)(cid:81)(cid:87)(cid:3)(cid:87)(cid:82)(cid:3)(cid:80)(cid:72)(cid:72)(cid:87)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:55)(cid:72)(cid:70)(cid:75)(cid:81)(cid:76)(cid:70)(cid:68)(cid:79)(cid:3)(cid:54)(cid:83)(cid:72)(cid:70)(cid:76)(cid:73)(cid:76)(cid:70)(cid:68)(cid:87)(cid:76)(cid:82)(cid:81)(cid:3)(cid:11)(cid:55)(cid:54)(cid:12)(cid:3)(cid:79)(cid:76)(cid:80)(cid:76)(cid:87)(cid:3)(cid:73)(cid:82)(cid:85)(cid:3)(cid:76)(cid:81)(cid:3)(cid:83)(cid:79)(cid:68)(cid:70)(cid:72)(cid:3)(cid:83)(cid:72)(cid:81)(cid:72)(cid:87)(cid:85)(cid:68)(cid:87)(cid:76)(cid:82)(cid:81)(cid:3)(cid:68)(cid:81)(cid:71)(cid:3) (cid:79)(cid:72)(cid:68)(cid:78)(cid:68)(cid:74)(cid:72)(cid:3)(cid:87)(cid:72)(cid:86)(cid:87)(cid:76)(cid:81)(cid:74)(cid:3)(cid:82)(cid:73)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:43)(cid:40)(cid:51)(cid:36)(cid:3)(cid:73)(cid:76)(cid:79)(cid:87)(cid:72)(cid:85)(cid:3)(cid:69)(cid:68)(cid:81)(cid:78)(cid:86)(cid:17)(cid:3) The test identified the as-found leakage for the upstream HEPA filter bank was 0.11 percent and the as-found downstream HEPA filter bank leakage was 0.16 percent. The HEPA filters were replaced, and the system was retested. The system was declared operable on February 20, 2025, at 11:44. The B (cid:87)rain of SGTS was last tested on March 19, 2020. The as-found leakage of the upstream filter bank was 0.044 percent, and the as-found downstream HEPA filter bank was 0.046 percent. Since the leakage was close to the TS acceptance criteria, the issue was entered into the corrective action process. A note was added to the Issue Report (IR 4328138) stating the HEPA filters should be replaced prior to the next performance of the test. The exact time the B (cid:87)rain of SGTS was inoperable cannot be determined. (cid:37)(cid:68)(cid:86)(cid:72)(cid:71)(cid:3)(cid:82)(cid:81)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:79)(cid:72)(cid:68)(cid:78)(cid:68)(cid:74)(cid:72)(cid:3)(cid:80)(cid:72)(cid:68)(cid:86)(cid:88)(cid:85)(cid:72)(cid:71)(cid:3)(cid:76)(cid:81)(cid:3)(cid:21)(cid:19)(cid:21)(cid:19)(cid:3)(cid:68)(cid:81)(cid:71)(cid:3) (cid:87)(cid:75)(cid:72)(cid:3)(cid:68)(cid:86)(cid:16)(cid:73)(cid:82)(cid:88)(cid:81)(cid:71)(cid:3)(cid:79)(cid:72)(cid:68)(cid:78)(cid:68)(cid:74)(cid:72)(cid:3)(cid:80)(cid:72)(cid:68)(cid:86)(cid:88)(cid:85)(cid:72)(cid:71)(cid:3)(cid:76)(cid:81)(cid:3)(cid:21)(cid:19)(cid:21)(cid:24)(cid:15)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:79)(cid:72)(cid:68)(cid:78)(cid:68)(cid:74)(cid:72)(cid:3)(cid:79)(cid:76)(cid:78)(cid:72)(cid:79)(cid:92)(cid:3)(cid:72)(cid:91)(cid:76)(cid:86)(cid:87)(cid:72)(cid:71)(cid:3)(cid:73)(cid:82)(cid:85)(cid:3)(cid:74)(cid:85)(cid:72)(cid:68)(cid:87)(cid:72)(cid:85)(cid:3)(cid:87)(cid:75)(cid:68)(cid:81)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:55)(cid:54)(cid:3)(cid:68)(cid:70)(cid:70)(cid:72)(cid:83)(cid:87)(cid:68)(cid:81)(cid:70)(cid:72)(cid:3)(cid:70)(cid:85)(cid:76)(cid:87)(cid:72)(cid:85)(cid:76)(cid:68)(cid:3)(cid:73)(cid:82)(cid:85)(cid:3)(cid:74)(cid:85)(cid:72)(cid:68)(cid:87)(cid:72)(cid:85)(cid:3) (cid:87)(cid:75)(cid:68)(cid:81)(cid:3)(cid:86)(cid:72)(cid:89)(cid:72)(cid:81)(cid:3)(cid:71)(cid:68)(cid:92)(cid:86)(cid:17) Additionally, since the exact date the B (cid:87)rain of SGTS became inoperable cannot be determined, there were times that the A (cid:87)(cid:85)(cid:68)(cid:76)(cid:81)(cid:3)(cid:82)(cid:73)(cid:3)SGTS was (cid:79)(cid:76)(cid:78)(cid:72)(cid:79)(cid:92)(cid:3)inoperable while the B(cid:3)(cid:87)(cid:85)(cid:68)(cid:76)(cid:81)(cid:3)(cid:82)(cid:73) SGTS was also inoperable. The action for both SGTS trains being inoperable was not entered. This condition is reportable per 10 CFR 50.73(a)(2)(i)(B). Analysis of the Event The HEPA filters failed (cid:69)(cid:72)(cid:70)(cid:68)(cid:88)(cid:86)(cid:72)(cid:3)(cid:40)(cid:81)(cid:74)(cid:76)(cid:81)(cid:72)(cid:72)(cid:85)(cid:76)(cid:81)(cid:74)(cid:3)(cid:71)(cid:76)(cid:71)(cid:3)(cid:81)(cid:82)(cid:87)(cid:3)(cid:72)(cid:81)(cid:86)(cid:88)(cid:85)(cid:72)(cid:3)(cid:80)(cid:68)(cid:76)(cid:81)(cid:87)(cid:72)(cid:81)(cid:68)(cid:81)(cid:70)(cid:72)(cid:3)(cid:90)(cid:68)(cid:86)(cid:3)(cid:86)(cid:70)(cid:75)(cid:72)(cid:71)(cid:88)(cid:79)(cid:72)(cid:71)(cid:3)(cid:68)(cid:81)(cid:71)(cid:3)(cid:72)(cid:91)(cid:72)(cid:70)(cid:88)(cid:87)(cid:72)(cid:71)(cid:3)(cid:83)(cid:85)(cid:76)(cid:82)(cid:85)(cid:3)(cid:87)(cid:82)(cid:3)(cid:72)(cid:91)(cid:70)(cid:72)(cid:72)(cid:71)(cid:76)(cid:81)(cid:74)(cid:3) (cid:87)(cid:75)(cid:72)(cid:3)(cid:55)(cid:54)(cid:3)(cid:79)(cid:76)(cid:80)(cid:76)(cid:87)(cid:17) (cid:3)The issue report for the degraded high HEPA filter bank leakage was not flagged as system health issue and the subsequent reviews did not identify the challenge to the TS limit. | ML25111A262 | 0 | good
Browns Ferry Nuclear Plant | Unit 3 | Reactor Coolant System Pressure Boundary Leakage Identified from Recirculation System Small Bore Piping | 04-24-2025 | On June 3, 2024, an increase in Browns Ferry (BFN) Unit 3 Drywell Unidentified Leakage was identified. This condition was monitored and trended from June 3, 2024, to October 4, 2024. The unidentified leakage came from two different sources. Prior to shutdown, total drywell unidentified leakage was approximately 1.0 gallon per minute. On October 5, 2024, at 0456, during the initial drywell entry of BFN Unit 3 Planned Outage 13 for replacement of a suspected defective fuel bundle, the drone operator observed water leaking from the elbow near the 1-inch sensing line off the 3B recirculation pump. In addition to this, the drone operator also observed water leaking from near the 3A recirculation pump vent line on a 3/4-inch elbow. The direct cause of the code class boundary leakage were cracks in two socket welds. The corrective actions for the direct cause were to replace the small bore piping elbows. The apparent cause was high-cycle fatigue. The corrective actions to address this are to implement modifications on the 3A and 3B Recirculation Pump Vent and Seal Vent Line Piping and sensing lines. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ☒ 050 SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 3 00296 NUMBER NO. ☐ 052 2024 - 004 - 01 | I. Plant Operating Conditions before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN) Unit 3 was in Mode 4 at 0 percent power. II. Description of Event A. Event Summary On June 3, 2024, an increase in BFN Unit 3 Drywell Unidentified Leakage was identified. This condition was monitored and trended from June 3, 2024, to October 4, 2024. The unidentified leakage came from two different sources. Prior to shutdown, total drywell unidentified leakage was approximately 1.0 gallons per minute (gpm). On October 21, 2024, Tennessee Valley Authority (TVA) completed a Past Operability Evaluation (POE). Technical Requirements Manual (TRM) Limiting Condition of Operability (LCO) 3.4.3, Structural Integrity states that the structural integrity of American Society of Mechanical Engineers (ASME) Code Class 1, 2, and 3 equivalent components shall be maintained in accordance with Technical Specification Requirement (TSR) 3.4.3.1 and TSR 3.4.3.2 throughout the life of the plant. Technical Specification (TS) 3.4.4 LCO (a) states that Reactor Coolant System (RCS) operational leakage shall be limited to no pressure boundary leakage while in Modes 1, 2, and 3. The structural integrity of the Reactor Coolant Pressure Boundary (RCPB) was inoperable for both TRM LCO 3.4.3 and TS LCO 3.4.4 (a) due to the cracks in the 1-inch elbow on the high pressure side sensing line for 3-PDT-068-0082 (BFN-3-VTV-068-0255) and the 3/4-inch recirculation pump vent elbow weld, which are both ASME Code Class 2 pipes. The starting date of inoperability is June 3, 2024, when Unit 3 showed an increase in Drywell Unidentified Leakage, and the ending date is October 5, 2024, when Unit 3 shutdown for BFN Unit 3 Planned Outage 13 (F313) and the sources of the leaks were discovered. The Tennessee Valley Authority is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant’s Technical Specifications. | ML25114A051 | 0 | good
Limerick Generating Station | Unit 2 | HPCI Valve Isolated During a Surveillance Test Due to a Degraded Test Connector | 05-02-2025 | On March 03, 2025, at 10:44 during planned surveillance testing, the High Pressure Coolant Injection (HPCI) system Turbine Exhaust Line Vacuum Breaker Outboard primary containment isolation valve (PCIV) closed. The valve closed due to a degraded cannon plug connector that caused a short within the Emergency Core Cooling System (ECCS) Contact Test Unit being used for the test. The test equipment was removed, and the valve was re-opened. This event is being reported because it resulted in an unplanned inoperability of a single train safety system that could have prevented fulfillment of a safety function. An eight (8) hour ENS notification was completed on March 03, 2025, at 18:09 (ENS 57582). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024> Estimated burden per response to oomply with this mandatory collection request: 00 tiours. Reported lesso11S learned are incorporated into the licensing process and red back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to Ille FOIA, Library, and lnfonmatioo Collecllons Brandl (T-6 A1 0Ml, U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resourte@nrc.gov, and the 0MB reviewer al: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nudear Regulatory Commission, 72517th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor. and a person is not required lo http:l/www.nrc govtreadjng-rmtdoc-collectionslnuregs/staff/sr10221r3/l respond to, a collection of information unless the document requesting or requiring Ille collection displays a C1Jrrenlly valid 0MB conlrol number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ~------------~oo 050 r:Y:E:A:R7 SEQUENTIAL REV ~-I NUMBER 1-NO0. Limerick Generating Station, Unit 2 I □ 052 353 I 001 | Unit Condition Prior to the Event Prior to the event, Unit 2 was in Operational Condition (OPCON) 1 (Power Operation) at approximately 100% power. There were no other structures, systems, or components out of service that contributed to this event. Description of the Event On March 03, 2025, a surveillance test was being conducted for Unit 2 High Pressure Coolant Injection (HPCI) System (BJ] to verify that the HPCI logic circuit actuated on a simulated HPCI Steam Supply Pressure- Low signal. At 10:44, the HPCI Turbine Exhaust Line Vacuum Breaker Outboard primary containment isolation valve (PCIV) closed and the HPCI system was declared inoperable. The test was aborted by removing the ECCS Contact Test Unit (test box), resetting the isolation, and restoring operability of the system. The HPCI System was returned to service on March 03, 2025, at 13:51. An eight (8) hour ENS notification (57582) was completed on March 03, 2025, at 18:09 hours. Analysis of the Event The HPCI System was operable during the performance of the instrument testing. The Limerick Technical Specifications allows the system to remain operable for up to eight hours during the instrument testing provided at least one operable channel in the same trip system is monitoring that parameter. During the instrument testing, when the isolation signal was actuated (Low Steam Line Pressure) the HPCI Turbine Exhaust Line Vacuum Breaker Outboard PCIV closed rendering HPCI inoperable. Immediately following the isolation, the ECCS Contact Test Unit was removed from the HPCI System circuit by unplugging the cannon plug from the panel. Resistance checks were performed of the unit and one electrical short circuit was found. This electrical short circuit resulted in the closure of HPCI Turbine Exhaust Line Vacuum Breaker Outboard PCIV. Safety Consequence There was no actual safety consequences associated with this event and the potential safety consequences of this event were minimal. The Reactor Core Isolation {RCIC) System, Automatic Depressurization System (ADS), Residual Heat Removal (RHR) System, and Core Spray (CS) System remained operable during the period that HPCI was inoperable. This condition resulted in a loss of safety function for the HPCI System and is reportable per 10 CFT 50. 73(a)(2)(v)(D). Cause of the Event The cannon plug connector was degraded resulting in a short within the ECCS Contact Test Unit. | ML25122A139 | 0 | good
Brunswick Steam Electric Plant (BSEP) | Unit 2 | Automatic Actuation of Containment Isolation Valves during Testing | 05-01-2025 | At approximately 14:09 Eastern Daylight Time (EDT) on March 28, 2025, with Unit 2 in Mode 2 at approximately 1% rated thermal power during reactor startup, an actuation of Group 1 Primary Containment Isolation Valves (PCIVs) occurred during performance of the Unit 2 Turbine Control/Stop Valves Tightness Test procedure. The Group 1 PCIV actuation resulted when the Turbine Stop Valves were opened (with Control Valves remaining closed) while main condenser vacuum was below 10 inches Hg. The PCIVs automatically closed as designed when the Group 1 actuation signal was received. This event resulted from legacy procedural inadequacies. Corrective actions include procedural revisions to ensure the Turbine Control/Stop Valves Tightness Test procedure is not executed with main condenser vacuum below 10 inches Hg. There was no impact on the health and safety of the public or plant personnel. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) due to valid actuation of the Primary Containment Isolation System. (See Page 2 for required number of digits/characters for each block) (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION (04-02-2024) LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME  050  052 2. DOCKET NUMBER 3. LER NUMBER Brunswick Steam Electric Plant (BSEP), Unit 2 00324 YEAR SEQUENTIAL NUMBER REV NO. 2025 - 001 - 00 | Not Found | ML25126A035 | 1 | ok
Grand Gulf Nuclear Station | Unit 1 | Automatic Emergency Diesel Generator Actuation Caused by Grid Transient | 05-13-2025 | On March 15, 2025, Grand Gulf Nuclear Station (GGNS), Unit 1 was in MODE 1 at 100 percent power with all safety systems operable. At 12:48 CDT, a grid transient caused the 17AC breaker to trip open. In response, the division Ill emergency diesel generator automatically started and repowered the 17 AC safety-related electrical bus as designed. The grid transient was caused by degraded voltage of the offsite grid. The 17 AC breaker was successfully closed after the grid transient with no further issues. No other safety systems actuated, and no radiological release occurred. All remaining offsite power sources remained energized. This report is being made in accordance with 10 CFR 50.73(a)(2)(iv)(A) for any event that resulted in automatic actuation of an emergency diesel generator. NRC ,F,O RM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024..). .... Estimated b'urden per response to comply with this mandatory collection request: 80 hours. Reported , lessons learned are incorporated into the licensing process and fed back to industry. Send comments f~'\ LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. \~.... , ~ . l CONTINUATION SHEET N ln u fo c c le o a ll r e cts R .R e e g s u o la u t r o c r e y @ nr C c. o g m ov m , i a ss n i d on t , h e 0 W M a B s h r i e n v g i t e o w n e , r a D t: C 0 MB 2 0 O 5 f 5 fi 5 ce -0 0 o 0 f 1 In , form or a tion b y a nd e R -m eg a u il lator t y o Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRG may not conduct or sponsor, and a person is not required to respond https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER C8l 050 YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 NUMBER NO. 00416 □ 052 2025 002 00 | Plant Conditions: At the time of the event Grand Gulf Nuclear Station (GGNS), Unit 1 was in MODE 1 at 100 percent power and all safety systems were operable. Description of Event: On March 15, 2025, at 12:48 CDT, a grid transient caused the 17AC breaker to trip open. In response, the division Ill emergency diesel generator (EOG) automatically started and repowered the 17A C safety-related electrical bus as designed. No other safety systems actuated, and no radiological release occurred. All remaining offsite power sources remained energized. Reportability: This report is being made in accordance with 10 CFR 50.73(a)(2)(iv)(A) for any event that resulted in automatic actuation of an emergency diesel generator. Cause(s): A degraded voltage of the offsite grid caused the event to occur. Corrective Actions: Completed Actions: - After the grid transient passed, the 17A C offsite source feeder breaker was successfully closed in and the division Ill EOG was secured with no further issues. Safety Significance: There were no actual safety consequences associated with this condition. Plant systems responded as designed and the plant remained at 100 percent power. Previous Similar Events: None identified. NRG FORM 366A (04-02-2024) Page 2 of 2 | ML25133A192 | 0 | good
Edwin I. Hatch Nuclear Plant | Unit 2 | 2A Emergency Diesel Generator Inoperable Due to Inadvertent Overspeed Trip | 05-23-2025 | The 2A Emergency Diesel Generator (EDG) unexpectedly tripped during a test on 2/13/2025, due to its emergency overspeed switch (EOS) falsely signaling an overspeed condition. An initial investigation and operability review found no firm evidence suggesting that the 2A EDG was unable to perform its safety function prior to the trip. Subsequently, the EOS was replaced, the 2A EDG successfully completed its operability surveillance on 2/15/2025, and the original EOS was sent off for failure analysis. On 3/26/2025, at 14:53 EDT, Unit 2 was operating at approximately 22 percent power in MODE 1 when results from the failure analysis of the EOS for the 2A EDG were received. Contrary to the findings of the initial investigation and operability review, the analysis revealed that the condition experienced with the EOS during the 2/13/2025 test most likely caused the 2A EDG to be inoperable longer than allowed by Technical Specifications (TS). Additionally, during the time period the 2A EDG was inoperable, the 1B EDG was tagged out in support of planned maintenance for the standby plant service water pump resulting in two EDGs being inoperable for Unit 2 longer than allowed by TS. Having two EDGs inoperable for the same unit resulted in an event or condition that could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/l displays a currently valid 0MB control number. ~1. FAC-ILITY- NAM-E ------~ ~ 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV Edwin I. Hatch Nuclear Plant Unit 2 00366 □ NUMBER NO. ~-I 1-G □ 052 I 002 I | EVENT DESCRIPTION The 2A Emergency Diesel Generator (EOG) (EIIS: DG) unexpectedly tripped during a test on 2/13/2025, due to its emergency overspeed switch (EOS) falsely signaling an overspeed condition. An initial investigation and operability review found no firm evidence suggesting that the 2A EOG was unable to perform its safety function prior to the trip. Subsequently, the EOS was replaced, the 2A EOG successfully completed its operability surveillance on 2/15/2025, and the original EOS was sent off for failure analysis. On 3/26/2025, at 14:53 EDT, Unit 2 was operating at approximately 22 percent power in MODE 1 when results from the failure analysis of the EOS for the 2A EOG were received. Contrary to the findings of the initial investigation and operability review, the analysis revealed that the condition experienced with the EOS during the 2/13/2025 test most likely caused the 2A EOG to be inoperable from 6/6/2024, the date the EOS was installed, to when the 2A EOG successfully completed its operability surveillance on 2/15/2025, which is longer than allowed by Technical Specifications {TS) 3.8.1.B. Additionally, while reviewing the 2A EOG EOS trip event, it was discovered that the 1 B EOG {EIIS: DG) was tagged out for eighteen hours and forty-nine minutes in support of planned maintenance for the standby plant service water pump on 6/21/2024, during the same time the 2A EOG was inoperable. The overlapping time of the inoperabilities of the 2A EOG and the 1 B EOG resulted in two EDGs being inoperable for Unit 2 longer than allowed by TS 3.8.1.F. Having two EDGs inoperable for the same unit resulted in an event or condition that could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident. FAILED COMPONENTS Name: Emergency Overspeed Switch (EOS) Master Parts List Number: N/A; the EOS is a subcomponent of the 2A EOG (2R43S001A) Manufacturer: Honeywell Model: BZE6-RQ Type: Limit Switch EVENT CAUSE ANALYSIS Analysis showed that a loose retaining nut on the EOS impacted switch operation and caused the EOS to falsely signal an overspeed condition during the 2/13/2025 test. The EOS installed near the actuation point also contributed to the inadvertent trip of the 2A EOG. SAFETY ASSESSMENT There were no actual safety consequences as a result of these events. However, while the 2A EOG was inoperable, both the 2C EOG and the 1 B swing EOG remained operable for Unit 2, except when TS surveillances were performed and when the 1 B EOG was required to be tagged out for eighteen hours and forty-nine minutes on 6/21/24 in support of planned maintenance for the standby plant service water pump. Due to the 2A EOG being inoperable longer than allowed by TS and the overlapping time of the inoperabilities of the 2A EOG and the 1 B EOG, resulting in two EDGs being inoperable for Unit 2 longer than allowed by TS, the completion times of TS 3.8.1.B and TS 3.8.1.F were not met. Additionally, the completion time associated with TS 3.8.1.H to be in MODE 3 in 12 hours was also not met. Therefore, these events are reportable as conditions prohibited by TS per 10 CFR 50.73(a)(2)(i)(B). Additionally, having the 2A EDG and the 18 EDG simultaneously inoperable on the same unit is a condition that could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident and is, therefore, reportable per 10 CFR 50.73(a)(2)(v)(D). | ML25143A260 | 0 | good
Browns Ferry Nuclear Plant | Unit 3 | Automatic Reactor Scram Following Main Generator Trip | 05-29-2025 | On February 8, 2025, at 2248 Central Standard Time, while at approximately 70 percent rated thermal power, Unit 3 experienced a main generator trip causing an automatic reactor scram. Plant equipment responded as expected and Unit 3 was transitioned to Mode 4. The Unit 3 isophase bus electrical fault was most likely initiated by a combination of particulate buildup on standoff insulators and elevated humidity. The root cause of the event was that the station failed to maintain an adequate maintenance strategy for the bus duct system due to perceived system reliability. Repairs were made to the main generator bus which allowed the reactor to restart and sync to the electrical grid on March 6, 2025. Actions planned include revising the applicable Preventive Maintenance items and procedure to inspect and clean all insulators and ensure proper grounding connections. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME ☒ 050 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 3 00296 NUMBER NO. ☐ 052 2025 - 001 - 01 | I. Plant Operating Conditions before the Event At the time of this event, Browns Ferry Nuclear Plant (BFN) Unit 3 was in Mode 1 at approximately 70 percent Rated Thermal Power (RTP). II. Description of Event A. Event Summary On February 8, 2025, at 2248 Central Standard Time (CST), while at approximately 70 percent RTP, BFN Unit 3 experienced a main generator [EL] trip causing an automatic reactor scram [JC]. Plant equipment responded as expected and Unit 3 was transitioned to Mode 4. During the scram response, there was a valid actuation of the Primary Containment Isolation System (PCIS) [JM] Groups 2, 3, 6, and 8. Upon receipt of these signals, components actuated as required. A loss of power to the 3EA and 3EB 4KV shutdown boards resulted in a valid actuation of the 3A and 3B emergency diesel generators (EDGs) [EK] which successfully re-energized the boards as designed. The Tennessee Valley Authority (TVA) is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(iv)(A), as an automatic actuation of the Reactor Protection System (RPS), the PCIS, and the EDGs. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components whose inoperability contributed to this event. | ML25149A021 | 0 | good
Monticello Nuclear Generating Plant | Unknown Unit | Low Pressure Coolant Injection Inoperable Due To Motor Valve Failure | 05-30-2025 | On June 28, 2024 at 0110 CDT, Monticello Nuclear Generating Plant was in Mode 1 at 100 percent power and performing OSP-RHR-0556 “Residual Heat Removal (RHR) Water Fill Verification” Technical Specification Surveillance Procedure. When the RHR Low Pressure Coolant I Injection (LPCI) Motor Valve MO-2012 "RHR Division 1 LPCI Injection Outboard Valve" was attempted to be cycled, the Outboard Motor I Valve opened approximately one inch then stopped. With the Outboard Motor Valve incapable of opening, the A LPCI injection path was inoperable for injection as an Emergency Core Cooling system; and due to the plant design of the LPCI Loop Select Logic, this rendered both I subsystems of LPCI inoperable. Subsequent evaluation determined that the Outboard Motor Valve was considered inoperable when it was I configured closed based on the potential to have Reactor pressure on the inboard side of the valve due to leakage past the associated RHR I Division 1 LCPI Injection Inboard Motor Valve. I The cause of the event was that the Outboard Motor Valve's motor pinion was not secured to the motor shaft because an incorrect-sized set screw was installed. The shorter motor pinion set screw relaxed, allowing the motor pinion to move axially along the motor shaft until it no longer engaged the worm shaft clutch gear. I On June 29, 2024, the Outboard Motor Valve's motor pinion was adjusted back into position on the motor shaft. On August 7, 2024, the I incorrect motor pinion set screw on the Outboard Motor Valve was replaced with the correct set screw. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 YEAR SEQUENTIAL REV NUMBER NO. Monticello Nuclear Generating Plant 263 I 2024 052 - 002 - 01 | EVENT DESCRIPTION On June 28, 2024 at 0110 CDT, Monticello Nuclear Generating Plant (MNGP) was in Mode 1 at 100 percent power and performing OSP-RHR-0556 “Residual Heat Removal (RHR) Water Fill Verification” Technical Specification Surveillance Procedure. When the RHR Low Pressure Coolant Injection (LPCI) [EIIS CODE: BO] Motor Valve MO-2012 “RHR I Division 1 LPCI Injection Outboard Valve” was attempted to be opened via the control room hand switch, the Outboard I Motor Valve opened approximately one inch then stopped. With the Outboard Motor Valve incapable of opening, the A LPCI injection path was inoperable for injection as an Emergency Core Cooling system; and due to the plant design of the LPCI Loop Select Logic, this rendered both subsystems of LPCI inoperable. Specifically, if the B Recirc loop was I determined to be broken, the automatic logic would be incapable of opening the path to the A LPCI injection path and I neither division would automatically inject. Subsequent evaluation determined that the Outboard Motor Valve was I inoperable when it was configured closed based on the potential to have Reactor pressure on the inboard side of the I valve due to leakage past the associated Inboard Motor Valve MO-2014 "RHR Division 1 LCPI Injection Inboard valve." This event is reportable per 10 CFR 50.73(a)(2)(i)(B) for a condition prohibited by Technical Specifications and 10 CFR I 50.73(a)(2)(v)(B) and 10 CFR 50.73(a)(2)(v)(D) for an event or condition that could have prevented the fulfillment of a I safety function of structures or systems that are needed to remove residual heat and mitigate the consequences of an accident based on the safety function at the RHR LPCI system level. This issue was evaluated for a Safety System Functional Failure (SSFF) in accordance with NEI 99-02. This event is a Safety System Functional Failure (SSFF) due to meeting reporting criteria per 10 CFR 50.73(a)(2)(v)(B) and 10 CFR 50.73(a)(2)(v)(D). DATES AND APPROXIMATE TIMES OF MAJOR OCCURANCES I • October 18, 2023 at 1407 CDT: The Outboard Motor Valve was closed due to leakage past the Inboard Motor Valve. I I • October 22, 2023 at 0207 CDT: The required completion time to be in Mode 3 due to Technical Specification 3.5.1 Condition F, as directed by Condition D. I I • November 15, 2023 at 1619 CST: The Outboard Motor Valve was opened. I • April 14, 2024 at 1455 CDT: The Outboard Motor Valve was closed due to leakage past the Inboard Motor Valve. I • April 18, 2024 at 0255 CDT: The required completion time to be in Mode 3 due to Technical Specification 3.5.1 I Condition F, as directed by Condition D. I • June 27, 2024 at 2158 CDT: Technical Specification 3.5.1 Condition D entered for Technical Specification I Surveillance Procedure OSP-RHR-0556. I • June 28, 2024 at 0110 CDT: Event Date. The Outboard Motor Valve was incapable of fully opening during Technical I Specification Surveillance Procedure SP-RHR-0556. I • June 29, 2024 at 1533 CDT: Technical Specification 3.5.1 Condition D exited following completion of maintenance on the Outboard Motor Valve. I I • August 05, 2024: Identification that the adjustment made to the Outboard Motor Valve’s motor pinion, completed on June 29, 2024, should not have been possible if the motor pinion had been installed per the vendor technical I manual. I • August 07, 2024 at 0500 CDT: Technical Specification 3.5.1 Condition B and D entered for investigation of and I repairs to the Outboard Motor Valve. I • August 08, 2024 at 1058 CDT: Technical Specification 3.5.1 Condition B and D exited following installation of the I correct motor pinion set screw on the Outboard Motor Valve. I I • April 03, 2025: Determination that the Outboard Motor Valve should have been considered inoperable when it was I configured closed with the incorrect motor pinion set screw and had the potential to have Reactor pressure on the I inboard side of the valve due to leakage past the Inboard Motor Valve. NR C FORM 366A (04-02-2024) Page 2 of 4 | ML25150A333 | 0 | good
Quad Cities Nuclear Power Station | Unit 1 | Loss of Suppression Chamber Vacuum Breaker Safety Function due to Configuration Control Error | 06-04-2025 | On 04/05/2025 at 04:00, Operations determined that a mispositioned manual isolation valve made both trains of Reactor Building to Suppression Chamber Vacuum Breakers simultaneously inoperable. The vacuum breaker inoperability could have prevented fulfillment of primary containment function following a design-basis accident with no operator intervention. The valve was not properly repositioned following refuel outage activities in March of 2025. The cause of the valve mispositioning was inadequate standards in Procedure Use and Adherence during refuel outage activities. Immediate corrective action was to open the isolation valve. Subsequent actions will be to make the valve a locked- open valve, to improve related procedures, and to provide training related to this event. This is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D), any event or condition that could have prevented the fulfillment of the safety function of systems needed to mitigate the consequences of an accident, and 1 O CFR 50.73(a)(2)(i)(B), any operation or condition prohibited by Technical Specifications. NRC FORM 366A (04-02-2024) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME ■ 050 Quad Cities Nuclear Power Station Unit 1 □ 052 | PLANT AND SYSTEM IDENTIFICATION Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and led back to industry. Send comments regarding burden estimate to the FOIA. Library. and lnlormation Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission. Washington, DC 20555·0001, or by email to lnlocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office ol Information and Regulatory Aflairs, (3150-0104), Alln: Desk Ollicer for the Nuclear Regulatory Commission. 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection ol information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 2. DOCKET NUMBER YEAR 00254 2025 - 3. LE R NUMBER SEQUENTIAL NUMBER 004 REV NO. 00 General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Loss of Suppression Chamber Vacuum Breaker Safety Function due to Configuration Control Error A. CONDITION PRIOR TO EVENT Unit: 1 Reactor Mode: 1 Event Date: May 5, 2025 Mode Name: Power Operation Event Time: 0400 hours CST Power Level: 100% No systems, structures, or components that were inoperable at the start of the event contributed to the event. B. DESCRIPTION OF EVENT On 04/05/2025 at 04:00, Operations discovered that manual isolation valve [V] 1-1601-84B, U1 Torus Line 1- 1635B-1/2 inch LA Root Valve, was in the closed position. Closure of the 1-1601-84B (-84B) valve prevents operation of air operated Reactor Building to Suppression Chamber Vacuum Breakers [VACB][BF] 1-1601- 20A and 1-1601-20B, hereafter denoted as "the vacuum breakers." The -84B valve isolated differential pressure sensors [DPS] from the suppression pool atmosphere, subsequently preventing the operation of solenoid valves [PDSV] providing air to the vacuum breakers. Technical Specification {TS) 3.6.1.7, Reactor Building to Suppression Chamber Vacuum Breakers, Conditions C and E were entered for each vacuum breaker. Condition C is for one line with one or more reactor building to suppression chamber vacuum breakers inoperable for opening; Condition E is for two lines with one or more vacuum breakers inoperable for opening. The -84B valve was opened, and TS 3.6.1.7 was exited on 04/05/2025 at 0400. The vacuum breaker inoperability could have prevented fulfillment of primary containment function following a design-basis accident with no operator intervention. Additionally, the TS 3.6.1.7 Condition E Completion Time of 1 hour was not met based on the Required Action to restore vacuum breakers in one of two lines to operable status following entry into Mode 2. Also, TS Limiting Condition for Operation (LCO) 3.0.4 was not met when Mode 2 was entered without any specific allowances or risk assessments performed for the vacuum breaker inoperability related to TS 3.6.1.7. During the refuel outage, March 10, 2025, through April 1, 2025, Local Leak Rate Tests (LLRTs) and valve maintenance activities included closure of the -84B valve. At the conclusion of the as-left LLRT on 03/28/25, steps to open the -84B and other valves were annotated that they were to be left closed per the Unit Supervisor, with a Senior Reactor Operator (SRO) having an expectation that subsequent outage clearance order activities would later recover the desired valve position. No peer reviews were performed on the incomplete steps, nor were any verifications made related to the applicable clearance order, resulting in the isolation valves remaining closed the duration of the refuel outage. | ML25155A098 | 0 | good
River Bend Station | Unit 1 | Human Performance Error Results in Manual Reactor Trip | 06-05-2025 | At 1607 CDT on April 8, 2025, with River Bend Station, Unit 1 operating in Mode 1 at 81 % power, control room operators responded to alarms received for a total loss of normal service water. The control room operators entered AOP-0009, Loss of Normal Service Water, and subsequently inserted a manual reactor trip. The direct cause of the loss of normal service water was the result of non-licensed operators failing to close SWP- MOV55A block valve, SWP-V3302, prior to post maintenance testing. Two causal factors were identified during the investigation: (1) Non-licensed operators did not appropriately apply human performance tools and verification practices when performing equipment protection tagout task; and, (2) Operations supervisor did not ensure adequate pre-job brief in accordance with EN-OP-102 and EN-HU-102 during briefing of equipment protection tagout installation - specifically, the risks involved if the work was performed incorrectly, stop-work criteria, and the key role of engagement by both performer and peer checker. This event is reportable in accordance with 10 CFR 50.73 (a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73 (a)(2)(iv)(B). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and lnfonmation Collection Branch (T-6 A1 OM), U S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of lnfonmation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond https:/lwww.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) to, a collection of infonmation unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LERNUMBER ~ 050 YEAR SEQUENTIAL REV River Bend Station, Unit 1 NUMBER NO. 00458 0 052 2025 001 00 | Event Description At 1607 CDT on April 8, 2025, with River Bend Station (RBS), Unit 1 operating in Mode 1 at 81 % power, control room operators responded to alarms received for a total loss of normal service water [Bl]. The control room operators entered AOP-0009, Loss of Normal Service Water and subsequently inserted a manual reactor trip. The control room operators entered the appropriate post trip procedures and appropriately responded to the uncomplicated reactor trip. This event was reported on April 8, 2025, at 1911 EDT in accordance with 10 CFR 50.72(b)(2)(iv)(B) for reactor protection system actuation and 10 CFR 50.72(b)(3)(iv)(A) due to an expected reactor water level 3 isolation signal (EN 57655). Event Cause The direct cause of a loss of normal service water was the result of non-licensed operators failing to close SWP-V3302 [Bl:SHV], SWP-MOV55A block valve, prior to post maintenance testing. During post maintenance testing, maintenance personnel requested Operations to open SWP-MOV55A [Bl:ISV], Standby Cooling Tower Division 1 Return Isolation Valve, as the valve opened all normal service water pumps [Bl:P] received a low-pressure lockout condition due to an open flow path to the Standby Cooling Tower. Two causal factors were identified during the investigation: (1) Non-licensed operators did not appropriately apply human performance tools and verification practices when performing equipment protection tagout task; and, (2) Operations supervisor did not ensure adequate pre-job brief in accordance with EN-OP-102, Protective and Caution Tagging, and EN-HU-102, Human Performance Traps and Tools, during briefing of equipment protection tagout installation - specifically, the risks involved if the work was performed incorrectly, stop-work criteria, and the key role of engagement by both performer and peer checker. Safety Assessment The actual consequence of this human performance error was a loss of normal service water and a subsequent manual plant trip. Standby Service Water initiated as expected and Normal Service Water was restored 37 minutes after loss. There were no other actual consequences to general safety of the public, nuclear safety, industrial safety and radiological safety for this event. Corrective Actions Completed: • Performance management actions were taken with the operators involved in the event. In progress: • Operations Shift Managers perform standards reset blitz. • Create and implement verification challenge activity utilizing the simulator for non-licensed individuals. • Operations Management perform standards reset with Senior Reactor Operators on utilizing quizzing during reverse briefs/pre-job briefs to ensure operations clearly understand the risk, probability of one, all instructions, and components to be manipulated. The discussion will include "I own the risk" and risk presented by operator performance. Previous Occurrences No previous similar events at RBS have occurred within the past 5 years in which a component misposition results in a reactor trip. | ML25156A246 | 0 | good
Cooper Nuclear Station 298 1 of 5 | Unknown Unit | Inoperable Diesel Generator Jacket Water Pump Results in Condition Prohibited by Technical Specifications | 06-06-2025 | On April 8, 2025, with Cooper Nuclear Station (CNS) reactor in Mode 1, Power Operation, scheduled monthly surveillance testing of Diesel Generator (DG) 1 was being performed. During this test, a low jacket water (DGJW) temperature alarm was received. Initial investigation identified that the DGJW pump may not be providing sufficient cooling water to the DG. DG1 was subsequently secured and declared inoperable. During disassembly of the DGJW pump on April 9, 2025, it was discovered that the pump impeller had slipped on the shaft. Repairs were made, subsequent testing performed satisfactorily, and Operations personnel declared DG1 operable. Investigation into the pump impeller failure identified the direct cause to be that the impeller to shaft fit with an inadequate fit during pump seal replacement on February 5, 2025. DG1 was determined to have been potentially inoperable from as early as February 5, 2025 until April 8, 2025, resulting in a past operation or condition prohibited by Technical Specifications and a condition that could have prevented the fulfillment of a safety function. Corrective actions include purchase of new impellers with correct tolerances and revision to Preventative Maintenance and Vendor Manual work instructions. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process LICENSEE EVENT REPORT (LER) and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104 ), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC (See NUREG-1022, R.3 for instruction and guidance for completing this form may not conduct or sponsor, and a person is not required to respond to, a collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Cooper Nuclear Station 05000-298 NUMBER NO. 2025 001 00 | PLANT STATUS Cooper Nuclear Station (CNS) was in Mode 1, Power Operation, at 100% power at the time the condition was discovered on April 8, 2025. Diesel Generator (DG) 1 was declared inoperable due to failure of the Diesel Generator Jacket Water (DGJW) [EIIS:LB] pump [EIIS:P] during the monthly operability test. BACKGROUND The purpose of the standby (emergency) Alternating Current (AC) power system [EIIS:EK] is to provide a single failure proof source of on-site AC power adequate for maintaining the safe shutdown of the reactor following abnormal operational transients and postulated accidents. This system consists of two independent AC power sources, the Emergency Diesel Generators (EOG) [EIIS:DG]. Each DG shall be capable of automatic start at any time and capable of continued operation at rated load, voltage, and frequency until manually stopped. During normal plant operations both DGs are in standby. A DG starts automatically on a loss of coolant accident (LOCA) signal (i.e., low reactor water level signal or high drywell pressure) or on loss of voltage on a critical bus or Loss of Offsite Power (LOOP) event. The DG automatically connects to its respective bus after off-site power is tripped as a consequence of critical bus loss of voltage or degraded voltage. Each DG has an associated DGJW subsystem. The DGJW subsystem is a closed recirculating water circuit containing treated demineralized water for engine cooling. It consists of a standpipe, an engine driven pump, a heat exchanger, a bypass pump, a heater and the associated piping and instrumentation. The DGJW subsystem is required to be operable to support the associated DG operability. CNS Technical Specifications (TS) require that two EDGs be operable when the plant is in Modes 1, 2, or 3, and that one DG be operable when the plant is in Modes 4 or 5. EVENT DESCRIPTION On April 8, 2025, with CNS reactor in Mode 1, Power Operation, scheduled monthly surveillance testing of DG1 was being performed. The engine started and loaded as expected per procedure, however, at full load, the jacket water low temperature alarm [EIIS:TA] was received. Upon reading local DG1 jacket water temperature indication, the jacket water entering the engine was approximately 82 degrees F and the outlet temperature was reading approximately 182 degrees F. Expected condition is for the inlet and outlet jacket water temperatures to converge between 162-166 degrees F. | ML25157A104 | 0 | good
Columbia Generating Station | Unknown Unit | Pressure Boundary Leakage Resulting in a Technical Specification Required Plant Shutdown, Degraded Condition, and Condition Prohibited by Technical Specifications | 06-10-2025 | At 02:23 on April 12, with the unit in Mode 3 at 0 percent power, pressure boundary leakage was identified on the bonnet vent line elbow connection of the Reactor Recirculation (RRC) Pump 1B discharge isolation valve, RRC-V-67B. Leakage from the area was initially identified during a drywell entry at 15 percent reactor power and later confirmed as pressure boundary leakage during a subsequent entry in Mode 3. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(A) as a Plant Shutdown Required by Technical Specifications, 10 CFR 50.73(a)(2)(ii)(A) as a Degraded or Unanalyzed Condition that Resulted in the condition of the nuclear power plant, including its principal safety barriers being seriously degraded, and 10 CFR 50.73(a)(2)(i)(B) as an Operation or Condition Prohibited by Technical Specifications. There were no structures, systems, or components that were inoperable at the beginning of the event that contributed to the event. (cid:16)(cid:28)(cid:21)(cid:32)(cid:30)(cid:25)(cid:23)(cid:27)(cid:1)(cid:17)(cid:27)(cid:33)(cid:22)(cid:26)(cid:28)(cid:29)(cid:22)(cid:1)(cid:19)(cid:16)(cid:13)(cid:1) (cid:5)(cid:16)(cid:14)(cid:15)(cid:12) (cid:6)(cid:2)(cid:5)(cid:12)(cid:4)(cid:4)(cid:2)(cid:7)(cid:8)(cid:3)(cid:3)(cid:2)(cid:12)(cid:8)(cid:8)(cid:4)(cid:2)(cid:4)(cid:15)(cid:8)(cid:16)(cid:15)(cid:15)(cid:4) (cid:18)(cid:10)(cid:11)(cid:12) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments . :/¥ 0-"''"•"'-<,. . . . LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. E i Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET 0 t -s," ......... . 0~ <> I A n f f f o a c ir o s l , l e ( c 3 t 1 s 5 .R 0- e 0 s 1 o 0 u 4 rc ), e A @ tt n n r : c . D go e v s , k a O n f d fi c th e e r f O or M t B he r e N v u ie c w le e a r r a R t: e g O u M lat B o r O y f C fic o e m o m f i I s n s f i o o r n m , a 7 t 2 io 5 n 1 a 7 n th d S R t e re g e u t l a N to W ry , (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER I I~ (cid:374) 050 YEAR SEQUENTIAL REV NUMBER NO. Columbia Generating Station 397 □ D 052 2025 - I 001 - 00 I | Description of events: (cid:36)(cid:87)(cid:3)(cid:19)(cid:21)(cid:29)(cid:21)(cid:22)(cid:3)(cid:82)(cid:81)(cid:3)(cid:36)(cid:83)(cid:85)(cid:76)(cid:79)(cid:3)(cid:20)(cid:21)(cid:15)(cid:3)(cid:21)(cid:19)(cid:21)(cid:24)(cid:15)(cid:3)(cid:76)(cid:81)(cid:3)(cid:48)(cid:82)(cid:71)(cid:72)(cid:3)(cid:22)(cid:15)(cid:3)(cid:68)(cid:3)(cid:79)(cid:72)(cid:68)(cid:78)(cid:3)(cid:76)(cid:81)(cid:3)(cid:82)(cid:81)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:69)(cid:82)(cid:81)(cid:81)(cid:72)(cid:87)(cid:3)(cid:89)(cid:72)(cid:81)(cid:87)(cid:3)(cid:79)(cid:76)(cid:81)(cid:72)(cid:3)(cid:72)(cid:79)(cid:69)(cid:82)(cid:90)(cid:3)(cid:70)(cid:82)(cid:81)(cid:81)(cid:72)(cid:70)(cid:87)(cid:76)(cid:82)(cid:81)(cid:3)(cid:82)(cid:73)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:53)(cid:72)(cid:68)(cid:70)(cid:87)(cid:82)(cid:85)(cid:3)(cid:53)(cid:72)(cid:70)(cid:76)(cid:85)(cid:70)(cid:88)(cid:79)(cid:68)(cid:87)(cid:76)(cid:82)(cid:81)(cid:3) (cid:11)(cid:53)(cid:53)(cid:38)(cid:12)(cid:3)(cid:83)(cid:88)(cid:80)(cid:83)(cid:3)(cid:20)(cid:37)(cid:3)(cid:71)(cid:76)(cid:86)(cid:70)(cid:75)(cid:68)(cid:85)(cid:74)(cid:72)(cid:3)(cid:76)(cid:86)(cid:82)(cid:79)(cid:68)(cid:87)(cid:76)(cid:82)(cid:81)(cid:3)(cid:89)(cid:68)(cid:79)(cid:89)(cid:72)(cid:15)(cid:3)(cid:53)(cid:53)(cid:38)(cid:16)(cid:57)(cid:16)(cid:25)(cid:26)(cid:37)(cid:3)(cid:62)(cid:36)(cid:39)(cid:16)(cid:44)(cid:54)(cid:57)(cid:64)(cid:3)(cid:90)(cid:68)(cid:86)(cid:3)(cid:76)(cid:71)(cid:72)(cid:81)(cid:87)(cid:76)(cid:73)(cid:76)(cid:72)(cid:71)(cid:3)(cid:68)(cid:86)(cid:3)(cid:83)(cid:85)(cid:72)(cid:86)(cid:86)(cid:88)(cid:85)(cid:72)(cid:3)(cid:69)(cid:82)(cid:88)(cid:81)(cid:71)(cid:68)(cid:85)(cid:92)(cid:3)(cid:79)(cid:72)(cid:68)(cid:78)(cid:68)(cid:74)(cid:72)(cid:17)(cid:3)(cid:47)(cid:72)(cid:68)(cid:78)(cid:68)(cid:74)(cid:72)(cid:3) (cid:73)(cid:85)(cid:82)(cid:80)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:68)(cid:85)(cid:72)(cid:68)(cid:3)(cid:90)(cid:68)(cid:86)(cid:3)(cid:76)(cid:81)(cid:76)(cid:87)(cid:76)(cid:68)(cid:79)(cid:79)(cid:92)(cid:3)(cid:76)(cid:71)(cid:72)(cid:81)(cid:87)(cid:76)(cid:73)(cid:76)(cid:72)(cid:71)(cid:3)(cid:71)(cid:88)(cid:85)(cid:76)(cid:81)(cid:74)(cid:3)(cid:71)(cid:85)(cid:92)(cid:90)(cid:72)(cid:79)(cid:79)(cid:3)(cid:72)(cid:81)(cid:87)(cid:85)(cid:92)(cid:3)(cid:68)(cid:87)(cid:3)(cid:20)(cid:24)(cid:3)(cid:83)(cid:72)(cid:85)(cid:70)(cid:72)(cid:81)(cid:87)(cid:3)(cid:85)(cid:72)(cid:68)(cid:70)(cid:87)(cid:82)(cid:85)(cid:3)(cid:83)(cid:82)(cid:90)(cid:72)(cid:85)(cid:3)(cid:82)(cid:81)(cid:3)(cid:36)(cid:83)(cid:85)(cid:76)(cid:79)(cid:3)(cid:20)(cid:20)(cid:15)(cid:3)(cid:21)(cid:19)(cid:21)(cid:24)(cid:15)(cid:3)(cid:68)(cid:81)(cid:71)(cid:3)(cid:79)(cid:68)(cid:87)(cid:72)(cid:85)(cid:3) (cid:70)(cid:82)(cid:81)(cid:73)(cid:76)(cid:85)(cid:80)(cid:72)(cid:71)(cid:3)(cid:68)(cid:86)(cid:3)(cid:83)(cid:85)(cid:72)(cid:86)(cid:86)(cid:88)(cid:85)(cid:72)(cid:3)(cid:69)(cid:82)(cid:88)(cid:81)(cid:71)(cid:68)(cid:85)(cid:92)(cid:3)(cid:79)(cid:72)(cid:68)(cid:78)(cid:68)(cid:74)(cid:72)(cid:3)(cid:71)(cid:88)(cid:85)(cid:76)(cid:81)(cid:74)(cid:3)(cid:68)(cid:3)(cid:86)(cid:88)(cid:69)(cid:86)(cid:72)(cid:84)(cid:88)(cid:72)(cid:81)(cid:87)(cid:3)(cid:72)(cid:81)(cid:87)(cid:85)(cid:92)(cid:3)(cid:76)(cid:81)(cid:3)(cid:48)(cid:82)(cid:71)(cid:72)(cid:3)(cid:22)(cid:17)(cid:3)Technical Specification (TS) (cid:47)(cid:76)(cid:80)(cid:76)(cid:87)(cid:76)(cid:81)(cid:74)(cid:3) (cid:38)(cid:82)(cid:81)(cid:71)(cid:76)(cid:87)(cid:76)(cid:82)(cid:81)(cid:3)(cid:82)(cid:73)(cid:3)(cid:50)(cid:83)(cid:72)(cid:85)(cid:68)(cid:87)(cid:76)(cid:82)(cid:81)(cid:3)3.4.5(cid:17)(cid:68)(cid:3)(cid:85)(cid:72)(cid:84)(cid:88)(cid:76)(cid:85)(cid:72)(cid:86)(cid:3)(cid:81)(cid:82)(cid:3)(cid:83)(cid:85)(cid:72)(cid:86)(cid:86)(cid:88)(cid:85)(cid:72)(cid:3)(cid:69)(cid:82)(cid:88)(cid:81)(cid:71)(cid:68)(cid:85)(cid:92)(cid:3)(cid:79)(cid:72)(cid:68)(cid:78)(cid:68)(cid:74)(cid:72)(cid:3)(cid:76)(cid:81)(cid:3)(cid:48)(cid:82)(cid:71)(cid:72)(cid:86)(cid:3)(cid:20)(cid:15)(cid:3)(cid:21)(cid:15)(cid:3)(cid:82)(cid:85)(cid:3)(cid:22)(cid:17)(cid:3)(cid:55)(cid:72)(cid:70)(cid:75)(cid:81)(cid:76)(cid:70)(cid:68)(cid:79)(cid:3)(cid:54)(cid:83)(cid:72)(cid:70)(cid:76)(cid:73)(cid:76)(cid:70)(cid:68)(cid:87)(cid:76)(cid:82)(cid:81)(cid:3) (cid:36)(cid:70)(cid:87)(cid:76)(cid:82)(cid:81)(cid:86) (cid:22)(cid:17)(cid:23)(cid:17)(cid:24)(cid:3)C(cid:17)(cid:20) (cid:68)(cid:81)(cid:71)(cid:3)(cid:38)(cid:17)(cid:21)(cid:3)(cid:85)(cid:72)(cid:84)(cid:88)(cid:76)(cid:85)(cid:72)(cid:3)(cid:87)he unit to be in Mode 3 within 12 hours and Mode 4 in 36 hours. The unit was in Mode 3 at the time(cid:3)of(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:72)(cid:89)(cid:72)(cid:81)(cid:87). Mode 4 was entered at 09:32 on April 12, 2025. Plant Conditions: At the time of the event, the plant was (cid:76)(cid:81)(cid:3)(cid:48)(cid:82)(cid:71)(cid:72)(cid:3)(cid:22)(cid:3)at (cid:19)(cid:3)percent po(cid:90)(cid:72)(cid:85). Energy Industry Identification System (EIIS) codes are identified as [XX]. Background: On 7/1/2023 (approximately 2 weeks after startup from the previous refueling outage) an indication was received that a Reactor Coolant System (RCS) [AB] leak existed wh(cid:72)(cid:81)(cid:3)(cid:69)(cid:82)(cid:87)(cid:75)(cid:3)Containment Monitoring System Radiation Ratemeters [IK(cid:16) (cid:48)(cid:55)(cid:53)] were reading higher than normal and tracking similarly. During this time Equipment Drain Radioactive (EDR) [WK] leakage and Floor Drain Radioactive (FDR) [WK] leakage, containment temperature, and containment pressure were steady and did not indicate a leak.(cid:3)Chemistry performed an isotopic analysis of a grab sample of the containment atmosphere which did not indicate leakage.(cid:3)(cid:44)(cid:81)(cid:3)(cid:45)(cid:88)(cid:79)(cid:92)(cid:3)2023, a Technical Issues Resolution Process was initiated to analyze trends indicating potential leaks in containment.(cid:3)(cid:44)(cid:81)(cid:3)(cid:36)(cid:88)(cid:74)(cid:88)(cid:86)(cid:87) 2023, an (cid:50)perational (cid:39)ecision-(cid:48)aking (cid:44)ssue (cid:11)(cid:50)(cid:39)(cid:48)(cid:44)(cid:12)(cid:3)was created to establish RCS leakage monitoring criteria and identify trigger points with actions. The leakage remained constant throughout the operating cycle and did not challenge the TS RCS Operational limits of 5 gallons per minute of unidentified leakage, or an increase of 2 gallons per minute over 24 hours of unidentified leakage. Root Cause: Vent piping attached to the bonnet of RRC-V-(cid:25)(cid:26)B was not designed to prevent high cycle fatigue. This resulted in cyclic fatigue of a weld on a 3/4-inch vent line from the RRC-V-67B socket welded connection. This is a legacy issue associated with the original design’s lack of dynamic analysis, or with the 1996 and 1997 GE analysis and testing of small-bore piping in support of Adjustable Speed Drive modifications. (cid:36)(cid:71)(cid:77)(cid:88)(cid:86)(cid:87)(cid:68)(cid:69)(cid:79)(cid:72)(cid:3)(cid:86)(cid:83)(cid:72)(cid:72)(cid:71)(cid:3)(cid:71)(cid:85)(cid:76)(cid:89)(cid:72)(cid:3)(cid:70)(cid:82)(cid:81)(cid:87)(cid:85)(cid:82)(cid:79)(cid:86)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:86)(cid:83)(cid:72)(cid:72)(cid:71)(cid:3)(cid:82)(cid:73)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:53)(cid:53)(cid:38)(cid:3)(cid:62)(cid:36)(cid:39)(cid:64)(cid:17)(cid:3) Safety Significance: The (cid:53)(cid:72)(cid:68)(cid:70)(cid:87)(cid:82)(cid:85)(cid:3)(cid:38)(cid:82)(cid:82)(cid:79)(cid:68)(cid:81)(cid:87)(cid:3)(cid:54)(cid:92)(cid:86)(cid:87)(cid:72)(cid:80)(cid:3)(cid:11)(cid:53)(cid:38)(cid:54)(cid:12)(cid:3)(cid:62)(cid:36)(cid:37)(cid:64)(cid:3)(cid:79)(cid:72)(cid:68)(cid:78) was (cid:76)(cid:81)(cid:76)(cid:87)(cid:76)(cid:68)(cid:79)(cid:79)(cid:92)(cid:3)estimated to be between 0.05 and 0.10 gallons per minute. While the leak remained below the TS RCS(cid:3)(cid:50)(cid:83)(cid:72)(cid:85)(cid:68)(cid:87)(cid:76)(cid:82)(cid:81)(cid:68)(cid:79)(cid:3)(cid:79)(cid:76)(cid:80)(cid:76)(cid:87)(cid:86)(cid:3)(cid:73)(cid:82)(cid:85)(cid:3)(cid:88)(cid:81)(cid:76)(cid:71)(cid:72)(cid:81)(cid:87)(cid:76)(cid:73)(cid:76)(cid:72)(cid:71)(cid:3)(cid:79)(cid:72)(cid:68)(cid:78)(cid:86)(cid:3)(cid:73)(cid:85)(cid:82)(cid:80)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:87)(cid:76)(cid:80)(cid:72)(cid:3)(cid:82)(cid:73)(cid:3)(cid:76)(cid:81)(cid:76)(cid:87)(cid:76)(cid:68)(cid:79)(cid:3)(cid:76)(cid:81)(cid:71)(cid:76)(cid:70)(cid:68)(cid:87)(cid:76)(cid:82)(cid:81)(cid:3)(cid:88)(cid:81)(cid:87)(cid:76)(cid:79)(cid:3) (cid:83)(cid:82)(cid:86)(cid:76)(cid:87)(cid:76)(cid:89)(cid:72)(cid:3)(cid:76)(cid:71)(cid:72)(cid:81)(cid:87)(cid:76)(cid:73)(cid:76)(cid:70)(cid:68)(cid:87)(cid:76)(cid:82)(cid:81), (cid:76)(cid:73)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:79)(cid:72)(cid:68)(cid:78)(cid:3)(cid:75)(cid:68)(cid:71)(cid:3)(cid:76)(cid:81)(cid:70)(cid:85)(cid:72)(cid:68)(cid:86)(cid:72)(cid:71)(cid:3)(cid:68)(cid:81)(cid:71)(cid:3)(cid:72)(cid:91)(cid:70)(cid:72)(cid:72)(cid:71)(cid:72)(cid:71)(cid:3)(cid:55)(cid:54)(cid:3)(cid:88)(cid:81)(cid:76)(cid:71)(cid:72)(cid:81)(cid:87)(cid:76)(cid:73)(cid:76)(cid:72)(cid:71)(cid:3)(cid:79)(cid:72)(cid:68)(cid:78)(cid:3)(cid:85)(cid:68)(cid:87)(cid:72)(cid:3)(cid:79)(cid:76)(cid:80)(cid:76)(cid:87)(cid:86)(cid:15)(cid:3)(cid:68)(cid:81)(cid:3)(cid:82)(cid:85)(cid:71)(cid:72)(cid:85)(cid:79)(cid:92)(cid:3)(cid:86)(cid:75)(cid:88)(cid:87)(cid:71)(cid:82)(cid:90)(cid:81)(cid:3)(cid:90)(cid:82)(cid:88)(cid:79)(cid:71)(cid:3) (cid:75)(cid:68)(cid:89)(cid:72)(cid:3)(cid:69)(cid:72)(cid:72)(cid:81)(cid:3)(cid:76)(cid:81)(cid:76)(cid:87)(cid:76)(cid:68)(cid:87)(cid:72)(cid:71)(cid:3)(cid:68)(cid:81)(cid:71)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:85)(cid:72)(cid:68)(cid:70)(cid:87)(cid:82)(cid:85)(cid:3)(cid:90)(cid:82)(cid:88)(cid:79)(cid:71)(cid:3)(cid:75)(cid:68)(cid:89)(cid:72)(cid:3)(cid:69)(cid:72)(cid:72)(cid:81)(cid:3)(cid:83)(cid:79)(cid:68)(cid:70)(cid:72)(cid:71)(cid:3)(cid:76)(cid:81)(cid:3)(cid:70)(cid:82)(cid:79)(cid:71)(cid:3)(cid:86)(cid:75)(cid:88)(cid:87)(cid:71)(cid:82)(cid:90)(cid:81)(cid:3)(cid:70)(cid:82)(cid:81)(cid:71)(cid:76)(cid:87)(cid:76)(cid:82)(cid:81)(cid:3)(cid:76)(cid:81)(cid:3)(cid:68)(cid:70)(cid:70)(cid:82)(cid:85)(cid:71)(cid:68)(cid:81)(cid:70)(cid:72)(cid:3)(cid:90)(cid:76)(cid:87)(cid:75)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:55)(cid:54)(cid:17)(cid:3) Immediate Corrective Actions: The RRC-V-67B weld leak was re(cid:83)(cid:68)(cid:76)(cid:85)(cid:72)(cid:71)(cid:17) | ML25161A146 | 0 | good
i | Unknown Unit | Not Found | 06-18-2025 | On April 20, 2025 at 1246 CDT, while Monticello Nuclear Generating Plant was in Mode 5 for Refueling Outage 1R32, it was discovered that the Inboard Reactor Recirculation Sample Line Isolation Air Operated Valve, CV-2790, had been inoperable and potentially unable to close as required in the event of a design basis accident since Refueling Outage 1R29 in 2019. With CV-2790 inoperable, Technical Specification (TS) 3.6.1.3 “Primary Containment Isolation Valves (PCIVs)" condition A required the affected penetration be isolated within 4 hours and, if condition A was not completed, condition F required the plant to be in Mode 3 in 12 hours. Since the condition of inoperability of CV-2790 was not known upon entering Mode 2 following Refueling Outage 1R29 on May 12, 2019 at 1858 CDT, the affected penetration was not isolated. This issue is reportable under 10 CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by TS. The cause was an erroneous evaluation of the diagnostic test of CV-2790 during Refueling Outage 1R29 in 2019. The evaluation assessed the average closing friction, which was deemed acceptable, rather than evaluating the maximum closing friction. During Refueling Outage 1R32 in 2025, CV-2790 was overhauled and the subsequent diagnostic test correctly evaluated the valve’s performance, confirming its ability to meet the required closing function. A 0 0 NRC FORM 366A (04-02-2024) U.S. NUCLEAR REGULATORY COMMISSION LICENSEE EVENT REPORT (LER) CONTINUATION SHEET APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) | Not Found | ML25169A213 | 2 | ok
i | Unknown Unit | Not Found | 06-18-2025 | On May 12, 2025 at 0344 CDT, while Monticello Nuclear Generating Plant was in Mode 4 for Refueling Outage 1R32, it was discovered that the 2 Inch Inboard Torus Purge Exhaust Air Operated Valve, CV-2384, had been inoperable and potentially unable to close as required in the event of a design basis accident. With CV-2384 inoperable, Technical Specification 3.6.1.3 “Primary Containment Isolation Valves (PCIVs)" condition A required the affected penetration be isolated with the automatic valve de-activated within 4 hours and, if condition A was not completed, condition F required the plant to be in Mode 3 in 12 hours. While CV-2384 is normally closed, since the condition of inoperability of CV-2384 was not known, no valves in this penetration had been closed and de-activated when the plant had been in Modes 1, 2, or 3. This issue is reportable under 10 CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by Technical Specifications. The cause is that the lower bench set pressure of CV-2384 had insufficient closing force. In 2009, the Air Operated Valve Program engineer determined an updated lower bench set pressure, but no work order was performed to implement this new setpoint. The lower bench set pressure of CV-2384 was raised during Refueling Outage 1R32 and the valve operability was restored. NRC FORM 366A (04-02-2024) U.S. NUCLEAR REGULATORY COMMISSION LICENSEE EVENT REPORT (LER) CONTINUATION SHEET APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) | Not Found | ML25169A246 | 2 | ok
Catawba Nuclear Station | Unit 1 | lnoperability of 1B Emergency Diesel Generator due to Fuel Oil Leak | 07-21-2025 | On 4/23/2025, Catawba Unit 1 was in Mode 1 operating at approximately 100 percent power. At 0248 hours, the 1B Emergency Diesel Generator (EOG) was started for a 24 hour surveillance. Approximately 11 hours into the surveillance a leak originated on the common fuel supply line under a compression fitting. The leak was estimated to be greater than 0.5 gpm and at 1457 hours the 1 B EOG was secured and declared inoperable at 1459 hours. Repairs were made and the 1B EOG was returned to service on 4/25/2025 at 0600 hours. Investigation revealed a circumferential crack located within a tubing fitting. The crack originated prior to the attempted 24 hour surveillance but was not through-wall and there was no indication of leakage. The crack propagated during the surveillance due to high cycle fatigue. The existence of the crack, even though no leakage was present, prior to the 24-hour surveillance is evidence that the 1B EOG was inoperable for a time longer than allowed by Technical Specifications. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) as operation or condition prohibited by Technical Specifications. There was no impact to the health and safety of the public. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04..02-2024) ...... Estimated burden per response to comply with this mandatory collection request: 80 ..,,.. hours. Reported lessons learned are incorporated into the licensing process and fed l.\ . LICENSEE EVENT REPORT (LER) back to industry. Send comments regarding burden estimate to the FOIA, Library, • II and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory ~ ~ l CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by email to *••·· lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information (See NUREG-1022, R.3 for instruction and guidance for completing this form and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of 2. DOCKET NU~~ER - .s. • ;" ~~~ia·a -lililillilllilioiil . 1. - FA - CIL - ITY - N - AM - E -----------,I [lg 050 YEAR SEQUENTIAL REV 00413, 00414 ~ NUMBER NO. I-~ Catawba Nuclear Station, Units 1 and 2 0 □ -1 052 002 | BACKGROUND The following information is provided to assist readers in understanding the event described in this LER. Applicable Energy Industry Identification System [EIIS] and component codes are enclosed within brackets. Catawba's unique system and component identifiers are contained within parentheses. The onsite standby power source for each 4160 volt Engineered Safety Features (ESF) bus at Catawba is a dedicated EOG. For each unit, EDGs A and Bare dedicated to ESF buses ETA and ETB, respectively. Each EOG starts automatically on a Safety Injection signal (i.e., low pressurizer pressure or high containment pressure) or on an ESF bus degraded voltage or undervoltage signal. After the EOG has started, it will automatically tie to its respective bus after offsite power is tripped as a consequence of ESF bus undervoltage or degraded voltage, independent of or coincident with an SI signal. The EDGs will also start and operate in the standby mode without tying to the ESF bus on an SI signal alone. Following the trip of offsite power, a sequencer strips loads from the ESF bus. When the EOG is tied to the ESF bus, loads are then sequentially connected to its respective ESF bus by the automatic load sequencer. In the event of a loss of preferred power, the ESF electrical loads are automatically connected to the EDGs in sufficient time to provide for safe reactor shutdown and to mitigate the consequences of a Design Basis Accident such as a Loss of Coolant Accident (LOCA). There are also provisions to accommodate the connecting of the Emergency Supplemental Power Source (ESPS) to one train of either unit's Class 1E AC Distribution System. The ESPS consists of two 50% capacity non-safety related commercial grade EDGs. Manual actions are required to align the ESPS to the station and only one of the station's four onsite Class 1E Distribution System trains can be supplied by the ESPS at any given time. The ESPS is made available to support extended Completion Times in the event of an inoperable EOG as well as a defense-in-depth source of AC power to mitigate a station blackout event. The ESPS remains disconnected from the Class 1 E AC Distribution System unless required for supplemental power to one of the four 4.16 kV ESF buses. The primary purpose of the Diesel Fuel Oil System (FD) [DC] is to store and supply fuel to the diesel generators' engines for a period of operation of no less than seven days. Each diesel is equipped with two 45,000 gallon fuel oil storage tanks with a combined capacity sufficient to operate the diesel at full load for a period of no less than seven days, plus a margin to allow for periodic testing. Fuel oil is transferred by gravity from the storage tanks to the day tank which is located within retaining walls inside the Diesel Building. The day tank capacity is sufficient to operate the diesel generator engine for a minimum of 60 minutes at full load. The fuel oil is pumped from the day tank to the engine by an engine driven fuel oil pump. Excess fuel not consumed by the engine is returned to the day tank via the fuel return line. | ML25202A164 | 0 | good
Edwin I. Hatch Nuclear Plant | Unit 1 | Unit 1 High Pressure Coolant Injection System Inoperable | 07-29-2025 | At 2137 EDT on 06/03/2025, while Unit 1 was operating at 98% power in MODE 1, the High Pressure Coolant Injection (HPCI) turbine stop valve (TSV) failed to open as required during the testing of the auxiliary oil pump, resulting in the HPCI system being declared INOPERABLE. The cause of the TSV failing to open was a degraded reset spring located in the trip knob assembly of the valve. The reset spring was replaced, the valve was tested satisfactorily, and the safety function was restored at 0115 EDT on 06/05/2025 when the HPCI system was declared OPERABLE. The Reactor Core Isolation Cooling (RCIC) and low pressure Emergency Core Cooling Systems (ECCS) were OPERABLE during the time HPCI was INOPERABLE. However, because HPCI does not have a redundant system, the failed TSV resulting in HPCI being INOPERABLE represents a condition that could have prevented the fulfillment of the HPCI safety function to mitigate the consequences of an accident and is reportable per 50.73(a)(2)(v)(D). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/l displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ~ 050 YEAR SEQUENTIAL REV NUMBER NO. Edwin I. Hatch Nuclear Plant Unit 1 □ 052 00321 I 2025 I - I 001 1-G I I | EVENT DESCRIPTION At 2137 EDT on 06/03/2025, while Unit 1 was operating at 98% power in MODE 1, the High Pressure Coolant Injection (HPCI) (EIIS: BJ) turbine stop valve (TSV) failed to open as required during the testing of the auxiliary oil pump, resulting in the HPCI system being declared INOPERABLE. The safety function was restored at 0115 EDT on 06/05/2025 when HPCI was declared OPERABLE. The Reactor Core Isolation Cooling (RCIC) System (EIIS: BN) and the low-pressure Emergency Core Cooling Systems (ECCS) remained operable during the time the HPCI was INOPERABLE. FAILED COMPONENT INFORMATION: Master Parts List Number: 1 E41 F3053 Manufacturer: AMETEK Model Number: 69-XC-103 Type: Turbine Stop Valve (TSV) EVENT CAUSE ANALYSIS The cause of the TSV failing to open was a degraded reset spring located in the trip knob assembly of the valve. The degradation of the reset spring occurred because there was no preventive maintenance scheduled for replacing the spring. As a result, the degraded reset spring lacked the necessary spring force to assist in opening the valve. SAFETY ASSESSMENT Even though HPCI was declared INOPERABLE, the RCIC System and the low-pressure ECCS remained OPERABLE during the event. However, because HPCI does not have a redundant system, the failed TSV resulting in HPCI being INOPERABLE represents a condition that could have prevented the fulfillment of the HPCI safety function to mitigate the consequences of an accident and is reportable per 50.73(a)(2)(v)(D). There were no actual safety consequences as a result of this event, and the operating crew responded correctly. The event was within the analysis of UFSAR Chapter 15. CORRECTIVE ACTIONS The reset spring was replaced, the valve was tested satisfactorily, and the safety function was restored at 0115 EDT on 06/05/2025 when the HPCI system was declared OPERABLE. Additionally, the HPCI maintenance procedure and the HPCI twelve-year preventive maintenance overhaul are being revised to include the replacement of the reset spring. Also, the HPCI surveillance procedure is being updated with a more conservative spring force acceptance criteria. PREVIOUS SIMILAR EVENTS None. | ML25210A397 | 0 | good
Month | Unknown Unit | Loss of Power to the 1A Reactor Protection System Resulted in Multiple Invalid Primary Containment Isolations 06 13 2025 2025 002 00 08 12 2025 1 100 ✔ Jordan Rajan, Regulatory Assurance Manager 610-718-3400 B JC RLY A500 Yes ✔ 16. Abstract (Limit to 1326 spaces, i.e., approximately 13 single-spaced typewritten lines) On June 13, 2025, at 10:23, Limerick Generating Station (LGS) Unit 1 experienced a loss of power to the "A" Reactor Protection System (RPS) 120 VAC Distribution Panel that resulted in a Unit 1 "A" RPS half scram, Main Steam Isolation Valve (MSIV) half isolation signal, and primary containment isolations in multiple systems. The most probable cause of the power loss was due to an under-frequency relay spurious trip condition. The under-frequency relay was replaced and post maintenance testing was completed satisfactorily. Power was restored to the panel and all systems were returned to service. This event caused invalid primary containment isolation signals in multiple systems which is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). /~•"''"'"•,.,\ \,~ ~j ,;, ... ,. ••• + □ □ □ □ I □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ NRC FORM 366A (04-02-2024) U.S. NUCLEAR REGULATORY COMMISSION LICENSEE EVENT REPORT (LER) CONTINUATION SHEET APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) NARRATIVE NRC FORM 366A (04-02-2024) Page of 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR - SEQUENTIAL NUMBER - REV NO. 052 050 Unit Condition Prior to Event Prior to the event, Unit 1 was in Operational Condition (OPCON) 1 (Power Operation) at approximately 100 percent power. There were no other structures, systems, or components out of service that contributed to this event. Description of the Event On June 13, 2025, at 10:23, Limerick Generating Station (LGS) Unit 1 was at 100 percent power. The Unit 1 "A" (1A) Reactor Protection System (RPS) [JC] 120 VAC Distribution Panel experienced a loss of power resulting in a 1A RPS half scram, Main Steam Isolation Valve (MSIV) half isolation signal, and multiple primary containment isolations. The following systems isolated: Drywell Chilled Water (DWCW), Reactor Enclosure Cooling Water (RECW), Primary Containment Instrument Gas (PCIG), Reactor Water Cleanup (RWCU), Containment Leak Detection, Drywell Equipment & Floor Sump Drains, and Reactor Enclosure ventilation. A single train of the Standby Gas Treatment System (SGTS) started. All systems responded as designed. Troubleshooting determined the most probable cause to be a spurious trip of an under-frequency relay, 81-CY24801, for a supply circuit breaker to the 1A RPS 120 VAC Distribution Panel. The 1A RPS circuit breaker bypass disconnect switch was closed to restore power to the panel and reset isolation signals. On June 14, 2025, the relay was replaced and the normal alignment was restored. These system actuations were not in response to actual plant conditions or parameters satisfying the requirements for initiation of the system. The plant responded as expected due to loss of power to the 1A RPS 120 VAC Distribution Panel. This event is reportable as an invalid actuation in accordance with 10 CFR 50.73(a)(2)(iv)(A). Analysis of the Event The supply circuit breaker within the 1A RPS 120 VAC Distribution Panel tripped open, due to a spurious actuation of the under-frequency relay, 81-CY24801. System actuations responded to the loss of power condition as expected with no issues. The station performed troubleshooting to identify the cause of the loss of power to the 1A RPS 120 VAC Distribution Panel. Once the problem was identified, the station restored power to the panel, reset the isolations, and returned the systems to service. Safety Consequence There were no actual nuclear safety consequences. The affected systems responded as designed to an invalid under- frequency trip signal. No safety functions were lost during this event. Cause of the Event The most probable cause of the loss of power to the 1A RPS 120 VAC Distribution Panel was due to a spurious trip of the under-frequency relay. Failure analysis was unable to determine a definitive cause for the spurious operation. 2 3 Limerick Generating Station, Unit 1 352 2025 002 00 ■ ,><,,.y-P. AEOt,<.,> • 0. f i . . i'+? ,i! ··••"' I I~ I I□ I 11 D NRC FORM 366A (04-02-2024) U.S. NUCLEAR REGULATORY COMMISSION LICENSEE EVENT REPORT (LER) CONTINUATION SHEET APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) NARRATIVE NRC FORM 366A (04-02-2024) Page of 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR - SEQUENTIAL NUMBER - REV NO. 052 050 Corrective Actions Completed The under-frequency relay was replaced. Corrective Actions Planned The station will evaluate implementing a replacement strategy for the under-frequency relay. Previous Similar Occurrences Unit 1 LER 2024-002-00 Invalid Actuation Due to a Trip of 1B RPS Circuit Breaker - This trip was caused by a defective circuit breaker occurring after the completion of testing. Component Data System - JC (Plant Protection System) Component - RLY Manufacturer - A500 (Asea Inc) 3 3 Limerick Generating Station, Unit 1 352 2025 002 00 ■ ,><,,.y-P. AEOt,<.,> • 0. f i . . i'+? ,i! ··••"' I I~ I I□ I 11 D | 08-12-2025 | On June 13, 2025, at 10:23, Limerick Generating Station (LGS) Unit 1 experienced a loss of power to the "A" Reactor Protection System (RPS) 120 VAC Distribution Panel that resulted in a Unit 1 "A" RPS half scram, Main Steam Isolation Valve (MSIV) half isolation signal, and primary containment isolations in multiple systems. The most probable cause of the power loss was due to an under-frequency relay spurious trip condition. The under-frequency relay was replaced and post maintenance testing was completed satisfactorily. Power was restored to the panel and all systems were returned to service. This event caused invalid primary containment isolation signals in multiple systems which is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). /~•"''"'"•,.,\ \,~ ~j ,;, ... ,. ••• + □ □ □ □ I □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ NRC FORM 366A (04-02-2024) U.S. NUCLEAR REGULATORY COMMISSION LICENSEE EVENT REPORT (LER) CONTINUATION SHEET APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) | Not Found | ML25224A176 | 1 | ok
Fermi 2 | Unknown Unit | Division I Transformer 64 Load Tap Changer Failure Potentially Prohibited by Technical Specifications and Potential Loss of Safety Function | 04-30-2027 | On 6/17/25 around 1755 Eastern Prevailing Time (EPT), Station Service Transformer (SST) 64 low voltage alarm was received on Division I Bus after starting Circulating Water Pump #4. SST 64 Load Tap Changer (LTC) was found to be non-functional requiring manual operation of the LTC to be initiated. Subsequent diagnostics revealed a failed time- delay closing relay in the LTC circuitry, which was replaced on 6/19/25 at 1932 EPT. After reviewing historical data, the LTC was last found to be functioning on 2/7/2024. The non-functional LTC could potentially result in lower than minimum required voltages during a postulated loss of coolant accident coincident with degraded voltage conditions. This Licensee Event Report (LER) is being made under the corresponding requirement in Title 10 of the Code of Federal Regulations (CFR) 50.73(a)(2)(i)(B), due to a condition that is potentially prohibited by Technical Specifications. This LER is also being made pursuant to 10 CFR 50.73(a)(2)(v)(D) as a potential condition that could have prevented the fulfillment of the safety function needed to mitigate the consequences of an accident. Further investigation is being conducted to determine the extent of the condition, and a supplement is planned. The event had no significant effect on public health and safety. <)P~ ••c,,._. /·"~ .<I'\ ~ ·n i ~ - ._,, C 91'11i!")l-l!:'""_lfS 'o:-/,,_,:;'-0 4'+0# ···~· I □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ ~ ~ □ □ □ □ □ □ 11 □ 1~ NRC FORM 366A (04-02-2024) Page 2 of 3 NRC FORM 366A (04-02-2024) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Fermi 2 05000-341 YEAR SEQUENTIAL NUMBER REV NO. 2025 - 001 - 00 | INITIAL PLANT CONDITIONS MODE – 1 Reactor Power – 100 There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT On 6/17/25 around 1755 Eastern Prevailing Time (EPT), Station Service Transformer (SST) [XFMR] 64, Maximo Location Number R1200S002, low voltage alarm was received on Division I Bus [EB] [BU] after starting Circulating Water Pump #4 [KA][P]. SST 64, Load Tap Changer (LTC) [TTC] (General Electric, Model LR-65) was found to be non-functional requiring manual operation of the LTC to be initiated. The LTC was manually adjusted, which cleared the alarm and raised the bus voltage to 118 V. The LTC was then returned to automatic mode. SST 64 voltage was recorded hourly to ensure voltage was maintained within the operability band (122-to-124-meter volts) and adjusted as necessary to maintain the band. The transformer was confirmed to be operable after manual voltage control was maintained within the required band. Subsequent diagnostics revealed a failed time-delay closing relay [TDC] in the LTC circuitry, which was replaced and tested on 6/19/25 at 1932 EPT. After reviewing historical data, the LTC was last found to be working on 2/7/2024. The primary function of SST 64 is to provide a means to step down voltage (13.8 kV) from Bus 11 to 4160V for distribution to Division 1 Engineered Safety Feature (ESF) (class 1E power requirements) and Balance of Plant loads. Operability is based on the ability to supply power from the 120 kV switchyard, through SST 64, to 4160V buses 64B and 64C. This transformer is also sized to accommodate the simultaneous starting of all ESF loads on receipt of an accident signal, without the need for load sequencing. The LTC modulates the voltage on the transformer to keep a nominal 121.8 meter-Volts to ensure Division 1 offsite source has adequate voltage to support the startup and subsequent functionality of the Fermi 2, Division 1 ESF loads without tripping during a Loss of Offsite Coolant Accident (LOCA) transient. While SST 64, LTC control switch was set to automatic, would not automatically tap to control voltage. While the LTC is in manual mode, procedure states that if the voltage range of 122-to-124-meter volts is not met, then Buses 64B and 64C are considered INOPERABLE. The basis of this requirement is the offsite circuit cannot be lost (i.e. by actuation of the degraded voltage relaying) during a design basis accident and must be capable of starting all required ESF loads on the receipt of an accident signal, so this condition impacts the ability to meet the requirements of Technical Specification (TS) 3.8.1. TS 3.8.1 “AC Sources – Operating” requires (During MODES 1,2 and 3) two qualified circuits between the offsite transmission network and the onsite Class IE AC Electrical Power Distribution System and two emergency diesel generators (EDGs) per division. When one offsite circuit is inoperable, then CONDITION D is entered to restore the offsite circuit to OPERABLE status within 72 hours. If the REQUIRED ACTION and COMPLETION TIME is not met, MODE 3 needs to be entered within 12 hours. Further investigation is being done to determine when the voltage level was outside of the voltage band exceeding the completion time of 72 hours along with determining whether the condition was a potential loss of a safety function. The results from the investigation will be provided in a supplemental report. SIGNIFICANT SAFETY CONSEQUENCES AND IMPLICATIONS Further investigation is being conducted for the safety consequences and implications and will be supplemented. I oJ>"llfGc,~ I l·~ '.'\ \ ~,,; ... . ·~•"' | ML25226A116 | 0 | good
River Bend Station | Unit 1 | Turbine Control Valve Closure Results in Loss of Safety Function | 08-14-2025 | On June 18, 2025, at 0553 CDT, with River Bend Station (RBS), Unit 1 operating in Mode 1 at 100% power, High Pressure Turbine Main Steam Supply Line “D” Control Valve (MSS-HYVCV3) closed causing both Turbine Bypass Valves to open. Reactor power was lowered to approximately 95% and the Bypass Valves Closed. At 0646 CDT, MSS-HYVCV3 was observed opening and all other Turbine Control Valves intermittently changing position causing the Bypass Valves to open again. Reactor power was lowered to approximately 90% and the Bypass Valves closed. The Bypass Valves were open for approximately one minute for each of the two occurrences. With the Bypass Valves open, Technical Specification (TS) required instrumentation that utilize turbine first stage pressure were declared inoperable. The direct cause of this event was a failure of the Redundant Valve Positioner “B” (RVP-B) for MSS-HYVCV3. The RVP-B was replaced on June 19, 2025. This event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(A) and 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of the safety function of structures or systems that are needed to: (A) shut down the reactor and maintain it in a safe shutdown condition and (D) mitigate the consequences of an accident. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV River Bend Station, Unit 1 NUMBER NO. 00458 052 2025 003 00 | Event Description On June 18, 2025, at 0553 CDT, with River Bend Station (RBS), Unit 1 operating in Mode 1 at 100% power, the High- Pressure Turbine Main Steam Supply Line “D” Control Valve (MSS-HYVCV3) [TG:VLV] closed causing both Turbine Bypass Valves [JI:V] to open. Control room operatorsentered appropriate procedures and began to lower reactor power. Reactor power was lowered to approximately 95% and the Turbine Bypass Valves closed. At 0646 CDT, MSS-HYVCV3 was observed opening and all other High-Pressure Turbine Main Steam Supply Line Control Valves were observed intermittently changing positions causing the Turbine Bypass Valves to open again. Reactor power was lowered to approximately 90% and the Bypass Valves closed. During the time the Turbine Bypass Valves were open, Technical Specification (TS) required instrumentation that utilizes turbine first stage pressure were declared inoperable. Safety Related Functions of TS 3.3.1.1 (RPS Instrumentation), TS 3.3.2.1 (Control Rod Block Instrumentation) and TS 3.3.4.1 (End of Cycle Recirculation Pump Trip) were declared inoperable. This event was reported on June 18, 2025, at 1126 CDT in accordance with 10 CFR 50.72(b)(3)(v)(A) and 10 CFR 50.72(b)(3)(v)(D) as an event or condition that at the time of discovery could have prevented fulfillment of a safety function of structures or systems that are needed to: (A) shut down the reactor and maintain it in a safe shutdown condition and (D) mitigate the consequences of an accident. (EN 57767) Event Cause The direct cause of this event was a failure of the Redundant Valve Positioner “B” (RVP-B) for MSS-HYVCV3. This failure resulted in the closing of MSS-HYVCV3 resulting in the opening of the Turbine Bypass Valves to maintain reactor pressure at the selected setpoint. The RVP-B was replaced on June 19, 2025. Safety Assessment During the transient there were no radiological impacts and therefore no actual impact to the health and safety of the public. The event is considered of small safety significance from the Probabilistic Risk Assessment (PRA) perspective as no PRA related mitigative components or strategies were affected by this event. While the corresponding functions were declared inoperable from a Technical Specification perspective, functionality was maintained, therefore this is not considered a safety system functional failure. Corrective Actions Planned: Perform a vendor analysis for the failed RVP module. Investigate a possible solution to mitigate or eliminate similar failures of the RVP modules. Previous Occurrences None Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. River Bend equipment codes are identified as (XX). | ML25226A231 | 0 | good
Grand Gulf Nuclear Station | Unit 1 | Manual Reactor Scram due to Degraded Main Condenser Vacuum Caused by Circulating Water Pump Trip | 08-18-2025 | On June 17, 2025, Grand Gulf Nuclear Station (GGNS) Unit 1 was in MODE 1 at 70 percent power with all safety systems operable. At 04:26 CT, a manual scram was initiated due to degraded main condenser vacuum caused by the loss of the 'A' Circulating Water Pump. The event was caused by a failure of an embedded winding Resistance Temperature Device (RTD) in the Circulating Water Pump 'A' Motor which resulted in false high winding temperatures and actuation of the motor thermal overload protection function. All control rods fully inserted, and no radiological release occurred. Immediately after the scram, an expected reactor water Level 3 isolation signal was received. The reactor level was maintained by main feedwater. Actions were taken to replace the failed RTD and update the trip logic in order to prevent recurrence. This report is being made in accordance with 10 CFR 50.73(a)(2)(iv)(A) for any event that resulted in manual actuation of the Reactor Protection System. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) .,,, ........ Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported !'¥\ lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) { ) i regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. \ if/ Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET .,...,1(-1, lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond https://www.nrc.gov/reading-rm/doc-collections/nureqs/staff/sr1022/r3Q to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 181 050 YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 NUMBER NO. 00416 0 052 2025 003 00 | Plant Conditions: At the time of the event, Grand Gulf Nuclear Station (GGNS) Unit 1 was in MODE 1 at 70 percent power and all safety systems were operable. Description of Event: On June 17, 2025, at 04:26 CT, a manual scram was initiated due to degraded main condenser vacuum [SG] caused by the loss of the 'A' Circulating Water Pump [KE:P]. All control rods fully inserted and there were no complications. Immediately after the scram, an expected reactor water Level 3 isolation signal was received. The reactor level was maintained by main feedwater [SJ]. No other safety systems actuated, and no radiological release occurred. Reportability: This report is being made in accordance with 10 CFR 50.73(a)(2)(iv)(A) for any event that resulted in manual actuation of the Reactor Protection System. Cause(s): The direct cause of the event was a failure of an embedded winding Resistance Temperature Device (RTD) in the Circulating Water Pump A Motor which resulted in false high winding temperatures and actuation of the motor thermal overload protection function. Corrective Actions: Completed Actions: - The failure was corrected by removing the failed RTD from the circuit and utilizing an installed spare. - The thermal overload trip logic was changed from a "1 out of 2" configuration to a "2 out of 2" configuration. Safety Significance: There were no actual safety consequences associated with this condition. Plant systems responded as designed. Previous Similar Events: LEA 2025-001-00, Manual Scram Due to Degraded Condenser Vacuum, described a manual scram due to degrading condenser vacuum and loss of seal steam caused by a loss of power to the static inverter. The loss of power to the static inverter was due to rainwater intrusion to load control center. NRG FORM 366A (04-02-2024) Page 2 of 2 | ML25230A099 | 0 | good
Browns Ferry Nuclear Plant (BFN) | Unit 2 | Main Steam Relief Valves Lift Settings Outside of Technical Specifications Required Setpoints | 08-25-2025 | On June 25, 2025, the Tennessee Valley Authority (TVA) was notified of as-found test results that four Main Steam Relief Valves (MSRVs) from Browns Ferry Nuclear Pant (BFN), Unit 2, were outside of their Surveillance Requirement limits for an indeterminate amount of time. These affected valves remained capable of maintaining reactor pressure within the American Society of Mechanical Engineers code limits and could perform their safety function. It was determined that four MSRVs failed above their setpoints due to corrosion bonding to the valve seats. One of these four had been declared inoperable during the fuel cycle due to simmering and gross leakage. All thirteen of the MSRV pilot valves were replaced during the Unit 2 Spring 2025 refueling outage (2R23). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ☒ 050 SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 2 00260 NUMBER NO. ☐ 052 2025 - 004 - 00 | I. Plant Operating Conditions before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN) Unit 2 was in Mode 1 at approximately 100 percent power. II. Description of Event A. Event Summary On June 25, 2025, NTS/Element notified the Tennessee Valley Authority (TVA) with the as-found test results of the thirteen Main Steam Relief Valves (MSRVs) [RV], which were removed during the Spring 2025 Unit 2 Refueling Outage 23 (2R23). Four MSRVs (2-PCV-001-0023, 2-PCV-001-0031, 2-PCV-001-0041, and 2-PCV-001-0179) had as-found lift settings which were outside of the +/- 3 percent band of their setpoints required by Technical Specification (TS) 3.4.3, Safety/Relief Valves (S/RVs), for an indeterminate amount of time. Throughout this event, the two-stage MSRV pilot valves remained capable of maintaining reactor pressure below 1375 pounds per square inch gauge (psig), which is the American Society of Mechanical Engineers (ASME) code limit of 110 percent of the vessel design pressure. The valves remained capable of performing their required safety function. TVA is submitting this report in accordance with Title 10 of the Code of Federal Regulations 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant’s TS. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML25237A236 | 0 | good
Browns Ferry Nuclear Plant | Unit 2 | Reactor SCRAM due to Low Electro-Hydraulic Control Pressure | 09-09-2025 | On May 12, 2025, at 1353 Central Standard Time (CST), Browns Ferry Nuclear Plant, Unit 2, experienced a significant electro-hydraulic control (EHC) leak, resulting in a turbine trip and automatic reactor SCRAM on low EHC pressure. The trip was not complex with all systems responding normally post trip except for the turbine bypass valves, which subsequently failed closed due to loss of EHC pressure. At 1407 CST, with Unit 2 in Mode 3, there was a second automatic RPS actuation due to a low reactor water level transient caused by manually opening and closing a main steam relief valve. Event Notification 57705 was made to the Nuclear Regulatory Commission (NRC) Operations Center on May 12, 2025, at 1731 CST. It was documented that three broken mounting cap screws were found. Failure analysis was completed on the broken cap screws and determined that the cap screws failed due to hydrogen embrittlement. Investigation into the source of hydrogen intrusion determined that there were two potential sources: environmental intrusion and pickling during the manufacturing process. The Tennessee Valley Authority is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(iv)(A), as any event or condition that resulted in manual or automatic actuation of the Reactor Protection System and the Primary Containment Isolation System. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME ☒ 050 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 2 00260 NUMBER NO. ☐ 052 2025 - 001 - 00 | I. Plant Operating Conditions before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Unit 2, was in Mode 1 at 100 percent power. II. Description of Event A. Event Summary On May 12, 2025, at 1353 Central Standard Time (CST), BFN Unit 2, experienced a significant electro-hydraulic control (EHC)[JA] leak resulting in a turbine trip and automatic reactor SCRAM on low EHC pressure. The trip was not complex with all systems responding normally post trip except for the turbine bypass valves [V], which subsequently failed closed due to loss of EHC pressure. Operations responded and stabilized the plant. At 1407, with Unit 2 in Mode 3, there was a second automatic Reactor Protection System (RPS) actuation due to a low reactor water level transient caused by manually opening and closing a main steam relief valve. Event Notification 57705 was made to the Nuclear Regulatory Commission (NRC) Operations Center. The Tennessee Valley Authority (TVA) is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(iv)(A), as any event or condition that resulted in manual or automatic actuation of the Reactor Protection System and the Primary Containment Isolation System (PCIS). B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML25252A080 | 0 | good
South Texas Project | Unit 1 | Loss of Offsite Power Resulting in Unit 1 Automatic Reactor Trip and Actuation of Emergency Diesel Generators and Auxiliary Feedwater Pumps | 09-11-2025 | 12.Licensee Contact for this LER Licensee Contact Phone Number (Include area code) Chris Warren, Licensing Engineer 361-972-7293 13.Complete One Line for each Component Failure Described in this Report Cause System Component Manufacturer Reportable to IRIS Cause System Component Manufacturer Reportable to IRIS X N/A INS G080 Y 14. Supplemental Report Expected Month Day Year 15. Expected Submission Date □✔ No □ Yes (If yes, complete 15. Expected Submission Date) 16.(cid:3)Abstract (Limit to 1326 spaces, i.e., approximately 13 single-spaced typewritten lines) On July 24, 2024, STP Unit 1 experienced a Loss of Offsite Power (LOOP), resulting in an automatic reactor trip and actuation of all three Unit 1 Standby Diesel Generators (SBDG) and all four Auxiliary Feedwater (AFW) pumps. All three trains of Engineered Safety Feature (ESF) buses were energized and all equipment responded as expected without any complications with the exception of Steam Generator Power Operated Relief Valve "1C." Unit 2 experienced a partial LOOP and automatic actuation of SBDG 22 and one of four AFW pumps. The systems for each unit actuated due to the Switchyard experiencing electrical faults during the Shunt Reactor RT-2 fire event, which was caused by the insulation breakdown on the C-Phase (H3) GE Type U high- voltage bushing. Immediate corrective actions included restoring offsite power circuits. A Transmission Distribution Service Provider (TDSP) had not established and implemented adequate management controls governing design changes to equipment in the Switchyard to ensure that changes were consistent with design requirements and aligned with requirements and recommendations of applicable Industry Standards; and subsequently, STPNOC did not rigorously implement management controls during the review and approval of design changes developed by the TDSP. Planned corrective actions include enhancements to STP procedure 0PGP05-ZA-0002, "10CFR50.59 Evaluations" and development and implementation of written instructions that include management controls to govern the review and approval of all four TD(cid:54)(cid:51)(cid:86)' Switchyard changes. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported /~•,.µ...-, .', \ lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. ; .i Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to . CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory <--+ o' Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, ♦--·· (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 YEAR SEQUENTIAL REV I I~ I I □ NUMBER D NO. South Texas Project Unit 1 00498 2024 I 052 - 004 - 01 I | 1. Description of the Reportable Event A. Reportable Event Classification This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in the valid actuation of the Reactor Protection System (RPS) including reactor trip (10 CFR 50.73(a)(2)(iv)(B)(1)), and automatic actuation of all four Unit 1 Auxiliary Feedwater (AFW) Pumps and Unit 2 AFW Pump 22 (10 CFR 50.73(a)(2)(iv)(B)(6), and automatic actuation of all three Unit 1 Standby Diesel Generators (SBDG) and Unit 2 SBDG 22 (10 CFR 50.73(a)(2)(iv)(B)(8)). B. Plant Operating Conditions Prior to Event Prior to the event, Units 1 and 2 were in Mode 1 at 100% power. C. Status of Structures, Systems, and Components That Were Inoperable at the Start of the Event that Contributed to the Event At the start of the event, there were no structures, systems, or components (SSCs) that were inoperable that contributed to the event. D. Narrative Summary of the Event Timeline (Note: All times are in Central Daylight Time) Unit 1 - 07/24/2024 (0702) - Unit 1 reactor trip due to fire in the switchyard. The 345kV North Bus and the Unit 1 Generator tripped. All SBDGs automatically actuated and sequenced on a Loss of Offsite Power. The following busses were deenergized: 13.8kV Auxiliary busses 1F, 1G, 1H, and 1J, 13.8kV Standby busses 1F, 1H, and 1G, and 480V Load Center 1W. Units 1 and 2 - 07/24/2024 (0702) - Due to loss of two independent offsite power circuits, entered Technical Specification 3.8.1.1, Action 'e'. Unit 1 - 07/24/2024 (0702) - All four Reactor Coolant Pumps (RCP) lost power. Entered Technical Specification 3.4.1.2. Unit 2 - 07/24/2024 (0703) - Report of explosion and fire in the switchyard. Entered off-normal procedure 0POP04-ZO-0008, Fire/Explosion. Unit 1 - 07/24/2024 (0735) - Verified natural circulation with Steam Generator (S/G) Power Operated Relief Valves (PORV) open in Manual. 07/24/2024 (0800) - Bay City Fire Department arrive on site at the switchyard. Unit 1 - 07/24/2024 (0848) - Spent Fuel Pool pump 1B is running, restoring cooling to the Spent Fuel Pool. 07/24/2024 (0925) - Fire in Shunt Reactor RT-2 is extinguished. | ML25254A061 | 0 | good
Catawba Nuclear Station | Unit 2 | 2B Emergency Diesel Generator Field Failed to Flash | 09-15-2025 | On 7/15/2025, Catawba Unit 2 was in Mode 1 operating at approximately 100 percent power. At 8:34 EDT the 2B Emergency Diesel Generator (DG)[EK] was manually started for scheduled testing. Upon start, voltage and frequency parameters indicated the 2B DG field did not flash. Investigation determined a sliding link in the field flash circuit was not in the closed position. This portion of the system energizes the field flash contactor to allow voltage buildup during 2B DG startup. The previous successful operation of the 2B DG was on 7/1/2025 for an approximate 12 hour run. During the time between 7/1/2015 and 7/15/2025 there were two instances when the 2A DG was removed from service. This condition resulted in both an "operation or condition prohibited by Technical Specifications" reportable under 1O CFR 50. 73(a)(2)(i)(B) and a "condition that could have prevented fulfillment of a safety function" reportable under 1O CFR 50.7 3(a)(2)(v)(D). There was no impact on the health and safety of the public. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed LICENSEE EVENT REPORT (LER) back to industry. Send comments regarding burden estimate to the FOIA. Library, and Information Collections Branch (T-6 A 1O M), U. S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information (See NUREG-1022, R.3 for instruction and guidance for completing this form and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not http://www.nrc.gov/reading-rm/doc-colleclions/nuregs/staff/sr1022/r3Q conduct or sponsor.., and a person is not req - u - ired to respond .. to, a collection of ~1. FA-CIL-ITY- N-AME- -------~•IB] 050 2. DOCKET NUMBER YEAR 3 S . E L Q t: U K E N N U T M IA t: L 11 :K REV 00413, 00414 ~ NUMBER NO. I-~ Catawba Nuclear Station, Units 1 and 2 0 □ -1 052 003 | BACKGROUND The following information is provided to assist readers in understanding the event described in this LER. Applicable Energy Industry Identification System [EIIS] and component codes are enclosed within brackets. Catawba's unique system and component identifiers are contained within parentheses. The onsite standby power source for each 4160 volt Engineered Safety Features (ESF) bus at Catawba is a dedicated DG. For each unit, DGs A and Bare dedicated to ESF buses ETA and ETB, respectively. Each DG starts automatically on a Safety Injection (SI) signal (i.e., low pressurizer pressure or high containment pressure) or on an ESF bus degraded voltage or undervoltage signal. After the DG has started, it will automatically tie to its respective bus after offsite power is tripped as a consequence of ESF bus undervoltage or degraded voltage, independent of or coincident with an SI signal. The DGs will also start and operate in the standby mode without tying to the ESF bus on an SI signal alone. Following the trip of offsite power, a sequencer strips loads from the ESF bus. When the DG is tied to the ESF bus, loads are then sequentially connected to its respective ESF bus by the automatic load sequencer. In the event of a loss of preferred power, the ESF electrical loads are automatically connected to the DGs in sufficient time to provide for safe reactor shutdown and to mitigate the consequences of a Design Basis Accident such as a Loss of Coolant Accident (LOCA). There are also provisions to accommodate the connecting of the Emergency Supplemental Power Source (ESPS) to one train of either unit's Class 1E AC Distribution System. The ESPS consists of two 50% capacity non-safety related commercial grade DGs. Manual actions are required to align the ESPS to the station and only one of the station's four onsite Class 1 E Distribution System trains can be supplied by the ESPS at any given time. The ESPS is made available to support extended Completion Times in the event of an inoperable DG as well as a defense-in-depth source of AC power to mitigate a station blackout event. The ESPS remains disconnected from the Class 1E AC Distribution System unless required for supplemental power to one of the four 4.16 kV ESF buses. Technical Specifications: Catawba TS 3.8.1 governs the DGs for each unit that is in Modes 1, 2, 3, and 4. Limiting Condition for Operation (LCO) 3.8.1( b) requires two operable DGs capable of supplying the Onsite Essential Auxiliary Power Systems. With one LCO 3.8.1 (b) DG inoperable, the inoperable DG must be restored to operable status within 72 hours per Required Action 8.6. LCO 3.8.1 (d) requires two DGs from the opposite unit necessary to supply power to the shared systems and the Nuclear Service Water System (NSWS) pump(s). With one LCO 3.8.1 (d) DG inoperable, the inoperable DG must be restored to operable status within 72 hours per Required Action D.6. If an inoperable DG is not restored to operable status within 72 hours, the unit must be placed in Mode 3 within 6 hours and in Mode 5 within 36 hours per LCO 3.8.1 Required Actions 1.1 and 1.2. In order to extend the Completion Time for an inoperable DG from 72 hours to 14 days, it is necessary to ensure the availability of the ESPS within 1 hour of entry into TS 3.8.1 LCO and every 12 hours thereafter. | ML25258A159 | 0 | good
River Bend Station | Unit 1 | Unsecured Pressure Boundary Door Resulting in Condition That Could Have Prevented Fulfillment of a Safety Function | 09-16-2025 | On July 21, 2025, at 1548 CDT, River Bend Station, Unit 1 (RBS) was operating in Mode 1 at 100% reactor power when the Central Alarm Station (CAS) received a door alarm indicating that an auxiliary building pressure boundary door, PW 123-01 (T-Tunnel Access to 114' Aux West Access), was not fully secured. A security officer was dispatched and found the door closed with the dogs not engaged. PW 123-01 is a Secondary Containment door. With the dogs not engaged, Secondary Containment was declared inoperable. At 1551 CDT, a security officer fully engaged the dogs, which restored Secondary Containment. This event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(C), as any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond https ://www .n re. gov/ reading-rm/doc-collections/nu regs/staff/sr1 022/r3/) to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ~ 050 YEAR SEQUENTIAL REV River Bend Station, Unit 1 NUMBER NO. 00458 □ 052 2025 004 00 | Event Description On July 21, 2025, at 1548 CDT, River Bend Station, Unit 1 (RBS) was operating in Mode 1 at 100% reactor power when the Central ~larm Station (CAS) received a door alarm indicating that an auxiliary building [NF] pressure boundary door [DR], PW 123-01 (T- rrunnel Access to 114' Aux West Access), was not fully secured. A security officer was dispatched and found the door closed with the dogs not engaged. PW 123-01 is a Secondary Containment door. With the dogs not engaged, Secondary Containment was declared inoperable. ~t 1548 CDT, Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.6.4.1 Condition A, Secondary Containment inoperable was entered. When the security officer fully engaged the dogs at 1551 CDT, restoring Secondary Containment, LCO 3.6.4.1, Condition A, was exited. rThe event was reported on July 21, 2025, at 2151 CDT in accordance with 10 CFR 50.72(b)(3)(v) for an event or condition that could have prevented fulfillment of a safety function due to the inoperability of Secondary Containment (EN 57820). Event Cause rThe direct cause of this event was a personnel error. PW123-01 was left unsecured because the individual passing through the door closed it but failed to fully engage the dogs. Safety Assessment rThe River Bend Updated Safety Analysis Report describes the sequence of events postulated to occur following a Loss of Coolant ~ccident (LOCA). Part of that analysis is a projection of the maximum radiation dose received by a person at the site boundary. The LOCA dose calculation assumes that the standby gas treatment system is initiated 20 minutes into the event, and that Secondary Containment is at the required negative pressure within 30 minutes, such that filtration may be credited. As such, the safety function of Secondary Containment is maintained as long as the boundary is secured (or capable of being secured) within 20 minutes of the ~ime of the security alarm. Since the subject door was secured within approximately 3 minutes of the time of the alarm, the safety ~unction of Secondary Containment was maintained. This event was of minimal significance with respect to the health and safety of ~he public. While the corresponding functions were declared inoperable from a TS perspective, functionality was maintained, ~herefore, this event is not considered a safety system functional failure. Corrective Actions Completed: -A Performance Analysis was utilized to evaluate if any training deficiencies exist that could have contributed to this event. -Verified Engineering Pre-Job Briefs include door management and traversing to work locations. In Progress: -Performance management actions will be used to reinforce proper behaviors with the individual to prevent future errors. Previous Occurrences rrwo similar events were reported by RBS in LER 050/458-2013-002-00 and LER 050/458-2017-009-00. Both LERs document individual(s) failing to properly secure a door in the auxiliary building pressure boundary. The audible tamper alarms installed as a result of LER 2017-009-00, operated as designed. The tamper alarms are designed to be audible when the door is opened and extinguished upon closure. In the event described in this LER the door was closed but not properly latched. | ML25259A219 | 0 | good
Grand Gulf Nuclear Station | Unit 1 | Standby Gas Treatment System Train Inoperable Which Led to a Failure to Identify Condition Prohibited by Technical Specifications | 09-22-2025 | On July 14, 2025, at 12:54 CT, it was identified that the flow recorder [FR] for the Standby Gas Treatment System (SGTS) B train was providing inaccurate information while SGTS B was in standby. SGTS B was determined to be inoperable. A failed flow switch was replaced and SGTS B operability was restored on July 14, 2025. On July 24, 2025, analysis determined that the flow recorder [FR] began receiving inaccurate information on June 21, 2025. This resulted in a condition that was in violation of Technical Specification (TS) 3.6.4.3, Condition A which states that when one SGTS train is inoperable, it must be restored to operable status within seven days. The failure to identify the prohibited condition was caused by operator rounds procedures not having a task to review the SGTS flow. An action has been created to update the relevant procedures. This report is being made in accordance with 10 CFR 50.73(a)(2)(i)(B) for any condition which was prohibited by the plants Technical Specifications. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A1 O M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRG may not conduct or sponsor, and a person is not required to respond https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER 1:8] 050 YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 NUMBER NO. 00416 0 052 2025 004 00 | Plant Conditions: At the time of the event, Grand Gulf Nuclear Station (GGNS) Unit 1 was in MODE 1 at 100 percent power and all safety systems were operable. Description of Event: On July 14, 2025, at 12:54 CT, it was identified that the flow recorder [FR] for the Standby Gas Treatment System (SGTS) B train was providing inaccurate information while SGTS B was in standby. SGTS B was determined to be inoperable. A failed flow switch was replaced and SGTS B operability was restored on July 14, 2025. On July 24, 2025, analysis determined that the flow recorder [FR] began receiving inaccurate information on June 21, 2025. This resulted in a condition that was in violation of Technical Specification (TS) 3.6.4.3, Condition A which states that when one SGTS train is inoperable, it must be restored to operable status within seven days. During this time, SGTS A was operable, and capable of fulfilling the SGTS safety function. Reportability: This report is being made in accordance with 10 CFR 50.73(a)(2)(i)(B) for any condition which was prohibited by the plants Technical Specifications. Cause(s): The failure to identify the prohibited condition was caused by operator rounds procedures not having a task to review the SGTS flow. The cause of the failure to properly detect the inaccurate data and failed flow switch was due to the lack of a task to review the SGTS flow in operator rounds. Corrective Actions: - Replace the faulty filter train B flow low switch. Action completed. - Update 02-S-01-31 Control Room Rounds procedure to include recording values from low flow switches. Action in progress. Safety Significance: There were no actual safety consequences associated with this condition. Plant systems responded as designed. Previous Similar Events: None | ML25265A025 | 0 | good
Monticello Nuclear Generating Plant | Unknown Unit | Rainwater Intrusion Caused Failure of Reactor Building Ventilation and Rise in Steam Chase Temperatures | 09-25-2025 | At 22:00 on July 28, 2025, with Monticello Nuclear Generating Plant (MNGP) operating at 100 percent power, secondary containment was declared inoperable due to a Reactor Building Ventilation System failure which caused a degradation of Reactor Building differential pressure that exceeded the Technical Specification limits. This Ventilation System failure led to elevated temperatures in the Steam Chase. Operators began to lower Reactor power to attempt to slow the rising Steam Chase temperature level. At 23:24 on July 28, 2025, with MNGP now operating at 41 percent power, the Reactor was manually scrammed due to Steam Chase temperatures reaching the procedural limit. Operators responded to the trip and stabilized the plant in accordance with approved procedures and safely placed the plant in Mode 3. All systems responded normally post trip. The Ventilation System failure was caused by rainwater intrusion through a leak in the plenum room roof that made contact with and then tripped energized Ventilation System components. The entire plenum room roof is in the process of being replaced. Immediate actions were taken to prevent rainwater intrusion from impacting Ventilation System components while the roof is being replaced. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to http://www.nrc.qov/readinq-rm/doc-collections/nuregs/staff/sr1022/r3/) respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV NUMBER NO. Monticello Nuclear Generating Plant -263 2025 □ 052 - 004 - 00 | EVENT DESCRIPTION AND ANALYSIS On the evening of July 28, 2025, Monticello Nuclear Generating Plant (MNGP) was operating at 100 percent power when a thunderstorm passed over the area. As the storm passed, rainwater began dripping through the roofing material into the plenum room which is located between the Reactor Building and Turbine Building. The water ran down the wall above cabinet N1131, V-EF-24 LOCAL CONTACTOR. At about 20:58 on July 28, 2025, this leak in the plenum roof led to an electrical short of a contactor for motor V-EF-24, REACTOR BUILDING EXHAUST FAN (Reliance Electric, model BFC SO7827-1) [VL]. This short caused a fuse in a General Electric 7700 line breaker B1131, V-EF-24A,B, REACTOR BUILDING MAIN EXHAUST FANS 480 VAC, to open resulting in a loss of power to both Reactor Building main exhaust fans. Then, V-AC-10A and V-AC-10B, REACTOR BUILDING MAIN SUPPLY HVAC UNITS, [VA] tripped as designed with the V-EF-24 flow interlock. With the failure of Reactor Building Exhaust Ventilation and then the subsequent trip of the Reactor Building Supply Ventilation, this resulted in a degradation of the Reactor Building differential pressure. At 22:00, on July 28, 2025, with MNGP still operating at 100 percent power, the differential pressure exceeded the Technical Specifications limit resulting in Secondary Containment being declared as inoperable. With the failure of the Ventilation System, Steam Chase temperatures started to rise. Operators began to lower Reactor power to attempt to slow the rising Steam Chase temperature level. At 23:24 on July 28, 2025, with MNGP now operating at a reduced power of 41 percent, the Operators inserted a manual scram of the Reactor due to the Steam Chase temperatures reaching the procedural limit of 180 degrees Fahrenheit per the criteria in the Ventilation System procedure. This event is reportable per 10 CFR 50.73(a)(2)(v)(C) and 10 CFR 50.73(a)(2)(v)(D) for an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material; and mitigate the consequences of an accident, and per 10 CFR 50.73(a)(2)(iv)(A) due to actuation of the Reactor Protection System. ASSESSMENT OF SAFETY CONSEQUENCES The scram was not complex, with all systems responding normally post scram. Reactor water level was maintained via the Feedwater System. Decay heat was removed by discharging steam to the main condenser using the turbine bypass valves. The health and safety of the public and site personnel were not impacted during this event. CAUSE OF THE EVENT The Ventilation System failure was caused by rainwater intrusion through a leak in the plenum room roof that then made contact with and tripped energized Ventilation System components | ML25268A050 | 0 | good
i | Unknown Unit | Not Found | 09-24-2025 | Not Found | G. The failure mode, mechanism, and effect of each failed component. The 11 RFP tripped on low suction pressure due to low water level within the Condenser Hotwell. Stuck/degraded (partially filled) vacuum air release valves on the Condenser reduced the scavenging system capability to remove air from the inner loop water boxes. Condenser Hotwell level control was challenged due to issues with the level controller. H. Operator actions Operations personnel stabilized the plant in Mode 3 following the reactor scram. I. Automatically and manually initiated safety system responses. RPS actuation and PCIS Group 2 isolation signals received, and the components actuated as required. Ill. Cause of the Event A Cause of each component or system failure or personnel error. The cause of the scram was low RPV water level due to a trip of the 11 RFP. The 11 RFP tripped on low suction pressure due to low water level within the Condenser Hotwell and air binding in the Circulating Water System. Several different issues resulted in air binding of the Condenser. Condenser tube sheet fouling caused air binding to occur in the condenser outlet piping. Stuck/degraded vacuum air release valves reduced the scavenging system capability to remove air from the inner loop water boxes. Hotwell level control issues challenged and increased the impact of the air binding within the Condenser and Circulating Water System. B. Cause(s) and circumstances for each human performance related root cause. No human performance errors were identified during the investigation. | ML25274A095 | 2 | ok
Peach Bottom Atomic Power Station (PBAPS) | Unit 2 | Invalid Actuation Due to Bus Failure | 10-08-2025 | On August 20th, 2025, an electrical fault in a metal enclosed bus duct resulted in the loss of startup switchgear (EIIS: EA) that supplies power to administrative buildings and cooling towers. The electrical transient produced because of this event led to a partial invalid Primary Containment Isolation System (PCIS) (EIIS: JM) isolation including isolation of the Reactor Water Cleanup System (RWCU) (EIIS: CE) on both units. On Unit 2, this condition resulted in actuations of PCIS Group II and III outboard valves and isolation of the RWCU. On Unit 3, this condition resulted in actuations of PCIS Group II and III inboard valves and isolation of RWCU. Additionally, the ‘A’ and ‘B’ Cooling Tower Lift Pumps tripped. Based on the as-found condition of the bus duct, the cause of failure is attributed to a compromised seal on the bus duct cover. The seal degraded over time, allowing water intrusion and ultimately led to a short circuit condition. This condition is reportable under 50.73(a)(2)(iv)(A) as an invalid actuation of general containment isolation signals affecting containment isolation valves in more than one system. The isolation was caused by a loss of power. The actuation was invalid because the conditions for which isolation is required were not present. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid OMB control number. 1.FACILITY NAME 2.DOCKET NUMBER 3. LER NUMBER  050 SEQUENTIAL REV YEAR Peach Bottom Atomic Power Station (PBAPS), NUMBER NO. 00277 Unit 2  052 2025 - 001 - 00 | Plant Operating Conditions Before the Event Prior to the event, Peach Bottom Atomic Power Station, Units 2 and 3 were operating at approximately 100% power in MODE 1. There were no structures, systems or components (SSC) that were inoperable at the start of the event that contributed to the event, except as described below. Event Description On August 20th, 2025 at approximately 04:30am, an electrical fault in a metal enclosed bus duct resulted in the loss of startup switchgear (EIIS: EA) that supplies power to administrative buildings and cooling towers. The electrical transient produced because of this event led to a partial invalid Primary Containment Isolation System (PCIS) (EIIS: JM) isolation including isolation of the Reactor Water Cleanup System (RWCU) (EIIS: CE) on both units. On Unit 2, this condition resulted in actuations of PCIS Group II and III outboard valves and isolation of RWCU. On Unit 3, this condition resulted in actuations of PCIS Group II and III inboard valves and isolation of RWCU. Additionally, the ‘A’ and ‘B’ Cooling Tower Lift Pumps tripped. During the initial inspection of the bus duct, multiple degraded connections were observed. These deteriorations resulted from water intrusion through a degraded seal, leading to corrosion. The degraded seal allowed moisture to enter the bus duct, accelerating the corrosion process and adversely affecting the integrity of the electrical connections. The bus duct heater, which is designed to minimize condensation in the bus assembly, was found to be non-functional. This condition is reportable under 50.73(a)(2)(iv)(A) as an invalid actuation of general containment isolation signals affecting containment isolation valves in more than one system. The isolation was caused by a loss of power. The actuation was invalid because the conditions for which isolation is required were not present. Safety Consequences There were no challenges to plant safety as a result of this event. Both units responded as designed to the electrical transient, and isolations were reset without error. Corrective Actions Corrective actions for this condition include installation of new bus bar and bus duct and establishing a routine inspection of this portion of the bus. Previous Similar Events Peach Bottom experienced invalid actuations due to an emergency bus breaker relay failure in 2019, ref. LER 2019-001-00. | ML25281A097 | 0 | good
Peach Bottom Atomic Power Station (PBAPS) | Unit 2 | Uncoordinated DC Circuits Cause Unanalyzed Condition | 10-08-2025 | On 09/04/2025, an analysis was completed which confirmed that six cables associated with direct current circuits (EIIS:EI) at PBAPS Units 2 and 3 were non-compliant with 10CFR50 Appendix R, Section III.G.1, Fire protection of safe shutdown capability. It was determined that the circuits were uncoordinated due to inadequate fuse sizing, meaning that during a postulated fire, the circuit’s fuse may not act to protect the circuit from a fire-induced hot short. Without adequate overcurrent protection for these circuits, a fire-induced short could lead to excessive current through the circuits. This could lead to secondary damage in another fire area where the circuits are routed, challenging the ability to achieve and maintain safe shutdown. Compensatory measures have been implemented and will remain until the identified non-compliant conditions are resolved. This event is reported under 10CFR50.73(a)(2)(ii)(B) as an unanalyzed condition because a fire that affects multiple fire areas is outside the bounds of the 10CFR50 Appendix R Fire Safe Shutdown Analysis. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid OMB control number. 1.FACILITY NAME 2.DOCKET NUMBER 3. LER NUMBER  050 SEQUENTIAL REV YEAR Peach Bottom Atomic Power Station NUMBER NO. 00277 (PBAPS), Unit 2  052 2025 - 002 - 00 | Plant Operating Conditions Before the Event Prior to the event, Peach Bottom Atomic Power Station (PBAPS), Unit 2 was operating at approximately 100% power in MODE 1. PBAPS, Unit 3 was operating at approximately 96% power in MODE 1. There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. Event Description On 09/04/2025, an analysis was completed which confirmed that six cables associated with direct current circuits (EIIS:EI) at PBAPS, Units 2 and 3 were non-compliant with 10 CFR 50 Appendix R, Section III.G.2,Fire protection of safe shutdown capability. It was determined that the circuits were uncoordinated due to inadequate fuse sizing, meaning that during a postulated fire, the circuit’s fuse may not act to protect the circuit from a fire-induced hot short. Without adequate overcurrent protection for these circuits, a fire-induced short could lead to excessive current through the circuits. This could lead to secondary damage in another fire area where the circuits are routed, challenging the ability to achieve and maintain safe shutdown. Compensatory actions were implemented immediately for the affected fire areas in accordance with procedural requirements. Compensatory actions will remain in place until the identified non-compliant conditions are resolved. The circuits for PBAPS,Units 2 and 3 noted above were reported under ENS 57899 per 10CFR50.72(b)(3)(ii)(B) as an unanalyzed condition because a fire that affects multiple fire areas is outside the bounds of the 10CFR50 Appendix R Fire Safe Shutdown Analysis. Safety Consequences There were no actual consequences caused by this condition. The potential consequence of a hot short condition is for fire damage in one fire area to occur which subsequently damages cables in a second fire area. This chain of events could cause a loss of safe shutdown capability outside the bounds of the Fire Safe Shutdown Analysis. However, the risk of fire damage is limited by the use of fire retardant cabling, divisional separation, and fire protection features such as automatic suppression and detection, where required. Additionally, the station Fire Brigade is trained and will readily respond to all fire conditions. Cause and Corrective Actions The cause is an inadequate design dating back to original construction. Fire Protection Program compensatory measures were implemented as immediate actions to mitigate the risk of the affected circuits. Corrective Actions will include modification of the affected circuits to ensure they are properly coordinated. Previous Similar Events Peach Bottom LER 2-18-001, dated 05/18/2018, reported an unanalyzed condition due to valve cables not being protected from spurious operation during a postulated fire. Peach Bottom LER 2-14-001, dated 07/17/2014, reported an unanalyzed condition due to broken wires in breakers credited in the Appendix R Post-Fire Safe Shutdown Analysis. Peach Bottom LER 3-11-04, dated 01/13/2012, reported an unanalyzed condition due to an error in cable routing which affected the Post-Fire Safe Shutdown Analysis. | ML25281A104 | 0 | good
Prairie Island Nuclear Generating Plant | Unit 1 | 121 Control Room Chiller Inoperable Due to Purge System Failure. | 10-10-2025 | On June 21,2025, at 17:56 CDT, Units 1 and 2 of Prairie Island Nuclear Generating Plant (PINGP) were both in Mode 1 and operating at 100 percent power when the 121 Control Room (CR) Chiller tripped on "High Refrigerant Pressure". A Past Operability Review was performed and concluded that 121 CR Chiller was considered inoperable and unable to achieve its 30-day mission time from April 22, 2025 until it tripped on June 21, 2025. In addition, during this period of inoperability of the 121 CR Chiller, there were periods when the 122 CR Chiller was also inoperable due to support system inoperability. The cause of the 121 CR Chiller tripping was a buildup of non-condensable gases due to a failed purge compressor. A temporary purge compressor skid has been installed to ensure that the non-condensable gases are removed, and that the Chiller will operate for its 30-day mission time. The 121 and 122 CR Chiller purge compressor skids are planned to be replaced with new units per an approved engineering change. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to http://www.nrc.qov/readinq-rm/doc-collections/nureqs/staff/sr1022/r3/1 respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME im~l 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV NUMBER NO. Prairie Island Nuclear Generating Plant, Unit 1 -282 □ 052 2025 - 002 - 00 | Plant Operating Conditions Prior to the Event: Unit 1 - Mode 1, 100 percent Power. Unit 2 - Mode 1, 100 percent Power. EVENT DESCRIPTION On June 21, 2025, at 17:56 CDT, Units 1 and 2 of Prairie Island Nuclear Generating Plant (PINGP) were both in Mode 1 and operating at 100 percent power. At this time, annunciator [IB] alarm 47022-0302, 121 CONTROL ROOM WATER CHILLER TRIPPED was received and outplant operators reported that the 121 Control Room (CR) Chiller (Trane Air Conditioning, PCV-1C) [VI] tripped on "High Refrigerant Pressure". Dates And Approximate Times of Major Occurrences: • January 17, 2025, at 10:06 CST: While performing Test Procedure 1687 - 121 CONTROL ROOM CHILLER INSPECTION, it was documented that the timer on the purge compressor (Trane Air Conditioning, PRGAA2A1BA0B) was not advancing. This was later determined to be the time when the purge compressor failed. • April 22, 2025, at 09:31 CDT: 121 CR Chiller was considered inoperable and unable to achieve its 30-day mission time per the Past Operability Review (POR) that was completed on August 15, 2025. • April 23, 2025, from 03:30 to 10:59 CDT: 122 CR Chiller was inoperable due to invoking Technical Specifications (TS) Limiting Conditions for Operation (LCO) 3.0.6 based on the entry of support system TS LCO 3.7.8 Condition A for 22 Diesel Driven Cooling Water Pump (DDCLP) being inoperable. • May 03, 2025, from 15:23 to 15:28 CDT: 122 CR Chiller was inoperable due to invoking TS LCO 3.0.6. based on the entry of support system TS LCO 3.8.9 Condition A for Motor Control Center 1 AB Bus 2 being inoperable. • May 20, 2025, from 09:53 to 11:17 CDT: 122 CR Chiller was inoperable due to invoking TS LCO 3.0.6 based on the entry of support system TS LCO 3.7.8 Condition B for “B” Cooling Water Header being inoperable. • May 22, 2025, from 22:14 to 22:30 and 22:31 to 22:43 CDT, 122 CR Chiller was inoperable due to invoking TS LCO 3.0.6. based on the entry of support system TS LCO 3.7.8 Condition A for 22 DDCLP being inoperable. • June 21, 2025, at 17:56 CDT: The amount of non-condensable gases reached a level that permitted the 121 CR Chiller to trip on "High Refrigerant Pressure" and the Chiller was taken out of service and TS LCO 3.7.11 Condition A was entered. • July 5, 2025, at 18:55 CDT: 121 CR Chiller was returned to service and TS LCO 3.7.11 Condition A was exited. • August 15, 2025 [Discovery Date]: A POR was completed and concluded that 121 CR Chiller was considered inoperable from April 22, 2025 until it tripped on June 21, 2025. TS LCO 3.7.11 pertains to the Safeguards Chilled Water System (SCWS). Under Condition A of TS LCO 3.7.11, if one SCWS loop becomes inoperable, it must be restored to operable status within 30 days. The POR determined that the 121 CR Chiller was inoperable for greater than 30 days from April 22, 2025 until it tripped on June 21,2025. Therefore, the required action under Condition A was not met. Condition B of TS LCO 3.7.11 requires entry into Mode 3 within 6 hours if Condition A is not completed. The action to transition to Mode 3 for both Unit 1 and 2 was not completed. Under Condition E of TS LCO 3.7.11, if both SCWS loops are inoperable while in Modes 1-4, the plant must immediately enter LCO 3.0.3. This requires the plant to be in Mode 3 within 7 hours. During the time the 121 CR Chiller was considered inoperable, the 122 CR Chiller was also inoperable for greater than 7 hours on April 23, 2025. LCO 3.0.3 was not entered, and the required transition to Mode 3 for both Unit 1 and 2 was not completed. (EVENT DESCRIPTION continued on next page) | ML25283A066 | 0 | good
Joseph M. Farley Nuclear Plant | Unit 1 | Emergency Diesel 1C Unable to Achieve 110% of Maximum Load | 10-14-2025 | On August 13, 2025, at approximately 2126 CDT with Unit 1 and Unit 2 in Mode 1 at 100% power the 1C Emergency Diesel Generator (EOG) was unable to be loaded to 3100 kilowatts (kW) as required by Surveillance Requirement (SR) 3.8.1.12 (24 hour run). The 1C EOG can be aligned to Farley Nuclear Plant (FNP) Unit 1 or Unit 2. During the 24 hour run, SR 3.8.1.12 requires operating the 1C EOG at a load greater than or equal to 110% (3100 kW) capacity for a time of greater than two hours of the 24 hour requirement. When operators were adding the additional load to the 1C EOG, the generator was only capable of reaching 2950 kW. Per SR 3.0.1 failure to meet the SR means the Limiting Condition of Operation (LCO) is not met. FNP operators declared the 1C EOG inoperable. It was determined that during the 1C EOG outage in October of 2024 that the EOG governor linkage was removed and re-installed to the fuel rack. The fuel rack was found limited in movement by the governor linkage preventing further loading. The 1C EOG governor linkage was corrected and the 1C EOG successfully completed post maintenance testing on August 14, 2025, and was declared operable. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of infonmation unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/l displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 SEQUENTIAL REV I NUMBER NO. Joseph M. Farley Nuclear Plant, Unit 1 348 1-G □ 052 001 | Plant Conditions / Event Description: On August 13, 2025, at approximately 2126 CDT, with Farley Nuclear Plant (FNP) Unit 1 and Unit 2 in Mode 1 at 100% power, the 1C Emergency Diesel Generator (EOG) [EIIS: DC/ DG] was unable to reach a load of 3100 kilowatts (kW) during the Technical Specification (TS) Surveillance Requirement (SR) 3.8.1.12 (24 hour run). The 1C EOG can be aligned to Farley Nuclear Plant (FNP) Unit 1 or Unit 2 thus both units were affected. Event Analysis: During the 24 hour run, SR 3.8.1.12 requires operating the 1C EOG [Manufacturer: Fairbanks Morse] at a load of 2850 kW or higher. The SR also requires that the 1C EOG run loaded greater than or equal to 3100 kW for a time of greater than two hours of this 24 hour requirement. When operators were adding the additional load to the 1C EOG the diesel generator was only capable of reaching 2950 kW. FNP operators declared the 1C EOG inoperable due to failure to meet the SR. Reportability and Safety Assessment: Per SR 3.0.1, failure to meet the SR means the Limiting Condition of Operation (LCO) is not met. Since the LCO for Technical Specification 3.8.1 was not met, FNP had been in a condition prohibited by TS since October 25, 2024. The event was within the analysis of UFSAR Chapter 15 and is reportable per 10 CFR 50.73(a)(2)(i)(B) for the 1C EOG being inoperable for longer than allowed by TS 3.8.1. The Safety Function was met as the 1C EOG provides loads for Loss of Offsite Power (LOSP) which was met by meeting 100% load demand of 2850 kW. Cause(s): It was determined that during the 1C EOG outage in October of 2024 that the EOG governor linkage was removed and re-installed to the fuel rack. Following the August 13, 2025, run of the 1C EOG, the investigation found that the fuel rack was limited in movement by the governor linkage preventing further loading. It was determined that the FNP PMT guidance did not require a PMT of 110% (3100 kW) capacity upon the replacement of the fuel injector pump. Additionally, maintenance procedures did not require a 110% loaded run upon the adjustment or replacement of equipment that could adversly impact EOG performance criteria. Corrective Actions Planned/ Completed: The 1C EOG governor linkage was corrected and the 1C EOG successfully completed PMT on August 14, 2025, and was declared operable. Fleet and site procedures are being revised to ensure 110% load PMT occurs when work is performed on systems that affect combustion engine performance. Revisions are being tracked in the site's Corrective Action Program. An extent of condition was performed on all 4 remaining diesel generators which determined the same condition did not exist. Previous Similar Events: No known previous events. | ML25287A034 | 0 | good
River Bend Station | Unit 1 | Potential Loss of Safety Function of Control Building Chillers Due to a Valve Mispositioned | 10-20-2025 | On August 23, 2025, at 1433 CDT, River Bend Station, Unit 1 (RBS) was operating in Mode 1 at 100% reactor power, a post maintenance test was being performed on Division II Control Building Chilled Water System Chiller B (HVK- CHL1B). During this test, Division I Control Building Chilled Water System (HVK) was declared Inoperable as a result of HVK Chiller A (HVK-CHL1A) failing to start. HVK-CHL1A failed to start due to the HVK Low Side Isolation Valve, HVK-FTY5B-V2L, being in the closed position. The closed isolation valve prevented a “low flow” signal from the transmitter and render Division I of the HVK Chillers, HVK-CHL1A and HVK-CHL1C, inoperable. Operations immediately alternated back to HVK-CH1B, with HVK-CH1C in standby. This event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(A) and 10 CFR 50.73(a)(2)(v)(D) as an event that could have prevented the fulfillment of the safety function of structures or systems that are needed to shut down the reactor and maintain it in a safe shutdown condition and mitigate the consequences of an accident. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV River Bend Station, Unit 1 NUMBER NO. 00458 052 2025 006 00 | Event Description On August 23, 2025, at 1433 CDT, River Bend Station, Unit 1 (RBS) was operating in Mode 1 at 100% reactor power, a post maintenance test was being performed on Division II Control Building Chilled Water System Chiller B (HVK-CHL1B) [VI:CHU]. During this test, while transferring operation from HVK Chiller B (HVK-CHL1B) to HVK Chiller A (HVK-CHL1A), HVK-CHL1A failed to start. Division I Control Building Chilled Water System (HVK) was declared Inoperable. The inoperability of Division I and II Control Building Chilled Water Systems could have prevented the fulfillment of a safety function. HVK-CHL1A failed to start due to the HVK Low Side Isolation Valve, HVK-FTY5B-V2L, being in the closed position. The closed isolation valve prevented a “low flow” signal from the transmitter and render Division I of the HVK Chillers, HVK-CHL1A and HVK- CHL1C, inoperable. Operations immediately alternated back to HVK-CH1B, with HVK-CH1C in standby. Limiting Conditions for Operation (LCO) 3.7.3, Control Room Air Conditioning System Condition A (One control room AC subsystem inoperable) and 3.7.7, Control Building Air Conditioning System Condition A (one control building air conditioning subsystem inoperable) was entered. After further investigation, it was determined that Instrument and Control (I&C) Technicians manipulated HVK-FTY5B-V2L to the closed position earlier that day during performance of a work order to fill and vent transmitters on the Control Building Chiller 1B. The I&C Technicians failed to document the change of valve position as required by EN-MA-157, Maintenance Configuration Control, therefore the valve was not returned to its proper position (i.e., open). Event Cause The direct cause of this event was due to the misposition of HVK-FTY5B-V2L that resulted in the valve being left in the closed position by I&C Technicians. The causal factor was determined to be that the workers failed to stop work and notify supervision when a potential issue was encountered. The workers did not utilize EN-MA-157, Maintenance Configuration Control, before manipulating a valve. The workers failed to identify potential error traps and failed to utilize human performance tools as required by EN-HU-102, Human Performance Traps & Tools. Safety Assessment Dedicated operator actions had been established to maintain the safety function for the HVK system in the event that the standby chiller doesn’t start and the previously running chiller doesn’t start when alternating divisions of control building chilled water as a planned evolution. Safety function is maintained if a chiller is started within 23 minutes, which is the Environmental Design Criteria limitation. The safety significance of this event is low based on temperatures in the areas cooled by the HVK systems remained below maximum environmental design criteria and actions taken by Operations. Corrective Actions Completed: - Maintenance Department held a stand-down for a standards reset. - Maintenance Department maintained 100% Supervisor job oversight for 2 weeks following the event. | ML25293A255 | 0 | good
River Bend Station | Unit 1 | Unidentified Drywell Leakage Increase Results in Shutdown | 10-20-2025 | On May 21, 2025, at 0324 CDT, with River Bend Station (RBS), Unit 1 operating in Mode 1 at 100% power, unidentified drywell leakage experienced a greater than 2 gallon per minute change over a 24-hour period. Technical Specifications (TS) Limiting Condition of Operations (LCO) 3.4.5 Condition C was entered. The required action to verify the source of unidentified leakage increase could not be completed within the allowable completion time. As a result, a plant shutdown was initiated at 0656 CDT. While investigating the unidentified leakage source, RBS determined that a degraded condition existed following the examination of the Residual Heat Removal (RHR) 'A' injection line testable check valve. The leakage from the RHR 'A' injection line testable check valve was determined to be Reactor Coolant System pressure boundary leakage. The direct cause of the leakage past RHR 'A' injection line testable check valve was due to improper gasket seating. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(A) as a Plant Shutdown Required by Technical Specifications, 10 CFR 50.73(a)(2)(ii)(A) as a Degraded or Unanalyzed Condition that resulted in the condition of the nuclear power plant, including its principal safety barriers being seriously degraded, and 10 CFR 50.73(a)(2)(i)(B) as an Operation or Condition Prohibited by Technical Specifications. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRG may not conduct or sponsor, and a person is not required to respond https:/lwww.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER [2:1 050 YEAR SEQUENTIAL REV River Bend Station, Unit 1 NUMBER NO. 00458 0 052 2025 002 01 | Event Description On May 21, 2025, at 0324 CDT, with River Bend Station (RBS), Unit 1 operating in Mode 1 at 100% power, unidentified drywell leakage experienced a greater than 2 gallon per minute change over a 24-hour period. Technical Specifications (TS) Limiting Condition of Operations (LCO) 3.4.5 Condition C was entered. The required action to verify the source of unidentified leakage increase is not service sensitive type 304, type 316 austenitic stainless steel, or other inter-granular stress corrosion cracking susceptible material within 4 hours, could not be completed within the allowable completion time due to the drywell being inaccessible during plant operation. As a result, a controlled manual plant shutdown was initiated at 0656 CDT. At 1405 CDT, the control room operators placed the mode switch to Shutdown. The control room operators entered the appropriate post scram procedures and appropriately responded to the reactor scram. This event was reported on May 21, 2025, at 0950 CDT in accordance with 10 CFR 50.72(b)(2)(i), as an event or condition that results in a TS required plant shutdown. (EN 57725) During the investigation of the unidentified leakage following the shutdown, RBS determined that a degraded condition existed following the performance of a visual examination of E12-AOVF041A (Residual Heat Removal 'A' Injection Line Testable Check Valve) [BO:V]. This examination was conducted on May 22, 2025, at 2358 CDT. This event was reported on May 23, 2025, at 0121 CDT in accordance with 10 CFR 50.72(a)(2)(ii)(A), as Degraded or Unanalyzed Condition that resulted in the condition of the nuclear power plant, including its principal safety barriers being seriously degraded. (EN 57731) The elevated drywell leakage was determined to be Reactor Coolant System (RCS) [AB] pressure boundary leakage and required actions were not completed within the completion time as required by TS LCO 3.4.5. Therefore, this event is also being reported under 10 CFR 50.73(a)(2)(i)(B) as an Operation or Condition Prohibited by TS. Event Cause The direct cause of this event was improper gasket seating, resulting from erosion of the gasket seating surface. The erosion was caused by steam cutting to the base metal of the gasket seat surface. In this degraded state, the base metal did not provide the required support as designed. Two causal factors were identified; (1) The organization did not fully understand the degraded condition of E12-AOVF041A valve body due to steam cutting; therefore, an adequate repair strategy was not formulated or executed and (2) Required VT-3 inspections were not added to the Job Plan as the plan was in Approved status and therefore not routed for additional reviews. In addition, the inspectors failed to realize the need for an inspection as it was not listed in the Job Plan description. Safety Assessment The actual consequence of these events was the initiation of a controlled manual plant shutdown. Following the controlled manual plant shutdown, reactor pressure was maintained by the Turbine Steam Drains [TF] and reactor water level was maintained by the Feedwater [SJ] system. | ML25293A384 | 0 | good
River Bend Station | Unit 1 | Containment Unit Coolers Inoperable Due to Compensatory Measures | 10-20-2025 | On August 20, 2025, at 1020 CDT, River Bend Station, Unit 1 (RBS) was operating at 100% power, when it was discovered that previously implemented compensatory measures were determined to have rendered Containment Unit Cooler 'A' (HVR-UC1A) and Containment Unit Cooler 'B' (HVR-UC1B) inoperable. On August 14, 2025, RBS placed HVR-UC 1A and HVR-UC 1B in lockout as a compensatory measure to ensure operability following a Part 21 notification from General Electric. On August 20, 2025, it was discovered that the lockout function would delay the start of a time-delay relay needed for load sequencing in the event of an accident. The cause of this event was due to inadequate compensatory measures that were established by plant personnel. These compensatory measures would have prevented the containment unit coolers from performing their safety function. This event is being reported under 10 CFR 50.73 (a)(2)(ii)(B) as any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety, 10 CFR 50.73(a)(2)(v)(C) and 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of a safety function that is needed to control the release of radioactive material and mitigate the consequences of an accident, and 10 CFR 50.73(a)(2)(i)(B) as an Operation or Condition Prohibited by Technical Specifications. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and lnfonmation Collection Branch (T-6 A1 OM), U S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of lnfonmation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond https:/lwww.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) to, a collection of infonmation unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LERNUMBER ~ 050 YEAR SEQUENTIAL REV River Bend Station, Unit 1 NUMBER NO. 00458 0 052 2025 005 00 | Event Description On August 14, 2025, River Bend Station, Unit 1 (RBS) placed Containment Unit Cooler 'A' (HVR-UC1A) [VA:CLR] and Containment Unit Cooler 'B' (HVR-UC1 B) [VA:CLR] in lockout as a compensatory measure to ensure operability following a Part 21 notification from General Electric. On August 20,2025, it was discovered that the lockout function would delay the start of a time-delay relay [RL Y] needed for load sequencing in the event of an accident. This condition would prevent the unit coolers from starting within their required sequence following a Loss of Offsite Power. The compensatory measures included actions to place HVR-UC1A and HVR-UC1 Bin a continuously running state during normal plant operation. In the event of a Loss of Offsite Power, a dedicated operator would be required to reset the lockout pushbuttons for each unit cooler to meet the safety function time requirement associated with the load sequence. Following a review of the compensatory actions on August 20, 2025, it was determined that the compensatory actions were inappropriately applied. The compensatory actions that were implemented would have caused HVR-UC1A and HVR-UC1 B to start up to 10 minutes after the dedicated operator reset the lockout pushbuttons, instead of 10 minutes following a Loss of Offsite Power. During the time that HVR-UC1A and HVR-UC1 B were in lockout, Technical Specifications (TS) Limiting Condition for Operation 3.6.1.7, Primary Containment Unit Cooler, Condition B was applicable. On August 20, 2025, at 1219 CDT, these compensatory measures were removed. This event was reported under 10 CFR 50.72(b)(3)(ii)(B) as any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety, as well as, 10 CFR 50.72(b)(3)(v)(C) and 10 CFR 50.72(b)(3)(v)(D) as an event or condition that could have prevented fulfillment of a safety function that is needed to control the release of radioactive material and mitigate the consequences of an accident and 10 CFR 50.73(a)(2)(i)(B) as an Operation or Condition Prohibited by TS. Event Cause The cause of the event was due to multiple ineffective reviews of electrical drawings resulting in Engineering personnel failing to recognize the impact of the compensatory measures on the loading sequence of the containment unit coolers. During review and validation prior to implementation, Operations personnel did not recognize the impact of the compensatory measures. As a result, compensatory measures were implemented which would have prevented the containment unit coolers from performing their safety function. Safety Assessment The actual consequences of this event were minimal. A loss of offsite power did not occur during the duration that HVR-UC1A and HVR-UC1 B were inoperable. There were also no radiological impacts. Therefore, there was no actual impact on the health and safety of the public. | ML25293A447 | 0 | good
Dresden Nuclear Power Station | Unit 2 | Not Found | 10-23-2025 | On 4/30/2024 at 10:07 CST when starting a Containment Cooling Service Water (CCSW) Pump, the Dresden Unit 2 Containment Cooling Heat Exchanger Division I Tube Side Discharge Valve failed to open. The safety related function of the valve is to control cooling water flow through the heat exchanger tubes to remove heat from containment. The condition was corrected at 03: 10 on 5/1/2024. The station determined the Division I CCSW system was inoperable for 28.5 days, therefore, an Operation or Condition Prohibited by Technical Specifications existed for greater than the Limiting Condition of Operation (LCO) time of 7 days. During this period, surveillance testing performed on 4/3/2024 resulted in the Division II subsystem being inoperable for 3 hours and 39 minutes resulting in an Event or Condition that Could Have Prevented Fulfillment of a Safety Function. The root cause of the event was a cracked yoke weld that allowed the actuator to flex away from the valve body. This resulted in overtravel of the valve position potentiometer during valve closure, causing an open permissive in the valve's control logic. This was corrected by a weld repair, potentiometer and valve stroke length adjustments. This report is being submitted under 10 CFR 50. 73(a)(2)(i)(B), 10 CFR 50.7 3(a)(2)(v)(B) and 10 CFR 50. 73(a)(2)(v)(D). NRG FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection http://www. n re.gov /reading-rm/doc-collections/nu regs/staffi s r1 022/r3/l displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 SEQUENTIAL REV YEAR NUMBER NO. Dresden Nuclear Power Station, Unit 2 00237 □ 052 2024 - 001 01 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 megawatts thermal rated core power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. CONDITIONS PRIOR TO EVENT Unit: 2 Event Date: April 30, 2024 Event Time: 10:07 CST Reactor Mode: 1 Mode Name: Power Operation Power Level: 100 percent No structures, systems, or components were inoperable at the time of the event that contributed to the event. A. DESCRIPTION OF EVENT On 4/30/2024 at 10:07 CST, with Dresden Unit 2 at 100 percent power, while performing operations to support Suppression Pool [BO] level control, no CCSW [Bl] flow was observed on the instrumentation in the Main Control Room (MCR) following system start. When 2A CCSW [Bl] Pump was started per Dresden Operating Procedures, the Heat Exchanger [HX] 'A' Tube Side Discharge Valve [PDCV] did not automatically open (dual indication) as expected. The system is designed to remove energy from the suppression pool [NH] by rejecting heat to the CCSW [Bl] system. Suppression pool cooling [BO] or containment [NH] sprays may be initiated following a Loss of Coolant Accident (LOCA) using a portion of the non-selected Low Pressure Coolant Injection (LPCI) [BO] loop, which is not required to perform a LPCI [BO] function. When CCSW [Bl] is initiated, the Heat Exchanger [HX] 'A' Tube Side Discharge Valve [PDCV] is designed to open based on demand from a Differential Pressure (DP) Controller [PDC]. A past operability review was completed on 6/20/2024 and determined that the Heat Exchanger [HX] 'A' Tube Side Discharge Valve [PDCV] was incapable of performing its function after the valve [PDCV] was opened and closed for Post Maintenance Testing (PMT) at 14:24 CST on 4/2/2024. This was not discovered until the past operability was reviewed for reporting criteria on 11/27/2024 and determined to be reportable under 10 CFR 50.73. When the Heat Exchanger [HX] 'A' Tube Side Discharge Valve [PDCV] failed to open on 4/30/2024, Technical Specification (TS) 3.7.1 Conditions A and C were entered for Division 1 CCSW [Bl] being declared inoperable. Division 1 Suppression Pool Cooling [BO], Suppression Pool [NH] Spray and Drywell [NH] Spray were also INOPERABLE (TS 3.6.2.3, 3.6.2.4 and 3.6.2.6 respectively). The Limiting Condition of Operation (LCO) time for one subsystem inoperable is 7 days, therefore an Operation or Condition Prohibited by TS existed from 4/10/2024 02:24 CST to 5/1/2024 03:10 CST. This is being reported under 10 CFR 50.73(a)(2)(i)(B). Additionally, from 00:42 to 04:21 CST on 4/3/2024, the opposite Division II CCSW [Bl], Suppression Pool Cooling [BO], Suppression Pool [NH] Spray and Drywell [NH] Spray were inoperable due to surveillance testing on Unit 2 LPCI [BO] Initiation circuitry. This also resulted in an Event or Condition that Could Have | ML25296A231 | 1 | ok
Dresden Nuclear Power Station | Unit 3 | Low Pressure Coolant Injection Pump Suction Relief Valve Inoperable as a Primary Containment Isolation Valve Resulted in a Condition Prohibited bv Technical Soecifications | 10-23-2025 | On 11/20/2024 at 1407 CST, the Main Control Room was notified that the operating handle for the 3A Low Pressure Coolant Injection (LPCI) Suction Relief Valve was found positioned higher than the operating handle for the other relief valves in the system, making the valve inoperable as a Primary Containment Isolation Valve (PCIV). Technical Specification (TS) 3.6.1 .3 Condition C was entered. At 1650 CST, the operating handle for the relief valve was moved to the down position in accordance with station procedure and TS 3.6.1.3 Condition C was exited. The valve had been replaced during refueling outage activities on 11/3/2024. At 0202 on 11/15/2024, Unit 3 entered Mode 2 and Limited Condition of Operation (LCO) 3.6.1.3 became applicable. LCO 3.6.1.3 Required Action C.1 directs isolation of the affected flow path within 4 hours. When the flow path was not isolated by 0602 on 11/15/2024, Required Actions E.1 and E.2 directed shutdown to Mode 3 within 12 hours and Mode 4 within 36 hours, respectively. Therefore, a condition prohibited by Ts existed by the failure to be in Mode 3 by 1802 on 11/15/2024, and Mode 4 by 1802 on 11/16/2024. This event is being reported in accordance with 10 CFR 50. 73(a)(2)(i)(B) for an Operation or Condition Prohibited by TS. NRC FORM 366A (04-02-2024) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc gov/reading-rm/doc-collect1ons/nuregs/staff/sr1022/r3/) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA. library, and Information Collections Branch (T-6 A 10M), U S Nuclear Regulatory Commission. Washington. DC 20555-0001 . or by email to lnfocollects Resource@nrc gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs. (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission 725 17th Street NW Washington. DC 20503. The NRC may not conduct or sponsor. and a person is not required to respond to. a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 YEAR Dresden Nuclear Power Station □ 052 00249 2024 - | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 megawatts thermal rated core power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. A. CONDITIONS PRIOR TO EVENT SEQUENTIAL NUMBER 002 Unit: 3 Reactor Mode: 1 Event Date: November 20, 2024 Mode Name: Power Operation Event Time: 1407 CST Power Level: 100% No structures, systems or components were inoperable at the time of the event that contributed to the event. B. DESCRIPTION OF EVENT REV NO. 02 On 11/20/2024 at 1407 CST, with Dresden Unit 3 at 100 percent power, the Main Control Room was notified that the operating handle for the 3A Low Pressure Coolant Injection (LPCI) [BO] Suction Relief Valve [RV] was found position higher than the operating handles of the other relief valves in the system. The relief valve [RV] is normally seated closed and relieves back to the suppression pool [NH] to provide over-pressure protection of the LPCI [BO] piping when the pump [Pl is isolated. The relief valve [RV] also functions as a Primary Containment Isolation Valve (PCIV) [ISV]. As a PCIV [ISV], its safety-related function is to isolate containment from the LPCI [BO] system. Technical Specification (TS) 3.6.1.3 Condition C requires lines with only one PCIV [ISV] to be isolated within 4 hours and to be verified isolated every 31 days when in Operating Modes 1, 2, and 3. If this action is not met, Condition E of TS 3.6.1.3 requires the operating unit to be placed in Mode 3 within 12 hours and Mode 4 within 36 hours. At 0202 on 11/15/2024, Unit 3 entered Mode 2 and Limited Condition of Operation (LCO) 3.6.1.3 became applicable. LCO 3.6.1.3 Required Action C.1 directs isolation of the affected flow path within 4 hours. When the flow path was not isolated by 0602 on 11/15/2024, Required Actions E.1 and E.2 directed shutdown to Mode 3 within 12 hours and Mode 4 within 36 hours, respectively. Therefore, a condition prohibited by TS existed by the failure to be in Mode 3 by 1802 on 11/15/2024, and Mode 4 by 1802 on 11/16/2024. The operating handle for the 3A LPCI [BO] Suction Relief Valve [RV] was moved to the down position in accordance with station procedure and TS 3.6.1.3 Condition C was exited at 1650 CST on 11/20/2024. This event is being reported in accordance with 10 CFR 50. 73(a)(2)(i)(B) for an Operation or Condition Prohibited by Technical Specifications. C. CAUSE OF EVENT The relief valve [RV] had been replaced on 11/03/2024 during a refueling outage. Prior to the replacement of the relief valve [RV]. there is no record of valve failure or mispositioning. | ML25296A468 | 0 | good
Browns Ferry Nuclear Plant | Unit 2 | Primary Containment Isolation and Manual Reactor Trip Due to Dual Recirculation Pump Trips | 10-27-2025 | On May 30, 2025, Recirculation (Recirc) Pump Variable Frequency Drive (VFD) 2A and 2B 120VAC Auxiliary Power Distribution had a contactor fail to transmit power from the normal source and fail to transfer to the alternate source resulting in the loss of Normal and Alternate power to the VFD Cooling Fans. Subsequently, excessive temperatures in VFD cabinets caused multiple VFD cells to auto bypass which caused automatic trips of both Recirc Pumps and, ultimately, an insertion of a manual reactor scram in accordance with 2-AOI- 68-1, Recirc Pump Trip/Core Flow Decrease. The power loss was caused by an incorrect risk evaluation/preventative maintenance strategy for a contactor. Corrective actions included contactor replacement, which allowed the reactor to restart and sync to the electrical grid on June 6, 2025. Preventative actions include similar contactor replacements, evaluations, and maintenance strategies as well as the future addition of power supply redundancies. The Tennessee Valley Authority is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(iv)(A), as any event or condition that resulted in manual or automatic actuation of the Reactor Protection System and the Primary Containment Isolation System. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid OMB control number. 1. FACILITY NAME ☒ 050 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 2 00260 NUMBER NO. ☐ 052 2025 - 003 - 01 | I. Plant Operating Conditions before the Event At the time of this event, Browns Ferry Nuclear Plant (BFN) Unit 2 was in Mode 1 at approximately 39 percent Rated Thermal Power (RTP). II. Description of Event A. Event Summary On May 30, 2025, at 2247 hours CST with Unit 2 operating in Mode 1 at 39% Reactor Power due to the trip of the Reactor Recirculation [AD] Pump (2A), the reactor was manually tripped due to a trip of the only operating Reactor Recirculation Pump (2B). The reactor shutdown was uncomplicated with all systems responding as designed. Operations responded and stabilized the plant. The Primary Containment Isolation System (PCIS) [JM] received an actuation signal for Groups 2, 3, 6, and 8 on reactor water level at +2 inches. All primary containment systems that received an actuation signal performed as designed. Reactor water level control was via Condensate [SD] and Feedwater [SJ] and reactor cooldown was completed using turbine bypass valves to the main condenser [SG]. Due to manual actuation of the Reactor Protection System (RPS) [JC] while critical, this event was reported as a four-hour non-emergency notification per Title 10 of the Code of Federal Regulations (10 CFR) 50.72(b)(2)(iv)(B). The actuation of RPS and PCIS also required an eight- hour non-emergency report per 10 CFR 50.72(b)(3)(iv)(A). Refer to Event Notification report 57737. The Tennessee Valley Authority (TVA) is submitting this report in accordance with 10 CFR 50.73(a)(2)(iv)(A), as an automatic actuation of the RPS and the PCIS. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event No structures, components, or systems were identified as inoperable at the start of the event or that contributed to the event. | ML25300A115 | 0 | good
Grand Gulf Nuclear Station | Unit 1 | Loss of Secondary Containment Due to Unsecured Roof Hatch | 11-03-2025 | On September 4, 2025, at 0855 CT while at 100 percent power Grand Gulf Nuclear Station (GGNS) Unit 1 staff discovered the Enclosure Building Roof Hatch was unsecured and slightly open which resulted in inoperability of secondary containment. The hatch had last been accessed at 0845 CT. After discovery, the hatch was secured, and secondary containment was restored. A lack of proper oversight and failure of the watch team to properly understand their duty resulted in the Enclosure Building Roof Hatch becoming unsecured. Supervisor and paired observations will be periodically performed to prevent recurrence of the issue and an engineering barrier will be added to indicate when the hatch is open. This report is being made in accordance with 10 CFR 50.73(a)(2)(v)(C) as a condition which could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 0 4 / 3 0 / 2 0 2 7 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond https://www .nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 181 050 YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 NUMBER NO. 00416 □ 052 2025 005 00 | Plant Conditions: At the time of the event, Grand Gulf Nuclear Station (GGNS) Unit 1 was in MODE 1 at 100 percent power, and all safety systems were operable. Description of Event: On September 4, 2025, at 0855 CT, operators discovered the Enclosure Building Roof Hatch was unsecured and open by approximately one inch. This resulted in inoperability of secondary containment. Following the discovery, the hatch was immediately closed and latched, and secondary containment was restored to operability at 0940 CT. Based on available information the hatch had been last accessed at 0845 CT. Reportability: This report is being made in accordance with 10 CFR 50.73(a)(2)(v)(C) as a condition which could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. Cause(s): Failure of the hatch watch to properly understand their duty and inadequate oversight by supervisors resulted in the Enclosure Building Roof Hatch becoming unsecured. Corrective Actions: - The Enclosure Building Roof Hatch was closed and secured. - Daily observations will be performed by supervisors to ensure that the hatch watch is properly fulfilling their functions. - Additional paired observations of roof hatch usage will be performed. - Engineering barrier will be developed to provide indication and alarm when the hatch is open. Safety Significance: There were no actual safety consequences associated with this condition. Previous Similar Events: LER 2016-003 LER 2018-006 | ML25307A235 | 0 | good
Susquehanna Steam Electric Station (SSES) | Unit 1 | Both Sub-Systems of the Control Room Emergency Outside Air Supply System Impacted by Concurrent, Unrelated Equipment Issues in the Control Structure Heating, Ventilation & Air Conditioning System | 11-03-2025 | On September 4, 2025, while the "A" Control Structure Heating, Ventilation and Air Conditioning (HVAC) fan (0V103A) was out of service for planned, proactive belt replacement, the hydro motor for the "B'' Control Room Fan (0V117B) discharge damper failed resulting in the damper going closed. With both the 0V103A and 0V117B fans out of service, both subsystems of the Control Room Emergency Outside Air Supply (CREOAS) system were rendered inoperable. The 0V103A fan was expeditiously worked, tested, and returned to service thereby restoring one sub-system to operable status. The approximately 35-minute concurrent inoperability of both subsystems of CREOAS is being reported in accordance with 10 CFR 50. 73(a)(2)(v)(C) as an event or condition that could have prevented fulfillment of a safety function. There were no actual consequences to the health and safety of the public as a result of this event. ... NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory ccllection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of lnfonmation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRG may not conduct or sponsor, and a person is not required to respond to, a collection of infonmation unless the document requesting or requiring the collection http:l/www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid 0MB control number. ,1. -FA-CIL-ITY- NA-ME- ----------, ~ 050 I 2. DOCKET NUMBER Ic Y:E:AR7 3 S . E L Q E U R E N N U T M IA B L E R REV NUMBER NO • Susquehanna Steam Electric Station Unit 1 00387 1-0 □ 052 . 1~-1 ° 02 | CONDITIONS PRIOR TO THE EVENT: Unit 1: Mode 1, approximately 95% Rated Thermal Power Unit 2: Mode 1, approximately 100% Rated Thermal Power There were no inoperable structures, systems, or components at the start of the issues that contributed to the event. EVENT DESCRIPTION On September 4, 2025, two concurrent, unrelated equipment issues associated with the Control Structure HVAC system [EIIS System Code: VI] resulted in both sub-systems of the Control Room Emergency Outside Air Supply (CREOAS) system being adversely impacted. The following is a timeline of the significant points associated with the event. September 4, 2025, at approximately 1341: The "A" Control Structure HVAC fan (0V103A) [EIIS Component Code: FAN] was proactively removed from service to facilitate replacement of the belts which had contributed to elevated vibration. September 4, 2025, at approximately 1515: Control room personnel noted a change in background noise which was subsequently determined to have been caused by the failure of the Control Structure Supply Fan 0V117B discharge damper hydro motor [EIIS Component Code: COMP] resulting in the damper [EIIS Component Code: DMP] closing. Reduced air flow through the control room dampers was also noted. September 4, 2025, at approximately 1550: Belt replacement on the 0V103A fan was completed. Following successful post maintenance testing, the 0V103A fan was returned to service resulting in restoration of the 'A' CREOAS subsystem. The duration of the concurrent inoperability of the 0V103A and 0V117B fans was approximately 35 minutes. September 5, 2025, at approximately 2111: the discharge damper hydro motor for the 0V1178 fan was replaced, tested and placed back in service resulting in restoration of the 'B' CREOAS subsystem. CAUSE OF THE EVENT Two separate and independent events occurred concurrently that impacted the CREOAS system. Vibration is routinely monitored on the 0V103A fan. Following vibration data collection on September 4, 2025, the station elected to proactively remove the 0V103A fan from service to replace the fan belts. In accordance with station procedures, the belt replacement was planned during a window where no conflicting work was being performed, or redundant equipment was out of service. While the 0V103A fan was out of service for the planned belt replacement, the 0V117B discharge damper hydro motor failed. There had been no indications of degraded performance with the 0V117B hydro motor prior to the failure. | ML25307A312 | 0 | good
Quad Cities Nuclear Power Station | Unit 1 | Estimated burden per response to COITl)ly with this mandatory collection request 80 hours. Reported lessons learned are incorporated inlll the licensing process and fed back Ill induslry Send comments regil'ding burden estimate to the FOIA. Libril'y, and Information Collections Branch [T-6 A10M), U. S. Nuclu Regulatory Commission, Washingllln, DC 20555-0001. or by emai Ill lnfocollects.Resource@nrc.gov. and the 0MB rewewer at 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nucleil' Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required Ill respond Ill, a conection of information unless the document requesting or requiring the collection displays a currently valid 0MB conlrol number. 1Z1 050 2. Docket Number 3.Page 0 052 00254 1 OF 4 High Pressure Coolant Injection Inoperable Due to Turbine Inlet Valve Failure to Open | 11-04-2025 | On September 4, 2025 at 1845 during the performance of a Unit 1 High Pressure Coolant Injection (HPCI) Operability Test, it was identified that the system's steam inlet motor operated valve (MOV) failed to open. The inability to open this valve prevented the steam driven system from fulfilling its function of providing emergency core cooling. The cause of this condition, discovered on September 5, 2025, was a degraded breaker which was found to contain a degraded open coil and a binding contact roller. This prevented electrical power from being provided to the valve. The degraded coil was replaced and the roller attachment was cleaned, lubricated, and reinstalled. The breaker failed due to an inadequate maintenance strategy. This report is being submitted in accordance with 10 CFR 50. 73(a)(2)(v)(D) for an event or condition that could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident. NRC FORM 366A (04-02-2024) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate lo the FOIA, library, and Information Collections Branch (T-6 A 10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to lnfocollecls.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currenUy valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER ■ 050 00254 YEAR 3. LER NUMBER SEQUENTIAL NUMBER REV NO. Quad Cities Nuclear Power Station Unit 1 □ 052 2025 - 006 - 00 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. EVENT IDENTIFICATION High Pressure Coolant Injection Inoperable Due to Turbine Inlet Valve Failure to Open A. CONDITION PRIOR TO EVENT Unit: 1 Reactor Mode: 1 Event Date: September 5, 2025 Mode Name: Power Operation Event Time: 1845 hours CST Power Level: 100% No systems, structures, or components that were inoperable at the start of the event contributed to the event. B. DESCRIPTION OF EVENT On September 4, 2025 at 1845 during the performance of a High Pressure Coolant Injection (HPCI) [BJ] Operability Test, operators discovered that the Turbine Inlet Motor Operated Valve (MOV) [V] 1-2301-3 would not open. Multiple attempts were made to open the MOV from the control switch and the associated breaker contacts could not be heard cycling. Troubleshooting on September 5, 2025 at 0130, determined that the electrical breaker [BKR] feeding the MOV had an opening coil [CL] that had failed, and rollers associated with the coil assembly were binding. Discovery of the opening coil degradation confirmed that the MOV would fail to open in either manual or automatic HPCI demands, as opposed to failure to operate only from the valve control switch. The coil was replaced, and the roller assembly was cleaned and relubricated. Post maintenance testing of the MOV was completed on September 5, 2025 at 2228. The MOV breaker prevented proper HPCI operation for 27 hours and 43 minutes. The HPCI Operability Test was subsequently completed with satisfactory results. Event Notification System (ENS) report number 57905 was submitted to the NRC on September 5, 2025. This report is being submitted in accordance with 10 CFR 50. 73(a)(2)(v)(D) for an event or condition that could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident. | ML25308A004 | 0 | good
Edwin I. Hatch Nuclear Plant | Unit 2 | Unit 2 Manual Reactor SCRAM Due to Trip of Both Reactor Recirculation Pumps | 11-11-2025 | At 1704 EDT on 09/13/2025, with Unit 2 in MODE 1 at 70-percent power, the reactor was manually tripped due to the loss of both reactor recirculation pumps during turbine control valve testing. Investigation determined that a procedure step to bypass the recirculation pump trip logic had not been performed, resulting in the recirculation pumps tripping during valve testing. The reactor trip was not complex, with all safety systems responding normally including the closure of containment isolation valves (CIVs) in multiple systems, as designed, due to reaching the actuation setpoint on reactor water level. The operating crew responded correctly to the event and stabilized the plant. The event is reportable per 10 CFR 50.73(a)(2)(iv)(A) as any event or condition that resulted in the manual or automatic actuation of any of the systems listed in paragraph 10 CFR 50. 73(a )(2)(iv)(B ). Systems that actuated during this event that are listed in (a)(2)(iv)(B) include: the Reactor Protection System and CIVs in multiple systems. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV Edwin I. Hatch Nuclear Plant Unit 2 00366 □ NUMBER NO. ~- I 1-G □ 052 I I 003 | EVENT DESCRIPTION At 1704 EDT on 09/13/2025, with Unit 2 in MODE 1 at 70-percent power, the reactor was manually tripped due to the loss of both reactor recirculation pumps (EIIS Code: P) during turbine control valve (EIIS Code: FCV) testing. The reactor trip was not complex, with all safety systems responding normally including the closure of containment isolation valves (CIVs) (EIIS Code: ISV) in multiple systems, as designed, due to reaching the actuation setpoint on reactor water level. The operating crew responded correctly to the event and stabilized the plant. There were no inoperable systems that contributed to this event. EVENT CAUSE ANALYSIS The event was caused by inadequate place-keeping by licensed operators, which led to a missed critical step to bypass the recirculation pump trip logic resulting in the pumps tripping during valve testing. SAFETY ASSESSMENT AND REPORTABILITY There were no safety consequences as a result of this event with all safety related systems functioning as designed. The operating crew responded correctly to the event. The applicable abnormal and emergency operating procedures were properly entered and the plant was stabilized. The event was within the analysis of the Updated Final Safety Analysis Report (UFSAR) Chapter 15. The event is reportable per 10 CFR 50_73(a)(2)(iv)(A) as any event or condition that resulted in the manual or automatic actuation of any of the systems listed in paragraph 10 CFR 50. 73(a)(2)(iv)(B). Systems that actuated during this event that are listed in (a)(2)(iv)(B) include: the Reactor Protection System (EIIS Code: JC) and CIVs in multiple systems. CORRECTIVE ACTIONS Corrective actions include highlighting all critical procedural steps, followed by the supervisor reviewing the critical steps during the pre-job brief, implementing supervisor hold points prior to the execution of each critical step, and place-keeping page numbers during performance of any continuous use procedure. Also, lessons learned from the event have been communicated to site personnel. PREVIOUS SIMILAR EVENTS None. | ML25315A010 | 0 | good
Peach Bottom Atomic Power Station (PBAPS) | Unit 2 | Invalid Actuation Due to Transformer Trip | 11-13-2025 | On September 19th, 2025, the 13 kV non-safety related AS4 feeder breaker, which powers the B Cooling Tower Lift Pump (EIIS:NN) tripped as a result of an electrical fault downstream of the breaker. The electrical fault resulted in a momentary voltage dip on the offsite power source (3SU). This condition led to a partial invalid Primary Containment Isolation System (PCIS) (EIIS: JM) isolation including isolation of the Reactor Water Cleanup System (RWCU) (EIIS: CE) on both units. The cause of the breaker trip was a faulted disconnect switch, likely due to component aging. This condition is reportable under 50.73(a)(2)(iv)(A) as an invalid actuation of general containment isolation signals affecting containment isolation valves in more than one system. The isolation was caused by degraded voltage. The actuation was invalid because the conditions for which isolation is required were not present. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid OMB control number. 1.FACILITY NAME 2.DOCKET NUMBER 3. LER NUMBER  050 SEQUENTIAL REV YEAR Peach Bottom Atomic Power Station (PBAPS), NUMBER NO. 00277 Unit 2  052 2025 - 003 - 00 | Plant Operating Conditions Before the Event Prior to the event, Peach Bottom Atomic Power Station, Unit 2 was operating at approximately 100% power in MODE 1. Unit 3 was operating at approximately 91% power in MODE 1 in end-of-cycle coast down. There were no structures, systems or components (SSC) that were inoperable at the start of the event that contributed to the event. Event Description On September 19th, 2025, at approximately 9:34am, operators received alarms indicating that the 480V motor control center that supplies support power to the B Cooling Tower (EIIS: NN) lift pump tripped and caused various isolations on both units. On Unit 2, the voltage reduction caused a partial invalid Primary Containment Isolation System (PCIS) (EIIS: JM) isolation of Group II and Group III inboard valves including isolation of the Reactor Water Cleanup System (RWCU) (EIIS: CE), isolation of nitrogen compressors (EIIS: LK), failure of the B vent stack radiation monitor (EIIS: IL), and loss of flow to containment hydrogen and oxygen analyzers (EIIS: IK). On Unit 3, this condition resulted in actuations of PCIS Group II and III outboard valves, isolation of RWCU, isolation of nitrogen compressors and a trip of a service water booster pump (EIIS: DA). The A train of flow indication to the Main Stack sampler (EIIS: IL) was also lost. The cause of the breaker trip was a faulted disconnect switch, likely due to component aging and general corrosion. The failed switch is located outdoors and was replaced in 2007 after a similar failure. Preventive maintenance had not been performed since the 2007 failure. This condition is reportable under 50.73(a)(2)(iv)(A) as an invalid actuation of general containment isolation signals affecting containment isolation valves in more than one system. The isolation was caused by degraded voltage. The actuation was invalid because the conditions for which isolation is required were not present. Safety Consequences There were no challenges to plant safety as a result of this event. Both units responded as designed to the electrical transient, and PCIS isolations were reset without error within approximately one hour of the trip. Corrective Actions Corrective actions for this condition include replacement of the components that were damaged by the fault, including radiation monitors, transformer disconnect switch and cabling. The maintenance strategy for this equipment will be reviewed. Previous Similar Events Peach Bottom experienced the following similar events: - Invalid actuations due to a trip of the AS4 feeder breaker in 2007, ref. EN# 43910 - Invalid actuations due to an emergency bus breaker relay failure in 2019, ref. LER 2019-001-00. - Invalid actuations due to a bus failure on August 20, 2025, rev. LER 2025-001-00. | ML25317A674 | 0 | good
Susquehanna Steam Electric Station (SSES) | Unit 1 | APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 Estimated burden per response to comply with tills mandatory collection request 80 hours. Reported lessons learned are Incorporated Into the llcens!ng process and fed back to Industry, Send comments regarding burden estimate to the FOIA, Library, and lnfom,ation Collections Branch (TƄ6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by small to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRG may not conduct or sponsor, and a person Is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB oontrol number. 00 050 2. Docket Number 3. Page 052 00387 1 OF 3 Manual Reactor Scram Following Loss of Cooling to Main Transformer | 11-13-2025 | On July 22, 2025, at approximately 15:10, Susquehanna Steam Electric Station (SSES) Unit 1 was manually scrammed following a partial loss of cooling to the main transformer (one of two cooling fan groups were found tripped). The event was reported by Event Notification 57822 in accordance with 10 CFR 50. 72(b )(2)(iv)(A), 10 CFR 50. 72(b )(2)(iv)(B) and 10 CFR 50. 72(b )(3)(iv)(A). This event is also reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a manual actuation of the Reactor Protection System (including a reactor scram) and actuation of the emergency core cooling system. Following restoration of both cooling fan groups, SSES Unit 1 was restored to Mode 1 operation on July 25, 2025. The root cause of the event was determined to be that Operations leadership did not ensure the Operators were prepared to respond to a loss of cooling event on the main transformer to minimize the potential for a required manual scram. There were no actual consequences to the health and safety of the public as a result of this event. - --- - --- -------- ------ □ NRC FORM 366A (04-02-2024) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D 1. FACILITY NAME ,------------------, 00 Susquehanna Steam Electric Station (SSES) Unit 1 | CONDITIONS PRIOR TO THE EVENT □ 050 052 Unit 1: Mode 1, approximately 96% Rated Thermal Power Unit 2: Mode 1, approximately 100% Rated Thermal Power Estimated burden per response to comply with this mandatory collection request BO hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and lnfonmation Collections Branch [f-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at 0MB Qffice of lnfonmatlon and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRG may not conduct or sponsor, and a person is not required to respond to, a collection of infonmatlon unless the document requesting or requiring the collection displays a currently valid 0MB control number. 2. DOCKET NUMBER 3. LER NUMBER I 00387 [::7 NUMBER NO. I YEAR SEQUENTIAL REV ~-I 001 1-0 There were no inoperable structures, systems, or components at the start of the event that contributed to the event EVENT DESCRIPTION On July 22, 2025, a Main Transformer 1X101 [EIIS System Code/ Component Code - EL/ XFMR] trouble alarm was received in the Control Room and Operators entered a 10-minute manual scram requirement in accordance with the Alarm Response procedure. The non-licensed operator (NLO) responding in the field to the Main Transformer correctly determined that only a partial loss of cooling had occurred with Group 1 cooling fans [IEEE Component Code - FAN] not running and Group 2 cooling fans in service. However, imprecise communications resulted in operators in the Control Room and Work Control Center (WCC) incorrectly believing that a total loss of cooling had occurred. As a result, a second NLO, dispatched to the transformer by the WCC, attempted to restore transformer cooling. Failing to recognize that partial cooling for the transformer was in fact in service, the second NLO secured the running Group 2 cooling fans while attempting to switch to the alternate power supply resulting in the total loss of transformer cooling. At approximately 15: 10, control room operators manually scrammed SSES Unit 1 following a loss of cooling to the Main Transformer. All systems responded normally following the manual scram. High Pressure Coolant Injection [EIIS System Code - BJ] actuated briefly to assist in restoring reactor water level. The 1 B Reactor Feedwater Pump [El IS System Code/ Component Code - SJ/ P] stabilized and maintained reactor water level. Decay heat was removed by discharging steam to the main condenser using the turbine bypass valves. The event was reported by Event Notification 57822 in accordance with 10 CFR 50 .72(b)(2)(iv)(A), 10 CFR 50.72(b)(2)(iv) (B) and 1 O CFR 50. 72(b)(3)(iv)(A). This event is also reportable in accordance with 10 CFR 50. 73(a)(2)(iv)(A) as an event that resulted in a manual actuation of the Reactor Protection System (including a reactor scram) and actuation of the emergency core cooling system. Following restoration of both cooling fan groups, SSES Unit 1 was returned to Mode 1 operation on July 25, 2025. CAUSE OF THE EVENT The direct cause of the event was ineffective communication and direction between control room and field personnel responding to a partial loss of main transformer cooling (Group 1 Cooling). This resulted in incorrect operator actions being taken that caused a complete loss of transformer cooling. NRG FORM 366A (04-02-2024) Page 2 of 3 | ML25317A743 | 0 | good
Calvert Cliffs Nuclear Power Plant | Unit 1 | Control Room Loss of Ventilation due to Smoke Detector Failure Causing Common Supply Damper to Shut | 07-31-2025 | On July 31, 2025, at 1744, the Main Control Room (MCR), shared by Units 1 and 2, experienced a loss of ventilation due to the Control Room supply damper fully closing. Closure of the damper isolated the ventilation flow to the Control Room which resulted in both trains of the Control Room Emergency Ventilation System and Control Room Emergency Temperature System being inoperable, resulting in Technical Specification Limiting Conditions for Operation (LCOs) 3.7.8 and 3.7.9 not being met, respectively, for Units 1 and 2. At time 1745, the Units exited the associated LCOs after the damper returned to its normal, open position. Field troubleshooting isolated the cause of the intermittent closure of the damper to a MCR ventilation smoke detector. The smoke detector functions to shut the MCR supply damper by energizing the associated solenoid valve. This event is reportable in accordance with 10 CFR 50. 73(a)(2)(v)(D) and 10 CFR 50. 73(a)(2)(vii). The direct cause of the smoke detector failure was an electrical short, due to condensation, on the control board of the Control Room Air Conditioning (A/C) return duct smoke detector (OAE5347) that sends an automatic closure signal to the Control Room A/C dampers. NRC FORM 366A (04-02-2024) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/readinq-rm/doc-collections/nuregs/staff/sr1022/r30 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRG may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER ■ 050 Calvert Cliffs Nuclear Power Plant, Unit 1 0 052 05000317 | PLANT AND SYSTEM IDENTIFICATION YEAR 2025 - 3. LER NUMBER SEQUENTIAL NUMBER 001 REV NO. 01 Calvert Cliffs Nuclear Power Plant, Units 1 and 2, are Combustion Engineering Pressurized Water Reactors with a licensed maximum power level of 2737 megawatts thermal. The Energy Industry Identification System code used in the text is identified as [VI]. A. CONDITION PRIOR TO EVENT Units: 1/2 Date: July 31, 2025 Power Level: 100/100 percent Mode: MODE 1/1 B. DESCRIPTION OF EVENT On July 31 , 2025, at 1744, the Main Control Room (MCR), shared by Units 1 and 2, experienced a loss of ventilation due to the MCR supply damper fully closing. Closure of the damper isolated the ventilation flow to the MCR which resulted in both trains of the Control Room Emergency Ventilation System (CREVS) and Control Room Emergency Temperature System (CRETS) being inoperable, resulting in Technical Specification (TS) Limiting Conditions for Operation (LCO) 3.7.8 and 3.7.9 not being met, respectively, for Units 1 and 2. At time 1745 the Units exited the associated LCOs after the damper returned to its normal, open position. C. DA TES AND APPROXIMATE TIMES OF MAJOR OCCURRENCES July 31, 2025 • 17:44:00 Unit 1 entered LCOs 3.0.3, 3.7.8, and 3.7.9 due to ventilation damper 0-CV-5342 closing rendering two CREVS trains inoperable in MODE 1. • 17:44:00 Unit 2 entered LCO 3.0.3, 3.7.8, and 3.7.9 due to ventilation damper 0-CV-5342 closing rendering two CRETS trains inoperable in MODE 1. • 17:44:30 Ventilation damper 0-CV-5342 re-opened. (time is approximate) • 17:45:00 Unit 1 exited 3.0.3, 3.7.8, and 3.7.9 due to damper 0-CV-5342 returned to its normal open position. Both Trains of CREVS and CRETS were restored to service. • 17:45:00 Unit 2 exited 3.0.3, 3.7.8, and 3.7.9 due to damper 0-CV-5342 returned to its normal open position. Both Trains of CREVS and CRETS were restored to service. | ML25323A433 | 0 | good
River Bend Station | Unit 1 | Division 1 Balance of Plant Isolation Results in Manual Reactor Trip | 12-08-2025 | On October 9, 2025, at 1207 CDT, River Bend Station (RBS) was operating at 100% reactor power when a manual reactor trip was inserted as a result of a Division I Balance of Plant (BOP) isolation. The BOP isolation resulted in the loss of the Instrument Air System (IAS) and the Component Cooling Primary System (CCP) to containment. All plant systems responded as designed. Immediately following the manual trip, a reactor water low level 3 isolation signal was received as expected. Due to the swell from the main turbine trip, a reactor water high level 8 actuation signal was received at 1208 CDT. The level 8 actuation signal was reset at 1211 CDT. At 1237 CDT, Control Room Operators entered the Emergency Operating Procedure (EOP) for high containment pressure caused by the isolation of the containment vent flow path. The isolation signal for IAS and CCP was reset at 1255 CDT. Following the restoration of the isolation signal, Control Room Operators lowered containment pressure and exited the EOP at 1305 CDT. The direct cause of this event was a failed fuse caused by a human performance error. This report is made pursuant to 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of the Reactor Protection System. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and lnfonmation Collection Branch (T-6 A1 OM), U S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of lnfonmation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond https:/lwww.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) to, a collection of infonmation unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LERNUMBER ~ 050 YEAR SEQUENTIAL REV River Bend Station, Unit 1 NUMBER NO. 00458 0 052 2025 007 00 | Event Description On October 9, 2025, at 1207 CDT, with River Bend Station (RBS), Unit 1 operating at 100% reactor power, a manual reactor trip was inserted as a result of a Division I Balance of Plant (BOP) isolation. The Division 1 BOP isolation resulted in the loss of the Instrument Air System (IAS) [LO] and the Component Cooling Primary System (CCP) [CC] to containment. On October 9, 2025, at 1203 CDT, a Division 1 BOP isolation signal was received. Control Room operators recognized the loss of IAS and CCP to containment and entered the appropriate procedures. The Control Room operators were unable to reset the Division 1 BOP isolation signal. At 1207 CDT, the Control Room Operators inserted a manual reactor trip by placing the Mode Switch to Shutdown. All plant systems responded as designed. Immediately following the manual trip, a low reactor water level isolation signal was received as expected. Due to the swell from the Main Turbine [TA] trip, a high reactor water level actuation signal was received at 1208 CDT. The high reactor water level actuation caused the Reactor Feedwater System (FWS) [SJ] to trip as designed. The high reactor water level actuation signal was reset at 1211 CDT and Reactor Feedwater Pump C (FWS-P1 C) was restarted to maintain reactor water level. Reactor pressure was maintained by the Turbine Bypass Valves [JI]. At 1237 CDT, Control Room operators entered the Emergency Operating Procedure (EOP) for high containment pressure. The increase in containment pressure was due to the isolation of the containment vent flow path. At 1255 CDT, the isolation signal for IAS and CCP was reset. Following the restoration of the isolation signal, Control Room operators lowered containment pressure and exited the EOP at 1305 CDT. This event was reported on October 9, 2025, at 1539 CDT in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) as an event or condition that results in actuation of the RPS when the reactor is critical and as a specified system actuation due to the expected low reactor water level isolation signal immediately following the reactor scram and a subsequent high reactor water level signal (EN 57975). Event Cause Prior to the Division 1 BOP isolation, plant personnel were performing surveillance STP-058-4201, Containment and Drywell Manual Isolation Actuation Logic System Functional Test. During the surveillance, a technician lifted a lead and did not appropriately account for the length of wire allowing the wire to retract and contact the metal enclosure. This caused the Division 1 Isolation Logic Supply Fuse (B21 H-F28A) [JM] to fail. Due to the failure of B21 H-F28A, a Division 1 BOP isolation actuation occurred. The Division 1 BOP isolation resulted in the loss of the IAS and CCP to containment. Safety Assessment The actual consequence of this event was a Division 1 BOP containment isolation that was unable to be reset and a subsequent reactor scram. There were no other actual consequences to general safety of the public, nuclear safety, industrial safety and radiological safety for this event. Corrective Actions Planned: • Complete performance management with personnel involved to address personal accountability. • Develop and implement a non-training intervention plan to reinforce standards and expectations. | ML25342A438 | 0 | good
edwin i. hatch | Unknown Unit | Unit 1 Reactor Protection System Instrumentation for Turbine Control Valve Fast Closure Inoperable | 12-19-2025 | With Unit 1 at 100-percent power on 10/22/2025 at 0918 EDT, after performance of a past operability evaluation, it was determined that three Reactor Protection System (RPS) pressure switches for the Turbine Control Valve (TCV) Fast Closure trip on low Electrohydraulic Control (EHC) oil pressure were likely inoperable longer than allowed by Technical Specifications (TS). These three TCV RPS pressure switches failed TS Surveillances (SRs) on 4/5/2025 and 4/6/2025. Additionally, one of the same TCV RPS pressure switches failed a TS SR on 12/17 /25. The failures of the TCV RPS pressure switches are attributed to elevated ambient temperatures which degraded EHC oil locally at the pressure switches, impeding proper depressurization of the EHC sensing lines during TCV actuation. Corrective actions included purging the EHC sensing lines, replacing the fast acting solenoid for one of the TCVs, installing temporary fluid conditioning units, increasing the TCV SR frequency, which helps prevent fluid stagnation and flushes contaminants, reducing varnish buildup and sticking. The event is reportable per 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by technical specifications, 10 CFR 50.73(a)(2)(v)(A) for a condition that could have prevented fulfillment of a safety function, and 10 CFR 50.73(a)(2)(vii) for a common cause inoperability of independent channels. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to oomply with this manda1ay oollection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden es1imate to the FOIA, Library, and lnfonnation Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washr,gton, DC 20565-0001, or by email to CONTINUATION SHEET lnlooollects.Resource@m.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs. (3150-0104). Attn: Desk Officer for the Nudear Regulatory Commission. 72517th Street NW. (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required lo respond to, a collection of information unless the document requesting or requiring the oollection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/} displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER .-------------, ~ 050 YEAR SEQUENTIAL REV Edwin I. Hatch Nuclear Plant Unit 1 00321 □ NUMBER NO. 1- 0 I □ - 1 □ 052 I 002 | EVENT DESCRIPTION With Unit 1 at 1O D-percent power on 10/22/2025 at 0918 EDT, after performance of a past operability evaluation, it was determined that three Reactor Protection System (RPS) (EIIS Code: JC) pressure switches (EIIS Code: PS) for the Turbine Control Valve (TCV) (EIIS Code: FCV) Fast Closure trip on low Electrohydraulic Control (EHC) (EIIS Code: TG) oil pressure were likely inoperable longer than allowed by Technical Specifications (TS). These three TCV RPS pressure switches failed TS SRs on 4/5/2025 and 4/6/2025. Additionally, one of the same RPS pressure switches failed a TS SR on 12/17/25. EVENT CAUSE ANALYSIS The failures of the TCV RPS pressure switches are attributed to elevated ambient temperatures which degraded EHC oil locally at the pressure switches. The degraded EHC oil prevented the TCV Fast Acting Solenoid (FAS) (EIIS Code: SOL) from fully shuttling which inhibited depressurization of the RPS pressure switch sensing line when the TCVs actuated. Because the sensing line did not depressurize when the TCVs were actuated, the pressure switches were unable to generate the RPS reactor trip signal on low EHC oil pressure as required. SAFETY ASSESSMENT AND REPORTABILITY The RPS pressure switches associated with the TCV Fast Closure trip are credited in the Updated Final Safety Analysis Report (UFSAR) Chapter 15 for initiating a reactor trip during both the Turbine Trip and Generator Load Reject events. For the Turbine Trip event, the UFSAR credits both the TCV RPS pressure switches and the Turbine Stop Valve (TSV) (EIIS Code: ISV} RPS instrumentation for initiating a reactor trip. During the period when the TCV RPS pressure switches were inoperable, the TSV instrumentation remained operable; therefore, a Turbine Trip event would have resulted in a reactor trip. For the Generator Load Reject event, the UFSAR credits only the TCV RPS pressure switches for initiating a reactor trip. However, the UFSAR evaluates the condition when the reactor is not tripped by the TCV RPS instrumentation during a Generator Load Reject event. In such cases, a High Flux scram is credited to mitigate the event, concluding that no fuel damage would occur and that the event remains within acceptance criteria. Accordingly, there were no safety consequences as a result of the inoperability of the TCV RPS pressure switches. Considering the failure history of the TCV RPS pressure switches, the simultaneous inoperability of multiple TCV RPS pressure switches, and since there is no other equipment in the same system as the TCV RPS pressure switches that would trip the reactor during a Generator Load Reject, this event is reportable per 10 CFR 50.73(a)(2)(i}(B) as a condition prohibited by TS and per 10 CFR 50.73(a)(2)(v)(A) as a condition that could have prevented fulfillment of a safety function. Additionally, the event is also reportable per 10 CFR 50. 73(a}(2)(vii) due to degraded EHC oil creating a common cause condition that resulted in the inoperability of multiple, independent RPS channels. CORRECTIVE ACTIONS Corrective actions included purging the EHC sensing lines, replacing the fast acting solenoid for one of the TCVs, installing temporary fluid conditioning units, increasing the TCV SR frequency, which helps prevent fluid stagnation and flushes contaminants, reducing varnish buildup and sticking. Additional, planned corrective actions include replacing TCV insulation, replacing the remaining fast acting and test solenoids, and implementing a permanent EHC filtration upgrade. PREVIOUS SIMILAR EVENTS None. | ML25353A533 | 0 | good
Dresden Nuclear Power Station | Unit 2 | Valid Reactor Protection System Actuation While Shutdown | 12-26-2025 | At 0117 CDT on 10/27/2025, with Unit 2 in Mode 3 at 0 percent power, an actuation of the Reactor Protection System (RPS) occurred during restoration of the Scram Discharge Volume (SDV) high level bypass switch to normal. The cause of the RPS system actuation was a valid high level in the SDV. All control rods had been previously inserted and the RPS system automatically initiated a scram signal as designed when the SDV high level signal was received. The scram was reset in accordance with station procedures at 0121 CDT. An evaluation of this event is currently in progress to determine any contributing causes to the event as well as additional corrective actions. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) for a valid RPS system actuation. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, library, and Information Collections Branch (T-6 A1 0M), U. S. Nuclear Regulalory Commission. Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/readinq-rm/doc-collections/nuregs/staff/sr1022/r3D displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 SEQUENTIAL REV YEAR NUMBER NO. Dresden Nuclear Power Station 00237 □ 052 2025 - 002 - 00 | PLANT AND SYSTEM IDENTIFICATION - UNIT 2 General Electric - Boiling Water Reactor, 2957 megawatts thermal rated core power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. A. CONDITIONS PRIOR TO EVENT Unit: 2 Event Date: October 27, 2025 Event Time: 0117 CDT Reactor Mode: 3 Mode Name: Hot Shutdown Power Level: 0% No systems, structures, or components that were inoperable at the start of the event contributed to the event. 8. DESCRIPTION OF EVENT At 0117 CDT on 10/27/2025, with Unit 2 in Mode 3 at O percent power, an actuation of the Reactor Protection System (RPS) [JC] occurred during restoration of the Scram Discharge Volume (SDV) high level bypass switch to bypass switch to normal. The cause of the RPS [JC] system actuation was a valid high level in the SDV. All control rods had been previously inserted and the RPS [JC] system automatically initiated a scram signal as designed when the SDV high level signal was received. The scram was reset 0121 CDT in accordance with station procedures. ENS report #58008 was transmitted to the NRC at 0750 CDT on 10/27/2025. An evaluation of this event is currently in progress. This event is being reported in accordance with 10 CFR 50. 73(a)(2)(iv)(A). C. CAUSE OF EVENT The cause of the event was a valid high level in the SDV. An evaluation of the event is currently in progress. A supplemental report will be submitted with the conclusions of this evaluation. D. SAFETY ANALYSIS The RPS [JC] monitors reactor [RCT] core parameters. If these parameters exceed predetermined limits, the RPS [JC] logic will initiate a scram. The SDV is used to limit the loss of, and contain, the reactor vessel [RPV] water from all Control Rod Drives (CRDs) [AA] during a scram. During normal operation, the SDV is empty with open drain [ORN] and vent valves [VTV]. On a scram signal, the RPS [JC] is deenergized and the SDV pilot valves [V] vent the discharge volume valve [VJ operators, causing them to close. All systems and components responded as expected to the valid high SDV level signal. Additionally, all CRDs [AA] had been previously inserted. There was no impact to the health and safety of the public from this event. | ML25360A001 | 0 | good
Clinton Power Station 00461 1 OF 3 | Unknown Unit | Manual Scram Due to Main EHC Leak | 12-16-2025 | On October 22, 2025, at 1535, the Clinton Unit 1 reactor was manually scrammed due to low turbine Main Electro-Hydraulic Control oil system (Main EHC) reservoir level caused by a leak that had developed on Turbine Control Valve #3 (TCV3). This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) for "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section." The specific system listed in that paragraph that actuated was the "Reactor protection system (RPS) including: reactor scram or reactor trip." NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Ubrary, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nn::.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 SEQUENTIAL REV YEAR NUMBER NO. Clinton Power Station 00461 □ 052 2025 - 003 00 | CONDITION PRIOR TO THE EVENT Unit: 1 Event Date: October 22, 2025, Event Time: 15:35 CST Mode: 1 Mode Name: Power Operation Reactor Power: 86% EVENT DESCRIPTION On October 22, 2025, 1504, operators observed abnormal valve conditions (main turbine bypass valves open and TCV3 indicated closed) and initiated off-normal procedures to lower power in response to unexpected loss of feedwater heating. Main EHC reservoir level was observed to be dropping rapidly (approximately 1 inch/minute), prompting an immediate operator action to makeup reservoir level. Due to the large leak being un-isolable and Main EHC fluid level reaching the low reservoir level in which Main EHC pumps are required to be secured, a manual scram was inserted at 1535 with the reactor at 86% power. Final Main EHC fluid reservoir level was -24.5" and an estimated 440 gallons of EHC fluid leaked during this event. CAUSE OF THE EVENT The apparent cause of the Main EHC leak was a failure of four tie rods associated with TCV3 due to high cyclic fatigue as a result of inadequate torquing during the most recent refurbishment by the vendor. Post-SCRAM inspections identified significant mechanical damage to the TCV3 actuator, including a dislodged backing plate, and sheared four of the eight tie rods. Two of the remaining four tie rods were found to be under-torqued (one finger tight, the other at under 200 ft-lbs). The TCV3 actuator has since been replaced to correct the source of the leak. During the extent of condition investigation, Turbine Control Valve #1 (TCV1) actuator tie rods failed an initial resonance test and were replaced to preclude a similar failure. While preparing to install the replacement actuator for TCV1, the tie rods on the new actuator were torque-tested and three were found to be under torqued at 350 ft-lbs rather than the prescribed torque of 500 ft-lbs. In addition, the lower O-ring was visible in the groove when observed with a borescope from inside the cylinder. When properly torqued, the lower O-ring was no longer visible. SAFETY CONSEQUENCES There were no safety consequences impacting plant or public safety as a result of this event. The trip was not complex, with all systems responding normally post-trip. Decay heat was removed post-trip by discharging steam to the Main Condenser using the Turbine Bypass Valves which have a separate electro-hydraulic oil system. There was no loss of any safety function that would have prevented fulfillment of actions necessary to 1) shutdown the reactor and maintain it in a safe shutdown condition, 2) remove residual heat, 3) control the release of radioactive material, or 4) mitigate the consequences of an accident. NRG FORM 366A (04-02-2024) Page_2_ of _3_ | ML25364A102 | 0 | good
Clinton Power Station | Unknown Unit | Emergency Diesel Generator Automatic Start due to Emergency Reserve Auxiliary Transformer Trip | 01-13-2026 | At 1351 on 11/14/25, with the unit in Mode 1 at 99% power, an actuation of the Division 1, 2, and 3 Emergency Diesel Generators (EDGs) occurred when a fault occurred on the Emergency Reserve Auxiliary Transformer (ERAT). The Reserve Auxiliary Transformer (RAT) B was previously de-energized and isolated for maintenance. The cause of the Division 1, 2, and 3 EDGs auto-start was an actuation of the Loss of Voltage Function undervoltage relays for each respective bus. The Division 1, 2, and 3 ED Gs automatically started as designed when the applicable Loss of Voltage signals were received. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) for "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section." The specific system listed in that paragraph that actuated was the "Emergency ac electrical power systems, including: emergency diesel generators (EDGs); ... and BWR dedicated Division 3 EDGs." ( N 04 R -0 G 2 -2 F 0 O 24 R I M 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 Estimated burden per response to ccmp\y with this mandatory cclleclion request. 80 hours. Reported LICENSEE EVENT REPORT (LER) r le e s g s a o rd n i s n g le a b r u n r e d d e n a r e e s t i i n m c a o t r e p o lo ra t t e he d F in O to I A th e li b li r c a e r n y s . in a g n d p I r n o f c o e r s m s a a ti n o d n f C ed o ll b e a c c tio k n t s o i B n r d a u n s c t h ry . I T S -6 e n A d 1 0 c M om J. m U e . n S ts . CONTINUATION SHEET N ln u fo c c le o a ll r e cts. R R e e g s u o la u t , o c r e y @ nr C c. o g m ov m . is a s n i d o n t . h e 0 W M a B s h r i e n v g i t e o w n e . r at D : C 0 MB 2 O 05 ff 5 ic 5 e -0 o 0 f 0 I 1 n , f orm o a r t ion b a y n d R em eg a u il l ator t y o (See NUREG-1022, R.3 for instruction and guidance for completing this form A W ff a a s ir h s in . g (3 to 1 n 5 . 0 - D 0 C 10 4 2 ) 0 , 5 A 0 t 3 tn . · T D h e e s k N R O C ffi c m er a y fo r n t o h t e c N o u n c d l u e c a t r o R r e s g p u o la n to so ry r . C a o n m d m a is s p i e o r n s , o 7 n 2 5 is 1 n 7 o 1h t r S e t q re u e ir t e d N W to , b.l!_p_//wwvf~D re. gov/ re ad inq-rm/doc-coll ections/n ureq s/staff/sr1 022/r3/) d re is s p p l o a n y d s a lo c . u a rre c n o tl l y le c v t a io lid n 0 o M f B in f c o o rm nt a ro ti l o n n u m un b l e e r s . s the document requesting er requiring the collecf,on 1. FACILITY NAME II 050 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Clinton Power Station 00461 NUMBER NO. D 052 2025 - 004 00 | CONDITION PRIOR TO THE EVENT Unit: 1 Event Date: November 14, 2025, Event Time: 13:51 CST Mode: 1 Mode Name: Power Operation Reactor Power: 99% EVENT DESCRIPTION A v r 3 n p N s e a t . o e r 3 o s e l u e 1 i . v p d v 8 3 r d e e c i . 5 e o 1 a m e c 1 d u u t ) i b . s L t v C a o e l o e T y n m S r s h d b t s 9 T a e a u , t u k o o i s t 2 e c t r f n e i i 0 n l p V i s s z 2 N t o o i w 5 a u n o l u . r t g n a a v t t A t s e g i s a o l t m e i a f g b 3 t h s n o b F r 0 e e e t a e u - h r s d l r n v t u i a t o i c m 1 o c l y f t t 4 e f i e t o s , o h R i n a 2 f o t e i e n s 0 a f u d k D 2 t s p n h 5 o i I m h d v e n , u i a e f s a C r e o s r c i d o v v r l e e i m e e o n n - s n t l t e t o b o 1 t a w d , - o n , g p e t t 2 C h e h h r P , e e a o o r i a n e s m w r s n o e l e a t d p e p a s y d l r e t t e 3 s i o i o S r f t r f a i f E n o e e t o b a n D d r r w l t e e i G o e T n t a o a n a s t i s m i c . n a t U h i h d l e n A e n o l C l u f i L i v r o t n t C l e a r h n 1 a r O s r o r c v e e e s r u a e x m q 3 r i 1 p u . l r a 8 a E E e e ir . b l O n 1 r e 4 l i l t e d i e G . n 1 c n e s 6 t R o a o c u 0 n c A e s p V t s d t d T i a o u i o t A r n p i a 8 n o t C e p n A t d ( o N r 3 i . b r A p 2 o 4 a t u , . v 5 n o m s c e W d f k o a a m t V h h o m i c n b e e p tu p t o e n e e a l f E r e r n f t t a s R 1 h t e a i i t 6 n t e d n e A e , g c d T E a 2 e p r s p 0 R ( o e a 1 r 2 d w q A o t 3 5 e u p T e 8 2 . s i e r r 0 i t e k r g r s 0 l i V d y n o p 0 , e u p a o C d c r e c f c a , f d S t s e i r , p o T i ) r t y r n t e h h o o i s n e a v p n g A i d o d T w t i S b n h 1 e e g e a r e i s r a n CAUSE OF THE EVENT Actuation of the Division 1, 2, and 3 loss of voltage undervoltage relays due to a trip of the ERAT SAFETY CONSEQUENCES T i T b t c i m n h h l u h a e d p s i e s s e , a C s p E c e a l e t a 1 s v R i n n s e E A w d g s n T b e e t 1 p u n l w l t E l s t r a a a . a o n A s s n I f t n C s t t b o h h f t o o r e h p a . u r e o p t m E n w u u e d D s b s e v e l e G t r i e d c h d n s s e s b y t t t o a y s e h o t f l e e e f t s e h m m l t t c o y a e t s s , r r a i t a e s c e s n l a a v a o n a l e a c f d l s p h y b r , s o e l o o E i w s r t s a h e O u e d s o l G n t r p f t o o f o h U r s r f o n e m e F t m d h t S r a e e i i s A l s d t d h o R u e a e a f v n f u p s C e 1 d t i p o n t h a 3 e r m t n a 8 o , s t p k p a a o V t r t b n e i i u c a u d o r a r t s c f e 1 l e t f l e h s l y 5 s y s i e . . t s e r to o T e t a f s h r t w o p h e te u a e o d i r s w n c t r s e e a n a t n r o r n t u d o ( s r r m i a e e l 4 o d s e n 1 a e i n t o 6 . d r t a 0 a v e T c e V t d h i t o i e a a v b n n r e u y e d a x c r n i w e l e o i d a l e m n e r r c t a y e e r o s o r b n e g l n s u t o e r a s o a n s s l n c v s s a d y o o f f e l o c t r c a t e i r i y a r g s c e t e c e e u a o r d i c t v t n o r h e w y s e e C i t w t a r q h a l c h a u n h t i s e c h s s n h i o f s o c n 1 a r e e s E m r s v i e t e A e e r n C s t ) . to CORRECTIVE ACTIONS t t I h r m a e m n n s e f r e d e r i s a r t e t o e d r e C t d o o t a r o r n e t c h o t e f i f v s e E it R e A A c s T t o io . u n r R c s A e : T T s h u B e p w p s l a e y s c in t g i r o e n t t h u o e rn f e lo E d a R d t A o w T s it e b h r u v s i i t c s a e E f f f e O ro c G m te s d p e l b c a y u n r n t e h e d e d a fa m n u d a l t i p n w l t a e a c n s e a d i n s c o in e la . a te E s d a t c a a h n n d d C b l q y a u s l a i s n r e a 1 u n E p t i . 4 n 1 e 6 d 0 . V P o A w C e b r u w s a s w as PREVIOUS OCCURRENCES A S ta re ti v o i n e . w of Licensee Event Reports for the past five years identified no previous similar occurrences at Clinton Power Page_2_ of _2_ | ML26015A092 | 0 | good
Dresden Nuclear Power Station | Unit 2 | High Pressure Coolant Injection Inoperable Due to Failed Indicating Light and Blown Fuse | 01-15-2026 | At 1613 CST on 11 /17 /25 with Unit 2 in Mode 2, Startup, at 2 percent power, it was discovered that the single train of high 1 pressure coolant injection (HPCI) was inoperable. The cause of the HPCI inoperability was a damaged stop valve closed indicating light socket and an opened negative 125 VDC fuse that occurred when the Unit 2 HPCI Turbine Turning Gear engaged. The turning gear motor turned off without operator action. The stop valve closed indicating circuit was isolated and the fuse was replaced in accordance with station procedures and HPCI operability was restored at 2253 CST. An evaluation of the event is in progress and a supplemental report will be submitted with the conclusions of the evaluation. This report is being submitted in accordance with 10 CFR 50. 73(a)(2)(v)(D) for an event or condition that could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04--02-2024) Estimated burden per response to comply with this mandatory collection request 80 hours. Reported .$ •• lessons learned are incorporated into the licensing process and fed back to industry. Send comments F ••• . LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA Library. and Information Collections Branch (T-6 A10M). U S Nuclear Regulatory Commission, Washington, DC 20555-0001 or by email to ..... CONTINUATION SHEET lnfocollects Resource@nrc.gov, and the 0MB reviewer at 0MB Office of Information and Regulatory Affalfs. (3150-0104), Attn Desk Officer for the Nuclear Regulatory Commission 725 17th Street NW Washington, DC 20503 The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to. a collection of information unless the document requesting or requmng the collection http://www.n rc.qov/reading-rm/doc-collections/n uregs/staff/sr1022/r30 displays a currently valid 0MB control number 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 SEQUENTIAL REV YEAR NUMBER NO. Dresden Nuclear Power Station, Unit 2 00237 □ 052 2025 - 003 - 00 | PLANT AND SYSTEM IDENTIFICATION - UNIT 2 General Electric - Boiling Water Reactor, 2957 megawatts thermal rated core power Energy Industry Identification System (EIIS) codes are identified in the text as [XX] A. CONDITIONS PRIOR TO EVENT Unit: 2 Event Date: November 17, 2025 Event Time: 1613 CST Reactor Mode: 2 Mode Name: Startup Power Level: 2% Pressure level: 185 psig Temperature: 376 °F No systems, structures, or components that were inoperable at the start of the event contributed to the event. B. DESCRIPTION OF EVENT At 1613 CST on 11/17/25, with Unit 2 in Mode 2, Startup, at 2 percent power, it was discovered that the single train of high pressure coolant injection (HPCI) [BJ] was inoperable. The cause of the HPCI inoperability was a failed stop valve indicating light [IL] circuit and a blown negative 125 VDC fuse [FU] that occurred when the Unit 2 HPCI Turbine [TRB] Turning Gear [TGR] engaged. The turning gear motor [MO] turned off without operator action. The indicating light circuit was isolated and the negative 125 VDC fuse was replaced in accordance with station procedures and HPCI operability was restored at 2253 CST on 11/17/25. Event Notification System (ENS) report number 58043 was transmitted to the NRC at 2328 CST on 11/17/25. This event is being reported in accordance with 1O CFR 50.7 3(a)(2)(v)(D). C. CAUSE OF EVENT The cause of the event was a damaged indicating light socket and a blown negative 125 VDC fuse when the HPCI Turbine Turning Gear was engaged. The negative 125 VDC fuse in question is required for the initiation of the steam turbine. An evaluation of the event is currently in progress. A supplemental report will be submitted with the conclusions of this evaluation. D. SAFETY ANALYSIS System Design The HPCI system is designed to ensure that adequate core cooling takes place for all break sizes less than those for which Low Pressure Coolant Injection (LPCI) [BO] or Core Spray [BM] systems can adequately protect the core without assistance from other engineered safety features. The negative 125 VDC fuse in | ML26022A036 | 0 | good
Browns Ferry Nuclear Plant | Unit 1 | Reactor SCRAM due to Low Reactor Water Level | 01-29-2026 | On August 1, 2025, at 2350 Central Daylight Time, Browns Ferry Unit 1 experienced an automatic scram due to low reactor water level. A low reactor water level of +2 inches resulted in a valid actuation of the Reactor Protection System which caused all of the rods to insert. During the scram response, there was a valid actuation of the Primary Containment Isolation System groups 2, 3, 6, & 8. Upon receipt of these signals, all components actuated as required. Following the scram, reactor water level lowered below the -45 inch setpoint, actuating High Pressure Coolant Injection and Reactor Core Isolation Coolant and tripped both Reactor Recirculation pumps as required. Operations responded and stabilized the plant. The root cause was determined to be the installed Foxboro Feedwater Level Control system design and subsequent reviews failed to identify the single point vulnerability and inherit potential failure modes for the Foxboro System. The root cause will be addressed through elimination of the single point vulnerability in the Reactor Feed Pump speed control system. The Tennessee Valley Authority is submitting this report in accordance with Title 10 of the Code of Federal Regulations 50.73(a)(2)(iv)(A), as any event or condition that resulted in manual or automatic actuation of the Reactor Protection System and the Primary Containment Isolation System. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ☒ 050 SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 1 00259 NUMBER NO. ☐ 052 2025 - 001 - 01 | I. Plant Operating Conditions before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Unit 1, was in Mode 1 at 100 percent power. There were no impacts on Units 2 and 3. II. Description of Event A. Event Summary On August 1, 2025, at 2350 Central Daylight Time (CDT), Browns Ferry Unit 1 experienced an automatic scram due to low reactor water level. A low reactor water level of +2 inches resulted in a valid actuation of the Reactor Protection System (RPS)[JC] which caused all of the rods to insert. During the scram response, there was a valid actuation of the Primary Containment Isolation System (PCIS)[JM] groups 2, 3, 6, & 8. Upon receipt of these signals, all components actuated as required. Following the scram, reactor water level lowered below the -45 inch setpoint, actuating High Pressure Coolant Injection (HPCI)[BJ] and Reactor Core Isolation Coolant (RCIC)[BN] and tripped both Reactor Recirculation pumps as required. Operations responded and stabilized the plant. Event Notification 57847 was made to the NRC Operations Center on August 2, 2025, at 0429 EDT. The Tennessee Valley Authority (TVA) is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(iv)(A), as any event or condition that resulted in manual or automatic actuation of the RPS and the PCIS. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML26029A088 | 0 | good
Browns Ferry Nuclear Plant | Unit 3 | Reactor Core Isolation Cooling Inoperable due to a Failed Ramp Generating Signal Converter | 02-02-2026 | On August 19, 2025, at 1128 Central Daylight Time (CDT), during the performance of 3-SR-3.5.3.3, RCIC System Rated Flow at Normal Operating Pressure, the Reactor Core Isolation Cooling system (RCIC) failed to achieve required flow rate and pump discharge pressure due to an issue with the governor control system. Upon investigation, it was determined that the Unit 3 RCIC Ramp Generating Signal Converter (RGSC) module had failed on July 20, 2025. On August 23, 2025, at approximately 0108 CDT, the Unit 3 RCIC was declared operable following replacement of the RGSC and successful Cold Quick Start Post Maintenance Testing. The apparent cause of this condition was accumulated stress over time on the operational amplifiers leading to failure of the RGSC. The corrective actions for this condition are to replace the Unit 3 RCIC RGSC, to replace aging RGSCs and Electro-Governor Magnetic Pickups at the earliest opportunity, and to create new PMs to periodically replace similar components on the Unit 1, 2, and 3 RCIC and High Pressure Coolant Injection systems. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION (04-02-2024) LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME ց 050 2. DOCKET NUMBER 3. LER NUMBER Browns Ferry Nuclear Plant, Unit 3 00296 YEAR SEQUENTIAL NUMBER REV NO. տ 052 2025 - 002 - 01 | Not Found | ML26033A500 | 1 | ok
Browns Ferry Nuclear Plant | Unknown Unit | Unit 1/2 480V Load Shed Logic Division I/II Inoperable Longer Than Allowed by Technical Specifications | 02-17-2026 | At Browns Ferry Nuclear Plant, Units 1 and 2, on November 5, 2025, at 1157 Central Daylight Time, the performance of 480V Load Shedding Logic System Functional Test (Division I) and subsequent troubleshooting discovered that the tripping circuit for the 480V Control Bay Vent Board (CBVB) A Normal Feeder Breakers position switch was not closed. From the past operability evaluation, it was concluded that, in the event of there were a Unit 1 and/or Unit 2 loss of offsite power and an accident signal, the loads on the 480V CBVB A would not have shed, and the potential to overload Diesel Generator (DG) A existed. Based on the results of the analysis and the overloading scenarios associated with this condition, it was concluded that DG A would not have been overloaded and was capable to perform its intended safety function for its mission time. Because of this condition, the 480V Load Shed logic did not meet Technical Specifications (TS) Limited Condition of Operation 3.8.1 multiple times in Modes 1, 2, and 3 from November 5, 2022, to November 5, 2025. Because it was determined that DG A was fully capable of performing its safety functions with the additional load from 480V CBVB A, there is no safety significance with this condition present. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION (04-02-2024) LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 050 2. DOCKET NUMBER 3. LER NUMBER Browns Ferry Nuclear Plant, Units 1 and 2 00259 YEAR SEQUENTIAL NUMBER REV NO. 052 2025 - 002 - 00 | Not Found | ML26048A077 | 1 | ok
Susquehanna Steam Electric Station (SSES) | Unit 2 | Arc Flash on 500 kilovolt Transmission Lines Resulted in Main Generator Trip and Automatic Reactor Scram | 02-24-2026 | On October 28, 2025, at approximately 19:04, Susquehanna Steam Electric Station (SSES) Unit 2 experienced a main turbine trip followed by an automatic reactor scram when an arc flash on the 500 kilovolt (kV) lines occurred during a hydrogen vendor manual venting evolution. The event was reported by Event Notification 58012 in accordance with 10 CFR 50.72(b)(2)(iv)(B) as an event that resulted in an automatic actuation of the Reactor Protection System and 10 CFR 50. 72(b )(2)(xi) as an event that resulted in an offsite notification made to the Pennsylvania Emergency Management Agency. This event is also reportable in accordance with 10 CFR 50. 73(a)(2)(iv)(A) as an event that resulted in an automatic actuation of the Reactor Protection System. The cause of the event was arc flash as a result of hydrogen gases vented from the vendor-owned Hydrogen Tank Farm during normal vendor evolution contacting overhead 500 kV transmission lines. Key corrective actions include establishment of an alternative location for venting the vendor hydrogen tank trailer, revision of venting evolution instructions, and evaluation and implementation of options to increase clearance between the Hydrogen Tank Farm vent and overhead transmission lines. NRC FORM 366A (04-02-2024) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001 , or by email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 2. DOCKET NUMBER 3. LER NUMBER 1. FACILITY NAME ,-------------, ~ Susquehanna Steam Electric Station (SSES) Unit2 □ 050 052 I 00388 D NUMBER NO. I YEAR SEQUENTIAL REV ~-I 001 1-0 | CONDITIONS PRIOR TO THE EVENT Unit 1: Mode 1, approximately 100% Rated Thermal Power Unit 2: Mode 1, approximately 100% Rated Thermal Power There were no inoperable structures, systems, or components at the start of the event that contributed to the event. EVENT DESCRIPTION On October 28, 2025, at approximately 19:04, Susquehanna Steam Electric Station (SSES) Unit 2 experienced a main turbine trip [EIIS System Code - IT] followed by an automatic reactor scram when an arc flash on the 500 kilovolt (kV) lines occurred during a hydrogen vendor manual venting evolution. The event was reported by Event Notification 58012 in accordance with 10 CFR 50. 72(b )(2)(iv)(B) as an event that resulted in an automatic actuation of the Reactor Protection System and 10 CFR 50. 72(b )(2)(xi) as an event that resulted in an off site notification made to the Pennsylvania Emergency Management Agency. This event is also reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in an automatic actuation of the Reactor Protection System (including a reactor scram). The following timeline demonstrates the sequence of events: 10/28/2025 Before 18: 16: Vendor driver notifies Control Room that they will be filling the liquid hydrogen tank at the Hydrogen Tank Farm. 10/28/2025 18: 16: Vendor driver begins filling the liquid hydrogen tank at the Hydrogen Tank Farm. 10/28/2025 19:04: Liquid hydrogen tank is filled. Vendor driver begins to depressurize the tanker truck via the hydrogen tank exhaust stack at the Hydrogen Tank Farm. 10/28/2025 19:04: An arc is visible in the area of the resultant plume from the hydrogen release on the 500 kV conductors overhead the hydrogen tank in the Hydrogen Tank Farm. 10/28/2025 19:04: Unit 2 experiences an automatic scram due to Main Turbine trip caused by Main Generator [EIIS System Code - TB] differential line current and enters Mode 3. All plant systems responded normally following the automatic reactor scram. Decay heat was removed by discharging steam to the main condenser using the turbine bypass valves. Unit 1 was unaffected by the event and remained at approximately 100% Rated Thermal Power. The affected 500 kV lines were placed in service in August 2023. While similar liquid hydrogen activities are routinely performed at this location, this type of event has not previously occurred. Following visual inspection and testing of the 500kV lines and a review of the post-trip plant response, SSES Unit 2 was returned to Mode 1 operation on October 31, 2025. | ML26055A051 | 0 | good
LaSalle County Station | Unit 1 | Manual Scram Due to Degrading Containment Parameters | 02-24-2026 | On December 28, 2025, at 1606 CST, LaSalle Station Unit 1 was manually scrammed due to degrading containment parameters associated with a leak from the 'B' reactor recirculation pump line. The scram was not complex. All control rods fully inserted as expected; no Emergency Core Cooling Systems actuated or injected into the core. This event did not pose a threat to the health and safety of the public. This event was reported via Event Notification #58100 under 1 OC FR 50.72(b)(2)(iv)(B) as an event that resulted in actuation of the Reactor Protection System when the Reactor was critical. Subsequent Event Notification #58102 under 10 CFR 50.72(b)(3)(ii)(A) reported a degraded reactor coolant system pressure boundary due to a through-wall leak identified on a reactor recirculation system three-quarter inch vent valve. Failure analysis attributed the cause of the leakage to vibration induced cyclic fatigue. Corrective actions include replacement of the affected component and planned inspections/modifications to similar equipment configurations. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply v,;th this mandatory collection request 80 hours. Reported lessons learned are incorporated into Ille licensing process and led back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and lnfonnation Collections Branch (Hi A10M), U, S. Nudear Regulatory Commission, Washington, DC 20555-0001, or by emaa to CONTINUATION SHEET lnfocollects.Resource@nrc.gov. and the 0MB reviewer at: 0MB Office of lnfonnation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nudear Regulatory Commission, 725 17111 Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of infonnation unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D displays a currenfly valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 SEQUENTIAL REV YEAR NUMBER NO. LaSalle County Station, Unit 1 00373 □ 052 2025 - 002 00 | Plant and System Identification LaSalle Country Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected systems were the Reactor Protection System (RPS) and Reactor Recirculation (RR) System. Condition Prior to Event Unit(s): 1 Date: December 28, 2025 Time: 1606 CST Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 93 percent No systems, structures, or components that were inoperable at the start of the event contributed to the event. Description On December 28, 2025 at 1606 CST, LaSalle County Station Unit 1 was manually scrammed due to degrading containment parameters caused by unidentified drywell leakage. Following the manual scram, personnel entered the Unit 1 drywell to investigate the source of the leakage. The investigation identified a degraded reactor coolant system pressure boundary due to a through wall leak from an RR system vent valve. Cause Through wall leakage was identified on the bonnet and body-to-bonnet seal weld of the upstream manually operated vent valve for a reactor recirculation pump discharge flow control valve. Failure analysis determined the leakage was caused by vibration induced fatigue cracking. Reportability and Safety Analysis The safety significance of this event was minimal. All control rods fully inserted and all systems responded as expected to the scram. Makeup capability was adequate to compensate for the leak. Emergency Core Cooling Systems were not needed, but operable and capable of fulfilling their intended safety functions. This event did not meet the NEI 99-02 definition of an unplanned scram with complications. The event did not constitute a safety system functional failure (SSFF) as defined in accordance with NEI 99-02, "Regulatory Assessment Performance Indicator Guideline." RPS actuation is reportable under 10 CFR 50. 72(b )(2)(iv)(B) as an event or condition that results in the actuation of the RPS when the reactor is critical. An ENS report was made to the NRC at 2026 EST on December 28, 2025 (EN #58100). Upon determination of the leakage source, ENS report #58102 under 10 CFR 50.72(b)(3)(ii)(A) addressed the degraded reactor coolant system pressure boundary. Corrective Actions Immediate corrective actions taken in response to the condition were: • Removed the failed valve assembly and installed blind flange connection • Initiated failure analysis and causal investigation Planned corrective actions are: • Installation of replacement vent valve assembly • Inspection and/or replacement of similar piping and valve assemblies | ML26055A084 | 0 | good
Clinton Power Station 00461 1 OF 2 | Unknown Unit | Automatic SCRAM on High Reactor Water Level | 03-03-2026 | On October 6, 2025, during reactor startup, the Clinton Unit 1 reactor automatically scrammed due to high reactor water level. The cause of the high reactor water level was a failure of a Turbine Driven Reactor Feed Pump (TDRFP) servo valve that resulted in excessive feedwater flow to the reactor vessel. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) for “Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section.” The specific system listed in that paragraph that actuated was the “Reactor protection system (RPS) including: reactor scram or reactor trip.” NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 SEQUENTIAL REV YEAR NUMBER NO. Clinton Power Station 00461  052 2025 - 002 - 00 | CONDITION PRIOR TO THE EVENT Unit: 1 Event Date: October 6, 2025 Event Time: 03:21 CST Mode: 1 Mode Name: Power Operation Reactor Power: 23% EVENT DESCRIPTION On October 6, 2025, during reactor startup from the Clinton Unit 1 refueling outage, Turbine Driven Reactor Feed Pump (TDRFP) ‘A ‘was placed in service. While manually raising the speed of the TDRFP, the operator noticed that there was no rise in speed initially. The operator attempted again to raise pump speed. Speed then rose rapidly to 1300 rpm and went above the target setpoint of 1000 rpm. The operator placed the pump speed control mode in automatic to lower speed. TDRFP speed stabilized for about a minute before speed unexpectedly began rising rapidly to 4300 rpm. The operator then tripped the TDRFP. At the time of the trip, reactor water level was approximately 47 inches and rising. Reactor water level continued to rise, and when it reached 52 inches, an automatic reactor scram occurred. CAUSE OF THE EVENT A Root Cause investigation determined the event was caused by scoring on the A-port side of the servo valve body, confirming abrasive interaction. The scoring, caused by lodged debris, increased friction or temporarily locked the servo swing plate. The servo motor had to overcome additional drag, which it could not do effectively. As a result, the valve did not respond to a decreasing demand signal, causing failure to control the operating cylinder responsible for closing the low- pressure steam control valve resulting in a Reactor Protective System (RPS) SCRAM on level 8. SAFETY CONSEQUENCES There were no safety consequences impacting plant or public safety as a result of this event. The reactor trip system responded automatically due to the trip signal received. Additionally, the TDRFP was tripped prior to the scram, so no additional feedwater would have been injected. There was no loss of any function that would have prevented fulfillment of actions necessary to 1) shutdown the reactor and maintain it in a safe shutdown condition, 2) remove residual heat, 3) control the release of radioactive material, or 4) mitigate the consequences of an accident There was no loss of safety function for this event. CORRECTIVE ACTIONS TDRFP B has the same control loop as TDRFP A and would be susceptible to the same failures under the conditions that occurred during start-up. To mitigate the same failures, the TDRFP B servo valve SV-2 was replaced before operation. To reduce risk during future startups, operating procedures will be changed to exclusively utilize a “rolling standby” mode before feeding the Reactor Pressure Vessel. Servo tested at power labs and final report of findings issued back to CPS. Prior data of historical start-ups that included perturbations of the feed pump show evidence of starting up and having potential material or air in the oil that works through the system during initial start-up. PREVIOUS OCCURRENCES A review of Licensee Event Reports for the past five years identified no previous similar occurrences at Clinton Power Station. | ML26078A183 | 0 | good
LaSalle County Station | Unit 1 | Automatic Scram Due to Turbine Control Valves Fast Closure on Generator Lockout | 03-27-2026 | On November 2, 2025, at 1346 CST, LaSalle Station Unit 1 experienced a Unit Auxiliary Transformer (UAT) trip. A generator lockout, turbine control valves fast closure, and reactor scram was automatically initiated by the plant in response to the trip. All control rods fully inserted as expected; no Emergency Core Cooling Systems actuated or injected. Plant operators effectively maintained reactor pressure and level. I I This event did not pose a threat to the health a~d safety of the public. This event was reported via Event No~ification #58018 under 1O CFR 50. 72(b)(2)(iv)(B) as an event that resulted in actuation of the Reactor Protection System when the Reactor was critical. The cause of the transformer trip was corrosion and inadequate divisional separation of test switches which allowed potential unintended interaction between DC divisions within protective relay circuitry. Due to this underlying condition, ground troubleshooting activities caused an inadvertent actuation of the UAT sudden pressure relay trip circuit, resulting in the Unit 1 scram. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRG may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 SEQUENTIAL REV YEAR NUMBER NO. LaSalle County Station, Unit 1 00373 □ 052 2025 - 001 01 | Plant and System Identification LaSalle Country Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the Reactor Protection System (RPS). Condition Prior to Event Unit(s): 1 Date: November 2, 2025 Time: 1346 CST Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 100 percent No systems, structures, or components that were inoperable at the start of the event contributed to the event. Description On October 29, 2025, the Main Control Room received an unexpected 125 VDC ground detector alarm. Troubleshooting activities narrowed the ground location to the Unit 1 UAT trouble alarm circuitry. On November 2, 2025, test switches were opened to isolate the previously identified ground. Opening the switches resulted in a generator lockout, UAT deluge system actuation, turbine control valves fast closure, and automatic reactor scram initiated by RPS in response to the trip. All control rods fully inserted as expected and no Emergency Core Cooling Systems actuated or injected. Plant operators effectively maintained reactor pressure and level, and reset the deluge system following verification of no fire at the transformer. Investigation following the scram identified the UAT sudden pressure relay circuit had energized, however circuit monitoring light indication and oil sample analysis concluded that sudden pressure conditions were not present to trigger a legitimate actuation. Inspection of the UAT local control cabinet identified corrosion at the test switch blocks. Cause The cause of the transformer trip was corrosion and inadequate divisional separation of test switches which allowed potential unintended interaction between DC divisions within protective relay circuitry. Due to this underlying condition, ground troubleshooting activities caused an inadvertent actuation of the UAT sudden pressure relay trip circuit, resulting in the Unit 1 scram. Reportability and Safety Analysis The safety significance of this event was minimal. All control rods fully inserted and all systems responded as expected to the scram. Emergency Core Cooling Systems were not challenged. This event did not meet the NEI 99-02 definition of an unplanned scram with complications. There were no safety system functional failures. RPS actuation is reportable under 1© C FR 50. 72(b )(2)(iv)(B) as an event or condition that results lin the actuation of the RPS when the reactor is critical. AnjENS report was made to the NRC at 1837 EST on Novemb9r 2, 2025 (EN #58018). Corrective Actions Replaced test switch blocks that had exhibited corrosion Relocated test switches to provide divisional separation Disabled sudden pressure relay logic trips of the UAT | ML26086A018 | 0 | good