River Bend Station | Unit 1 | Unsecured Pressure Boundary Door Resulting in Condition That Could Have Prevented Fulfillment of a Safety Function | 09-16-2025 | On July 21, 2025, at 1548 CDT, River Bend Station, Unit 1 (RBS) was operating in Mode 1 at 100% reactor power when the Central Alarm Station (CAS) received a door alarm indicating that an auxiliary building pressure boundary door, PW 123-01 (T-Tunnel Access to 114' Aux West Access), was not fully secured. A security officer was dispatched and found the door closed with the dogs not engaged. PW 123-01 is a Secondary Containment door. With the dogs not engaged, Secondary Containment was declared inoperable. At 1551 CDT, a security officer fully engaged the dogs, which restored Secondary Containment. This event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(C), as any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond https ://www .n re. gov/ reading-rm/doc-collections/nu regs/staff/sr1 022/r3/) to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ~ 050 YEAR SEQUENTIAL REV River Bend Station, Unit 1 NUMBER NO. 00458 □ 052 2025 004 00 | Event Description On July 21, 2025, at 1548 CDT, River Bend Station, Unit 1 (RBS) was operating in Mode 1 at 100% reactor power when the Central ~larm Station (CAS) received a door alarm indicating that an auxiliary building [NF] pressure boundary door [DR], PW 123-01 (T- rrunnel Access to 114' Aux West Access), was not fully secured. A security officer was dispatched and found the door closed with the dogs not engaged. PW 123-01 is a Secondary Containment door. With the dogs not engaged, Secondary Containment was declared inoperable. ~t 1548 CDT, Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.6.4.1 Condition A, Secondary Containment inoperable was entered. When the security officer fully engaged the dogs at 1551 CDT, restoring Secondary Containment, LCO 3.6.4.1, Condition A, was exited. rThe event was reported on July 21, 2025, at 2151 CDT in accordance with 10 CFR 50.72(b)(3)(v) for an event or condition that could have prevented fulfillment of a safety function due to the inoperability of Secondary Containment (EN 57820). Event Cause rThe direct cause of this event was a personnel error. PW123-01 was left unsecured because the individual passing through the door closed it but failed to fully engage the dogs. Safety Assessment rThe River Bend Updated Safety Analysis Report describes the sequence of events postulated to occur following a Loss of Coolant ~ccident (LOCA). Part of that analysis is a projection of the maximum radiation dose received by a person at the site boundary. The LOCA dose calculation assumes that the standby gas treatment system is initiated 20 minutes into the event, and that Secondary Containment is at the required negative pressure within 30 minutes, such that filtration may be credited. As such, the safety function of Secondary Containment is maintained as long as the boundary is secured (or capable of being secured) within 20 minutes of the ~ime of the security alarm. Since the subject door was secured within approximately 3 minutes of the time of the alarm, the safety ~unction of Secondary Containment was maintained. This event was of minimal significance with respect to the health and safety of ~he public. While the corresponding functions were declared inoperable from a TS perspective, functionality was maintained, ~herefore, this event is not considered a safety system functional failure. Corrective Actions Completed: -A Performance Analysis was utilized to evaluate if any training deficiencies exist that could have contributed to this event. -Verified Engineering Pre-Job Briefs include door management and traversing to work locations. In Progress: -Performance management actions will be used to reinforce proper behaviors with the individual to prevent future errors. Previous Occurrences rrwo similar events were reported by RBS in LER 050/458-2013-002-00 and LER 050/458-2017-009-00. Both LERs document individual(s) failing to properly secure a door in the auxiliary building pressure boundary. The audible tamper alarms installed as a result of LER 2017-009-00, operated as designed. The tamper alarms are designed to be audible when the door is opened and extinguished upon closure. In the event described in this LER the door was closed but not properly latched. | ML25259A219
Grand Gulf Nuclear Station | Unit 1 | Standby Gas Treatment System Train Inoperable Which Led to a Failure to Identify Condition Prohibited by Technical Specifications | 09-22-2025 | On July 14, 2025, at 12:54 CT, it was identified that the flow recorder [FR] for the Standby Gas Treatment System (SGTS) B train was providing inaccurate information while SGTS B was in standby. SGTS B was determined to be inoperable. A failed flow switch was replaced and SGTS B operability was restored on July 14, 2025. On July 24, 2025, analysis determined that the flow recorder [FR] began receiving inaccurate information on June 21, 2025. This resulted in a condition that was in violation of Technical Specification (TS) 3.6.4.3, Condition A which states that when one SGTS train is inoperable, it must be restored to operable status within seven days. The failure to identify the prohibited condition was caused by operator rounds procedures not having a task to review the SGTS flow. An action has been created to update the relevant procedures. This report is being made in accordance with 10 CFR 50.73(a)(2)(i)(B) for any condition which was prohibited by the plants Technical Specifications. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A1 O M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRG may not conduct or sponsor, and a person is not required to respond https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER 1:8] 050 YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 NUMBER NO. 00416 0 052 2025 004 00 | Plant Conditions: At the time of the event, Grand Gulf Nuclear Station (GGNS) Unit 1 was in MODE 1 at 100 percent power and all safety systems were operable. Description of Event: On July 14, 2025, at 12:54 CT, it was identified that the flow recorder [FR] for the Standby Gas Treatment System (SGTS) B train was providing inaccurate information while SGTS B was in standby. SGTS B was determined to be inoperable. A failed flow switch was replaced and SGTS B operability was restored on July 14, 2025. On July 24, 2025, analysis determined that the flow recorder [FR] began receiving inaccurate information on June 21, 2025. This resulted in a condition that was in violation of Technical Specification (TS) 3.6.4.3, Condition A which states that when one SGTS train is inoperable, it must be restored to operable status within seven days. During this time, SGTS A was operable, and capable of fulfilling the SGTS safety function. Reportability: This report is being made in accordance with 10 CFR 50.73(a)(2)(i)(B) for any condition which was prohibited by the plants Technical Specifications. Cause(s): The failure to identify the prohibited condition was caused by operator rounds procedures not having a task to review the SGTS flow. The cause of the failure to properly detect the inaccurate data and failed flow switch was due to the lack of a task to review the SGTS flow in operator rounds. Corrective Actions: - Replace the faulty filter train B flow low switch. Action completed. - Update 02-S-01-31 Control Room Rounds procedure to include recording values from low flow switches. Action in progress. Safety Significance: There were no actual safety consequences associated with this condition. Plant systems responded as designed. Previous Similar Events: None | ML25265A025
Monticello Nuclear Generating Plant | Unknown Unit | Rainwater Intrusion Caused Failure of Reactor Building Ventilation and Rise in Steam Chase Temperatures | 09-25-2025 | At 22:00 on July 28, 2025, with Monticello Nuclear Generating Plant (MNGP) operating at 100 percent power, secondary containment was declared inoperable due to a Reactor Building Ventilation System failure which caused a degradation of Reactor Building differential pressure that exceeded the Technical Specification limits. This Ventilation System failure led to elevated temperatures in the Steam Chase. Operators began to lower Reactor power to attempt to slow the rising Steam Chase temperature level. At 23:24 on July 28, 2025, with MNGP now operating at 41 percent power, the Reactor was manually scrammed due to Steam Chase temperatures reaching the procedural limit. Operators responded to the trip and stabilized the plant in accordance with approved procedures and safely placed the plant in Mode 3. All systems responded normally post trip. The Ventilation System failure was caused by rainwater intrusion through a leak in the plenum room roof that made contact with and then tripped energized Ventilation System components. The entire plenum room roof is in the process of being replaced. Immediate actions were taken to prevent rainwater intrusion from impacting Ventilation System components while the roof is being replaced. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to http://www.nrc.qov/readinq-rm/doc-collections/nuregs/staff/sr1022/r3/) respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV NUMBER NO. Monticello Nuclear Generating Plant -263 2025 □ 052 - 004 - 00 | EVENT DESCRIPTION AND ANALYSIS On the evening of July 28, 2025, Monticello Nuclear Generating Plant (MNGP) was operating at 100 percent power when a thunderstorm passed over the area. As the storm passed, rainwater began dripping through the roofing material into the plenum room which is located between the Reactor Building and Turbine Building. The water ran down the wall above cabinet N1131, V-EF-24 LOCAL CONTACTOR. At about 20:58 on July 28, 2025, this leak in the plenum roof led to an electrical short of a contactor for motor V-EF-24, REACTOR BUILDING EXHAUST FAN (Reliance Electric, model BFC SO7827-1) [VL]. This short caused a fuse in a General Electric 7700 line breaker B1131, V-EF-24A,B, REACTOR BUILDING MAIN EXHAUST FANS 480 VAC, to open resulting in a loss of power to both Reactor Building main exhaust fans. Then, V-AC-10A and V-AC-10B, REACTOR BUILDING MAIN SUPPLY HVAC UNITS, [VA] tripped as designed with the V-EF-24 flow interlock. With the failure of Reactor Building Exhaust Ventilation and then the subsequent trip of the Reactor Building Supply Ventilation, this resulted in a degradation of the Reactor Building differential pressure. At 22:00, on July 28, 2025, with MNGP still operating at 100 percent power, the differential pressure exceeded the Technical Specifications limit resulting in Secondary Containment being declared as inoperable. With the failure of the Ventilation System, Steam Chase temperatures started to rise. Operators began to lower Reactor power to attempt to slow the rising Steam Chase temperature level. At 23:24 on July 28, 2025, with MNGP now operating at a reduced power of 41 percent, the Operators inserted a manual scram of the Reactor due to the Steam Chase temperatures reaching the procedural limit of 180 degrees Fahrenheit per the criteria in the Ventilation System procedure. This event is reportable per 10 CFR 50.73(a)(2)(v)(C) and 10 CFR 50.73(a)(2)(v)(D) for an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material; and mitigate the consequences of an accident, and per 10 CFR 50.73(a)(2)(iv)(A) due to actuation of the Reactor Protection System. ASSESSMENT OF SAFETY CONSEQUENCES The scram was not complex, with all systems responding normally post scram. Reactor water level was maintained via the Feedwater System. Decay heat was removed by discharging steam to the main condenser using the turbine bypass valves. The health and safety of the public and site personnel were not impacted during this event. CAUSE OF THE EVENT The Ventilation System failure was caused by rainwater intrusion through a leak in the plenum room roof that then made contact with and tripped energized Ventilation System components | ML25268A050
Peach Bottom Atomic Power Station (PBAPS) | Unit 2 | Invalid Actuation Due to Bus Failure | 10-08-2025 | On August 20th, 2025, an electrical fault in a metal enclosed bus duct resulted in the loss of startup switchgear (EIIS: EA) that supplies power to administrative buildings and cooling towers. The electrical transient produced because of this event led to a partial invalid Primary Containment Isolation System (PCIS) (EIIS: JM) isolation including isolation of the Reactor Water Cleanup System (RWCU) (EIIS: CE) on both units. On Unit 2, this condition resulted in actuations of PCIS Group II and III outboard valves and isolation of the RWCU. On Unit 3, this condition resulted in actuations of PCIS Group II and III inboard valves and isolation of RWCU. Additionally, the ‘A’ and ‘B’ Cooling Tower Lift Pumps tripped. Based on the as-found condition of the bus duct, the cause of failure is attributed to a compromised seal on the bus duct cover. The seal degraded over time, allowing water intrusion and ultimately led to a short circuit condition. This condition is reportable under 50.73(a)(2)(iv)(A) as an invalid actuation of general containment isolation signals affecting containment isolation valves in more than one system. The isolation was caused by a loss of power. The actuation was invalid because the conditions for which isolation is required were not present. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid OMB control number. 1.FACILITY NAME 2.DOCKET NUMBER 3. LER NUMBER  050 SEQUENTIAL REV YEAR Peach Bottom Atomic Power Station (PBAPS), NUMBER NO. 00277 Unit 2  052 2025 - 001 - 00 | Plant Operating Conditions Before the Event Prior to the event, Peach Bottom Atomic Power Station, Units 2 and 3 were operating at approximately 100% power in MODE 1. There were no structures, systems or components (SSC) that were inoperable at the start of the event that contributed to the event, except as described below. Event Description On August 20th, 2025 at approximately 04:30am, an electrical fault in a metal enclosed bus duct resulted in the loss of startup switchgear (EIIS: EA) that supplies power to administrative buildings and cooling towers. The electrical transient produced because of this event led to a partial invalid Primary Containment Isolation System (PCIS) (EIIS: JM) isolation including isolation of the Reactor Water Cleanup System (RWCU) (EIIS: CE) on both units. On Unit 2, this condition resulted in actuations of PCIS Group II and III outboard valves and isolation of RWCU. On Unit 3, this condition resulted in actuations of PCIS Group II and III inboard valves and isolation of RWCU. Additionally, the ‘A’ and ‘B’ Cooling Tower Lift Pumps tripped. During the initial inspection of the bus duct, multiple degraded connections were observed. These deteriorations resulted from water intrusion through a degraded seal, leading to corrosion. The degraded seal allowed moisture to enter the bus duct, accelerating the corrosion process and adversely affecting the integrity of the electrical connections. The bus duct heater, which is designed to minimize condensation in the bus assembly, was found to be non-functional. This condition is reportable under 50.73(a)(2)(iv)(A) as an invalid actuation of general containment isolation signals affecting containment isolation valves in more than one system. The isolation was caused by a loss of power. The actuation was invalid because the conditions for which isolation is required were not present. Safety Consequences There were no challenges to plant safety as a result of this event. Both units responded as designed to the electrical transient, and isolations were reset without error. Corrective Actions Corrective actions for this condition include installation of new bus bar and bus duct and establishing a routine inspection of this portion of the bus. Previous Similar Events Peach Bottom experienced invalid actuations due to an emergency bus breaker relay failure in 2019, ref. LER 2019-001-00. | ML25281A097
Peach Bottom Atomic Power Station (PBAPS) | Unit 2 | Uncoordinated DC Circuits Cause Unanalyzed Condition | 10-08-2025 | On 09/04/2025, an analysis was completed which confirmed that six cables associated with direct current circuits (EIIS:EI) at PBAPS Units 2 and 3 were non-compliant with 10CFR50 Appendix R, Section III.G.1, Fire protection of safe shutdown capability. It was determined that the circuits were uncoordinated due to inadequate fuse sizing, meaning that during a postulated fire, the circuit’s fuse may not act to protect the circuit from a fire-induced hot short. Without adequate overcurrent protection for these circuits, a fire-induced short could lead to excessive current through the circuits. This could lead to secondary damage in another fire area where the circuits are routed, challenging the ability to achieve and maintain safe shutdown. Compensatory measures have been implemented and will remain until the identified non-compliant conditions are resolved. This event is reported under 10CFR50.73(a)(2)(ii)(B) as an unanalyzed condition because a fire that affects multiple fire areas is outside the bounds of the 10CFR50 Appendix R Fire Safe Shutdown Analysis. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid OMB control number. 1.FACILITY NAME 2.DOCKET NUMBER 3. LER NUMBER  050 SEQUENTIAL REV YEAR Peach Bottom Atomic Power Station NUMBER NO. 00277 (PBAPS), Unit 2  052 2025 - 002 - 00 | Plant Operating Conditions Before the Event Prior to the event, Peach Bottom Atomic Power Station (PBAPS), Unit 2 was operating at approximately 100% power in MODE 1. PBAPS, Unit 3 was operating at approximately 96% power in MODE 1. There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. Event Description On 09/04/2025, an analysis was completed which confirmed that six cables associated with direct current circuits (EIIS:EI) at PBAPS, Units 2 and 3 were non-compliant with 10 CFR 50 Appendix R, Section III.G.2,Fire protection of safe shutdown capability. It was determined that the circuits were uncoordinated due to inadequate fuse sizing, meaning that during a postulated fire, the circuit’s fuse may not act to protect the circuit from a fire-induced hot short. Without adequate overcurrent protection for these circuits, a fire-induced short could lead to excessive current through the circuits. This could lead to secondary damage in another fire area where the circuits are routed, challenging the ability to achieve and maintain safe shutdown. Compensatory actions were implemented immediately for the affected fire areas in accordance with procedural requirements. Compensatory actions will remain in place until the identified non-compliant conditions are resolved. The circuits for PBAPS,Units 2 and 3 noted above were reported under ENS 57899 per 10CFR50.72(b)(3)(ii)(B) as an unanalyzed condition because a fire that affects multiple fire areas is outside the bounds of the 10CFR50 Appendix R Fire Safe Shutdown Analysis. Safety Consequences There were no actual consequences caused by this condition. The potential consequence of a hot short condition is for fire damage in one fire area to occur which subsequently damages cables in a second fire area. This chain of events could cause a loss of safe shutdown capability outside the bounds of the Fire Safe Shutdown Analysis. However, the risk of fire damage is limited by the use of fire retardant cabling, divisional separation, and fire protection features such as automatic suppression and detection, where required. Additionally, the station Fire Brigade is trained and will readily respond to all fire conditions. Cause and Corrective Actions The cause is an inadequate design dating back to original construction. Fire Protection Program compensatory measures were implemented as immediate actions to mitigate the risk of the affected circuits. Corrective Actions will include modification of the affected circuits to ensure they are properly coordinated. Previous Similar Events Peach Bottom LER 2-18-001, dated 05/18/2018, reported an unanalyzed condition due to valve cables not being protected from spurious operation during a postulated fire. Peach Bottom LER 2-14-001, dated 07/17/2014, reported an unanalyzed condition due to broken wires in breakers credited in the Appendix R Post-Fire Safe Shutdown Analysis. Peach Bottom LER 3-11-04, dated 01/13/2012, reported an unanalyzed condition due to an error in cable routing which affected the Post-Fire Safe Shutdown Analysis. | ML25281A104
Prairie Island Nuclear Generating Plant | Unit 1 | 121 Control Room Chiller Inoperable Due to Purge System Failure. | 10-10-2025 | On June 21,2025, at 17:56 CDT, Units 1 and 2 of Prairie Island Nuclear Generating Plant (PINGP) were both in Mode 1 and operating at 100 percent power when the 121 Control Room (CR) Chiller tripped on "High Refrigerant Pressure". A Past Operability Review was performed and concluded that 121 CR Chiller was considered inoperable and unable to achieve its 30-day mission time from April 22, 2025 until it tripped on June 21, 2025. In addition, during this period of inoperability of the 121 CR Chiller, there were periods when the 122 CR Chiller was also inoperable due to support system inoperability. The cause of the 121 CR Chiller tripping was a buildup of non-condensable gases due to a failed purge compressor. A temporary purge compressor skid has been installed to ensure that the non-condensable gases are removed, and that the Chiller will operate for its 30-day mission time. The 121 and 122 CR Chiller purge compressor skids are planned to be replaced with new units per an approved engineering change. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to http://www.nrc.qov/readinq-rm/doc-collections/nureqs/staff/sr1022/r3/1 respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME im~l 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV NUMBER NO. Prairie Island Nuclear Generating Plant, Unit 1 -282 □ 052 2025 - 002 - 00 | Plant Operating Conditions Prior to the Event: Unit 1 - Mode 1, 100 percent Power. Unit 2 - Mode 1, 100 percent Power. EVENT DESCRIPTION On June 21, 2025, at 17:56 CDT, Units 1 and 2 of Prairie Island Nuclear Generating Plant (PINGP) were both in Mode 1 and operating at 100 percent power. At this time, annunciator [IB] alarm 47022-0302, 121 CONTROL ROOM WATER CHILLER TRIPPED was received and outplant operators reported that the 121 Control Room (CR) Chiller (Trane Air Conditioning, PCV-1C) [VI] tripped on "High Refrigerant Pressure". Dates And Approximate Times of Major Occurrences: • January 17, 2025, at 10:06 CST: While performing Test Procedure 1687 - 121 CONTROL ROOM CHILLER INSPECTION, it was documented that the timer on the purge compressor (Trane Air Conditioning, PRGAA2A1BA0B) was not advancing. This was later determined to be the time when the purge compressor failed. • April 22, 2025, at 09:31 CDT: 121 CR Chiller was considered inoperable and unable to achieve its 30-day mission time per the Past Operability Review (POR) that was completed on August 15, 2025. • April 23, 2025, from 03:30 to 10:59 CDT: 122 CR Chiller was inoperable due to invoking Technical Specifications (TS) Limiting Conditions for Operation (LCO) 3.0.6 based on the entry of support system TS LCO 3.7.8 Condition A for 22 Diesel Driven Cooling Water Pump (DDCLP) being inoperable. • May 03, 2025, from 15:23 to 15:28 CDT: 122 CR Chiller was inoperable due to invoking TS LCO 3.0.6. based on the entry of support system TS LCO 3.8.9 Condition A for Motor Control Center 1 AB Bus 2 being inoperable. • May 20, 2025, from 09:53 to 11:17 CDT: 122 CR Chiller was inoperable due to invoking TS LCO 3.0.6 based on the entry of support system TS LCO 3.7.8 Condition B for “B” Cooling Water Header being inoperable. • May 22, 2025, from 22:14 to 22:30 and 22:31 to 22:43 CDT, 122 CR Chiller was inoperable due to invoking TS LCO 3.0.6. based on the entry of support system TS LCO 3.7.8 Condition A for 22 DDCLP being inoperable. • June 21, 2025, at 17:56 CDT: The amount of non-condensable gases reached a level that permitted the 121 CR Chiller to trip on "High Refrigerant Pressure" and the Chiller was taken out of service and TS LCO 3.7.11 Condition A was entered. • July 5, 2025, at 18:55 CDT: 121 CR Chiller was returned to service and TS LCO 3.7.11 Condition A was exited. • August 15, 2025 [Discovery Date]: A POR was completed and concluded that 121 CR Chiller was considered inoperable from April 22, 2025 until it tripped on June 21, 2025. TS LCO 3.7.11 pertains to the Safeguards Chilled Water System (SCWS). Under Condition A of TS LCO 3.7.11, if one SCWS loop becomes inoperable, it must be restored to operable status within 30 days. The POR determined that the 121 CR Chiller was inoperable for greater than 30 days from April 22, 2025 until it tripped on June 21,2025. Therefore, the required action under Condition A was not met. Condition B of TS LCO 3.7.11 requires entry into Mode 3 within 6 hours if Condition A is not completed. The action to transition to Mode 3 for both Unit 1 and 2 was not completed. Under Condition E of TS LCO 3.7.11, if both SCWS loops are inoperable while in Modes 1-4, the plant must immediately enter LCO 3.0.3. This requires the plant to be in Mode 3 within 7 hours. During the time the 121 CR Chiller was considered inoperable, the 122 CR Chiller was also inoperable for greater than 7 hours on April 23, 2025. LCO 3.0.3 was not entered, and the required transition to Mode 3 for both Unit 1 and 2 was not completed. (EVENT DESCRIPTION continued on next page) | ML25283A066
Joseph M. Farley Nuclear Plant | Unit 1 | Emergency Diesel 1C Unable to Achieve 110% of Maximum Load | 10-14-2025 | On August 13, 2025, at approximately 2126 CDT with Unit 1 and Unit 2 in Mode 1 at 100% power the 1C Emergency Diesel Generator (EOG) was unable to be loaded to 3100 kilowatts (kW) as required by Surveillance Requirement (SR) 3.8.1.12 (24 hour run). The 1C EOG can be aligned to Farley Nuclear Plant (FNP) Unit 1 or Unit 2. During the 24 hour run, SR 3.8.1.12 requires operating the 1C EOG at a load greater than or equal to 110% (3100 kW) capacity for a time of greater than two hours of the 24 hour requirement. When operators were adding the additional load to the 1C EOG, the generator was only capable of reaching 2950 kW. Per SR 3.0.1 failure to meet the SR means the Limiting Condition of Operation (LCO) is not met. FNP operators declared the 1C EOG inoperable. It was determined that during the 1C EOG outage in October of 2024 that the EOG governor linkage was removed and re-installed to the fuel rack. The fuel rack was found limited in movement by the governor linkage preventing further loading. The 1C EOG governor linkage was corrected and the 1C EOG successfully completed post maintenance testing on August 14, 2025, and was declared operable. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of infonmation unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/l displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 SEQUENTIAL REV I NUMBER NO. Joseph M. Farley Nuclear Plant, Unit 1 348 1-G □ 052 001 | Plant Conditions / Event Description: On August 13, 2025, at approximately 2126 CDT, with Farley Nuclear Plant (FNP) Unit 1 and Unit 2 in Mode 1 at 100% power, the 1C Emergency Diesel Generator (EOG) [EIIS: DC/ DG] was unable to reach a load of 3100 kilowatts (kW) during the Technical Specification (TS) Surveillance Requirement (SR) 3.8.1.12 (24 hour run). The 1C EOG can be aligned to Farley Nuclear Plant (FNP) Unit 1 or Unit 2 thus both units were affected. Event Analysis: During the 24 hour run, SR 3.8.1.12 requires operating the 1C EOG [Manufacturer: Fairbanks Morse] at a load of 2850 kW or higher. The SR also requires that the 1C EOG run loaded greater than or equal to 3100 kW for a time of greater than two hours of this 24 hour requirement. When operators were adding the additional load to the 1C EOG the diesel generator was only capable of reaching 2950 kW. FNP operators declared the 1C EOG inoperable due to failure to meet the SR. Reportability and Safety Assessment: Per SR 3.0.1, failure to meet the SR means the Limiting Condition of Operation (LCO) is not met. Since the LCO for Technical Specification 3.8.1 was not met, FNP had been in a condition prohibited by TS since October 25, 2024. The event was within the analysis of UFSAR Chapter 15 and is reportable per 10 CFR 50.73(a)(2)(i)(B) for the 1C EOG being inoperable for longer than allowed by TS 3.8.1. The Safety Function was met as the 1C EOG provides loads for Loss of Offsite Power (LOSP) which was met by meeting 100% load demand of 2850 kW. Cause(s): It was determined that during the 1C EOG outage in October of 2024 that the EOG governor linkage was removed and re-installed to the fuel rack. Following the August 13, 2025, run of the 1C EOG, the investigation found that the fuel rack was limited in movement by the governor linkage preventing further loading. It was determined that the FNP PMT guidance did not require a PMT of 110% (3100 kW) capacity upon the replacement of the fuel injector pump. Additionally, maintenance procedures did not require a 110% loaded run upon the adjustment or replacement of equipment that could adversly impact EOG performance criteria. Corrective Actions Planned/ Completed: The 1C EOG governor linkage was corrected and the 1C EOG successfully completed PMT on August 14, 2025, and was declared operable. Fleet and site procedures are being revised to ensure 110% load PMT occurs when work is performed on systems that affect combustion engine performance. Revisions are being tracked in the site's Corrective Action Program. An extent of condition was performed on all 4 remaining diesel generators which determined the same condition did not exist. Previous Similar Events: No known previous events. | ML25287A034
River Bend Station | Unit 1 | Potential Loss of Safety Function of Control Building Chillers Due to a Valve Mispositioned | 10-20-2025 | On August 23, 2025, at 1433 CDT, River Bend Station, Unit 1 (RBS) was operating in Mode 1 at 100% reactor power, a post maintenance test was being performed on Division II Control Building Chilled Water System Chiller B (HVK- CHL1B). During this test, Division I Control Building Chilled Water System (HVK) was declared Inoperable as a result of HVK Chiller A (HVK-CHL1A) failing to start. HVK-CHL1A failed to start due to the HVK Low Side Isolation Valve, HVK-FTY5B-V2L, being in the closed position. The closed isolation valve prevented a “low flow” signal from the transmitter and render Division I of the HVK Chillers, HVK-CHL1A and HVK-CHL1C, inoperable. Operations immediately alternated back to HVK-CH1B, with HVK-CH1C in standby. This event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(A) and 10 CFR 50.73(a)(2)(v)(D) as an event that could have prevented the fulfillment of the safety function of structures or systems that are needed to shut down the reactor and maintain it in a safe shutdown condition and mitigate the consequences of an accident. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV River Bend Station, Unit 1 NUMBER NO. 00458 052 2025 006 00 | Event Description On August 23, 2025, at 1433 CDT, River Bend Station, Unit 1 (RBS) was operating in Mode 1 at 100% reactor power, a post maintenance test was being performed on Division II Control Building Chilled Water System Chiller B (HVK-CHL1B) [VI:CHU]. During this test, while transferring operation from HVK Chiller B (HVK-CHL1B) to HVK Chiller A (HVK-CHL1A), HVK-CHL1A failed to start. Division I Control Building Chilled Water System (HVK) was declared Inoperable. The inoperability of Division I and II Control Building Chilled Water Systems could have prevented the fulfillment of a safety function. HVK-CHL1A failed to start due to the HVK Low Side Isolation Valve, HVK-FTY5B-V2L, being in the closed position. The closed isolation valve prevented a “low flow” signal from the transmitter and render Division I of the HVK Chillers, HVK-CHL1A and HVK- CHL1C, inoperable. Operations immediately alternated back to HVK-CH1B, with HVK-CH1C in standby. Limiting Conditions for Operation (LCO) 3.7.3, Control Room Air Conditioning System Condition A (One control room AC subsystem inoperable) and 3.7.7, Control Building Air Conditioning System Condition A (one control building air conditioning subsystem inoperable) was entered. After further investigation, it was determined that Instrument and Control (I&C) Technicians manipulated HVK-FTY5B-V2L to the closed position earlier that day during performance of a work order to fill and vent transmitters on the Control Building Chiller 1B. The I&C Technicians failed to document the change of valve position as required by EN-MA-157, Maintenance Configuration Control, therefore the valve was not returned to its proper position (i.e., open). Event Cause The direct cause of this event was due to the misposition of HVK-FTY5B-V2L that resulted in the valve being left in the closed position by I&C Technicians. The causal factor was determined to be that the workers failed to stop work and notify supervision when a potential issue was encountered. The workers did not utilize EN-MA-157, Maintenance Configuration Control, before manipulating a valve. The workers failed to identify potential error traps and failed to utilize human performance tools as required by EN-HU-102, Human Performance Traps & Tools. Safety Assessment Dedicated operator actions had been established to maintain the safety function for the HVK system in the event that the standby chiller doesn’t start and the previously running chiller doesn’t start when alternating divisions of control building chilled water as a planned evolution. Safety function is maintained if a chiller is started within 23 minutes, which is the Environmental Design Criteria limitation. The safety significance of this event is low based on temperatures in the areas cooled by the HVK systems remained below maximum environmental design criteria and actions taken by Operations. Corrective Actions Completed: - Maintenance Department held a stand-down for a standards reset. - Maintenance Department maintained 100% Supervisor job oversight for 2 weeks following the event. | ML25293A255
River Bend Station | Unit 1 | Unidentified Drywell Leakage Increase Results in Shutdown | 10-20-2025 | On May 21, 2025, at 0324 CDT, with River Bend Station (RBS), Unit 1 operating in Mode 1 at 100% power, unidentified drywell leakage experienced a greater than 2 gallon per minute change over a 24-hour period. Technical Specifications (TS) Limiting Condition of Operations (LCO) 3.4.5 Condition C was entered. The required action to verify the source of unidentified leakage increase could not be completed within the allowable completion time. As a result, a plant shutdown was initiated at 0656 CDT. While investigating the unidentified leakage source, RBS determined that a degraded condition existed following the examination of the Residual Heat Removal (RHR) 'A' injection line testable check valve. The leakage from the RHR 'A' injection line testable check valve was determined to be Reactor Coolant System pressure boundary leakage. The direct cause of the leakage past RHR 'A' injection line testable check valve was due to improper gasket seating. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(A) as a Plant Shutdown Required by Technical Specifications, 10 CFR 50.73(a)(2)(ii)(A) as a Degraded or Unanalyzed Condition that resulted in the condition of the nuclear power plant, including its principal safety barriers being seriously degraded, and 10 CFR 50.73(a)(2)(i)(B) as an Operation or Condition Prohibited by Technical Specifications. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRG may not conduct or sponsor, and a person is not required to respond https:/lwww.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER [2:1 050 YEAR SEQUENTIAL REV River Bend Station, Unit 1 NUMBER NO. 00458 0 052 2025 002 01 | Event Description On May 21, 2025, at 0324 CDT, with River Bend Station (RBS), Unit 1 operating in Mode 1 at 100% power, unidentified drywell leakage experienced a greater than 2 gallon per minute change over a 24-hour period. Technical Specifications (TS) Limiting Condition of Operations (LCO) 3.4.5 Condition C was entered. The required action to verify the source of unidentified leakage increase is not service sensitive type 304, type 316 austenitic stainless steel, or other inter-granular stress corrosion cracking susceptible material within 4 hours, could not be completed within the allowable completion time due to the drywell being inaccessible during plant operation. As a result, a controlled manual plant shutdown was initiated at 0656 CDT. At 1405 CDT, the control room operators placed the mode switch to Shutdown. The control room operators entered the appropriate post scram procedures and appropriately responded to the reactor scram. This event was reported on May 21, 2025, at 0950 CDT in accordance with 10 CFR 50.72(b)(2)(i), as an event or condition that results in a TS required plant shutdown. (EN 57725) During the investigation of the unidentified leakage following the shutdown, RBS determined that a degraded condition existed following the performance of a visual examination of E12-AOVF041A (Residual Heat Removal 'A' Injection Line Testable Check Valve) [BO:V]. This examination was conducted on May 22, 2025, at 2358 CDT. This event was reported on May 23, 2025, at 0121 CDT in accordance with 10 CFR 50.72(a)(2)(ii)(A), as Degraded or Unanalyzed Condition that resulted in the condition of the nuclear power plant, including its principal safety barriers being seriously degraded. (EN 57731) The elevated drywell leakage was determined to be Reactor Coolant System (RCS) [AB] pressure boundary leakage and required actions were not completed within the completion time as required by TS LCO 3.4.5. Therefore, this event is also being reported under 10 CFR 50.73(a)(2)(i)(B) as an Operation or Condition Prohibited by TS. Event Cause The direct cause of this event was improper gasket seating, resulting from erosion of the gasket seating surface. The erosion was caused by steam cutting to the base metal of the gasket seat surface. In this degraded state, the base metal did not provide the required support as designed. Two causal factors were identified; (1) The organization did not fully understand the degraded condition of E12-AOVF041A valve body due to steam cutting; therefore, an adequate repair strategy was not formulated or executed and (2) Required VT-3 inspections were not added to the Job Plan as the plan was in Approved status and therefore not routed for additional reviews. In addition, the inspectors failed to realize the need for an inspection as it was not listed in the Job Plan description. Safety Assessment The actual consequence of these events was the initiation of a controlled manual plant shutdown. Following the controlled manual plant shutdown, reactor pressure was maintained by the Turbine Steam Drains [TF] and reactor water level was maintained by the Feedwater [SJ] system. | ML25293A384
River Bend Station | Unit 1 | Containment Unit Coolers Inoperable Due to Compensatory Measures | 10-20-2025 | On August 20, 2025, at 1020 CDT, River Bend Station, Unit 1 (RBS) was operating at 100% power, when it was discovered that previously implemented compensatory measures were determined to have rendered Containment Unit Cooler 'A' (HVR-UC1A) and Containment Unit Cooler 'B' (HVR-UC1B) inoperable. On August 14, 2025, RBS placed HVR-UC 1A and HVR-UC 1B in lockout as a compensatory measure to ensure operability following a Part 21 notification from General Electric. On August 20, 2025, it was discovered that the lockout function would delay the start of a time-delay relay needed for load sequencing in the event of an accident. The cause of this event was due to inadequate compensatory measures that were established by plant personnel. These compensatory measures would have prevented the containment unit coolers from performing their safety function. This event is being reported under 10 CFR 50.73 (a)(2)(ii)(B) as any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety, 10 CFR 50.73(a)(2)(v)(C) and 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of a safety function that is needed to control the release of radioactive material and mitigate the consequences of an accident, and 10 CFR 50.73(a)(2)(i)(B) as an Operation or Condition Prohibited by Technical Specifications. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and lnfonmation Collection Branch (T-6 A1 OM), U S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of lnfonmation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond https:/lwww.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) to, a collection of infonmation unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LERNUMBER ~ 050 YEAR SEQUENTIAL REV River Bend Station, Unit 1 NUMBER NO. 00458 0 052 2025 005 00 | Event Description On August 14, 2025, River Bend Station, Unit 1 (RBS) placed Containment Unit Cooler 'A' (HVR-UC1A) [VA:CLR] and Containment Unit Cooler 'B' (HVR-UC1 B) [VA:CLR] in lockout as a compensatory measure to ensure operability following a Part 21 notification from General Electric. On August 20,2025, it was discovered that the lockout function would delay the start of a time-delay relay [RL Y] needed for load sequencing in the event of an accident. This condition would prevent the unit coolers from starting within their required sequence following a Loss of Offsite Power. The compensatory measures included actions to place HVR-UC1A and HVR-UC1 Bin a continuously running state during normal plant operation. In the event of a Loss of Offsite Power, a dedicated operator would be required to reset the lockout pushbuttons for each unit cooler to meet the safety function time requirement associated with the load sequence. Following a review of the compensatory actions on August 20, 2025, it was determined that the compensatory actions were inappropriately applied. The compensatory actions that were implemented would have caused HVR-UC1A and HVR-UC1 B to start up to 10 minutes after the dedicated operator reset the lockout pushbuttons, instead of 10 minutes following a Loss of Offsite Power. During the time that HVR-UC1A and HVR-UC1 B were in lockout, Technical Specifications (TS) Limiting Condition for Operation 3.6.1.7, Primary Containment Unit Cooler, Condition B was applicable. On August 20, 2025, at 1219 CDT, these compensatory measures were removed. This event was reported under 10 CFR 50.72(b)(3)(ii)(B) as any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety, as well as, 10 CFR 50.72(b)(3)(v)(C) and 10 CFR 50.72(b)(3)(v)(D) as an event or condition that could have prevented fulfillment of a safety function that is needed to control the release of radioactive material and mitigate the consequences of an accident and 10 CFR 50.73(a)(2)(i)(B) as an Operation or Condition Prohibited by TS. Event Cause The cause of the event was due to multiple ineffective reviews of electrical drawings resulting in Engineering personnel failing to recognize the impact of the compensatory measures on the loading sequence of the containment unit coolers. During review and validation prior to implementation, Operations personnel did not recognize the impact of the compensatory measures. As a result, compensatory measures were implemented which would have prevented the containment unit coolers from performing their safety function. Safety Assessment The actual consequences of this event were minimal. A loss of offsite power did not occur during the duration that HVR-UC1A and HVR-UC1 B were inoperable. There were also no radiological impacts. Therefore, there was no actual impact on the health and safety of the public. | ML25293A447
Dresden Nuclear Power Station | Unit 3 | Low Pressure Coolant Injection Pump Suction Relief Valve Inoperable as a Primary Containment Isolation Valve Resulted in a Condition Prohibited bv Technical Soecifications | 10-23-2025 | On 11/20/2024 at 1407 CST, the Main Control Room was notified that the operating handle for the 3A Low Pressure Coolant Injection (LPCI) Suction Relief Valve was found positioned higher than the operating handle for the other relief valves in the system, making the valve inoperable as a Primary Containment Isolation Valve (PCIV). Technical Specification (TS) 3.6.1 .3 Condition C was entered. At 1650 CST, the operating handle for the relief valve was moved to the down position in accordance with station procedure and TS 3.6.1.3 Condition C was exited. The valve had been replaced during refueling outage activities on 11/3/2024. At 0202 on 11/15/2024, Unit 3 entered Mode 2 and Limited Condition of Operation (LCO) 3.6.1.3 became applicable. LCO 3.6.1.3 Required Action C.1 directs isolation of the affected flow path within 4 hours. When the flow path was not isolated by 0602 on 11/15/2024, Required Actions E.1 and E.2 directed shutdown to Mode 3 within 12 hours and Mode 4 within 36 hours, respectively. Therefore, a condition prohibited by Ts existed by the failure to be in Mode 3 by 1802 on 11/15/2024, and Mode 4 by 1802 on 11/16/2024. This event is being reported in accordance with 10 CFR 50. 73(a)(2)(i)(B) for an Operation or Condition Prohibited by TS. NRC FORM 366A (04-02-2024) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc gov/reading-rm/doc-collect1ons/nuregs/staff/sr1022/r3/) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA. library, and Information Collections Branch (T-6 A 10M), U S Nuclear Regulatory Commission. Washington. DC 20555-0001 . or by email to lnfocollects Resource@nrc gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs. (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission 725 17th Street NW Washington. DC 20503. The NRC may not conduct or sponsor. and a person is not required to respond to. a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 YEAR Dresden Nuclear Power Station □ 052 00249 2024 - | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 megawatts thermal rated core power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. A. CONDITIONS PRIOR TO EVENT SEQUENTIAL NUMBER 002 Unit: 3 Reactor Mode: 1 Event Date: November 20, 2024 Mode Name: Power Operation Event Time: 1407 CST Power Level: 100% No structures, systems or components were inoperable at the time of the event that contributed to the event. B. DESCRIPTION OF EVENT REV NO. 02 On 11/20/2024 at 1407 CST, with Dresden Unit 3 at 100 percent power, the Main Control Room was notified that the operating handle for the 3A Low Pressure Coolant Injection (LPCI) [BO] Suction Relief Valve [RV] was found position higher than the operating handles of the other relief valves in the system. The relief valve [RV] is normally seated closed and relieves back to the suppression pool [NH] to provide over-pressure protection of the LPCI [BO] piping when the pump [Pl is isolated. The relief valve [RV] also functions as a Primary Containment Isolation Valve (PCIV) [ISV]. As a PCIV [ISV], its safety-related function is to isolate containment from the LPCI [BO] system. Technical Specification (TS) 3.6.1.3 Condition C requires lines with only one PCIV [ISV] to be isolated within 4 hours and to be verified isolated every 31 days when in Operating Modes 1, 2, and 3. If this action is not met, Condition E of TS 3.6.1.3 requires the operating unit to be placed in Mode 3 within 12 hours and Mode 4 within 36 hours. At 0202 on 11/15/2024, Unit 3 entered Mode 2 and Limited Condition of Operation (LCO) 3.6.1.3 became applicable. LCO 3.6.1.3 Required Action C.1 directs isolation of the affected flow path within 4 hours. When the flow path was not isolated by 0602 on 11/15/2024, Required Actions E.1 and E.2 directed shutdown to Mode 3 within 12 hours and Mode 4 within 36 hours, respectively. Therefore, a condition prohibited by TS existed by the failure to be in Mode 3 by 1802 on 11/15/2024, and Mode 4 by 1802 on 11/16/2024. The operating handle for the 3A LPCI [BO] Suction Relief Valve [RV] was moved to the down position in accordance with station procedure and TS 3.6.1.3 Condition C was exited at 1650 CST on 11/20/2024. This event is being reported in accordance with 10 CFR 50. 73(a)(2)(i)(B) for an Operation or Condition Prohibited by Technical Specifications. C. CAUSE OF EVENT The relief valve [RV] had been replaced on 11/03/2024 during a refueling outage. Prior to the replacement of the relief valve [RV]. there is no record of valve failure or mispositioning. | ML25296A468
Browns Ferry Nuclear Plant | Unit 2 | Primary Containment Isolation and Manual Reactor Trip Due to Dual Recirculation Pump Trips | 10-27-2025 | On May 30, 2025, Recirculation (Recirc) Pump Variable Frequency Drive (VFD) 2A and 2B 120VAC Auxiliary Power Distribution had a contactor fail to transmit power from the normal source and fail to transfer to the alternate source resulting in the loss of Normal and Alternate power to the VFD Cooling Fans. Subsequently, excessive temperatures in VFD cabinets caused multiple VFD cells to auto bypass which caused automatic trips of both Recirc Pumps and, ultimately, an insertion of a manual reactor scram in accordance with 2-AOI- 68-1, Recirc Pump Trip/Core Flow Decrease. The power loss was caused by an incorrect risk evaluation/preventative maintenance strategy for a contactor. Corrective actions included contactor replacement, which allowed the reactor to restart and sync to the electrical grid on June 6, 2025. Preventative actions include similar contactor replacements, evaluations, and maintenance strategies as well as the future addition of power supply redundancies. The Tennessee Valley Authority is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(iv)(A), as any event or condition that resulted in manual or automatic actuation of the Reactor Protection System and the Primary Containment Isolation System. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid OMB control number. 1. FACILITY NAME ☒ 050 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 2 00260 NUMBER NO. ☐ 052 2025 - 003 - 01 | I. Plant Operating Conditions before the Event At the time of this event, Browns Ferry Nuclear Plant (BFN) Unit 2 was in Mode 1 at approximately 39 percent Rated Thermal Power (RTP). II. Description of Event A. Event Summary On May 30, 2025, at 2247 hours CST with Unit 2 operating in Mode 1 at 39% Reactor Power due to the trip of the Reactor Recirculation [AD] Pump (2A), the reactor was manually tripped due to a trip of the only operating Reactor Recirculation Pump (2B). The reactor shutdown was uncomplicated with all systems responding as designed. Operations responded and stabilized the plant. The Primary Containment Isolation System (PCIS) [JM] received an actuation signal for Groups 2, 3, 6, and 8 on reactor water level at +2 inches. All primary containment systems that received an actuation signal performed as designed. Reactor water level control was via Condensate [SD] and Feedwater [SJ] and reactor cooldown was completed using turbine bypass valves to the main condenser [SG]. Due to manual actuation of the Reactor Protection System (RPS) [JC] while critical, this event was reported as a four-hour non-emergency notification per Title 10 of the Code of Federal Regulations (10 CFR) 50.72(b)(2)(iv)(B). The actuation of RPS and PCIS also required an eight- hour non-emergency report per 10 CFR 50.72(b)(3)(iv)(A). Refer to Event Notification report 57737. The Tennessee Valley Authority (TVA) is submitting this report in accordance with 10 CFR 50.73(a)(2)(iv)(A), as an automatic actuation of the RPS and the PCIS. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event No structures, components, or systems were identified as inoperable at the start of the event or that contributed to the event. | ML25300A115
Grand Gulf Nuclear Station | Unit 1 | Loss of Secondary Containment Due to Unsecured Roof Hatch | 11-03-2025 | On September 4, 2025, at 0855 CT while at 100 percent power Grand Gulf Nuclear Station (GGNS) Unit 1 staff discovered the Enclosure Building Roof Hatch was unsecured and slightly open which resulted in inoperability of secondary containment. The hatch had last been accessed at 0845 CT. After discovery, the hatch was secured, and secondary containment was restored. A lack of proper oversight and failure of the watch team to properly understand their duty resulted in the Enclosure Building Roof Hatch becoming unsecured. Supervisor and paired observations will be periodically performed to prevent recurrence of the issue and an engineering barrier will be added to indicate when the hatch is open. This report is being made in accordance with 10 CFR 50.73(a)(2)(v)(C) as a condition which could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 0 4 / 3 0 / 2 0 2 7 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond https://www .nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 181 050 YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 NUMBER NO. 00416 □ 052 2025 005 00 | Plant Conditions: At the time of the event, Grand Gulf Nuclear Station (GGNS) Unit 1 was in MODE 1 at 100 percent power, and all safety systems were operable. Description of Event: On September 4, 2025, at 0855 CT, operators discovered the Enclosure Building Roof Hatch was unsecured and open by approximately one inch. This resulted in inoperability of secondary containment. Following the discovery, the hatch was immediately closed and latched, and secondary containment was restored to operability at 0940 CT. Based on available information the hatch had been last accessed at 0845 CT. Reportability: This report is being made in accordance with 10 CFR 50.73(a)(2)(v)(C) as a condition which could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. Cause(s): Failure of the hatch watch to properly understand their duty and inadequate oversight by supervisors resulted in the Enclosure Building Roof Hatch becoming unsecured. Corrective Actions: - The Enclosure Building Roof Hatch was closed and secured. - Daily observations will be performed by supervisors to ensure that the hatch watch is properly fulfilling their functions. - Additional paired observations of roof hatch usage will be performed. - Engineering barrier will be developed to provide indication and alarm when the hatch is open. Safety Significance: There were no actual safety consequences associated with this condition. Previous Similar Events: LER 2016-003 LER 2018-006 | ML25307A235
Susquehanna Steam Electric Station (SSES) | Unit 1 | Both Sub-Systems of the Control Room Emergency Outside Air Supply System Impacted by Concurrent, Unrelated Equipment Issues in the Control Structure Heating, Ventilation & Air Conditioning System | 11-03-2025 | On September 4, 2025, while the "A" Control Structure Heating, Ventilation and Air Conditioning (HVAC) fan (0V103A) was out of service for planned, proactive belt replacement, the hydro motor for the "B'' Control Room Fan (0V117B) discharge damper failed resulting in the damper going closed. With both the 0V103A and 0V117B fans out of service, both subsystems of the Control Room Emergency Outside Air Supply (CREOAS) system were rendered inoperable. The 0V103A fan was expeditiously worked, tested, and returned to service thereby restoring one sub-system to operable status. The approximately 35-minute concurrent inoperability of both subsystems of CREOAS is being reported in accordance with 10 CFR 50. 73(a)(2)(v)(C) as an event or condition that could have prevented fulfillment of a safety function. There were no actual consequences to the health and safety of the public as a result of this event. ... NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory ccllection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of lnfonmation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRG may not conduct or sponsor, and a person is not required to respond to, a collection of infonmation unless the document requesting or requiring the collection http:l/www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid 0MB control number. ,1. -FA-CIL-ITY- NA-ME- ----------, ~ 050 I 2. DOCKET NUMBER Ic Y:E:AR7 3 S . E L Q E U R E N N U T M IA B L E R REV NUMBER NO • Susquehanna Steam Electric Station Unit 1 00387 1-0 □ 052 . 1~-1 ° 02 | CONDITIONS PRIOR TO THE EVENT: Unit 1: Mode 1, approximately 95% Rated Thermal Power Unit 2: Mode 1, approximately 100% Rated Thermal Power There were no inoperable structures, systems, or components at the start of the issues that contributed to the event. EVENT DESCRIPTION On September 4, 2025, two concurrent, unrelated equipment issues associated with the Control Structure HVAC system [EIIS System Code: VI] resulted in both sub-systems of the Control Room Emergency Outside Air Supply (CREOAS) system being adversely impacted. The following is a timeline of the significant points associated with the event. September 4, 2025, at approximately 1341: The "A" Control Structure HVAC fan (0V103A) [EIIS Component Code: FAN] was proactively removed from service to facilitate replacement of the belts which had contributed to elevated vibration. September 4, 2025, at approximately 1515: Control room personnel noted a change in background noise which was subsequently determined to have been caused by the failure of the Control Structure Supply Fan 0V117B discharge damper hydro motor [EIIS Component Code: COMP] resulting in the damper [EIIS Component Code: DMP] closing. Reduced air flow through the control room dampers was also noted. September 4, 2025, at approximately 1550: Belt replacement on the 0V103A fan was completed. Following successful post maintenance testing, the 0V103A fan was returned to service resulting in restoration of the 'A' CREOAS subsystem. The duration of the concurrent inoperability of the 0V103A and 0V117B fans was approximately 35 minutes. September 5, 2025, at approximately 2111: the discharge damper hydro motor for the 0V1178 fan was replaced, tested and placed back in service resulting in restoration of the 'B' CREOAS subsystem. CAUSE OF THE EVENT Two separate and independent events occurred concurrently that impacted the CREOAS system. Vibration is routinely monitored on the 0V103A fan. Following vibration data collection on September 4, 2025, the station elected to proactively remove the 0V103A fan from service to replace the fan belts. In accordance with station procedures, the belt replacement was planned during a window where no conflicting work was being performed, or redundant equipment was out of service. While the 0V103A fan was out of service for the planned belt replacement, the 0V117B discharge damper hydro motor failed. There had been no indications of degraded performance with the 0V117B hydro motor prior to the failure. | ML25307A312
Quad Cities Nuclear Power Station | Unit 1 | Estimated burden per response to COITl)ly with this mandatory collection request 80 hours. Reported lessons learned are incorporated inlll the licensing process and fed back Ill induslry Send comments regil'ding burden estimate to the FOIA. Libril'y, and Information Collections Branch [T-6 A10M), U. S. Nuclu Regulatory Commission, Washingllln, DC 20555-0001. or by emai Ill lnfocollects.Resource@nrc.gov. and the 0MB rewewer at 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nucleil' Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required Ill respond Ill, a conection of information unless the document requesting or requiring the collection displays a currently valid 0MB conlrol number. 1Z1 050 2. Docket Number 3.Page 0 052 00254 1 OF 4 High Pressure Coolant Injection Inoperable Due to Turbine Inlet Valve Failure to Open | 11-04-2025 | On September 4, 2025 at 1845 during the performance of a Unit 1 High Pressure Coolant Injection (HPCI) Operability Test, it was identified that the system's steam inlet motor operated valve (MOV) failed to open. The inability to open this valve prevented the steam driven system from fulfilling its function of providing emergency core cooling. The cause of this condition, discovered on September 5, 2025, was a degraded breaker which was found to contain a degraded open coil and a binding contact roller. This prevented electrical power from being provided to the valve. The degraded coil was replaced and the roller attachment was cleaned, lubricated, and reinstalled. The breaker failed due to an inadequate maintenance strategy. This report is being submitted in accordance with 10 CFR 50. 73(a)(2)(v)(D) for an event or condition that could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident. NRC FORM 366A (04-02-2024) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate lo the FOIA, library, and Information Collections Branch (T-6 A 10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to lnfocollecls.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currenUy valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER ■ 050 00254 YEAR 3. LER NUMBER SEQUENTIAL NUMBER REV NO. Quad Cities Nuclear Power Station Unit 1 □ 052 2025 - 006 - 00 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. EVENT IDENTIFICATION High Pressure Coolant Injection Inoperable Due to Turbine Inlet Valve Failure to Open A. CONDITION PRIOR TO EVENT Unit: 1 Reactor Mode: 1 Event Date: September 5, 2025 Mode Name: Power Operation Event Time: 1845 hours CST Power Level: 100% No systems, structures, or components that were inoperable at the start of the event contributed to the event. B. DESCRIPTION OF EVENT On September 4, 2025 at 1845 during the performance of a High Pressure Coolant Injection (HPCI) [BJ] Operability Test, operators discovered that the Turbine Inlet Motor Operated Valve (MOV) [V] 1-2301-3 would not open. Multiple attempts were made to open the MOV from the control switch and the associated breaker contacts could not be heard cycling. Troubleshooting on September 5, 2025 at 0130, determined that the electrical breaker [BKR] feeding the MOV had an opening coil [CL] that had failed, and rollers associated with the coil assembly were binding. Discovery of the opening coil degradation confirmed that the MOV would fail to open in either manual or automatic HPCI demands, as opposed to failure to operate only from the valve control switch. The coil was replaced, and the roller assembly was cleaned and relubricated. Post maintenance testing of the MOV was completed on September 5, 2025 at 2228. The MOV breaker prevented proper HPCI operation for 27 hours and 43 minutes. The HPCI Operability Test was subsequently completed with satisfactory results. Event Notification System (ENS) report number 57905 was submitted to the NRC on September 5, 2025. This report is being submitted in accordance with 10 CFR 50. 73(a)(2)(v)(D) for an event or condition that could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident. | ML25308A004
Edwin I. Hatch Nuclear Plant | Unit 2 | Unit 2 Manual Reactor SCRAM Due to Trip of Both Reactor Recirculation Pumps | 11-11-2025 | At 1704 EDT on 09/13/2025, with Unit 2 in MODE 1 at 70-percent power, the reactor was manually tripped due to the loss of both reactor recirculation pumps during turbine control valve testing. Investigation determined that a procedure step to bypass the recirculation pump trip logic had not been performed, resulting in the recirculation pumps tripping during valve testing. The reactor trip was not complex, with all safety systems responding normally including the closure of containment isolation valves (CIVs) in multiple systems, as designed, due to reaching the actuation setpoint on reactor water level. The operating crew responded correctly to the event and stabilized the plant. The event is reportable per 10 CFR 50.73(a)(2)(iv)(A) as any event or condition that resulted in the manual or automatic actuation of any of the systems listed in paragraph 10 CFR 50. 73(a )(2)(iv)(B ). Systems that actuated during this event that are listed in (a)(2)(iv)(B) include: the Reactor Protection System and CIVs in multiple systems. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV Edwin I. Hatch Nuclear Plant Unit 2 00366 □ NUMBER NO. ~- I 1-G □ 052 I I 003 | EVENT DESCRIPTION At 1704 EDT on 09/13/2025, with Unit 2 in MODE 1 at 70-percent power, the reactor was manually tripped due to the loss of both reactor recirculation pumps (EIIS Code: P) during turbine control valve (EIIS Code: FCV) testing. The reactor trip was not complex, with all safety systems responding normally including the closure of containment isolation valves (CIVs) (EIIS Code: ISV) in multiple systems, as designed, due to reaching the actuation setpoint on reactor water level. The operating crew responded correctly to the event and stabilized the plant. There were no inoperable systems that contributed to this event. EVENT CAUSE ANALYSIS The event was caused by inadequate place-keeping by licensed operators, which led to a missed critical step to bypass the recirculation pump trip logic resulting in the pumps tripping during valve testing. SAFETY ASSESSMENT AND REPORTABILITY There were no safety consequences as a result of this event with all safety related systems functioning as designed. The operating crew responded correctly to the event. The applicable abnormal and emergency operating procedures were properly entered and the plant was stabilized. The event was within the analysis of the Updated Final Safety Analysis Report (UFSAR) Chapter 15. The event is reportable per 10 CFR 50_73(a)(2)(iv)(A) as any event or condition that resulted in the manual or automatic actuation of any of the systems listed in paragraph 10 CFR 50. 73(a)(2)(iv)(B). Systems that actuated during this event that are listed in (a)(2)(iv)(B) include: the Reactor Protection System (EIIS Code: JC) and CIVs in multiple systems. CORRECTIVE ACTIONS Corrective actions include highlighting all critical procedural steps, followed by the supervisor reviewing the critical steps during the pre-job brief, implementing supervisor hold points prior to the execution of each critical step, and place-keeping page numbers during performance of any continuous use procedure. Also, lessons learned from the event have been communicated to site personnel. PREVIOUS SIMILAR EVENTS None. | ML25315A010
Peach Bottom Atomic Power Station (PBAPS) | Unit 2 | Invalid Actuation Due to Transformer Trip | 11-13-2025 | On September 19th, 2025, the 13 kV non-safety related AS4 feeder breaker, which powers the B Cooling Tower Lift Pump (EIIS:NN) tripped as a result of an electrical fault downstream of the breaker. The electrical fault resulted in a momentary voltage dip on the offsite power source (3SU). This condition led to a partial invalid Primary Containment Isolation System (PCIS) (EIIS: JM) isolation including isolation of the Reactor Water Cleanup System (RWCU) (EIIS: CE) on both units. The cause of the breaker trip was a faulted disconnect switch, likely due to component aging. This condition is reportable under 50.73(a)(2)(iv)(A) as an invalid actuation of general containment isolation signals affecting containment isolation valves in more than one system. The isolation was caused by degraded voltage. The actuation was invalid because the conditions for which isolation is required were not present. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid OMB control number. 1.FACILITY NAME 2.DOCKET NUMBER 3. LER NUMBER  050 SEQUENTIAL REV YEAR Peach Bottom Atomic Power Station (PBAPS), NUMBER NO. 00277 Unit 2  052 2025 - 003 - 00 | Plant Operating Conditions Before the Event Prior to the event, Peach Bottom Atomic Power Station, Unit 2 was operating at approximately 100% power in MODE 1. Unit 3 was operating at approximately 91% power in MODE 1 in end-of-cycle coast down. There were no structures, systems or components (SSC) that were inoperable at the start of the event that contributed to the event. Event Description On September 19th, 2025, at approximately 9:34am, operators received alarms indicating that the 480V motor control center that supplies support power to the B Cooling Tower (EIIS: NN) lift pump tripped and caused various isolations on both units. On Unit 2, the voltage reduction caused a partial invalid Primary Containment Isolation System (PCIS) (EIIS: JM) isolation of Group II and Group III inboard valves including isolation of the Reactor Water Cleanup System (RWCU) (EIIS: CE), isolation of nitrogen compressors (EIIS: LK), failure of the B vent stack radiation monitor (EIIS: IL), and loss of flow to containment hydrogen and oxygen analyzers (EIIS: IK). On Unit 3, this condition resulted in actuations of PCIS Group II and III outboard valves, isolation of RWCU, isolation of nitrogen compressors and a trip of a service water booster pump (EIIS: DA). The A train of flow indication to the Main Stack sampler (EIIS: IL) was also lost. The cause of the breaker trip was a faulted disconnect switch, likely due to component aging and general corrosion. The failed switch is located outdoors and was replaced in 2007 after a similar failure. Preventive maintenance had not been performed since the 2007 failure. This condition is reportable under 50.73(a)(2)(iv)(A) as an invalid actuation of general containment isolation signals affecting containment isolation valves in more than one system. The isolation was caused by degraded voltage. The actuation was invalid because the conditions for which isolation is required were not present. Safety Consequences There were no challenges to plant safety as a result of this event. Both units responded as designed to the electrical transient, and PCIS isolations were reset without error within approximately one hour of the trip. Corrective Actions Corrective actions for this condition include replacement of the components that were damaged by the fault, including radiation monitors, transformer disconnect switch and cabling. The maintenance strategy for this equipment will be reviewed. Previous Similar Events Peach Bottom experienced the following similar events: - Invalid actuations due to a trip of the AS4 feeder breaker in 2007, ref. EN# 43910 - Invalid actuations due to an emergency bus breaker relay failure in 2019, ref. LER 2019-001-00. - Invalid actuations due to a bus failure on August 20, 2025, rev. LER 2025-001-00. | ML25317A674
Susquehanna Steam Electric Station (SSES) | Unit 1 | APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 Estimated burden per response to comply with tills mandatory collection request 80 hours. Reported lessons learned are Incorporated Into the llcens!ng process and fed back to Industry, Send comments regarding burden estimate to the FOIA, Library, and lnfom,ation Collections Branch (TƄ6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by small to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRG may not conduct or sponsor, and a person Is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB oontrol number. 00 050 2. Docket Number 3. Page 052 00387 1 OF 3 Manual Reactor Scram Following Loss of Cooling to Main Transformer | 11-13-2025 | On July 22, 2025, at approximately 15:10, Susquehanna Steam Electric Station (SSES) Unit 1 was manually scrammed following a partial loss of cooling to the main transformer (one of two cooling fan groups were found tripped). The event was reported by Event Notification 57822 in accordance with 10 CFR 50. 72(b )(2)(iv)(A), 10 CFR 50. 72(b )(2)(iv)(B) and 10 CFR 50. 72(b )(3)(iv)(A). This event is also reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a manual actuation of the Reactor Protection System (including a reactor scram) and actuation of the emergency core cooling system. Following restoration of both cooling fan groups, SSES Unit 1 was restored to Mode 1 operation on July 25, 2025. The root cause of the event was determined to be that Operations leadership did not ensure the Operators were prepared to respond to a loss of cooling event on the main transformer to minimize the potential for a required manual scram. There were no actual consequences to the health and safety of the public as a result of this event. - --- - --- -------- ------ □ NRC FORM 366A (04-02-2024) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D 1. FACILITY NAME ,------------------, 00 Susquehanna Steam Electric Station (SSES) Unit 1 | CONDITIONS PRIOR TO THE EVENT □ 050 052 Unit 1: Mode 1, approximately 96% Rated Thermal Power Unit 2: Mode 1, approximately 100% Rated Thermal Power Estimated burden per response to comply with this mandatory collection request BO hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and lnfonmation Collections Branch [f-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at 0MB Qffice of lnfonmatlon and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRG may not conduct or sponsor, and a person is not required to respond to, a collection of infonmatlon unless the document requesting or requiring the collection displays a currently valid 0MB control number. 2. DOCKET NUMBER 3. LER NUMBER I 00387 [::7 NUMBER NO. I YEAR SEQUENTIAL REV ~-I 001 1-0 There were no inoperable structures, systems, or components at the start of the event that contributed to the event EVENT DESCRIPTION On July 22, 2025, a Main Transformer 1X101 [EIIS System Code/ Component Code - EL/ XFMR] trouble alarm was received in the Control Room and Operators entered a 10-minute manual scram requirement in accordance with the Alarm Response procedure. The non-licensed operator (NLO) responding in the field to the Main Transformer correctly determined that only a partial loss of cooling had occurred with Group 1 cooling fans [IEEE Component Code - FAN] not running and Group 2 cooling fans in service. However, imprecise communications resulted in operators in the Control Room and Work Control Center (WCC) incorrectly believing that a total loss of cooling had occurred. As a result, a second NLO, dispatched to the transformer by the WCC, attempted to restore transformer cooling. Failing to recognize that partial cooling for the transformer was in fact in service, the second NLO secured the running Group 2 cooling fans while attempting to switch to the alternate power supply resulting in the total loss of transformer cooling. At approximately 15: 10, control room operators manually scrammed SSES Unit 1 following a loss of cooling to the Main Transformer. All systems responded normally following the manual scram. High Pressure Coolant Injection [EIIS System Code - BJ] actuated briefly to assist in restoring reactor water level. The 1 B Reactor Feedwater Pump [El IS System Code/ Component Code - SJ/ P] stabilized and maintained reactor water level. Decay heat was removed by discharging steam to the main condenser using the turbine bypass valves. The event was reported by Event Notification 57822 in accordance with 10 CFR 50 .72(b)(2)(iv)(A), 10 CFR 50.72(b)(2)(iv) (B) and 1 O CFR 50. 72(b)(3)(iv)(A). This event is also reportable in accordance with 10 CFR 50. 73(a)(2)(iv)(A) as an event that resulted in a manual actuation of the Reactor Protection System (including a reactor scram) and actuation of the emergency core cooling system. Following restoration of both cooling fan groups, SSES Unit 1 was returned to Mode 1 operation on July 25, 2025. CAUSE OF THE EVENT The direct cause of the event was ineffective communication and direction between control room and field personnel responding to a partial loss of main transformer cooling (Group 1 Cooling). This resulted in incorrect operator actions being taken that caused a complete loss of transformer cooling. NRG FORM 366A (04-02-2024) Page 2 of 3 | ML25317A743
Calvert Cliffs Nuclear Power Plant | Unit 1 | Control Room Loss of Ventilation due to Smoke Detector Failure Causing Common Supply Damper to Shut | 07-31-2025 | On July 31, 2025, at 1744, the Main Control Room (MCR), shared by Units 1 and 2, experienced a loss of ventilation due to the Control Room supply damper fully closing. Closure of the damper isolated the ventilation flow to the Control Room which resulted in both trains of the Control Room Emergency Ventilation System and Control Room Emergency Temperature System being inoperable, resulting in Technical Specification Limiting Conditions for Operation (LCOs) 3.7.8 and 3.7.9 not being met, respectively, for Units 1 and 2. At time 1745, the Units exited the associated LCOs after the damper returned to its normal, open position. Field troubleshooting isolated the cause of the intermittent closure of the damper to a MCR ventilation smoke detector. The smoke detector functions to shut the MCR supply damper by energizing the associated solenoid valve. This event is reportable in accordance with 10 CFR 50. 73(a)(2)(v)(D) and 10 CFR 50. 73(a)(2)(vii). The direct cause of the smoke detector failure was an electrical short, due to condensation, on the control board of the Control Room Air Conditioning (A/C) return duct smoke detector (OAE5347) that sends an automatic closure signal to the Control Room A/C dampers. NRC FORM 366A (04-02-2024) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/readinq-rm/doc-collections/nuregs/staff/sr1022/r30 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRG may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER ■ 050 Calvert Cliffs Nuclear Power Plant, Unit 1 0 052 05000317 | PLANT AND SYSTEM IDENTIFICATION YEAR 2025 - 3. LER NUMBER SEQUENTIAL NUMBER 001 REV NO. 01 Calvert Cliffs Nuclear Power Plant, Units 1 and 2, are Combustion Engineering Pressurized Water Reactors with a licensed maximum power level of 2737 megawatts thermal. The Energy Industry Identification System code used in the text is identified as [VI]. A. CONDITION PRIOR TO EVENT Units: 1/2 Date: July 31, 2025 Power Level: 100/100 percent Mode: MODE 1/1 B. DESCRIPTION OF EVENT On July 31 , 2025, at 1744, the Main Control Room (MCR), shared by Units 1 and 2, experienced a loss of ventilation due to the MCR supply damper fully closing. Closure of the damper isolated the ventilation flow to the MCR which resulted in both trains of the Control Room Emergency Ventilation System (CREVS) and Control Room Emergency Temperature System (CRETS) being inoperable, resulting in Technical Specification (TS) Limiting Conditions for Operation (LCO) 3.7.8 and 3.7.9 not being met, respectively, for Units 1 and 2. At time 1745 the Units exited the associated LCOs after the damper returned to its normal, open position. C. DA TES AND APPROXIMATE TIMES OF MAJOR OCCURRENCES July 31, 2025 • 17:44:00 Unit 1 entered LCOs 3.0.3, 3.7.8, and 3.7.9 due to ventilation damper 0-CV-5342 closing rendering two CREVS trains inoperable in MODE 1. • 17:44:00 Unit 2 entered LCO 3.0.3, 3.7.8, and 3.7.9 due to ventilation damper 0-CV-5342 closing rendering two CRETS trains inoperable in MODE 1. • 17:44:30 Ventilation damper 0-CV-5342 re-opened. (time is approximate) • 17:45:00 Unit 1 exited 3.0.3, 3.7.8, and 3.7.9 due to damper 0-CV-5342 returned to its normal open position. Both Trains of CREVS and CRETS were restored to service. • 17:45:00 Unit 2 exited 3.0.3, 3.7.8, and 3.7.9 due to damper 0-CV-5342 returned to its normal open position. Both Trains of CREVS and CRETS were restored to service. | ML25323A433
River Bend Station | Unit 1 | Division 1 Balance of Plant Isolation Results in Manual Reactor Trip | 12-08-2025 | On October 9, 2025, at 1207 CDT, River Bend Station (RBS) was operating at 100% reactor power when a manual reactor trip was inserted as a result of a Division I Balance of Plant (BOP) isolation. The BOP isolation resulted in the loss of the Instrument Air System (IAS) and the Component Cooling Primary System (CCP) to containment. All plant systems responded as designed. Immediately following the manual trip, a reactor water low level 3 isolation signal was received as expected. Due to the swell from the main turbine trip, a reactor water high level 8 actuation signal was received at 1208 CDT. The level 8 actuation signal was reset at 1211 CDT. At 1237 CDT, Control Room Operators entered the Emergency Operating Procedure (EOP) for high containment pressure caused by the isolation of the containment vent flow path. The isolation signal for IAS and CCP was reset at 1255 CDT. Following the restoration of the isolation signal, Control Room Operators lowered containment pressure and exited the EOP at 1305 CDT. The direct cause of this event was a failed fuse caused by a human performance error. This report is made pursuant to 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of the Reactor Protection System. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and lnfonmation Collection Branch (T-6 A1 OM), U S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of lnfonmation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond https:/lwww.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) to, a collection of infonmation unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LERNUMBER ~ 050 YEAR SEQUENTIAL REV River Bend Station, Unit 1 NUMBER NO. 00458 0 052 2025 007 00 | Event Description On October 9, 2025, at 1207 CDT, with River Bend Station (RBS), Unit 1 operating at 100% reactor power, a manual reactor trip was inserted as a result of a Division I Balance of Plant (BOP) isolation. The Division 1 BOP isolation resulted in the loss of the Instrument Air System (IAS) [LO] and the Component Cooling Primary System (CCP) [CC] to containment. On October 9, 2025, at 1203 CDT, a Division 1 BOP isolation signal was received. Control Room operators recognized the loss of IAS and CCP to containment and entered the appropriate procedures. The Control Room operators were unable to reset the Division 1 BOP isolation signal. At 1207 CDT, the Control Room Operators inserted a manual reactor trip by placing the Mode Switch to Shutdown. All plant systems responded as designed. Immediately following the manual trip, a low reactor water level isolation signal was received as expected. Due to the swell from the Main Turbine [TA] trip, a high reactor water level actuation signal was received at 1208 CDT. The high reactor water level actuation caused the Reactor Feedwater System (FWS) [SJ] to trip as designed. The high reactor water level actuation signal was reset at 1211 CDT and Reactor Feedwater Pump C (FWS-P1 C) was restarted to maintain reactor water level. Reactor pressure was maintained by the Turbine Bypass Valves [JI]. At 1237 CDT, Control Room operators entered the Emergency Operating Procedure (EOP) for high containment pressure. The increase in containment pressure was due to the isolation of the containment vent flow path. At 1255 CDT, the isolation signal for IAS and CCP was reset. Following the restoration of the isolation signal, Control Room operators lowered containment pressure and exited the EOP at 1305 CDT. This event was reported on October 9, 2025, at 1539 CDT in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) as an event or condition that results in actuation of the RPS when the reactor is critical and as a specified system actuation due to the expected low reactor water level isolation signal immediately following the reactor scram and a subsequent high reactor water level signal (EN 57975). Event Cause Prior to the Division 1 BOP isolation, plant personnel were performing surveillance STP-058-4201, Containment and Drywell Manual Isolation Actuation Logic System Functional Test. During the surveillance, a technician lifted a lead and did not appropriately account for the length of wire allowing the wire to retract and contact the metal enclosure. This caused the Division 1 Isolation Logic Supply Fuse (B21 H-F28A) [JM] to fail. Due to the failure of B21 H-F28A, a Division 1 BOP isolation actuation occurred. The Division 1 BOP isolation resulted in the loss of the IAS and CCP to containment. Safety Assessment The actual consequence of this event was a Division 1 BOP containment isolation that was unable to be reset and a subsequent reactor scram. There were no other actual consequences to general safety of the public, nuclear safety, industrial safety and radiological safety for this event. Corrective Actions Planned: • Complete performance management with personnel involved to address personal accountability. • Develop and implement a non-training intervention plan to reinforce standards and expectations. | ML25342A438
edwin i. hatch | Unknown Unit | Unit 1 Reactor Protection System Instrumentation for Turbine Control Valve Fast Closure Inoperable | 12-19-2025 | With Unit 1 at 100-percent power on 10/22/2025 at 0918 EDT, after performance of a past operability evaluation, it was determined that three Reactor Protection System (RPS) pressure switches for the Turbine Control Valve (TCV) Fast Closure trip on low Electrohydraulic Control (EHC) oil pressure were likely inoperable longer than allowed by Technical Specifications (TS). These three TCV RPS pressure switches failed TS Surveillances (SRs) on 4/5/2025 and 4/6/2025. Additionally, one of the same TCV RPS pressure switches failed a TS SR on 12/17 /25. The failures of the TCV RPS pressure switches are attributed to elevated ambient temperatures which degraded EHC oil locally at the pressure switches, impeding proper depressurization of the EHC sensing lines during TCV actuation. Corrective actions included purging the EHC sensing lines, replacing the fast acting solenoid for one of the TCVs, installing temporary fluid conditioning units, increasing the TCV SR frequency, which helps prevent fluid stagnation and flushes contaminants, reducing varnish buildup and sticking. The event is reportable per 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by technical specifications, 10 CFR 50.73(a)(2)(v)(A) for a condition that could have prevented fulfillment of a safety function, and 10 CFR 50.73(a)(2)(vii) for a common cause inoperability of independent channels. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to oomply with this manda1ay oollection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden es1imate to the FOIA, Library, and lnfonnation Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washr,gton, DC 20565-0001, or by email to CONTINUATION SHEET lnlooollects.Resource@m.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs. (3150-0104). Attn: Desk Officer for the Nudear Regulatory Commission. 72517th Street NW. (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required lo respond to, a collection of information unless the document requesting or requiring the oollection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/} displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER .-------------, ~ 050 YEAR SEQUENTIAL REV Edwin I. Hatch Nuclear Plant Unit 1 00321 □ NUMBER NO. 1- 0 I □ - 1 □ 052 I 002 | EVENT DESCRIPTION With Unit 1 at 1O D-percent power on 10/22/2025 at 0918 EDT, after performance of a past operability evaluation, it was determined that three Reactor Protection System (RPS) (EIIS Code: JC) pressure switches (EIIS Code: PS) for the Turbine Control Valve (TCV) (EIIS Code: FCV) Fast Closure trip on low Electrohydraulic Control (EHC) (EIIS Code: TG) oil pressure were likely inoperable longer than allowed by Technical Specifications (TS). These three TCV RPS pressure switches failed TS SRs on 4/5/2025 and 4/6/2025. Additionally, one of the same RPS pressure switches failed a TS SR on 12/17/25. EVENT CAUSE ANALYSIS The failures of the TCV RPS pressure switches are attributed to elevated ambient temperatures which degraded EHC oil locally at the pressure switches. The degraded EHC oil prevented the TCV Fast Acting Solenoid (FAS) (EIIS Code: SOL) from fully shuttling which inhibited depressurization of the RPS pressure switch sensing line when the TCVs actuated. Because the sensing line did not depressurize when the TCVs were actuated, the pressure switches were unable to generate the RPS reactor trip signal on low EHC oil pressure as required. SAFETY ASSESSMENT AND REPORTABILITY The RPS pressure switches associated with the TCV Fast Closure trip are credited in the Updated Final Safety Analysis Report (UFSAR) Chapter 15 for initiating a reactor trip during both the Turbine Trip and Generator Load Reject events. For the Turbine Trip event, the UFSAR credits both the TCV RPS pressure switches and the Turbine Stop Valve (TSV) (EIIS Code: ISV} RPS instrumentation for initiating a reactor trip. During the period when the TCV RPS pressure switches were inoperable, the TSV instrumentation remained operable; therefore, a Turbine Trip event would have resulted in a reactor trip. For the Generator Load Reject event, the UFSAR credits only the TCV RPS pressure switches for initiating a reactor trip. However, the UFSAR evaluates the condition when the reactor is not tripped by the TCV RPS instrumentation during a Generator Load Reject event. In such cases, a High Flux scram is credited to mitigate the event, concluding that no fuel damage would occur and that the event remains within acceptance criteria. Accordingly, there were no safety consequences as a result of the inoperability of the TCV RPS pressure switches. Considering the failure history of the TCV RPS pressure switches, the simultaneous inoperability of multiple TCV RPS pressure switches, and since there is no other equipment in the same system as the TCV RPS pressure switches that would trip the reactor during a Generator Load Reject, this event is reportable per 10 CFR 50.73(a)(2)(i}(B) as a condition prohibited by TS and per 10 CFR 50.73(a)(2)(v)(A) as a condition that could have prevented fulfillment of a safety function. Additionally, the event is also reportable per 10 CFR 50. 73(a}(2)(vii) due to degraded EHC oil creating a common cause condition that resulted in the inoperability of multiple, independent RPS channels. CORRECTIVE ACTIONS Corrective actions included purging the EHC sensing lines, replacing the fast acting solenoid for one of the TCVs, installing temporary fluid conditioning units, increasing the TCV SR frequency, which helps prevent fluid stagnation and flushes contaminants, reducing varnish buildup and sticking. Additional, planned corrective actions include replacing TCV insulation, replacing the remaining fast acting and test solenoids, and implementing a permanent EHC filtration upgrade. PREVIOUS SIMILAR EVENTS None. | ML25353A533
Dresden Nuclear Power Station | Unit 2 | Valid Reactor Protection System Actuation While Shutdown | 12-26-2025 | At 0117 CDT on 10/27/2025, with Unit 2 in Mode 3 at 0 percent power, an actuation of the Reactor Protection System (RPS) occurred during restoration of the Scram Discharge Volume (SDV) high level bypass switch to normal. The cause of the RPS system actuation was a valid high level in the SDV. All control rods had been previously inserted and the RPS system automatically initiated a scram signal as designed when the SDV high level signal was received. The scram was reset in accordance with station procedures at 0121 CDT. An evaluation of this event is currently in progress to determine any contributing causes to the event as well as additional corrective actions. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) for a valid RPS system actuation. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, library, and Information Collections Branch (T-6 A1 0M), U. S. Nuclear Regulalory Commission. Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/readinq-rm/doc-collections/nuregs/staff/sr1022/r3D displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 SEQUENTIAL REV YEAR NUMBER NO. Dresden Nuclear Power Station 00237 □ 052 2025 - 002 - 00 | PLANT AND SYSTEM IDENTIFICATION - UNIT 2 General Electric - Boiling Water Reactor, 2957 megawatts thermal rated core power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. A. CONDITIONS PRIOR TO EVENT Unit: 2 Event Date: October 27, 2025 Event Time: 0117 CDT Reactor Mode: 3 Mode Name: Hot Shutdown Power Level: 0% No systems, structures, or components that were inoperable at the start of the event contributed to the event. 8. DESCRIPTION OF EVENT At 0117 CDT on 10/27/2025, with Unit 2 in Mode 3 at O percent power, an actuation of the Reactor Protection System (RPS) [JC] occurred during restoration of the Scram Discharge Volume (SDV) high level bypass switch to bypass switch to normal. The cause of the RPS [JC] system actuation was a valid high level in the SDV. All control rods had been previously inserted and the RPS [JC] system automatically initiated a scram signal as designed when the SDV high level signal was received. The scram was reset 0121 CDT in accordance with station procedures. ENS report #58008 was transmitted to the NRC at 0750 CDT on 10/27/2025. An evaluation of this event is currently in progress. This event is being reported in accordance with 10 CFR 50. 73(a)(2)(iv)(A). C. CAUSE OF EVENT The cause of the event was a valid high level in the SDV. An evaluation of the event is currently in progress. A supplemental report will be submitted with the conclusions of this evaluation. D. SAFETY ANALYSIS The RPS [JC] monitors reactor [RCT] core parameters. If these parameters exceed predetermined limits, the RPS [JC] logic will initiate a scram. The SDV is used to limit the loss of, and contain, the reactor vessel [RPV] water from all Control Rod Drives (CRDs) [AA] during a scram. During normal operation, the SDV is empty with open drain [ORN] and vent valves [VTV]. On a scram signal, the RPS [JC] is deenergized and the SDV pilot valves [V] vent the discharge volume valve [VJ operators, causing them to close. All systems and components responded as expected to the valid high SDV level signal. Additionally, all CRDs [AA] had been previously inserted. There was no impact to the health and safety of the public from this event. | ML25360A001
Clinton Power Station 00461 1 OF 3 | Unknown Unit | Manual Scram Due to Main EHC Leak | 12-16-2025 | On October 22, 2025, at 1535, the Clinton Unit 1 reactor was manually scrammed due to low turbine Main Electro-Hydraulic Control oil system (Main EHC) reservoir level caused by a leak that had developed on Turbine Control Valve #3 (TCV3). This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) for "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section." The specific system listed in that paragraph that actuated was the "Reactor protection system (RPS) including: reactor scram or reactor trip." NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Ubrary, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nn::.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 SEQUENTIAL REV YEAR NUMBER NO. Clinton Power Station 00461 □ 052 2025 - 003 00 | CONDITION PRIOR TO THE EVENT Unit: 1 Event Date: October 22, 2025, Event Time: 15:35 CST Mode: 1 Mode Name: Power Operation Reactor Power: 86% EVENT DESCRIPTION On October 22, 2025, 1504, operators observed abnormal valve conditions (main turbine bypass valves open and TCV3 indicated closed) and initiated off-normal procedures to lower power in response to unexpected loss of feedwater heating. Main EHC reservoir level was observed to be dropping rapidly (approximately 1 inch/minute), prompting an immediate operator action to makeup reservoir level. Due to the large leak being un-isolable and Main EHC fluid level reaching the low reservoir level in which Main EHC pumps are required to be secured, a manual scram was inserted at 1535 with the reactor at 86% power. Final Main EHC fluid reservoir level was -24.5" and an estimated 440 gallons of EHC fluid leaked during this event. CAUSE OF THE EVENT The apparent cause of the Main EHC leak was a failure of four tie rods associated with TCV3 due to high cyclic fatigue as a result of inadequate torquing during the most recent refurbishment by the vendor. Post-SCRAM inspections identified significant mechanical damage to the TCV3 actuator, including a dislodged backing plate, and sheared four of the eight tie rods. Two of the remaining four tie rods were found to be under-torqued (one finger tight, the other at under 200 ft-lbs). The TCV3 actuator has since been replaced to correct the source of the leak. During the extent of condition investigation, Turbine Control Valve #1 (TCV1) actuator tie rods failed an initial resonance test and were replaced to preclude a similar failure. While preparing to install the replacement actuator for TCV1, the tie rods on the new actuator were torque-tested and three were found to be under torqued at 350 ft-lbs rather than the prescribed torque of 500 ft-lbs. In addition, the lower O-ring was visible in the groove when observed with a borescope from inside the cylinder. When properly torqued, the lower O-ring was no longer visible. SAFETY CONSEQUENCES There were no safety consequences impacting plant or public safety as a result of this event. The trip was not complex, with all systems responding normally post-trip. Decay heat was removed post-trip by discharging steam to the Main Condenser using the Turbine Bypass Valves which have a separate electro-hydraulic oil system. There was no loss of any safety function that would have prevented fulfillment of actions necessary to 1) shutdown the reactor and maintain it in a safe shutdown condition, 2) remove residual heat, 3) control the release of radioactive material, or 4) mitigate the consequences of an accident. NRG FORM 366A (04-02-2024) Page_2_ of _3_ | ML25364A102
Clinton Power Station | Unknown Unit | Emergency Diesel Generator Automatic Start due to Emergency Reserve Auxiliary Transformer Trip | 01-13-2026 | At 1351 on 11/14/25, with the unit in Mode 1 at 99% power, an actuation of the Division 1, 2, and 3 Emergency Diesel Generators (EDGs) occurred when a fault occurred on the Emergency Reserve Auxiliary Transformer (ERAT). The Reserve Auxiliary Transformer (RAT) B was previously de-energized and isolated for maintenance. The cause of the Division 1, 2, and 3 EDGs auto-start was an actuation of the Loss of Voltage Function undervoltage relays for each respective bus. The Division 1, 2, and 3 ED Gs automatically started as designed when the applicable Loss of Voltage signals were received. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) for "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section." The specific system listed in that paragraph that actuated was the "Emergency ac electrical power systems, including: emergency diesel generators (EDGs); ... and BWR dedicated Division 3 EDGs." ( N 04 R -0 G 2 -2 F 0 O 24 R I M 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 Estimated burden per response to ccmp\y with this mandatory cclleclion request. 80 hours. Reported LICENSEE EVENT REPORT (LER) r le e s g s a o rd n i s n g le a b r u n r e d d e n a r e e s t i i n m c a o t r e p o lo ra t t e he d F in O to I A th e li b li r c a e r n y s . in a g n d p I r n o f c o e r s m s a a ti n o d n f C ed o ll b e a c c tio k n t s o i B n r d a u n s c t h ry . I T S -6 e n A d 1 0 c M om J. m U e . n S ts . CONTINUATION SHEET N ln u fo c c le o a ll r e cts. R R e e g s u o la u t , o c r e y @ nr C c. o g m ov m . is a s n i d o n t . h e 0 W M a B s h r i e n v g i t e o w n e . r at D : C 0 MB 2 O 05 ff 5 ic 5 e -0 o 0 f 0 I 1 n , f orm o a r t ion b a y n d R em eg a u il l ator t y o (See NUREG-1022, R.3 for instruction and guidance for completing this form A W ff a a s ir h s in . g (3 to 1 n 5 . 0 - D 0 C 10 4 2 ) 0 , 5 A 0 t 3 tn . · T D h e e s k N R O C ffi c m er a y fo r n t o h t e c N o u n c d l u e c a t r o R r e s g p u o la n to so ry r . C a o n m d m a is s p i e o r n s , o 7 n 2 5 is 1 n 7 o 1h t r S e t q re u e ir t e d N W to , b.l!_p_//wwvf~D re. gov/ re ad inq-rm/doc-coll ections/n ureq s/staff/sr1 022/r3/) d re is s p p l o a n y d s a lo c . u a rre c n o tl l y le c v t a io lid n 0 o M f B in f c o o rm nt a ro ti l o n n u m un b l e e r s . s the document requesting er requiring the collecf,on 1. FACILITY NAME II 050 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Clinton Power Station 00461 NUMBER NO. D 052 2025 - 004 00 | CONDITION PRIOR TO THE EVENT Unit: 1 Event Date: November 14, 2025, Event Time: 13:51 CST Mode: 1 Mode Name: Power Operation Reactor Power: 99% EVENT DESCRIPTION A v r 3 n p N s e a t . o e r 3 o s e l u e 1 i . v p d v 8 3 r d e e c i . 5 e o 1 a m e c 1 d u u t ) i b . s L t v C a o e l o e T y n m S r s h d b t s 9 T a e a u , t u k o o i s t 2 e c t r f n e i i 0 n l p V i s s z 2 N t o o i w 5 a u n o l u . r t g n a a v t t A t s e g i s a o l t m e i a f g b 3 t h s n o b F r 0 e e e t a e u - h r s d l r n v t u i a t o i c m 1 o c l y f t t 4 e f i e t o s , o h R i n a 2 f o t e i e n s 0 a f u d k D 2 t s p n h 5 o i I m h d v e n , u i a e f s a C r e o s r c i d o v v r l e e i m e e o n n - s n t l t e t o b o 1 t a w d , - o n , g p e t t 2 C h e h h r P , e e a o o r i a n e s m w r s n o e l e a t d p e p a s y d l r e t t e 3 s i o i o S r f t r f a i f E n o e e t o b a n D d r r w l t e e i G o e T n t a o a n a s t i s m i c . n a t U h i h d l e n A e n o l C l u f i L i v r o t n t C l e a r h n 1 a r O s r o r c v e e e s r u a e x m q 3 r i 1 p u . l r a 8 a E E e e ir . b l O n 1 r e 4 l i l t e d i e G . n 1 c n e s 6 t R o a o c u 0 n c A e s p V t s d t d T i a o u i o t A r n p i a 8 n o t C e p n A t d ( o N r 3 i . b r A p 2 o 4 a t u , . v 5 n o m s c e W d f k o a a m t V h h o m i c n b e e p tu p t o e n e e a l f E r e r n f t t a s R 1 h t e a i i t 6 n t e d n e A e , g c d T E a 2 e p r s p 0 R ( o e a 1 r 2 d w q A o t 3 5 e u p T e 8 2 . s i e r r 0 i t e k r g r s 0 l i V d y n o p 0 , e u p a o C d c r e c f c a , f d S t s e i r , p o T i ) r t y r n t e h h o o i s n e a v p n g A i d o d T w t i S b n h 1 e e g e a r e i s r a n CAUSE OF THE EVENT Actuation of the Division 1, 2, and 3 loss of voltage undervoltage relays due to a trip of the ERAT SAFETY CONSEQUENCES T i T b t c i m n h h l u h a e d p s i e s s e , a C s p E c e a l e t a 1 s v R i n n s e E A w d g s n T b e e t 1 p u n l w l t E l s t r a a a . a o n A s s n I f t n C s t t b o h h f t o o r e h p a . u r e o p t m E n w u u e d D s b s e v e l e G t r i e d c h d n s s e s b y t t t o a y s e h o t f l e e e f t s e h m m l t t c o y a e t s s , r r a i t a e s c e s n l a a v a o n a l e a c f d l s p h y b r , s o e l o o E i w s r t s a h e O u e d s o l G n t r p f t o o f o h U r s r f o n e m e F t m d h t S r a e e i i s A l s d t d h o R u e a e a f v n f u p s C e 1 d t i p o n t h a 3 e r m t n a 8 o , s t p k p a a o V t r t b n e i i u c a u d o r a r t s c f e 1 l e t f l e h s l y 5 s y s i e . . t s e r to o T e t a f s h r t w o p h e te u a e o d i r s w n c t r s e e a n a t n r o r n t u d o ( s r r m i a e e l 4 o d s e n 1 a e i n t o 6 . d r t a 0 a v e T c e V t d h i t o i e a a v b n n r e u y e d a x c r n i w e l e o i d a l e m n e r r c t a y e e r o s o r b n e g l n s u t o e r a s o a n s s l n c v s s a d y o o f f e l o c t r c a t e i r i y a r g s c e t e c e e u a o r d i c t v t n o r h e w y s e e C i t w t a r q h a l c h a u n h t i s e c h s s n h i o f s o c n 1 a r e e s E m r s v i e t e A e e r n C s t ) . to CORRECTIVE ACTIONS t t I h r m a e m n n s e f r e d e r i s a r t e t o e d r e C t d o o t a r o r n e t c h o t e f i f v s e E it R e A A c s T t o io . u n r R c s A e : T T s h u B e p w p s l a e y s c in t g i r o e n t t h u o e rn f e lo E d a R d t A o w T s it e b h r u v s i i t c s a e E f f f e O ro c G m te s d p e l b c a y u n r n t e h e d e d a fa m n u d a l t i p n w l t a e a c n s e a d i n s c o in e la . a te E s d a t c a a h n n d d C b l q y a u s l a i s n r e a 1 u n E p t i . 4 n 1 e 6 d 0 . V P o A w C e b r u w s a s w as PREVIOUS OCCURRENCES A S ta re ti v o i n e . w of Licensee Event Reports for the past five years identified no previous similar occurrences at Clinton Power Page_2_ of _2_ | ML26015A092
Dresden Nuclear Power Station | Unit 2 | High Pressure Coolant Injection Inoperable Due to Failed Indicating Light and Blown Fuse | 01-15-2026 | At 1613 CST on 11 /17 /25 with Unit 2 in Mode 2, Startup, at 2 percent power, it was discovered that the single train of high 1 pressure coolant injection (HPCI) was inoperable. The cause of the HPCI inoperability was a damaged stop valve closed indicating light socket and an opened negative 125 VDC fuse that occurred when the Unit 2 HPCI Turbine Turning Gear engaged. The turning gear motor turned off without operator action. The stop valve closed indicating circuit was isolated and the fuse was replaced in accordance with station procedures and HPCI operability was restored at 2253 CST. An evaluation of the event is in progress and a supplemental report will be submitted with the conclusions of the evaluation. This report is being submitted in accordance with 10 CFR 50. 73(a)(2)(v)(D) for an event or condition that could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04--02-2024) Estimated burden per response to comply with this mandatory collection request 80 hours. Reported .$ •• lessons learned are incorporated into the licensing process and fed back to industry. Send comments F ••• . LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA Library. and Information Collections Branch (T-6 A10M). U S Nuclear Regulatory Commission, Washington, DC 20555-0001 or by email to ..... CONTINUATION SHEET lnfocollects Resource@nrc.gov, and the 0MB reviewer at 0MB Office of Information and Regulatory Affalfs. (3150-0104), Attn Desk Officer for the Nuclear Regulatory Commission 725 17th Street NW Washington, DC 20503 The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to. a collection of information unless the document requesting or requmng the collection http://www.n rc.qov/reading-rm/doc-collections/n uregs/staff/sr1022/r30 displays a currently valid 0MB control number 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 SEQUENTIAL REV YEAR NUMBER NO. Dresden Nuclear Power Station, Unit 2 00237 □ 052 2025 - 003 - 00 | PLANT AND SYSTEM IDENTIFICATION - UNIT 2 General Electric - Boiling Water Reactor, 2957 megawatts thermal rated core power Energy Industry Identification System (EIIS) codes are identified in the text as [XX] A. CONDITIONS PRIOR TO EVENT Unit: 2 Event Date: November 17, 2025 Event Time: 1613 CST Reactor Mode: 2 Mode Name: Startup Power Level: 2% Pressure level: 185 psig Temperature: 376 °F No systems, structures, or components that were inoperable at the start of the event contributed to the event. B. DESCRIPTION OF EVENT At 1613 CST on 11/17/25, with Unit 2 in Mode 2, Startup, at 2 percent power, it was discovered that the single train of high pressure coolant injection (HPCI) [BJ] was inoperable. The cause of the HPCI inoperability was a failed stop valve indicating light [IL] circuit and a blown negative 125 VDC fuse [FU] that occurred when the Unit 2 HPCI Turbine [TRB] Turning Gear [TGR] engaged. The turning gear motor [MO] turned off without operator action. The indicating light circuit was isolated and the negative 125 VDC fuse was replaced in accordance with station procedures and HPCI operability was restored at 2253 CST on 11/17/25. Event Notification System (ENS) report number 58043 was transmitted to the NRC at 2328 CST on 11/17/25. This event is being reported in accordance with 1O CFR 50.7 3(a)(2)(v)(D). C. CAUSE OF EVENT The cause of the event was a damaged indicating light socket and a blown negative 125 VDC fuse when the HPCI Turbine Turning Gear was engaged. The negative 125 VDC fuse in question is required for the initiation of the steam turbine. An evaluation of the event is currently in progress. A supplemental report will be submitted with the conclusions of this evaluation. D. SAFETY ANALYSIS System Design The HPCI system is designed to ensure that adequate core cooling takes place for all break sizes less than those for which Low Pressure Coolant Injection (LPCI) [BO] or Core Spray [BM] systems can adequately protect the core without assistance from other engineered safety features. The negative 125 VDC fuse in | ML26022A036
Browns Ferry Nuclear Plant | Unit 1 | Reactor SCRAM due to Low Reactor Water Level | 01-29-2026 | On August 1, 2025, at 2350 Central Daylight Time, Browns Ferry Unit 1 experienced an automatic scram due to low reactor water level. A low reactor water level of +2 inches resulted in a valid actuation of the Reactor Protection System which caused all of the rods to insert. During the scram response, there was a valid actuation of the Primary Containment Isolation System groups 2, 3, 6, & 8. Upon receipt of these signals, all components actuated as required. Following the scram, reactor water level lowered below the -45 inch setpoint, actuating High Pressure Coolant Injection and Reactor Core Isolation Coolant and tripped both Reactor Recirculation pumps as required. Operations responded and stabilized the plant. The root cause was determined to be the installed Foxboro Feedwater Level Control system design and subsequent reviews failed to identify the single point vulnerability and inherit potential failure modes for the Foxboro System. The root cause will be addressed through elimination of the single point vulnerability in the Reactor Feed Pump speed control system. The Tennessee Valley Authority is submitting this report in accordance with Title 10 of the Code of Federal Regulations 50.73(a)(2)(iv)(A), as any event or condition that resulted in manual or automatic actuation of the Reactor Protection System and the Primary Containment Isolation System. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ☒ 050 SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 1 00259 NUMBER NO. ☐ 052 2025 - 001 - 01 | I. Plant Operating Conditions before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Unit 1, was in Mode 1 at 100 percent power. There were no impacts on Units 2 and 3. II. Description of Event A. Event Summary On August 1, 2025, at 2350 Central Daylight Time (CDT), Browns Ferry Unit 1 experienced an automatic scram due to low reactor water level. A low reactor water level of +2 inches resulted in a valid actuation of the Reactor Protection System (RPS)[JC] which caused all of the rods to insert. During the scram response, there was a valid actuation of the Primary Containment Isolation System (PCIS)[JM] groups 2, 3, 6, & 8. Upon receipt of these signals, all components actuated as required. Following the scram, reactor water level lowered below the -45 inch setpoint, actuating High Pressure Coolant Injection (HPCI)[BJ] and Reactor Core Isolation Coolant (RCIC)[BN] and tripped both Reactor Recirculation pumps as required. Operations responded and stabilized the plant. Event Notification 57847 was made to the NRC Operations Center on August 2, 2025, at 0429 EDT. The Tennessee Valley Authority (TVA) is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(iv)(A), as any event or condition that resulted in manual or automatic actuation of the RPS and the PCIS. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML26029A088
Susquehanna Steam Electric Station (SSES) | Unit 2 | Arc Flash on 500 kilovolt Transmission Lines Resulted in Main Generator Trip and Automatic Reactor Scram | 02-24-2026 | On October 28, 2025, at approximately 19:04, Susquehanna Steam Electric Station (SSES) Unit 2 experienced a main turbine trip followed by an automatic reactor scram when an arc flash on the 500 kilovolt (kV) lines occurred during a hydrogen vendor manual venting evolution. The event was reported by Event Notification 58012 in accordance with 10 CFR 50.72(b)(2)(iv)(B) as an event that resulted in an automatic actuation of the Reactor Protection System and 10 CFR 50. 72(b )(2)(xi) as an event that resulted in an offsite notification made to the Pennsylvania Emergency Management Agency. This event is also reportable in accordance with 10 CFR 50. 73(a)(2)(iv)(A) as an event that resulted in an automatic actuation of the Reactor Protection System. The cause of the event was arc flash as a result of hydrogen gases vented from the vendor-owned Hydrogen Tank Farm during normal vendor evolution contacting overhead 500 kV transmission lines. Key corrective actions include establishment of an alternative location for venting the vendor hydrogen tank trailer, revision of venting evolution instructions, and evaluation and implementation of options to increase clearance between the Hydrogen Tank Farm vent and overhead transmission lines. NRC FORM 366A (04-02-2024) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001 , or by email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 2. DOCKET NUMBER 3. LER NUMBER 1. FACILITY NAME ,-------------, ~ Susquehanna Steam Electric Station (SSES) Unit2 □ 050 052 I 00388 D NUMBER NO. I YEAR SEQUENTIAL REV ~-I 001 1-0 | CONDITIONS PRIOR TO THE EVENT Unit 1: Mode 1, approximately 100% Rated Thermal Power Unit 2: Mode 1, approximately 100% Rated Thermal Power There were no inoperable structures, systems, or components at the start of the event that contributed to the event. EVENT DESCRIPTION On October 28, 2025, at approximately 19:04, Susquehanna Steam Electric Station (SSES) Unit 2 experienced a main turbine trip [EIIS System Code - IT] followed by an automatic reactor scram when an arc flash on the 500 kilovolt (kV) lines occurred during a hydrogen vendor manual venting evolution. The event was reported by Event Notification 58012 in accordance with 10 CFR 50. 72(b )(2)(iv)(B) as an event that resulted in an automatic actuation of the Reactor Protection System and 10 CFR 50. 72(b )(2)(xi) as an event that resulted in an off site notification made to the Pennsylvania Emergency Management Agency. This event is also reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in an automatic actuation of the Reactor Protection System (including a reactor scram). The following timeline demonstrates the sequence of events: 10/28/2025 Before 18: 16: Vendor driver notifies Control Room that they will be filling the liquid hydrogen tank at the Hydrogen Tank Farm. 10/28/2025 18: 16: Vendor driver begins filling the liquid hydrogen tank at the Hydrogen Tank Farm. 10/28/2025 19:04: Liquid hydrogen tank is filled. Vendor driver begins to depressurize the tanker truck via the hydrogen tank exhaust stack at the Hydrogen Tank Farm. 10/28/2025 19:04: An arc is visible in the area of the resultant plume from the hydrogen release on the 500 kV conductors overhead the hydrogen tank in the Hydrogen Tank Farm. 10/28/2025 19:04: Unit 2 experiences an automatic scram due to Main Turbine trip caused by Main Generator [EIIS System Code - TB] differential line current and enters Mode 3. All plant systems responded normally following the automatic reactor scram. Decay heat was removed by discharging steam to the main condenser using the turbine bypass valves. Unit 1 was unaffected by the event and remained at approximately 100% Rated Thermal Power. The affected 500 kV lines were placed in service in August 2023. While similar liquid hydrogen activities are routinely performed at this location, this type of event has not previously occurred. Following visual inspection and testing of the 500kV lines and a review of the post-trip plant response, SSES Unit 2 was returned to Mode 1 operation on October 31, 2025. | ML26055A051
LaSalle County Station | Unit 1 | Manual Scram Due to Degrading Containment Parameters | 02-24-2026 | On December 28, 2025, at 1606 CST, LaSalle Station Unit 1 was manually scrammed due to degrading containment parameters associated with a leak from the 'B' reactor recirculation pump line. The scram was not complex. All control rods fully inserted as expected; no Emergency Core Cooling Systems actuated or injected into the core. This event did not pose a threat to the health and safety of the public. This event was reported via Event Notification #58100 under 1 OC FR 50.72(b)(2)(iv)(B) as an event that resulted in actuation of the Reactor Protection System when the Reactor was critical. Subsequent Event Notification #58102 under 10 CFR 50.72(b)(3)(ii)(A) reported a degraded reactor coolant system pressure boundary due to a through-wall leak identified on a reactor recirculation system three-quarter inch vent valve. Failure analysis attributed the cause of the leakage to vibration induced cyclic fatigue. Corrective actions include replacement of the affected component and planned inspections/modifications to similar equipment configurations. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply v,;th this mandatory collection request 80 hours. Reported lessons learned are incorporated into Ille licensing process and led back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and lnfonnation Collections Branch (Hi A10M), U, S. Nudear Regulatory Commission, Washington, DC 20555-0001, or by emaa to CONTINUATION SHEET lnfocollects.Resource@nrc.gov. and the 0MB reviewer at: 0MB Office of lnfonnation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nudear Regulatory Commission, 725 17111 Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of infonnation unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D displays a currenfly valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 SEQUENTIAL REV YEAR NUMBER NO. LaSalle County Station, Unit 1 00373 □ 052 2025 - 002 00 | Plant and System Identification LaSalle Country Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected systems were the Reactor Protection System (RPS) and Reactor Recirculation (RR) System. Condition Prior to Event Unit(s): 1 Date: December 28, 2025 Time: 1606 CST Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 93 percent No systems, structures, or components that were inoperable at the start of the event contributed to the event. Description On December 28, 2025 at 1606 CST, LaSalle County Station Unit 1 was manually scrammed due to degrading containment parameters caused by unidentified drywell leakage. Following the manual scram, personnel entered the Unit 1 drywell to investigate the source of the leakage. The investigation identified a degraded reactor coolant system pressure boundary due to a through wall leak from an RR system vent valve. Cause Through wall leakage was identified on the bonnet and body-to-bonnet seal weld of the upstream manually operated vent valve for a reactor recirculation pump discharge flow control valve. Failure analysis determined the leakage was caused by vibration induced fatigue cracking. Reportability and Safety Analysis The safety significance of this event was minimal. All control rods fully inserted and all systems responded as expected to the scram. Makeup capability was adequate to compensate for the leak. Emergency Core Cooling Systems were not needed, but operable and capable of fulfilling their intended safety functions. This event did not meet the NEI 99-02 definition of an unplanned scram with complications. The event did not constitute a safety system functional failure (SSFF) as defined in accordance with NEI 99-02, "Regulatory Assessment Performance Indicator Guideline." RPS actuation is reportable under 10 CFR 50. 72(b )(2)(iv)(B) as an event or condition that results in the actuation of the RPS when the reactor is critical. An ENS report was made to the NRC at 2026 EST on December 28, 2025 (EN #58100). Upon determination of the leakage source, ENS report #58102 under 10 CFR 50.72(b)(3)(ii)(A) addressed the degraded reactor coolant system pressure boundary. Corrective Actions Immediate corrective actions taken in response to the condition were: • Removed the failed valve assembly and installed blind flange connection • Initiated failure analysis and causal investigation Planned corrective actions are: • Installation of replacement vent valve assembly • Inspection and/or replacement of similar piping and valve assemblies | ML26055A084
Clinton Power Station 00461 1 OF 2 | Unknown Unit | Automatic SCRAM on High Reactor Water Level | 03-03-2026 | On October 6, 2025, during reactor startup, the Clinton Unit 1 reactor automatically scrammed due to high reactor water level. The cause of the high reactor water level was a failure of a Turbine Driven Reactor Feed Pump (TDRFP) servo valve that resulted in excessive feedwater flow to the reactor vessel. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) for “Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section.” The specific system listed in that paragraph that actuated was the “Reactor protection system (RPS) including: reactor scram or reactor trip.” NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 SEQUENTIAL REV YEAR NUMBER NO. Clinton Power Station 00461  052 2025 - 002 - 00 | CONDITION PRIOR TO THE EVENT Unit: 1 Event Date: October 6, 2025 Event Time: 03:21 CST Mode: 1 Mode Name: Power Operation Reactor Power: 23% EVENT DESCRIPTION On October 6, 2025, during reactor startup from the Clinton Unit 1 refueling outage, Turbine Driven Reactor Feed Pump (TDRFP) ‘A ‘was placed in service. While manually raising the speed of the TDRFP, the operator noticed that there was no rise in speed initially. The operator attempted again to raise pump speed. Speed then rose rapidly to 1300 rpm and went above the target setpoint of 1000 rpm. The operator placed the pump speed control mode in automatic to lower speed. TDRFP speed stabilized for about a minute before speed unexpectedly began rising rapidly to 4300 rpm. The operator then tripped the TDRFP. At the time of the trip, reactor water level was approximately 47 inches and rising. Reactor water level continued to rise, and when it reached 52 inches, an automatic reactor scram occurred. CAUSE OF THE EVENT A Root Cause investigation determined the event was caused by scoring on the A-port side of the servo valve body, confirming abrasive interaction. The scoring, caused by lodged debris, increased friction or temporarily locked the servo swing plate. The servo motor had to overcome additional drag, which it could not do effectively. As a result, the valve did not respond to a decreasing demand signal, causing failure to control the operating cylinder responsible for closing the low- pressure steam control valve resulting in a Reactor Protective System (RPS) SCRAM on level 8. SAFETY CONSEQUENCES There were no safety consequences impacting plant or public safety as a result of this event. The reactor trip system responded automatically due to the trip signal received. Additionally, the TDRFP was tripped prior to the scram, so no additional feedwater would have been injected. There was no loss of any function that would have prevented fulfillment of actions necessary to 1) shutdown the reactor and maintain it in a safe shutdown condition, 2) remove residual heat, 3) control the release of radioactive material, or 4) mitigate the consequences of an accident There was no loss of safety function for this event. CORRECTIVE ACTIONS TDRFP B has the same control loop as TDRFP A and would be susceptible to the same failures under the conditions that occurred during start-up. To mitigate the same failures, the TDRFP B servo valve SV-2 was replaced before operation. To reduce risk during future startups, operating procedures will be changed to exclusively utilize a “rolling standby” mode before feeding the Reactor Pressure Vessel. Servo tested at power labs and final report of findings issued back to CPS. Prior data of historical start-ups that included perturbations of the feed pump show evidence of starting up and having potential material or air in the oil that works through the system during initial start-up. PREVIOUS OCCURRENCES A review of Licensee Event Reports for the past five years identified no previous similar occurrences at Clinton Power Station. | ML26078A183
LaSalle County Station | Unit 1 | Automatic Scram Due to Turbine Control Valves Fast Closure on Generator Lockout | 03-27-2026 | On November 2, 2025, at 1346 CST, LaSalle Station Unit 1 experienced a Unit Auxiliary Transformer (UAT) trip. A generator lockout, turbine control valves fast closure, and reactor scram was automatically initiated by the plant in response to the trip. All control rods fully inserted as expected; no Emergency Core Cooling Systems actuated or injected. Plant operators effectively maintained reactor pressure and level. I I This event did not pose a threat to the health a~d safety of the public. This event was reported via Event No~ification #58018 under 1O CFR 50. 72(b)(2)(iv)(B) as an event that resulted in actuation of the Reactor Protection System when the Reactor was critical. The cause of the transformer trip was corrosion and inadequate divisional separation of test switches which allowed potential unintended interaction between DC divisions within protective relay circuitry. Due to this underlying condition, ground troubleshooting activities caused an inadvertent actuation of the UAT sudden pressure relay trip circuit, resulting in the Unit 1 scram. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRG may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 SEQUENTIAL REV YEAR NUMBER NO. LaSalle County Station, Unit 1 00373 □ 052 2025 - 001 01 | Plant and System Identification LaSalle Country Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the Reactor Protection System (RPS). Condition Prior to Event Unit(s): 1 Date: November 2, 2025 Time: 1346 CST Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 100 percent No systems, structures, or components that were inoperable at the start of the event contributed to the event. Description On October 29, 2025, the Main Control Room received an unexpected 125 VDC ground detector alarm. Troubleshooting activities narrowed the ground location to the Unit 1 UAT trouble alarm circuitry. On November 2, 2025, test switches were opened to isolate the previously identified ground. Opening the switches resulted in a generator lockout, UAT deluge system actuation, turbine control valves fast closure, and automatic reactor scram initiated by RPS in response to the trip. All control rods fully inserted as expected and no Emergency Core Cooling Systems actuated or injected. Plant operators effectively maintained reactor pressure and level, and reset the deluge system following verification of no fire at the transformer. Investigation following the scram identified the UAT sudden pressure relay circuit had energized, however circuit monitoring light indication and oil sample analysis concluded that sudden pressure conditions were not present to trigger a legitimate actuation. Inspection of the UAT local control cabinet identified corrosion at the test switch blocks. Cause The cause of the transformer trip was corrosion and inadequate divisional separation of test switches which allowed potential unintended interaction between DC divisions within protective relay circuitry. Due to this underlying condition, ground troubleshooting activities caused an inadvertent actuation of the UAT sudden pressure relay trip circuit, resulting in the Unit 1 scram. Reportability and Safety Analysis The safety significance of this event was minimal. All control rods fully inserted and all systems responded as expected to the scram. Emergency Core Cooling Systems were not challenged. This event did not meet the NEI 99-02 definition of an unplanned scram with complications. There were no safety system functional failures. RPS actuation is reportable under 1© C FR 50. 72(b )(2)(iv)(B) as an event or condition that results lin the actuation of the RPS when the reactor is critical. AnjENS report was made to the NRC at 1837 EST on Novemb9r 2, 2025 (EN #58018). Corrective Actions Replaced test switch blocks that had exhibited corrosion Relocated test switches to provide divisional separation Disabled sudden pressure relay logic trips of the UAT | ML26086A018