## Sheet1
Facility Name | Unit | Title | Event Date | Abstract | Narrative | File Name
Browns Ferry Nuclear Plant | Unit 3 | Inoperable Residual Heat Removal Pump Results in Condition Prohibited by Technical Specifications and Safety System Functional Failure | 03-21-2016 | On January 19, 2016, at approximately 1100 Central Standard Time (CST), during troubleshooting of the Main Control Room (MCR) green light indication on the 3A Residual Heat Removal (RHR) Pump Motor Breaker Transfer Switch (MBTS), it was discovered that the 3A RHR Pump MBTS had malfunctioned, potentially preventing the pump from starting from the MCR. The 3A RHR Pump was declared inoperable. On January 20, 2016, at approximately 0030 CST, the 3A RHR Pump was declared operable following replacement of the 3A RHR Pump MBTS. A Past Operability Evaluation concluded that the 3A RHR Pump was inoperable from January 9 to January 20, 2016, exceeding the Technical Specification allowed outage time. During this time, the 3B and 3D RHR Pumps were also inoperable on January 14, 2016, from 0127 to 0215 CST, resulting in a Safety System Function Failure. A Probabilistic Risk Assessment determined there was a negligible increase in risk. The cause of this event was failure of the transfer switch to fully latch due to binding resulting from the MBTS being installed greater than its twenty-one year service life with no Preventative Maintenance (PM) performed. Corrective actions include verifying similar transfer switches are latched in the NORMAL positon on BFN, Units 1, 2, and 3, and creating a PM activity with a replacement schedule for these switches. N RC FORM 366A (11-2015) Page 2 of 7 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Browns Ferry Nuclear Plant, Unit 3 05000296 YEAR NUMBER NO. 2016 - 001 - 00 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Unit 3, was operating in Mode 1 at approximately 79 percent rated thermal power. BFN, Units 1 and 2, were unaffected by this event. II. Description of Events A. Event: On January 13, 2016, Operations personnel identified the MCR green light indication located above the 3A Residual Heat Removal (RHR)[BO] Pump handswitch was not illuminated. The light bulb was replaced but the light remained extinguished. A work order was initiated. Operations verified correct light indications locally at the breaker. On January 19, 2016, at approximately 1100 Central Standard Time (CST), during troubleshooting of the Main Control Room (MCR) green light indication on the 3A RHR Pump Motor Breaker [BKR] Transfer Switch (MBTS)[43], it was discovered that the 3A RHR Pump MBTS, 3-43-074-0005, had malfunctioned potentially preventing the pump from starting from the MCR. Contacts [CNTR] 4-4C in the MBTS were found to be open, creating an open circuit. Operations personnel declared 3A RHR Pump inoperable. On January 20, 2016, at approximately 0030 CST, Operations personnel declared 3A RHR Pump operable following replacement of 3A RHR Pump MBTS. A Past Operability Evaluation (POE) was performed for the 3A RHR Pump. The POE concluded that the 3A RHR Pump was inoperable from January 9, 2016, to January 20, 2016, exceeding the Technical Specification allowed outage time. During this time, 3B and 3D RHR Pumps were inoperable on January 14, 2016, from 0127 to 0215 CST, resulting in a Safety System Functional Failure. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event: No inoperable systems, structures, or components contributed to this event. | ML16078A138
Clinton Power Station | Unit 1 | Continuous Containment Purge Exhaust Fan Trip due to Unvalidated Assumptions in Work Planning Resulted in an Unanalyzed Condition of Primary to Secondary Containment Differential Pressure and Safety System Functional Failure | 03-18-2015 | On January 20, 2016 at 1311, during planned clean and inspect maintenance activities on the 4160/480 Volt Unit Substation K (OAP52E), the Unit Substation K switchgear breaker OAP52E-5D for Continuous Containment Purge (CCP) exhaust fan "A" was racked out which resulted in tripping off the CCP "B" exhaust fan. This event caused Clinton Power Station (CPS) to enter one hour Required Action A.1 under Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.6.1.4, Primary Containment Pressure, due to primary to secondary containment differential pressure being greater than +0.25 psid. Operations staff took appropriate actions to rack in breaker OAP52E-5D to restart CCP "B" exhaust fan, restore primary to secondary containment differential pressure within limits at 1339. Event Notification #51669 was transmitted to the NRC on January 20, 2016 at 1731. The root cause of this event is the station did not validate assumptions resulting in an inadequate work package. Corrective actions include updating the maintenance planning checklist, performing a read and sign and presenting a case study to maintenance planning personnel on this event. This event is reportable under 10 CFR 50.73(a)(2)(ii)(B) as an unanalyzed condition and 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented fulfillment of a safety function. NRC FORM 366 (11-2015) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3160-0104 EXPIRES: 01/31/20~7 02-2014) . G ~ . ,pY1•b:i"4~'\ • R Es e t p im or a te te d d le b s u s r o d n e s n le p a e r r n e re d s p a o re n s in e c o to rp c o o ra m te p d ly in w to ith t h t e h i l s ic e m n a s n in d g a t p o r r o y c e co ss lle a c n ti d o n f e r d e q b u a e c s k t : t o 8 0 in d h u o s u tr r y s . . ~ Send comments regarding burden estimate to the FOIA, Privacy and Information Collections ~ ~/) Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by ... LICENSEE EVENT REPORT (LER) internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, CONTINUATION SHEET Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 6. LER NUMBER 3. PAGE I I SEQUENTIAL REV YEAR NUMBER NO. Clinton Power Station, Unit 1 05000461 2 OF 4 2016 001 00 | PLANT AND SYSTEM IDENTIFICATION General Electric-- Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in text as [XX]. EVENT IDENTIFICATION Continuous Containment Purge Exhaust Fan Trip due to Unvalidated Assumptions in Work Planning Resulted in an Unanalyzed Condition of Primary to Secondary Containment Differential Pressure and Safety System Functional Failure A. Plant Operating Conditions Prior to the Event: Unit: 1 Event Date: 1/20/2016 Event Time: 1311 Central Time Mode: 1 Mode Name: Power Operation Reactor Power: 099 percent B. DESCRIPTION OF EVENT On January 17, 2016at1544 Operations de-energized 4160/480 Volt Unit Substation [USS] K (OAP52E) due to a loud crackling noise heard coming from the unit substation. Troubleshooting Work Order (WO) 1892378 was created to inspect the transformer [XFMR] located in the unit substation to determine the cause of the noise. At 2214 on January 17, 2016, Clearance Order (C/O) 130969 was hung to support the transformer inspection which placed the Main Feeder breaker [BKR] OAP52E-3B in the Racked Out position. On January 19, 2016 the-Electrical Maintenance Manager approached Electrical Maintenance Planning in regards to performing Preventive Maintenance Work Order (PMWO) 1575170 Clean and Inspect Unit Substation 'K' scheduled in July 2016 in conjunction i,,yith the troubleshooting WO 1892378. Electrical Maintenance requested that the work planner incorporate specific steps from the Clean and Inspect PMWO 1575170 into the current troubleshooting package WO 1892378 so that the PMWO could be credited. While adding the requested steps into the troubleshooting WO, the work planner noticed that an existing job step stated "Coordinate with Ops to ensure all breakers are open/racked out". Because the work planner believed that this was a duplicate of a requested step, the work planner believed the prerequisite conditions would be met and did not need to be added into the WO task being planned. Procedure WC-AA-104, Integrated Risk Management, Attachment 8, Risk Screening/Mitigation Plan was completed, but the need for an OPS review was not noted and therefore not completed. The form identified Auxiliary Power (AP) system impacts but did not take into account the Containment Building Ventilation (VR) system effects. The work activity was not properly screened for risk and there was no reference for ensuring validation of initial conditions prior to commencing the work under WO 1892378. | ML16082A281
Limerick Generating Station | Unit 1 | Inoperable Reactor Enclosure Secondary Containment Integrity Due to Open Airlock | 03-23-2016 | Unit 1 reactor enclosure secondary containment integrity was briefly declared inoperable when both doors on a reactor enclosure 201’ elevation pipe tunnel airlock were simultaneously opened. The cause of the event was a degraded closing mechanism on the airlock inboard door. The airlock doors were closed to restore reactor enclosure secondary containment integrity. The degraded inboard door closing mechanism was repaired. NRC FORM 366 (01-2014) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 01/31/2017 (01-2014) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by LICENSEE EVENT REPORT (LER) internet e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, CONTINUATION SHEET Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 6. LER NUMBER 3. PAGE SEQUENTIAL REV YEAR NUMBER NO. Limerick Generating Station, Unit 1 05000352 2 OF 4 2016 - 001 - 00 | Unit Conditions Prior to the Event Unit 1 was in Operational Condition (OPCON) 1 (Power Operation) at 100 percent power. There were no structures, systems or components out of service that contributed to this event. Description of the Event On Monday, January 25, 2016, Limerick Unit 1 was operating at 100 percent power with maintenance ongoing in the residual heat removal service water (RHRSW) / emergency service water (ESW) pipe tunnel. At approximately 1819 hours, the main control room supervisor (CRS) was notified that the local airlock open door alarm (EIIS:ALM) was activated when a worker in the pipe tunnel opened the airlock outboard (pipe tunnel side) door (EIIS:DR). The alarm indicated that both air lock doors were briefly opened for one reactor enclosure airlock. The reactor enclosure low pressure alarm setpoint is 0.20 inches of vacuum water gauge (WG) and the reactor enclosure low pressure alarm did not actuate during the event. The airlock was open for less than 10 seconds; therefore, the main control room airlock open alarm did not actuate. The reactor enclosure secondary containment integrity (EIIS:NH) was declared inoperable for the period when both doors were open. An investigation determined that a worker using the airlock properly verified that the door open blue light indication was not lit and then opened the outboard airlock door which activated the local airlock open alarm. The most likely cause of the alarm was a degraded inboard door closing mechanism that resulted in the inboard door opening far enough to activate the alarm when the outboard door was opened. The worker immediately reclosed the open outboard door when the local alarm actuated and the breach of secondary containment was terminated. The airlock was open for a period of less than 10 seconds. The worker notified Operations shift management of the containment breach. TS 3.6.5.1.1 Reactor Enclosure Secondary Containment Integrity surveillance requirement 4.6.5.1.1.a requires verification that reactor enclosure pressure is greater than or equal to 0.25 inches of vacuum water gauge on a 24-hour frequency. The TS surveillance requirement 4.6.5.1.1.b.2 requires at least one door in each access to the reactor enclosure be verified closed on a 31-day frequency. TS 3.6.5.1.1 is applicable in operational conditions (OPCON) 1, 2, and 3. This LER is being submitted pursuant to the requirements of 10CFR50.73(a)(2)(v)(C) for a condition that could have prevented the fulfillment of the safety function of structures or systems needed to control the release of radioactive material. NEI 99-02 (Revision 7), Regulatory Assessment Performance Indicator Guideline, section 2.2 Mitigating Systems Cornerstone, Safety System Functional Failures, Clarifying Notes, states the following: | ML16083A231
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | System Actuations during Manual Scram in Response to Frazil Ice Blockage and Residual Transfer | 03-23-2016 | On January 23, 2016, James A. FitzPatrick Nuclear Power Plant (JAF) was ascending in power when screenwell water level started to lower. At 89 percent power, at 22:23, Operators began taking compensatory measures to reduce power and mitigate water level lowering. At 22:40, a manual scram was initiated. The scram was complicated by a residual transfer that resulted in non-vital equipment trips. This event resulted in the manual actuation of the Reactor Protection System, High Pressure Coolant Injection, Reactor Core Isolation Cooling, Main Steam Isolation Valves and automatic actuation of Emergency Diesel Generators, Emergency Service Water, and containment isolations in multiple systems, reportable per 10 CFR 50.73(a)(2)(iv)(A). The lowering screenwell water level was caused by frazil ice blockage at the intake structure. The frazil ice stopped affecting screenwell water level after the manual scram. Corrective actions include strengthening mitigating actions in response to frazil ice. The residual transfer was caused by lubrication hardening in the lower control valve assembly of the 71PCB-10042 breaker. Corrective actions included replacing or reworking the lower control valve assembly. NRC FORM 366 (11-2015) Page 2 of 6 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 – 333 NUMBER N0. 2016 – 001 – 00 | Background James A. FitzPatrick’s (JAF) Ultimate Heat Sink [EIIS designation: BS] is Lake Ontario. Water from Lake Ontario is transported via a water intake structure. The intake structure is an underwater concrete structure on the lakebed. Lake water enters the intake structure, travels through the intake tunnel, and enters the intake bay. The intake bay is located inside the screen house building. The enclosed intake bay area is also called the screenwell. Located in the screenwell area, downstream of trash racks and rotating screens, are three Circulating Water pumps [KE], three Normal Service Water (NSW) pumps [KG], two Emergency Service Water (ESW) pumps [BI], four Residual Heat Removal Service Water (RHRSW) pumps [BI] and two Fire pumps [KP]. One Fire pump is upstream of the trash racks. The Circulating Water pumps supply cooling to the main condenser and are each operated at 133,000 gpm. NSW pumps are each rated at 17,800 gpm and supply cooling to plant loads during normal operating conditions. ESW pumps supply cooling to safety-related loads during both normal and accident conditions and are rated at 3,700 gpm each. RHRSW pumps, rated at 4,000 gpm each, supply cooling to the RHR heat exchangers. Intake / screenwell water level is normally slightly lower than lake level due to flow head losses (generally at about 244 feet elevation depending on seasonal changes). The screenwell level is monitored in the control room and on Operator rounds. The NSW, ESW, and RHRSW pumps require a minimum water elevation at 235 feet elevation for safe operation. The Circulating Water and the Fire pumps require a minimum water elevation of 239 feet 6 inches for safe operation. Frazil ice is a natural phenomenon in lakes and water ways, including Lake Ontario, when water freezes into loosely formed needle-like crystals. Surface water becomes supercooled when it loses heat rapidly to cold air without freezing. Turbulence, caused by winds, can mix the supercooled water throughout a body of water. The supercooled water encourages the formation of small ice crystals (frazil ice). Ice generally floats, but due to frazil ice's small size relative to current speeds, it can be carried to the bottom very easily. Frazil ice is more likely to occur when air temperatures decrease below freezing and when there is little ice cover on the lake, no cloud cover, winds are present, and the sun has set. Frazil ice has a negative impact on plant operations when it adheres to the intake structure. Supercooled water can reduce the intake structure surface temperatures below freezing then ice forms directly on the surface or frazil ice slush could drift into the structure and adhere to it. Since the intake structure actively draws in water it may draw in frazil ice. The intake structure entrance includes rack bars to screen large debris, consisting of 88 metal bars. These metal bars would normally be an optimal surface for frazil ice accumulation; however, deicing heaters are located in each. | ML16083A504
River Bend Station -Unit 1 05000 458 1 OF 3 | Unit 1 | Potential Loss of Secondary Containment Safety Function Due to Failure of Auxiliary Building Ventilation System | 03-07-2016 | On January 5, 2016, at 10:58 p.m. CST, with the plant operating at 100 pen,ent power, the main control room alarm indicating high pressure in the auxiliary building actuated. Operators confirmed that the building pressure was out of specification. Secondary containment was declared inoperable, and the Division 2 standby gas treatment system was started. This action restored building pressure to the acceptable range, and secondary containment was declared operable at 12:27 a.m. on January 6. An inspection of the auxiliary building normal ventilation system found that discharge dampers on the exhaust fans were degraded, and the flow control damper on the supply fans was not operating correctly. In order to restore the normal ventilation system to service, the troubleshooting plan for this condition temporarily altered the operating configuration of the system to close the suction damper on the idle exhaust fan. This prevents backflow through the idle fan, allowing the system to control building pressure within the required operating range. Corrective maintenance is being planned to restore the material condition of the normal ventilation system. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(C) as an event that caused the secondary containment to be potentially incapable of performing its safety function. NRC FORM 366 (02-2014) NRC FORM 366A U.S. NUCLEAR.REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 01/31/2017 (02-2014) Estimated burden per response to comply with this mandatory collection request 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections LICENSEE EVENT REPORT (LER) Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information CONTINUATION SHEET and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currenUy valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 6. LER NUMBERI 3. PAGE I YEAR SEQUENTIAL REV River Bend Station -Unit 1 NUMBER NO. 05000 458 2 OF 3 2016 • 001 • 00 | REPORTED CONDITION On January 5, 2016, at 10:58 p.m. CST, with the plant operating at 100 percent power, the main control room alarm indicating high pressw:e in the auxiliary building [NF] actuated. Operators confirmed that the building pressure was out of specification. Secondary containment was declared inoperable, and the Division 2 standby gas treatment system [BH] was started. This action restored building pressure to the acceptable range, and secondary containment was declared operable at 12:27 a.m. on January 6. This condition is being reported in accordance wi,th 10 CFR 50.73(a)(2)(iv)(A) as an event that caused the secondary containment to be potentially incapable of performing its safety function. BACKGROUND I The normal auxiliary building ventilation system [VF] is non-safety related, and comprises two 100 percent capacity supply fans, two 100 percent capacity exhaust fans, and the associated ductwork, dampers, and controls. A supply fan operates continuously, drawing air from outside and distributing it throughout the building. The supply fan discharge·dampers modulate automatically to maintain air flow at a nominal 10,000 standard cubic feet per minute. An exhaust fan continuously draws air from the building and expels it outside. The arrangement of the flow path through the building general equipment areas and pump rooms is balanced such that the system acts to maintain the building at a negative pressure. During design-basis accident conditions, the auxiliary building is maintained at negative pressure by the standby gas treatment system. That is a safety-related system that actuates automatically in response to certain plant parameters. INVESTIGATION and DvIMEDIATE ACTIONS . The normal ventilation system was inspected, and it was determined that a combination of degraded components caused the condition: •Seals on the exhaust fan (**FAN**) discharge damper (**BDI\1P**) vanes were degraded. This allowed air to flow backwards through the idle exhaust fan, causing the total exhaust outflow to decrease and building pressure to increase: •The flow controller for the supply fan modulating dampers (**CDI\1P**) had failed, allowing excessive air flow that caused building pressure to increase. In order to restore the normal ventilation system to service, the troubleshooting plan for this condition temporarily altered the operating configuration of the system to close the suction damper on the i4le exhaust fan. This prevents backflow through the idle fan, allowing the system to control building pressure within the required operating range. CORRECTIVE ACTION TO PREVENT RECURRENCE Corrective maintenance is being planned to (1) replace the seals in the exhaust fan discharge dampers to eliminate the backflow path, and (2) calibrate the supply fan modulating damper control circuit. NRG FORM 366A (02-2014) | ML16084A144
Prairie Island Nuclear Generating Plant | Unit 1 | Listed System Actuation - Motor-Driven Cooling Water Pump Auto-Start | 02-05-2016 | At 1110 Central Standard Time (CST) on 1/29/2016, the Prairie Island Nuclear Generating Plant (PINGP) performed a planned overspeed post-maintenance test (PMT) of 22 Diesel-Driven Cooling Water Pump (DDCLP) in accordance with plant maintenance procedure. During the overspeed trip test PMT, 22 DDCLP tripped as expected, and 121 Motor-Driven Cooling Water Pump (MDCLP) unexpectedly started automatically ("auto-started") on low pressure in the cooling water pump discharge header. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of an emergency service water system that does not normally run and that serves as ultimate heat sink. The cause of the 121 MDCLP auto-start was a low-pressure transient in the cooling water pump discharge header resulting from the trip of 22 DDCLP. There was no safety injection signal from PINGP Unit 1 nor Unit 2 when 121 MDCLP started. The health and safety of the public was not at risk. Corrective actions to be taken for this event include revising plant procedures to ensure 121 MDCLP is running prior to performing the overs peed trip test PMT and to ensure the pump is running or in pullout position to prevent auto-start of 121 MDCLP when stopping a DDCLP. NRC FORM 366 (11-2015) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to Industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the Information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR I SEQUENTIAL I REV Prairie Island, Unit 1 05000-282 NUMBER NO. 2016 -002 -00 | Event Description At 1110 CST on 1/29/2016, PINGP performed a planned overs peed trip test PMT of 22 DDCLP (EllS Component Identifier P) in accordance with preventive maintenance procedure PM 3002-2-22, 22 DDCLP Diesel Minor Periodic Maintenance. During the overspeed trip test, 22 DDCLP tripped, and 121 MDCLP (EllS Component Identifier P) auto-started on low pressure in the cooling water pump discharge header. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of an emergency service water system that does not normally run and that serves as ultimate heat sink. Event Analysis The PINGP Cooling Water (CL) System (EllS System Identifier Bl) is a shared system for Units 1 and 2 and provides a heat sink for the removal of process and operational heat from safety-related components during a Design Basis Accident or transient. During normal operation and shutdown, the CL System also provides this function for various safety-related and nonsafety-related components. Five CL pumps are connected to a common pump discharge header that directs CL flow into two separate headers: three motor-driven pumps and two diesel-driven pumps. 121 MDCLP can function as a safeguards replacement when a diesel driven pump is taken out of service. In this configuration, the pump is aligned manually to the appropriate train of safeguards power and motor-operated valves are administratively disabled in accordance with technical specifications. 11 and 21 MDCLPs were running, and 121 MDCLP was not aligned as safeguards. Data from the Emergency Response Computer System (ERCS) showed that tripping 22 DDCLP resulted in a reduction of 8 psig in Loop A CL header pressure, 10 psig in Loop B CL header pressure, and over 1000 gpm in Loop B CL flow. 22 DDCLP developed a greater than normal discharge pressure while running at higher than normal speed during the overs peed PMT, and tripping the pump the higher speed caused a higher than expected change in pressure compared to stopping the pump from normal speed. Operators correctly performed steps from plant operating and maintenance procedures intended to prevent an automatic start of 121 MDCLP. No inappropriate action was identified related to human performance. 121 MDCLP has auto-started on low pressure on previous occasions. Pressure transients in the discharge header occur when stopping a DDCLP. Corrective actions taken since the last auto-start in April 2012 were effective in preventing auto-starts during monthly surveillance testing according to SP 11 06A and SP 11068, but they were not effective in this instance. Those corrective actions focused on running two MDCLPs and ensuring the pump discharge header was cross-connected to minimize the discharge header pressure transient when stopping a DDCLP. During this event, 22 DDCLP was running at an elevated speed, resulting in a larger transient when 22 DDCLP was stopped. Safety Significance 121 MDCLP and other equipment operated as intended during the event. The low pressure transient was confined to the pump discharge header and did not result in below normal pressure in either cooling water | ML16085A181
River Bend Station -Unit 1 05000 458 1 OF 3 | Unit 1 | Actuation of the Division 1 Emergency Diesel Generator and Primary Containment Isolation Logic Due to Partial Loss of Offsite Power | 03-29-2016 | On January 29, 2016, at 1518 CST, with the plant in cold shutdown, power was lost on reserve station service (RSS) line no. I. This is one of two sources of offsite power required by Technical Specifications. The power loss de-energized the Division 1 onsite AC safety·- related switchgear, causing an automatic start of the Division 1 emergency diesel generator (EDG). The Division 1 reactor protection system (RPS) bus was also de-energized, causing a half-scram signal. Approximately 8 minutes later, a full actuation of the RPS occurred due to high water level in the control rod drive hydraulic system scram discharge volume header. All reactor control rods were already fully inserted. The loss of Division 1 RPS also caused the actuation of the Division 1 primary containment isolation logic. The Division 1 isolation valves in the balance-of-plant systems closed as designed. Both trains of the standby gas treatment system actuated. The loss ofRSS No. 1 was caused when company transmission department personnel working in the local 230kV switchyard executed a deficient work instruction while modifying relay settings. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as the automatic actuation of the Division 1 EDG, the Division 1 primary containment logic, and the reactor protection system (while subcritical). At the time of the event, the shutdown cooling system was operating on the Division 2 subloop, which was unaffected. 'fhe Division 1 EDG performed as designed. This event was, thus, of minimal significance to the health and safety of the public. NRG FORM 366. (02-2014) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 01/31/2017 (02-2014) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections LICENSEE EVENT REPORT (LER) Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information CONTINUATION SHEET and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 6. LER NUMBER I 3. PAGE I SEQUENTIAL REV YEAR River Bend Station -Unit 1 NUMBER NO. 05000 458 2 OF 3 2016 - 004 00 | REPORTED CONDITION On January 29, 2016, at 1518 CST, with the plant in cold shutdown, power was lost on reserve station service (RSS) line no. 1. This is one of two sources of offsite power required by Technical Specifications. The power loss de-energized the Division 1 onsite AC safety-related switchgear [EB], causing an automatic start of the Division 1 emergency diesel generator (EDG)(**DG**). The Division 1 reactor protection system (RPS)[JC] bus was also de-energized, causing a half-scram signal. Approximately 8 minutes later, a full actuation of the RPS occurred due to high water level in the control rod drive hydraulic system scram discharge volume header. All reactor control rods were already fully inserted. The loss of Division 1 RPS also caused the actuation of the Division 1 primary containment isolation logic. The Division 1 isolation valves in the balance-of-plant systems closed as designed. Both trains of the standby gas treatment system actuated. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A)° as the automatic actuation of the Division 1 EDG, the Division 1 primary containment logic, and the reactor protection system (while subcritical). INVESTIGATION AND IMMEDIATE CORRECTIVE ACTIONS At the time of the event, technicians from the company's transmission department were working in the local 230kV switchyard. A modification was being performed on relay setpoints to implement corrective actions stemming from a reactor scram that occurred on November 27, 2015, caused by a transient on a nearby 230kV transmission line. The investigation of that scram determined that one of two circuit breakers supplying RSS No. 1 tripped too soon during the transient. In developing the final corrective action, a change was made to the work package on the previous day regarding a specific relay setpoint. During the post-modification testing, a current signal was applied to the affected circuits without taking the necessary precautions to prevent an actuation of the protection logic, resulting in the unanticipated trip of the circuit breaker. This caused the loss of power to RSS No. 1. This investigation determined that the late change in the as-left relay setpoint caused the work to proceed without the development of step-by-step instructions that conformed to nuclear industry standards for such documents. As an interim measure, all work at the 230kV switchyard must be approved by the plant manager. CORRECTIVE ACTIONS TO PREVENT RECURRENCE The following actions are planned in response to this event. 1. Revise the operating agreement between the station and the transmission department to identify and communicate respective responsibilities with regard to all switchyard work and work package detail during outage and online activities. 2. Based on the specific revisions to the nuclear operating agreement, revise transmission department procedure(s) to provide detailed step by step work instructions, evaluation ofrisk, and clarification ofownership. | ML16097A416
North Anna Power Station | Unknown Unit | Emergency Diesel Generators Automatic Start Due to Loss of Power to "C" Reserve Station Service Transformer 5.EVENTDATE 6. LER NUMBER 7. REPORT DATE 8. OTHER FACILITIES INVOLVED I I FACILITYNAME ·DOCKET NUMBER MONTH DAY YEAR YEAR SE N Q U U M EN BE T R IA L· R N E O V . MONTH DAY YEAR North Anna Power Station 05000339 - FACILITY NAME DOCKET NUMBER 01 23 2016 2016 - 001 00 03 16 2016 05000 9. OPERATING MODE 11. TIDS REPORT IS.SUBMITTED PURSUANT TO THE REQUIREMENTS OF 10 CFR §: (Check all that apply) D -D D D 20.2201(b) 202203(a)(3)(i) 50.73(a)(2)(i)(C) 50.73(a)(2)(vii) D D D D 202201cd) 20.2203(a)(3)(ii) so.13(a)(2)(ii)(A) 50.73(a)(2)(viii)(A) 1 D · D D D 20.2203(a)(1) 202203(a)(4) 50.73(a)(2)(ii)(B) 50.73(a)(2)(viii)(B) D D D D 20.2203(a)(2)(i) 50.36(c)(l)(i)(A) so.13(a)(2)(iii) 50.73(a)(2)(ix)(A) D D D 10. POWER LEVEL 20.2203(a)(2)(ii) so.36(c)(1)(ii)C~) ~ 50.73(a)(2)(iv)(A) 50.73(a)(2)(x) D · D ·D D 202203(a)(2)(iii) so.36(c)(2) 50.73(a)(2)(v)(A) 73.71(a)(4) D D D D 20.2203(a)(2)(iv) so.46(a)(3)(ii) 50.73(a)(2)(v)(B) 13.11ca)(s) 100 D D D D 20.2203(a)(2)(v) 50.73(a)(2)(i)(A) 50.73(a)(2)(v)(C) OTHER D 20.2203(a)(2)(vi) D so.13(a)(2)(i)(B) D so.13c~)(2)(v)(D) · Specify in Abstract below or in NRC Form 366A 12. LICENSEE CONTACT FOR TIDS LER I LICENSEE CONTACT TELEPHONE NUMBER (Include Area Code) Gerald T. Bischof, Site Vice President (540) 894-2101 13. COMPLETE ONE LINE FOR EACH COMPONENT FAILU RE DESCRIBED IN TIDS REPORT MANU- REPORTABLE . MANU- REPORTABLE CAUSE SYSTEM COMPONENT FACTURER TOEPIX ~ CAUSE SYSTEM COMPONENT FACTURER TOEPIX c EA 63 S254 y I . . "·' 14. SUPPLEMENTAL REPORT EXPECTED 15. EXPECTED MONTH DAY YEAR D SUBMISSION YES.(Ifyes, compl~te 15. EXPECTED SUBMISSION DATE) ~No DATE ABSTRACT (Limit to 1400 spaces, i.e., approximately 15 single-spaced typewritten lines) On January 23, 2016, at approximately 1703 hours, with Units 1 and 2 operating at 100 percent power Mode 1 , the North Anna 34.5kv Bus 3, offsite power feed to the "C" Reserve Station Service Transform~r, was lost due to the opening of the L 102 breaker. This resulted in the.loss of power to the Unit 1 Hand Unit 2J emergency buses and the automatic start of the 1 Hand 2J emergency diesel generators (EOG). The Unit 1 Hemergency bus off-site power was restored and the 1 H EOG was secured and returned to automatic. The 2J EOG continued to carry the 2J bus until repairs to L 102 were completed.and the 72 hour limiting action for Unit 2 was exited at 1706 hours on 1/ 24/16. The direct cause for the opening of the L 102 breaker was ari internal switch contact failure due to moisture. At 1948 hours on January 23, 2016, an 8-hour Non-Emergency Report was made to the NRC in accordance with 10 CFR 50. 72(b)(3)(iv)(A) as a condition that resulted in valid actuation of Engirieered Safety Features (ESF). Units 1 and 2 continued to operate safely during the event. The health and safety of the public were not affected by this event. NRC FORM 366 (02,2014) ~CFORM366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 01131/2°017 02-2014) . .• Estimated burden per response to comply with this mandatory collection request: 80 hours. ~#"~" p ':; Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by \:.. ••••• ) LICENSEE EVENT REPORT (LER) internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, CONTINUATION SHEET Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or SP.onsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2.DOCKET 6. LER NUMBER 3.PAGE - YEAR I SE N Q U U M EN BE TI R A L I R N E O V . North Anna Power Station, Units 1 & 2 05000338 2 OF 3 . 2016 - 001 - 00 NARRATIVE 1.0 DESCRIPTION OF THE EVENT On January 23, 2016, at approximately 1703 hours, Switchyard breaker L 102 (EllS System - EA, Component - BKR), supply to 34.5kV bus #3, tripped open from the· Sulfur Hexafluoride (SF 6) gas pressure switch. This resulted in the loss of "C" Reserve Station Service Transformer (RSST) (EllS System - EA, Component-XFMR) which suppljes "F" transfer and 2G intake structure 4160VAC buses (EllS System - EB, Component - BU). The 2G bus fast .transferred to the 1G bus allowing all Unit 2 circulating water pumps to continue to run being supplied by Unit 1. The "F" transfer bus supplies the 1H and 2J emergency buses (EllS System - EK, Component - BU). Their associated Emergency Diesel Generators (EOG) (EllS System -EK, Component - OG) started and loaded to recover those buses. The 1 H bus was swapped to its · alternate supply from 1B station service and the 1 H EOG was shutdown ahd returned to auto standby. Limiting actions on Unit 1 were cleared at that time. The 2J EOG continued to carry the 2J bus. At 1948 hours on January· 23, 2016, an 8-hour No'n Emergency Report was made to the NRG in accordance with 10 CFR 50.72(b)(3)(iv)(A) _as a condition that resulted in valid actuation of ESF. As a result of the event, the Unit 2 Moisture Separator Reheater (MSR) fiow control valves (FCVs) (EllS System - SB, Component- FCV) went closed and reactor power reduced to approximately 96 percent. In addition, the Unit 1 "B" Charging pump (EllS System - CB, Component - P) auto-started due to the under-voltage condition on the 1 H bus. The pump was secured and returned to auto at 1720 hours on January 23, 2016. ·The MSR FCVs were reopened at ·0332 hours on January 24, 2016. At 1528 hours on January 24, 2016, the "C" . RSST was energized and normal power restored to the 2J Emergency bus. The 2J EOG was secured at 1541. hours. Repairs to breaker L 102 were com·pleted and the Unit 2 72 hour limiting action was exited at 1706 hours on January 24, 2016. 2.0 · SIGNIFICANT SAFETY CONSEQUENCES AND IMPLICATIONS Units 1 and 2 continued to operate, as designed, foilowing the loss of offsite power. No significant safety consequences resulted from this event because the 1 H and 2J EOGs · powered the emergency busses, as designed. Offs1te power sources were restored in a timely manner and the associated EOGs were secured and returned to automatic. The health and safety of the public were not affected by· this event. 3.0 CAUSE The direct cause for the opening of the L 102 breaker was an internal switch contact ., . · NRC FORM 366A (02-2014) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION (02-2014) LICENSEE EVENT REPORT (LER) CONTINUATION SHEET 1. FACILITY NAME· 2.DOCKET 6. LER NUMBER 3.PAGE I REV . YEAR I SE N Q U U M EN B T E I R A L NO. North Anna Power Station, Units 1 & 2 05000338 OF 3 2016 001 00 NARRATIVE failure due to moisture. Snow/moisture intrusion inside the cabinet likely shorted across the electrical terminals for the SF5 gas _pressure switch (63G) and caused the 63X relay to pick up, which tripped and locked out the breaker. · The SF pressure switch vendor was unable to find anything wrong with the calibration 6 of the switch. Subject matter experts-(SME) within the company along with the breaker m·anufacturer were also unable to find anything physically wrong. with the switch. ·· 4.0 IMMEDIATE CORRECTIVE ACTION(S) The L 102 SF gas pressure switch was rep_laced and the 72 hour limiting action for Unit 6 2 was exited. . 5.0 ADDITIONAL CORRECTIVE ACTIONS. In accordance with the manufacturer's and Dominion SME recommendations, all 34.5KV breakers· in the North Anna switchyard have had weather sealant applied to prevent moisture intrusion (rain/snow) where air gaps were noted to be around the conduit access plate and the mechanism access plate .at the bottom of the breaker cabinet which are the most likely intrusion areas. Additionally the L 102 and L202 breakers had weather sealant applied to the area .where the breaker cabinet top meets the breaker cabinet side walls along the front and two sides .. . . 6.0 ACTIONS TO PREVENT RECURRENCE The preventive maintenance procedure is being revised to include an additional check for snow and moisture intrusion path~· into cabinetS and seal as appropriate for the · breakers in question. Monitoring. of all the 34.5KV breakers for moisture intrusion will occur to determine if additional actions to seal the breakers are required for the remaining· nine (9) breakers. Inspections of the sealant will also be performed to ensure it remains intact. The monitoring period will be for approximately one year to allow the breakers to be exposed to all seasonal conditions. . · . 7 .0 SIMILAR EVENTS None 8.0 ADDITIONAL INFORMAT10N· Component: 63G pressure switch Manufacturer Solari Model 6TC Bulb type . NRC FORM366A (02-2014) | 03-16-2016 | On January 23, 2016, at approximately 1703 hours, with Units 1 and 2 operating at 100 percent power Mode 1 , the North Anna 34.5kv Bus 3, offsite power feed to the "C" Reserve Station Service Transform~r, was lost due to the opening of the L 102 breaker. This resulted in the.loss of power to the Unit 1 Hand Unit 2J emergency buses and the automatic start of the 1 Hand 2J emergency diesel generators (EOG). The Unit 1 Hemergency bus off-site power was restored and the 1 H EOG was secured and returned to automatic. The 2J EOG continued to carry the 2J bus until repairs to L 102 were completed.and the 72 hour limiting action for Unit 2 was exited at 1706 hours on 1/ 24/16. The direct cause for the opening of the L 102 breaker was ari internal switch contact failure due to moisture. At 1948 hours on January 23, 2016, an 8-hour Non-Emergency Report was made to the NRC in accordance with 10 CFR 50. 72(b)(3)(iv)(A) as a condition that resulted in valid actuation of Engirieered Safety Features (ESF). Units 1 and 2 continued to operate safely during the event. The health and safety of the public were not affected by this event. NRC FORM 366 (02,2014) ~CFORM366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 01131/2°017 02-2014) . .• Estimated burden per response to comply with this mandatory collection request: 80 hours. ~#"~" p ':; Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by \:.. ••••• ) LICENSEE EVENT REPORT (LER) internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, CONTINUATION SHEET Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or SP.onsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2.DOCKET 6. LER NUMBER 3.PAGE - YEAR I SE N Q U U M EN BE TI R A L I R N E O V . North Anna Power Station, Units 1 & 2 05000338 2 OF 3 . 2016 - 001 - 00 | 1.0 DESCRIPTION OF THE EVENT On January 23, 2016, at approximately 1703 hours, Switchyard breaker L 102 (EllS System - EA, Component - BKR), supply to 34.5kV bus #3, tripped open from the· Sulfur Hexafluoride (SF 6) gas pressure switch. This resulted in the loss of "C" Reserve Station Service Transformer (RSST) (EllS System - EA, Component-XFMR) which suppljes "F" transfer and 2G intake structure 4160VAC buses (EllS System - EB, Component - BU). The 2G bus fast .transferred to the 1G bus allowing all Unit 2 circulating water pumps to continue to run being supplied by Unit 1. The "F" transfer bus supplies the 1H and 2J emergency buses (EllS System - EK, Component - BU). Their associated Emergency Diesel Generators (EOG) (EllS System -EK, Component - OG) started and loaded to recover those buses. The 1 H bus was swapped to its · alternate supply from 1B station service and the 1 H EOG was shutdown ahd returned to auto standby. Limiting actions on Unit 1 were cleared at that time. The 2J EOG continued to carry the 2J bus. At 1948 hours on January· 23, 2016, an 8-hour No'n Emergency Report was made to the NRG in accordance with 10 CFR 50.72(b)(3)(iv)(A) _as a condition that resulted in valid actuation of ESF. As a result of the event, the Unit 2 Moisture Separator Reheater (MSR) fiow control valves (FCVs) (EllS System - SB, Component- FCV) went closed and reactor power reduced to approximately 96 percent. In addition, the Unit 1 "B" Charging pump (EllS System - CB, Component - P) auto-started due to the under-voltage condition on the 1 H bus. The pump was secured and returned to auto at 1720 hours on January 23, 2016. ·The MSR FCVs were reopened at ·0332 hours on January 24, 2016. At 1528 hours on January 24, 2016, the "C" . RSST was energized and normal power restored to the 2J Emergency bus. The 2J EOG was secured at 1541. hours. Repairs to breaker L 102 were com·pleted and the Unit 2 72 hour limiting action was exited at 1706 hours on January 24, 2016. 2.0 · SIGNIFICANT SAFETY CONSEQUENCES AND IMPLICATIONS Units 1 and 2 continued to operate, as designed, foilowing the loss of offsite power. No significant safety consequences resulted from this event because the 1 H and 2J EOGs · powered the emergency busses, as designed. Offs1te power sources were restored in a timely manner and the associated EOGs were secured and returned to automatic. The health and safety of the public were not affected by· this event. 3.0 CAUSE The direct cause for the opening of the L 102 breaker was an internal switch contact ., . | ML16099A386
Limerick Generating Station | Unit 1 | Condition Prohibited by Technical Specifications Due to Inoperable Safeguard Batteries During Cell Replacements | 04-11-2016 | The Unit 1 Division 1 125 VDC Safeguard Battery was rendered inoperable due to installation of temporary seismic restraints that had not been approved for use. This historical issue was identified during a preventive maintenance activity to replace the battery. The investigation identified fifteen reportable events over a three year period. The cause was incomplete scoping of the engineering analysis performed to support battery cell replacements. The analysis did not include the impact of battery replacement activities on the battery rack. The battery cell rack support strategy was revised and a technical evaluation was performed for the seismic qualification of the battery rack during battery cell replacement. The battery cell replacement procedure (M-095-005) will be revised to address the updated technical evaluation and ensure seismic qualification of the battery rack is maintained during maintenance activities. NRC FORM 366 (01-2014) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 01/31/2017 (01-2014) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by LICENSEE EVENT REPORT (LER) internet e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, CONTINUATION SHEET Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 6. LER NUMBER 3. PAGE SEQUENTIAL REV YEAR NUMBER NO. Limerick Generating Station, Unit 1 05000352 2 OF 4 2016 - 002 - 00 | Unit Conditions Prior to the Event Units 1 and 2 were in Operational Condition (OPCON) 1 (Power Operation) at 100% power. There were no structures, systems or components out of service that contributed to this event. Description of the Event On Monday, February 10, 2016, Limerick Units 1 and 2 were operating at 100% power. The Unit 1, Division 1, 1A1 125 VDC safeguard battery (EIIS:EJ) replacement was in progress under a preventive maintenance work order activity. The activity was to replace cells 43 through 51 (9 cells). At 0842 hours the battery (EIIS:BTRY) was declared inoperable to support installation of the temporary seismically qualified battery cart which provides substitute battery cells during maintenance and TS 3.8.2.1 D.C. Sources – Operating, Action “c” was entered. Action “c” required restoration of the inoperable battery within 2 hours. Otherwise, be in Hot Shutdown within the next 12 hours and in Cold Shutdown within the following 24 hours. At 0858 hours, the battery was declared operable and the TS action was exited. The next activity was to replace the 9 cells. At 0900 hours the cell replacement was suspended with 12 cells jumpered out, due to a question regarding the seismic qualification of the battery with temporary cell seismic restraints installed. A technical evaluation had not been approved to authorize the use of the temporary restraints. An Engineering technical evaluation of the battery temporary seismic restraints was subsequently performed. The remaining 1A1 battery cells were replaced using a revised strategy with approved temporary restraints. A subsequent investigation determined that the method for on-line battery cell replacement (developed in the early 1990’s) approved the use of a seismically qualified battery cart to jumper cells during replacement but did not approve the use of the temporary seismic restraints to maintain operability of the battery during cell replacement. A review of work history for the last three years identified that the following Unit 1 batteries were replaced using unapproved seismic restraints to maintain operability and exceeded the TS 3.8.2.1 allowed outage time (AOT): The 1A2 battery was replaced in September 2015. The 1B1 battery was replaced in December 2015. The 1A1 battery was replaced in February 2016. The following Unit 2 battery cell replacement was performed using unapproved seismic restraints to maintain operability and exceeded the TS 3.8.2.1 AOT: The 2A2-29 cell was replaced in July 2015. A review of the operator logs for the last three years identified that the TS 3.8.2.1 D.C. Sources – Operating, Action “c” to restore the inoperable battery within the 2 hour AOT and the “otherwise” Action to be in Hot Shutdown within the next 12 hours were exceeded fifteen times | ML16102A035
LaSalle County Station | Unit 1 | Secondary Containment Inoperable due to Reactor Building Ventilation Damper Failure f | 04-11-2016 | On February 10, 2016, Unit 1 was in Mode 1 at 91 percent powerand Unit2 was in Mode 1 at 100 percent power. At2207 hours CST, itwas reportedthatthe Unit 1 reactorbuilding ventilation exhaustdamper 1VRO5YA failed and began to showdual indication. As a result, the Unit 1 reactorbuilding ventilation exhaustfanstripped off, causing a positive reactorbuilding differential pressure on both units. The damperand secondary containmentwere declared inoperable, and Technical Specification 3.6.4.1 Required Action A.1 was entered on both units to restoresecondarycontainment to operable status within four hours. In addition, Technical Specification 3.6.4.2 RequiredAction A.1 was enteredto isolatethe penetration with one closed ordeactivated automaticvalve within eight hours. The causewas an intermittentfailure of asolenoid on one ofthe two half damper blades on the 1VRO5YA exhaust isolation damper. This led to the exhaustdamperblade half intermittentlychanging its position, which resulted in secondarycontainment pressure going positive. Thesolenoid valves on both halves ofthe 1VRO5YA exhaustdamperwere replaced, and the failed solenoid was sentto a vendorforfailure analysis. NRCFORM366)11-2015) Page 2 of 3 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY0MB: NO.3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimatedburdenperresponsetocomplywiththismandatorycollectionrequest:80hours.Reported lessons leerned ere incorporated into the licensing process and ted back to industry. Send commentsregardingburden estimatetothe FDIA, Pdvacy and InformationCollectionsBranch(1-5 F53), U.S. Nuclear RegulatoryCommission, Washington, DC 20555-0001, orby internet e-mail to 1 , 1111 IntocollectsResource@nrcgov andtotheDeskOtficer OfficeofInformationandRegulatoryAffairs •*“• CONTINUAT’ N SHEE u N s E e O d B to -10 im 20 p 2 o , se (31 e 5 n 0 i - n 0 f 1 o 0 r 4 m ) a , t O io f n fic c e ol o le t ct M io a n na d g o e e m s e n n o t t a d n is d pl B ay ud a ge c t u , r W ren a t s ly hin v g al t i o d n, 0M DC B 2 co 0 n 5 t 0 ro 3 l . n I u t m a b m er, ea t n h s e NRC may not conduct or sponsor, and a person is not required to respond to, the intormation collechon. 1. FACILITYNAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR NUMBER NO. LaSalle County Station, Unit 1 05000373 2016 001 00 - - | A. Condition Priorto Event: Unit(s): 1 /2 Event Date: February 10, 2016 Event Time: 2207 CST Reactor Mode(s): 1 / 1 Mode(s) Name: PowerOperation/PowerOperation Power Level: 91%/i00% B. Description of Event: On February 10, 2016, Unit 1 was in Mode 1 at 91 percent power and Unit 2 was in Mode 1 at 100 percent power. At 2207 hours CST, it was reported thatthe Unit 1 reactor building ventilation (VR) exhaust damper 1VRO5YAfailed and began to show dual indication. As a result, the Unit 1 reactor building ventilation exhaustfans tripped oft, causing a positive reactor building differential pressure on both units. The damperand secondarycontainmentwere declared inoperable, and Technical Specification 3.6.4.1 Required Action A.i was entered on both units to restore secondarycontainmentto operable within four hours. In addition, Technical Specification 3.6.4.2 Required Action A.1 was entered to isolate the penetration with one closed or deactivated automatic valve within eight hours. The loss ofsecondarycontainmentpressure is reportable in accordance with 10 CFR 50.73(a)(2)(v)fC) and 10 CFR 50.73(a)(2)fv)fD) as an event or condition that could have prevented the fulfillment ofthe safetyfunction of structuresor systems needed to control the release of radioactive material and to mitigate the consequencesof an accident. An ENS report was made to the NRC at 0120 EST on February ii, 2016 (EN #51725) pursuantto 10 CFR 50.72(b)(3)(v)(C) and (D). With the Unit 1 VR system shutdown, the 1VRO5YA damperwas cycled open. The damperwentfull open; however, a buzzing sound was heard near its associated solenoid. The solenoidswere inspected and itwas noticed that the buzzing solenoid was also leaking slightlythrough its exhaust port. Within a short period of time it was observedthatthe solenoid intermittently energized and de-energized. When the solenoidwas de-energized the damper indication was dual with one half of damper blade closed. The solenoidswere replaced on both halves ofthe damper blades on 1VRO5YA. Damper 1VRO5YA was declared operable on February 11,2016 at 1027. The Unit 1 VR system was subsequently restarted. The 1VRO5YA damper is a safety-related component associated with secondarycontainment isolation; however, the event was not a Safety System Functional Failure (SSFF). An engineering evaluation concluded that the safetyfunction of the 1VRO5YA damper isto close during an accident condition to ensure the secondary containment safetyfunction can be satisfied. Since the VR system exhaust isolation damper failedclosed during the event, the dampersafetyfunction was met; and therefore, this event is not being counted as a Safety System Functional Failure (SSFF) forthe NRC performance indicator. C. Cause of Event: An apparent cause investigation determinedthe cause was an intermittentfailure of a solenoid on one ofthe two half damper blades on the 1VRO5YA exhaust isolation damper. This led to the exhaust damper blade half intermittently changing its position, which resulted in the pressureof secondary containment going positive. There has not been a failure of anysolenoidvalves on all eight VR dampers in the last 15 years. The solenoids on 1VRO5YA are replaced on everyfourth outage (approximately eight-yearfrequency). Theywere last replaced on May20, 2002 and February 12, 2010. The next scheduled replacement is due in March 2018. This history indicates the solenoid on the 1VRO5YA exhaust damperfailed prematurely. The lastfailure on April 29, 2009 was on Unit 2 exhaust isolation damper 2VRO5YA (dual indication) due to improperadjustment of the speed controlleron the actuator. NRCFORM366A(11-2015) Page 3 of 3 | ML16102A143
Dresden Nuclear Power Station | Unknown Unit | Secondary Containment Differential Pressure Transient 5. EVENT'DATE 6. LEA NUMBER 7. REPORT DATE 8. OTHER FACILITIES INVOLVED FACILITY NAME DOCKET NUMBER MONTH DAY YEAR YEAR I SE N Q U U M E B N E T R IA L I R N E O V . MONTH DAY YEAR Dresden Unit 3 05000249 - FACILITY NAME DOCKET NUMBER 02 09 2016 2016 - 001 00 04 08 16 05000 9. OPERATING MODE 11. THIS REPORT IS SUBMITTED PURSUANT TO THE REQUIREMENTS OF 10 CFR §: (Check all that apply) D D D D 20.2201 (bl 20.2203(a)(3)(il 50.73(a)(2)(ii)(A) 50.73(a)(2)(viii)(A) D D D D 20.2201 (dl 20.2203(a)(3)(iil 50.73(a)(2)(ii)(B) 50.73(a)(2)(viii)(B) 1 D D D D 20.2203(a)(1 l 20.2203(a)(4l so.13(a)(2)(iiil 50.73(a)(2)(ix)(A) D D D D 20.2203(a)(2)(il 50.36(c)(1 )(i)(A) 50.73(a)(2)(iv)(A) 50.73(a)(2)(x) D D D D 10. POWER LEVEL 20.2203(a)(2)(iil 50.36(c)(1 )(ii)(A) 50.73(a)(2)(v)(A) 13.11 (a)(4l D D D D 20.2203(a)(2)(iiil so.3a(c)(2) 50.73(a)(2)(v)(B) 13.11 (a)(5l D 20.2203(a)(2)(iv) D so.4a(a)(3l(iil [8] 50.73(a)(2)(v)(C) D 13.11(a)(1) D D D D 100 20.2203(a)(2)(v) 50.73(a)(2)(i)(A) 50.73(a)(2)(v)(D) 13.11(a)(2)(il D D D D 20.2203(a)(2)(vi) 50.73(a)(2)(i)(B) 50.73(a)(2)(vii) 13.11(a)(2)(iil ::~2 ;;~,,~~~- ··::;?;W'.~ D so.13(a)(2)(il(Cl D OTHER Specify in Abstract below or in NRG Form 366A 12. LICENSEE CONTACT FOR THIS LEA LICENSEE CONTACT !TELEPHONE NUMBER (Include Area Code) Bruce Franzen - Regulatory Assurance Manager 815-416-2800 13. COMPLETE ONE LINE FOR EACH COMPONENT FAILURE DESCRIBED IN THIS REPORT MANU- REPORTABLE MANU- REPORTABLE CAUSE SYSTEM COMPONENT CAUSE SYSTEM COMPONENT FACTURER TO EPIX FACTURER TO EPIX B VA PDC J073 y 14. SUPPLEMENTAL REPQRT EXPECTED 15. EXPECTED MONTH DAY YEAR 0 YES (If yes, complete 15. EXPECTED SUBMISSION DATE) [8J NO SUB D M A IS TE S ION ABSTRACT (Limit to 1400 spaces, i.e., approximately 15 single-spaced typewritten Jines) On 2/9/16 at 19:00 CST, the operating heating boiler shutdown. At 19:15, the Main Control Room (MCR) received alarms for low reactor building (RB) differential pressure (DP). As directed by procedure, Operators verified local gauge readings and equipment configuration. At 21 :42, local gauge readings were averaged at -0.24 inches we which required entry into Tech Spec 3.6.4.1.A due to RB DP being greater than Technical Specification required -0.25 inches we by local average on the refuel floor. At 22:05, U3 RB ventilation was secured, and at 22:07 TS 3.6.4.1.A was exited when RB DP returned below -0.25 inches we. The cause of the event was determined to be a degraded area DP controller that restricted exhaust flow, preventing the system from maintaining RB DP greater than TS allowed value. Corrective actions include calibration of the area DP controller, enhancements to operational response procedures, a review of the associated maintenance strategy, and review for potential component upgrades. NRG FORM 366 (11-2015) Page 2 of 3 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/201 E (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send ~(,.;.,..11nrallt., comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 aI'! . LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, \+ ~IS., CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means I):***'*"' used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR NUMBER NO. Dresden Nuclear Power Station, Unit 2 05000-237 2016 - 001 - 00 NARRATIVE PLANT AND SYSTEM IDENTIFICATION Dresden Nuclear Power Station (DNPS), Unit 2, is a General Electric Company Boiling Water Reactor with a licensed maximum power level of 2957 megawatts thermal. The Energy Industry Identification System codes used in the text are identified as [XX]. A. Plant Conditions Prior to Event: | 04-08-2016 | On 2/9/16 at 19:00 CST, the operating heating boiler shutdown. At 19:15, the Main Control Room (MCR) received alarms for low reactor building (RB) differential pressure (DP). As directed by procedure, Operators verified local gauge readings and equipment configuration. At 21 :42, local gauge readings were averaged at -0.24 inches we which required entry into Tech Spec 3.6.4.1.A due to RB DP being greater than Technical Specification required -0.25 inches we by local average on the refuel floor. At 22:05, U3 RB ventilation was secured, and at 22:07 TS 3.6.4.1.A was exited when RB DP returned below -0.25 inches we. The cause of the event was determined to be a degraded area DP controller that restricted exhaust flow, preventing the system from maintaining RB DP greater than TS allowed value. Corrective actions include calibration of the area DP controller, enhancements to operational response procedures, a review of the associated maintenance strategy, and review for potential component upgrades. NRG FORM 366 (11-2015) Page 2 of 3 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/201 E (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send ~(,.;.,..11nrallt., comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 aI'! . LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, \+ ~IS., CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means I):***'*"' used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR NUMBER NO. Dresden Nuclear Power Station, Unit 2 05000-237 2016 - 001 - 00 | PLANT AND SYSTEM IDENTIFICATION Dresden Nuclear Power Station (DNPS), Unit 2, is a General Electric Company Boiling Water Reactor with a licensed maximum power level of 2957 megawatts thermal. The Energy Industry Identification System codes used in the text are identified as [XX]. A. Plant Conditions Prior to Event: Unit: 02 Event Date: 02/09/2016 Event Time: 1900 CST Reactor Mode: 1 Mode Name: Power Operation Power Level: 100 percent B. Description of Event: On 2/9/16 at 19:00, the operating heating boiler [LV] shutdown. At 19:15, the Main Control Room (MCR) received alarms indicating that Reactor Building (RB) [NG] DP was below -0.3" wc. An Equipment Operator (EO) was dispatched to take local RB DP readings on the Refuel Floor. Local readings were averaged to be -0.35" we. Operations verified that all Secondary Containment interlock doors, RB blowout panels and reactor building ventilation [VA] (RBV) exhaust hatches were in the proper configuration. Following the loss of the heating boiler, Operations entered the associated response procedure. This procedure directed field operators to block open all doors of both the U2 and U3 RBV supply plenums to prevent freezing of the ventilation filters and heating coils within the plenums. At 21 :42, another step change in RB DP was noticed by Operations. Main Control Room RB DP indication degraded from -0.25" wc to -0.12" we. An EO was dispatched to obtain local readings on the Refuel Floor. Local readings were averaged at -0.24" we which required entry into Tech Spec 3.6.4.1.A due to RB DP being greater than Tech Spec required -0.25" wc by local average on the refuel floor. At 22:05, U3 RBV was secured, and at 22:07 Tech Spec 3.6.4.1.A was exited when RB DP returned to below -0.25" we. An 8 hour non-emergency notification was made via Emergency Notification System #51721 in accordance with 1O CFR 50.72(b)(3)(v)(C) for the loss of Secondary Containment. | ML16104A031
Brunswick Steam Electric Plant (BSEP) | Unit 1 | Electrical Bus Fault Results in Lockout of Startup Auxiliary Transformer and Loss of Offsite Power | 00-06-2016 | On February 7, 2016, at 1312 Eastern Standard Time (EST), Unit 1 was in Mode 1 (i.e., Run) at 88 percent of rated power in end-of-cycle coastdown. At that time, an electrical fault occurred on a balance of plant 4160-volt bus, resulting in a lockout of the Startup Auxiliary Transformer (SAT) and a loss of both Reactor Recirculation pumps. Licensed personnel inserted a manual scram per procedure. Emergency Diesel Generators supplied emergency electrical busses until offsite power was restored at 1628 EST. The loss of power and reactor water level changes resulted in automatic closures of various Primary Containment Isolation Valves (PCIVs). The electrical fault resulted in an electrical explosion; therefore, an Alert was declared at 1326 EDT. The immediate cause of this event was a fault in a non-segregated electrical bus connected to the SAT. The root causes were insufficient detail in applicable maintenance instructions for inspecting the non-segregated bus housing and inadequate instructions for terminating electrical cables in a circuit breaker cubicle. Corrective actions include repairing equipment damaged by the electrical fault and revising the procedures and work instructions. NRC FORM.366 (11-2015) Page2 of 5 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant (BSEP) 05000-325 YEAR NUMBER NO. Unit 1 2016 - 001 000 | Energy Industry Identification System (EllS) codes are identified in the text as [XX]. Background Initial conditions On February 7, 2016, at 1312 Eastern Standard Time (EST), Unit 1 was in Mode 1 (i.e., Run) at a power level of 88 percent of rated thermal power in end-of-cycle coastdown. No out-of-service equipment contributed to, or affected the course of, this event. Reportability Criteria This event is being reported in accordance with 1O CFR 50.73(a)(2)(iv)(A) because it involved actuations of systems listed in 1O CFR 50.73(a)(2)(iv)(B). Specific actuations included: • The Reactor Protection System (RPS) [JE] was manually actuated due to loss of both Reactor Recirculation [AD] system pumps. • Several Primary Containment Isolation Valves (PCIVs) [JM] automatically closed per design in response to either loss of control logic power or reactor water level changes that resulted from the reactor scram. • Emergency Diesel Generators (EDGs) [EK] started and provided power to emergency electrical busses E1 and E2 [EB] in response to a loss of offsite power (LOOP). ' • The High Pressure Coolant Injection (HPCI) [BJ] system was manually started to control reactor pressure following the scram. • The Reactor Core Isolation Cooling (RCIC) [BN] system was manually started to control reactor water level following the scram. o The NRC was notified of the event, including the emergency declaration, per 1 CFR 50.72(a)(1 )(i), 10 CFR 50.72(b)(2)(iv)(B), and 10 CFR 50.72(b)(3)(iv)(A) via Event Notification (EN) number 51715 at 13:46 EST on February 7, 2016. Event Description On February 7, 2016, at 1312 EST, BSEP Unit 1 was in Mode 1 during end-of-cycle coastdown. Two arc flashes occurred in a 4160-volt electrical system which resulted in two phases of the system faulting to ground, which also constituted a phase-to-phase fault. The high differential current actuated the lockout on the Unit 1 Startup Auxiliary Transformer (SAT) [EA], which started all four emergency diesel generators. The loss of power to equipment fed from the SAT resulted in shutdown of both Reactor Recirculation system pumps. With both pumps not operating, station procedures require licensed personnel to insert a manual scram. This was performed immediately, and all control rods ,[AA] fully inserted into the core per design. The manual scram automatically shut down the main turbine [TA] and main generator [EL] per design. With the main generator offline, the power circuit breakers for the Unit Auxiliary Transformer (UAT) [EA] NRG FORM 366A (11-2015) Page 3 of 5 | ML16104A391
Clinton Power Station | Unit 1 | Trip of Fuel Building Ventilation Exhaust Fan Due to Moisture Formation Resulting In the Loss of Secondary Containment Vacuum | 04-13-2016 | On 02/13/2016 at 0206 (CST) the plant was at 99 percent reactor power when Fuel Building Exhaust Fan "A" (1VF04CA) tripped due to indicated high Secondary Containment (SC) vacuum during routine venting of the drywall per plant procedures. Following the fan trip, SC vacuum degraded, eventually exceeding the Technical Specification (TS) limit of 0.25 inch vacuum water gauge. The TS Limiting Condition for Operation (LCO) 3.6.4.1 Required Action A.1 and an Emergency Operating Procedure were entered. Plant Operations subsequently started the Standby Gas Treatment System (VG) and restored Secondary Containment within TS limits. An investigation determined that ice formed in the sensing line causing an inaccurate Secondary Containment vacuum reading on the indication and control loop for 1VF04CA. This caused 1VF04CA to trip which in turn led to a loss of Secondary Containment vacuum. A cause a.valuation established that prior instrument sensing line designs did not recognize the potential to trap water in the sensing line to the Secondary Containment pressure instrumentation. Corrective actions will include completing an engineering change to install an alternate Fuel Building Ventilation (VF) system sensing line design to prevent moisture accumulation line to ensure accurate indication and control of Secondary Containment pressure. This event is reportable under 10 CFR 50.73(a)(2)(v)(C). NRG FORM 366 (11-2015) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 01/31/2017 (02-2014) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Prtvacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by LICENSEE EVENT REPORT (LER) internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, CONTINUATION SHEET Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required.to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 6. LER NUMBER' 3. PAGE I SEQUENTIAL ,. REV YEAR NUMBER NO. Clinton Power Station, Unit 1 05000461 2 OF 4 2016 002 00 | PLANT AND SYSTEM IDENTIFICATION General Electric-Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified i~,the text as [XX] EVENT IDENTIFICATION Trip of Fuel Building Ventilation Exhaust Fan Due to Moisture Formation Resulting In the Loss of Secondary Containment Vacuum A. Plant Operating Conditions before the Event Unit: 1 Event Date: 2/13/16 Event Time: 0206 Mode: 1 Mode Name: Power Operation Reactor Power: 99 percent B. DESCRIPTION OF EVENT On February 13, 2016 at 0206, during routine venting of the drywell, the main control room (MCR) received a fuel building ventilation (VF) system alarm. At 0208 Fuel Building exhaust fan 1VF04CA tripped and 'B' exhaust fan 1VF04CB auto started, however, secondary containment vacuum continued to degrade. Secondary Containment was declared inoperable when the vacuum degraded to less than 0.25 inch water gauge 0JVG). TS LCO 3.6.4.1 "Secondary Containment", Required Action A.1 was entered. When Secondary Containment differential pressure value became greater than O inch of vacuum WG with 1V F04CB fan operating, procedure EOP-8, Secondary Containment Control, was entered. At 0212, Secondary Containment vacuum was at 0.15 inch WG with 1V F04CB running and 1V F04CA in standby. With Secondary Containment vacuum still outside TS limits, the MGR secured the VF exhaust fans at 0255 per CPS 3404.01, Fuel Building HVAC (VF). At 0256 Standby Gas Treatment System (VG) Train A was started per CPS 3319.01, Standby Gas Treatment (VG). Secondary Containment vacuum was restored to greater than 0.25 inch WG at 0257 and Secondary Containment was declared operable. TS LCO 3.6.4.1 Required Action A.1 and EOP-8 were exited. A troubleshooting team determined that ice had formed resulting in a blockage in the low side sensing line to the environment as the most probable cause of the event. Other locations for sensing line clogging were also investigated. After disassembling, thawing, and cleaning the intake tubing, technicians performed a blowdown of the instrumentation tubing. Following the blowdown, Operations successfully restarted VF exhaust fan 1V F04CA. Secondary Containment vacuum was restored to normal. | ML16106A305
SEQUENTIAL REV | Unknown Unit | Secondary Containment Inoperable Due to Interlock Doors Open 5. EVENTDATE 6. LER NUMBER 7. REPORTDATE J 8. OTHER FACILITIES INVOLVED MONTH DAY YEAR YEAR SEQUENTiAL MONTH DAY YEAR F N A / C A ILITYNAME N D /A OCKETNUMBER 02 17 2016 2016 - 001 - 00 04 18 2016 N FA / C A ILITYNAME N/ D A OCKETNUMBER 9. OPERATING MODE 11.THIS REPORTIS SUBMITTED PURSUANTTOTHE REQUIREMENTSOF 10 CFR§: (Checkallthatapply) El 20.2201(b) El 20.2203(a)(3)(i) El 50.73(a)(2)ci)(A) El 50.73(a)(2)(viii)(A) El 20.2201(d) El 20.2203(a)(3)(ii) El 50.73(a)(2)(ii)(B) El 50.73(a)(2)(viii)(B) El 20.2203(a)(1) El 20.2203(a)(4) C] 50.73(a)(2)(iii) El 50.73(a)(2)(ix)(A) El 20.2203(a)(2)(i) El 50.36(c)f1)(i)(A) El 50.73(a)(2)(iv)(A) C] 50.73(a)(2)(x) 10. POWER LEVEL C] 20.2203(a)(2)(ii) El 50.36(c)(i)fii)(A) C] 50.73(a)(2)(v)(A) El 73.71(a)(4) El 20.2203(a)(2)(iH) El 5D.36(c)(2) El 50.73(a)(2)(v)(B) [1 73.71fa)(5) El 20.2203(a)(2)(iv) C] 50.46fa)f3)(ii) 50.73fa)(2)(v)(C) C] 73.77(a)(i) 100 El 20.2203fa)f2)fv) El 50.73fa)(2)fi)(A) 50.73(a)f2)fv)f0) El 73.77fa)(2)fi) El 20.2203(a)(2)(vi) El 50.73(a)(2)(i)(B) El 50.73(a)(2)(vii) El 73.77(a)(2)(h) C] 50.73(a)(2)(i)(C) El OTHER SpecityinAbstractbeloworinNRCForm366A 12. LICENSEECONTACT FOR THIS LER LICENSEECONTACT TELEPHONENUMBER (IncludeAreaCode) Joe Fiesel, Maintenance Director (815) 415-2500 13. COMPLETE ONELINE FOR EACH COMPONENT FAILUREDESCRIBEDINTHIS REPORT CAUSE SYSTEM COMPONENT FACTURER REPORTABLE CAUSE SYSTEM COMPONENT FACTURER REPORTABLE X NG IMEC SDC Y 14. SUPPLEMENTALREPORTEXPECTED 15. EXPECTED MONTH DAY YEAR El YES (Ifyes, complete 75. EXPECTEDSUBMISSIONDATE) NO SUBMISSION DATE ABSTRACT (Limitto 1400spaces,i.e.,approximately15single-spacedtypewrittenlines) On February 17, 2016, Unit 2was in Mode 1 at 100 percent power and Unit 1 was in Mode 5for refueling outage LiRi6with nofuel movements oroperations withthe potential to drain the reactorvessel (OPDRV) in progress. At 1035 hours CST, both air-lock doors ofthe Unit2 ChemistryLab corridor/ Unit 2 Reactor Building interlockwere open atthe sametime forapproximatelyfive seconds. While both interlock doorswere open, Technical Specification (TS) Surveillance Requirement(SR) 3.6.4.1.2 to verifyone secondarycontainment access door in each access opening is closedwas not metfor Unit2. Secondary containment was declared inoperableforthe period oftimethatboth interlockdoors were open. TS 3.6.4.1 RequiredAction (RA) A.1 to restore secondary containmentto OPERABLE status within fourhours was entered and exited. The cause was failure ofthe relays on the doorcontrollercircuit card. The controllercircuit card was replaced, which restoredthe interlock functionality. Corrective actions include determining the cause ofvendorquality issues with the controllercircuit card relays and procurement of a more reliable controllercircuit card following the identification of the cause of the relayfailuresfrom vendoranalysis. NRCFORM366(11.2015) ___________ Page 2 of 4 NRC FORM 366A U.S. NUCLEARbULAToRYCOMMISSION APPROVED BY0MB: L.-1150-0104 EXPIRES: 10/3112018 (11-2015) Estimatedburdenperresponsetocomplywiththismandstorycollectionrequest:80hours.Reported lessons teamed are incorporated into the licensing process and led back to industry. Send commentsregardingburden estimate tothe FOIA, Privacy and Information Collections Branch (T-5 LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear RegulatoryCommission, Washington, DC 20555-0001, orby internete-mail to Ui lntocollects.Resourcethnrc.gov,andtotheDeskOfficer,OfficeatInformationandRegulatoryAffairs, ,- CONT NEOB-10202, (3150-0104),OfficeofManagementandBudget, Washington, DC 20503. Itameans usedtoimpose aninformation collectiondoesnotdisplay acurrentlyvalid0MBcontrol number,the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection, 1. FACILITY NAME 2. DOCKETNUMBER 3. LER NUMBER SEQUENTIAL REV YEAR LaSalle County Station, Unit 2 05000374 NUMBER NO. 2016 001 00 - - NARRATIVE A. Condition Priorto Event: | 04-18-2016 | On February 17, 2016, Unit 2was in Mode 1 at 100 percent power and Unit 1 was in Mode 5for refueling outage LiRi6with nofuel movements oroperations withthe potential to drain the reactorvessel (OPDRV) in progress. At 1035 hours CST, both air-lock doors ofthe Unit2 ChemistryLab corridor/ Unit 2 Reactor Building interlockwere open atthe sametime forapproximatelyfive seconds. While both interlock doorswere open, Technical Specification (TS) Surveillance Requirement(SR) 3.6.4.1.2 to verifyone secondarycontainment access door in each access opening is closedwas not metfor Unit2. Secondary containment was declared inoperableforthe period oftimethatboth interlockdoors were open. TS 3.6.4.1 RequiredAction (RA) A.1 to restore secondary containmentto OPERABLE status within fourhours was entered and exited. The cause was failure ofthe relays on the doorcontrollercircuit card. The controllercircuit card was replaced, which restoredthe interlock functionality. Corrective actions include determining the cause ofvendorquality issues with the controllercircuit card relays and procurement of a more reliable controllercircuit card following the identification of the cause of the relayfailuresfrom vendoranalysis. NRCFORM366(11.2015) ___________ Page 2 of 4 NRC FORM 366A U.S. NUCLEARbULAToRYCOMMISSION APPROVED BY0MB: L.-1150-0104 EXPIRES: 10/3112018 (11-2015) Estimatedburdenperresponsetocomplywiththismandstorycollectionrequest:80hours.Reported lessons teamed are incorporated into the licensing process and led back to industry. Send commentsregardingburden estimate tothe FOIA, Privacy and Information Collections Branch (T-5 LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear RegulatoryCommission, Washington, DC 20555-0001, orby internete-mail to Ui lntocollects.Resourcethnrc.gov,andtotheDeskOfficer,OfficeatInformationandRegulatoryAffairs, ,- CONT NEOB-10202, (3150-0104),OfficeofManagementandBudget, Washington, DC 20503. Itameans usedtoimpose aninformation collectiondoesnotdisplay acurrentlyvalid0MBcontrol number,the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection, 1. FACILITY NAME 2. DOCKETNUMBER 3. LER NUMBER SEQUENTIAL REV YEAR LaSalle County Station, Unit 2 05000374 NUMBER NO. 2016 001 00 - - | A. Condition Priorto Event: Unit(s): 1 /2 Event Date: February 17, 2016 EventTime: 1035 CST Reactor Mode(s): 5 / 1 Mode(s) Name: Refueling Mode/Power Operation Power Level: 0 percent/i00 percent B. Description of Event: On February 17, 2016, Unit 2 was in Mode 1 at 100 percent powerand Unit 1 was in Mode 5 for refueling outage L1R16 with no fuel movements, core alterations, orOPDRV in progress. At approximately 1035 hours CST, Operating Department received a reportthatan employee entered a secondary containment interlock and identified that both doors of the Unit 2 Chemistry Lab corridor/ Reactor Building interlock (door number247 and door number248) opened simultaneously. The employee immediately secured both doors in the interlock and notified the Main Control Room Supervisor. Both doors in the interlockwere open forapproximatelyfive seconds. With both doors open, TS SR 3.6.4.1.2 was not met for Unit 2. This rendered secondary containment inoperable in accordance with TS 3.6.4.1. Reactor Building differential pressure, as observed in the Main Control Room, remained less than -0.25 inches vacuum water gauge (w.g.) at all times. Administrative controls were put in place to ensure the doors remained closed pending repairs to the interlock. An emergency notification system (ENS) reportwas madetothe NRC at 1705 EST on February 17, 2016 (EN 51741) pursuant to 10 CFR 50.72(b)(3)(v)(C) and (D). This occurrence is reportable in accordance with 10 CFR 50.73(a)(2)(v)(C) and (D) as an event orcondition thatcould have prevented the fulfillment ofthe safetyfunction of the structures orsystems that are needed to control the release of radioactive material and to mitigate the consequences of an accident. A technical evaluation has determinedthis event did not meet the NEI 99-02 definition of a Safety System Functional Failure (SSFF). C. Cause of Event: The cause ofthe eventwas the failure of the relays ofthe UR2-4 controllercircuitcard in the interlock door. The exactcause ofthe relayfailures is currently unknown. However, corrective actions have been createdto identifythe cause and make changes to the card to eliminate the less than desired circuit card service life. D. SafetyAnalysis: The safetysignificance of this eventwas minimal. The Reactor Building-to-outside differential pressure remained negative throughout the period thatthe secondarycontainmentwas inoperable. This event did not result in the reactorenclosure differential pressure dropping belowthe design bases set point. Both the innerand outerdoors were promptlyclosed by station personnel, which ended the event. This eventdid not involve any kind of dooror airlock material condition preventing doorclosure. Additionally, both the innerand outer doors were closed by normal expected means and were capable of remaining closed as designed. The secondarycontainmentwas inoperableforapproximatelyfive seconds, which was significantly less than the four-hour Completion Time to restore the secondary containmentto operable status allowed by TS 3.6.4.1 Required Action Al. The function of the secondary containmentisto contain, dilute, and hold up fission productsthat may leakfromthe primary containmentfollowing a Design Basis Accident (DBA). Engineering Change (EC) 396711 was performedto showthat the event had no impact on the safetyfunction associated with secondarycontainment. The time that both doors were simultaneouslyopened was approximatelyfive seconds, which is bounded bythe technical evaluation. This event did not result in the reactorenclosure differential pressure dropping belowthe design bases set point of -0.25 inches w.g. Both the inner and outerdoors were promptly closed bystation personnel, which endedthe event. This event did not involve any kind of door orairlock material condition preventing doorclosure. Additionally, both the innerand outerdoors were closed by normal expected means and were capable of remaining closed as designed. NRCFORM366A(11-2015) Page 3 of 4 | ML16109A215
PAGE | Unknown Unit | Secondary Containment Declared Inoperable Due to an Airlock Doors Open Due to Random Occurrence | 10-31-2018 | On February 22, 2016 at approximately 1345, a contract employee leaving the Unit 1 Reactor Building swiped his keycard and received a green light to enter the airlock. Upon opening the airlock door, he discovered two Susquehanna employees entering the airlock from the opposite side. The statement from the Susquehanna employees indicates that the green light to enter the airlock was observed. They were entering the airlock to traverse to the Unit 1 Reactor Building when the door on the Unit 1 Reactor Building side opened. After this incident, the airlock indication was tested and all equipment checked satisfactorily. With both airlock doors open simultaneously, Secondary Containment was briefly inoperable due to failure to meet Surveillance Requirement (SR) 3.6.4.1.3. This event was reported in accordance with 10 CFR 50. 72(b)(3)(v)(C) as a condition that could have prevented fulfillment of a safety function (EN 51750). The condition also requires a Licensee Event Report (LER) in accordance with 10 CFR 50. 73(a)(2)(v)(C). The cause of the event was determined to be random occurrence. There were no corrective actions required to address the cause. Although human performance issues were not involved, actions have been taken to improve human performance associated with airlock door use. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366 (11-2015) Page 2 of 3 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T·5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555·0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITYNAME 2. DOCKET NUMBER 3. LER NUMBER I I YEAR SEQUENTIAL REV Susquehanna Steam Electric Station, Unit 1 NUMBER NO. 05000387 2016 -001 -00 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, 92 percent Rated Thermal Power Unit 2 - Mode 1, 10 0 percent Rated Thermal Power There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. EVENT DESCRIPTION On February 22, 2016 at approximately 1345, a contract employee leaving the Unit 1 Reactor Building [EllS System Identifier: NG] swiped his keycard and received a green light [EllS Component Identifier: IL] to enter the airlock [EllS Component Identifier: AL]. Upon opening the airlock door [EllS Component Identifier: DR], he discovered two Susquehanna employees entering the airlock from the opposite side. The statement from the Susquehanna employees indicates that the green light to enter the airlock was observed. They were entering the airlock to traverse to the Unit 1 Reactor Building when the door on the Unit 1 Reactor Building side opened. After this incident, the airlock indication was tested and all equipment checked satisfactorily. With both airlock doors open simultaneously, Secondary Containment was briefly inoperable due to failure to meet Surveillance Requirement (SR) 3.6.4.1.3. This event was reported in accordance with 10 CFR 50.72(b)(3)(v)(C) as a condition that could have prevented fulfillment of a safety function (EN 51750). The condition also requires a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(v)(C). CAUSE OF EVENT The direct cause has been determined to be random occurrence. ANALYSIS/SAFETY SIGNIFICANCE The actual consequence was a brief entry into Technical Specification 3.6.4.1 and an eight hour notification of the event to the Nuclear Regulatory Commission (NRC). An engineering evaluation was performed and concluded that secondary containment could have performed its safety function of isolating as assumed in the accident analysis and also of re-establishing 0.25 inches vacuum (drawdown) within the assumed accident analysis time (1 0 minutes). Therefore, the subject event did not cause a loss of safety function. This event will not be counted as a safety system functional failure (SSFF) for the NRC performance indicator based on the engineering analysis that shows there was no loss of ability to fulfill the safety function. NRC FORM 366 (11-2015) Page 3 of 3 | ML16109A238
Prairie Island Nuclear Generating Plant 05000 282 I 1 OF4 | Unknown Unit | Unanalyzed Condition - Procedures Credited by Appendix R Calculations not in Place | 01-07-2016 | On 1/7/2016, Prairie Island Nuclear Generating Plant (PINGP) reviewed corrective actions associated with the transition to National Fire Protection Association "Performance-Based Standard for Fire Protection for Light Water Reactor Electric Generating Plants" (NFPA 805). PINGP discovered no cold shutdown repair procedure existed to restore power to train B reactor coolant system (RCS) vent valves to reduce RCS pressure in event of fire in Fire Area (FA) 59 (Auxiliary Building Mezzanine Floor Unit 1) and FA 74 (Auxiliary Building Mezzanine Floor Unit 2). The PINGP Appendix R safe shutdown analysis (SSA) credits such actions for train 8 RCS vent valves for a fire in these areas. PINGP established compensatory measures for affected equipment and, with automatic detection and suppression capability, these measures ensured protection of potentially affected equipment. The health and safety of the public was not at risk. PINGP submitted Event Notification (EN) 51642 on 1/7/2016 as this event is reportable pursuant to 10 CFR 50.72(b)(3)(ii)(B) as an unanalyzed condition that significantly degrades plant safety. On 04/14/2005, a revision of the SSA was approved that credited a cold shutdown repair as a compliance strategy for FA 59 and 74, but no repair procedure existed in the event of a fire in FA 59 nor FA 74. On 1/11/2016, F5 Appendix D "Impact of Fire Outside Control/Relay Room" was issued and include::; cold shutdown repair procedures for Train 8 RCS vent valves. Lack of technical rigor to ensure procedure F5 Appendix D included actions required by the SSA is the identified cause. NRC FORM 366 (11-2015) 1 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported /"""" lessons learned are incorporated into the licensing process and fed back to industry. Send !:~:"~ comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 \~) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. L.ER NUMBER I I YEAR SEQUENTIAL REV Prairie Island 05000-282 NUMBER NO. 2016 • 003 -00 | Event Description On 1/7/2016, Prairie Island Nuclear Generating Plant (PINGP) reviewed corrective actions associated with the transition to National Fire Protection Association "Performance-Based Standard for Fire Protection for Light Water Reactor Electric Generating Plants" (NFPA 805) and discovered no cold shutdown repair procedure existed for train B RCS vent valves to reduce reactor coolant system (RCS) (EllS System Code AB) pressure in event of a fire in Fire Area (FA) 59 (Auxiliary Building Mezzanine Floor Unit 1) and FA 74 (Auxiliary Building Mezzanine Floor Unit 2). The PINGP Appendix R safe shutdown analysis (SSA) credits a cold shutdown repair procedure for train B RCS vent valves for a fire in these areas. This event is reportable pursuant to 10 CFR 50.73(a)(2)(ii){B) as an unanalyzed condition that significantly degrades plant safety. PINGP submitted Event Notification 51642 on 1/7/2016. PINGP established compensatory measures for affected areas: hourly fire watches, briefings of the operating crews and fire brigades on the impact of a fire, protecting fire detection zones, walkdowns to verify transient combustible materials were controlled according to plant procedures. Along with automatic fire detection and suppression capability, these measures ensured protection of potentially affected equipment. On 04/14/2005, a revision of the SSA was approved that credited a cold shutdown repair for train B RCS vent valves as a compliance strategy for FA 59 and 74, but no such repair procedure existed. On 4/21/2006, PINGP discovered during a self assessment that no cold shutdown repair procedure existed for train B RCS vent valves in event of fire in FA 59. No EN was submitted for this discovery in 2006. A condition evaluation performed on 7/7/2006 determined "repair action is not credited until well into the shutdown scenario, the means (equipment) to perform the repair are readily available, and a similar repair is already proceduralized, the lack of a formal repair procedure in this instance isn't considered to significantly impact the ability to safely shutdown the plant for a fire in Fire Area 59." The cause of the lack of the repair procedure is lack of technical rigor to ensure procedure F5 Appendix D "Impact of Fire Outside Control/Relay Room" included instructions to restore power to train B RCS vent valves in event of fire in FA 59 and FA 74 as credited in the SSA. On 1/11/2016, F5 Appendix D, Revision 36, was issued and includes cold shutdown repair procedures for Train B RCS vent valves. Event Analysis The SSA describes that the reactor coolant vent system is provided to exhaust non-condensable gases from the reactor coolant system that could inhibit natural Circulation core cooling. The vent path from the reactor vessel head and the vent path from the pressurizer each contain two normally closed, independently-powered valves in parallel and connect to a common header that discharges either to the containment atmosphere or to the Pressurizer Relief Tank (PRT). The head vent system solenoid valves are desired closed to prevent a flow diversion path from the RCS during hot standby. They may be used to vent non-condensable gases or as a letdown path for boration to achieve cold shutdown boron concentration. The RCS head vent lines are designed for RCS pressure to the second isolation valve; therefore, this flow path is not a high/low pressure interface concern. Thus, SV-37035 through SV-37040 and SV-37091 through SV-37096 are required components. The valves used to vent the RCS through train B are SV-37036, 1 RCS Vent Sys Przr Vent Trn B SV, and SV-37040, 1 RCS Vent Sys to Cntmt Trn B SV, for Unit 1 and SV-37092, 2 RCS Vent Sys Przr Vent Trn B SV, and SV-37096, 2 NRC FORM 366 (11-2015) 2 | ML16109A321
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Sticking DC Pilot in Solenoid Valve Cluster Assembly Results in Slow MSIV Closures | 04-25-2016 | On January 23, 2016, James A. FitzPatrick Nuclear Power Plant (JAF) initiated a manual Scram in response to lowering screenwell water level due to frazil ice blockage, and subsequently closed the Main Steam Isolation Valves (MSIV). A post Scram review identified that MSIV 29AOV-86B closed slowly. On January 26, 2016, testing per ST-1B identified that MSIV 29AOV-86C closed slowly. In both cases, the inboard MSIVs performed satisfactorily. Troubleshooting identified that the problem originated in the solenoid valve cluster assemblies (SVCA) and they were replaced and tested successfully. A failure analysis was performed by Exelon PowerLabs on the SVCAs. On February 25, 2016, the Exelon PowerLabs analysis concluded that the DC pilot valves, 29SOV-86B3 and 29SOV-86C3, exhibited slow vent times. Additional corrective actions include changing the preventative maintenance frequency from 8 years to 6 years and initiating further investigation through the component’s vendor. Two MSIVs exceeded the closing time of Technical Specification Surveillance Requirement (SR) 3.6.1.3.6. This condition caused two independent channels of a system used to control the release of radioactive material to become inoperable; reportable per 10 CFR 50.73(a)(2)(vii). NRC FORM 366 (11-2015) Page 2 of 4 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 – 333 NUMBER N0. 2016 – 002 – 00 | Background James A. FitzPatrick Nuclear Power Plant (JAF) has four main steam lines [EIIS identifier: SB] between the reactor and the main turbine [TA]. These lines are designed to isolate in the event of design basis accidents. In the event of a main steam line break, the isolation prevents further radiological release. In the event of a loss of coolant (LOCA) accident, they isolate to maintain coolant inside of containment. Two isolation valves are provided in series in a horizontal run of each main steam line, as close as practical to the primary containment. One inside (inboard) and the other outside (outboard) together form part of the primary containment barrier for Reactor Coolant System breaks inside the containment and part of the Reactor Coolant Pressure Boundary for main steam line breaks outside the primary containment. The closure time of the main steam isolation valves (MSIVs) is a significant variable from a radiological standpoint. The MSIVs are required to close within 3 to 5 seconds after signal generation. The closure speed is designed to be slower than 3 seconds in order to lessen the pressure transient caused by an inadvertent simultaneous closure of all steam lines. The closure speed is designed to be faster than 5 second to minimize the release of fission products to the environment and retain reactor coolant. Each MSIV is controlled by a solenoid valve cluster assembly (SVCA). There are three solenoid valves within the SVCA; AC Pilot solenoid valve, AC Test solenoid valve and a DC pilot solenoid valve. These three solenoids port air to and from other control valves. The normally energized AC pilot valve and DC pilot valve must move to the de-energized position to change the position of the 2 and 4 way valves which closes the MSIV. When both solenoids are de-energized, the below piston operator space is vented. Simultaneously, the above piston operator space is pressurized, thus assisting the spring in closing the MSIV. This licensee event report (LER) addresses a slow closure response for outboard MSIV 29AOV-86B and 29AOV-86C due to their DC pilot solenoid valves 29SOV-86B3 and 29SOV-86C3. Event Description On January 23, 2016, control room Operators inserted a manual Scram due to lowering intake levels resulting from frazil ice conditions in Lake Ontario. As part of the plant shutdown the MSIVs were closed. The closing time for the "B" outboard MSIV 29AOV-86B, was slow by as much as 9 seconds after the other valves indicated closed. The SVCA and 4-way valve were replaced and 29AOV-86B then stroked satisfactorily. On January 27, 2016, the MSIV fast closure test ST-1B was performed on all MSIVs. MSIV 29AOV-86C closed in 6.9 seconds and all other MSIVs tested satisfactorily. The SVCA and 4-way valve were replaced and 29AOV-86C then stroked satisfactorily. | ML16116A245
Braidwood Station | Unit 1 | Auxiliary Feedwater Diesel Intake Design Deficiency Related to Turbine Building High Energy Line Break Resulted in an Unanalyzed Condition Due to Insufficient Validation of Vendor Analysis Inputs | 04-28-2016 | On March 4, 2016, during the NRC Component Design Basis Inspection, a concern was raised regarding why it was acceptable for the diesel driven auxiliary feedwater (AF) pump engine combustion air intake to be located in the turbine building, a non-safety related structure. On March 6, 2016, the additional evaluations that were completed determined that the existing configuration did not adequately support diesel engine operation with high energy line break (HELB) conditions in the turbine building, and at 2000 hours, Operations entered Technical Specification Limiting Condition for Operation 3.7.5, "Auxiliary Feedwater (AF) System," Condition A, "One AF train inoperable," for one train (B-train) of AF inoperable for both Units 1 and 2. The AF trains were declared operable following a corrective action to install a temporary configuration change to provide engine combustion air intake from the auxiliary building. The cause of the event was insufficient validation of vendor analysis inputs in 1993 while reviewing the AF diesel engine's ability to function during a turbine building HELB event. The corrective actions planned are to develop and install a permanent modification to re-route the AF diesel engine intakes for Unit 1 and 2. NRG FORM 366 (11-2015) Page 2 of 4 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555·0001, or by internet e-mail to LICENSEE EVENT REPORT (LEA) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR NUMBER NO. Braidwood Station, Unit 1 05000456 2016 - 001 - 00 | A. Plant Operating Conditions Before the Event: Event Date: March 4, 2016 Unit: 1 Mode: 1 Reactor Power: 100 percent Unit: 2 Mode: 1 Reactor Power: 100 percent Unit 1 Reactor Coolant System (RCS) [AB]: Normal operating temperature and pressure Unit 2 Reactor Coolant System: Normal operating temperature and pressure No structures, systems or components were inoperable at the start of this event that contributed to the event. B. Description of Event: On March 4, 2016, during the NRC Component Design Basis Inspection, a concern was raised regarding why it was acceptable for the diesel-driven auxiliary feedwater (AF) [BAJ pump engine combustion air intake to be located in the turbine building, a non-safety related structure. Combustion air intake draws air from the turbine building via an intake pipe that enters the safety-related auxiliary building to the AF diesel-driven pump room. On March 6, 2016, during the review of documentation related to the combustion air intake, it was identified that the existing configuration did not adequately support diesel engine operation with high energy line break (HELB) environmental conditions in the turbine building. Prior evaluations did not fully account for the combustion air being a steam-air mixture in a post-HELB environment that reduces the available air density during the event. On March 6, 2016 at 2000 hours, Operations entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.5, "Auxiliary Feedwater (AF) System," Condition A, "One AF train inoperable," for one train (B-train) of AF inoperable, for both Units 1 and 2. NRC Event Notification (ENS) 51771 was made on March 7, 2016 at 0100 CST. A temporary configuration change was implemented to provide engine combustion air intake from the auxiliary building. The change allowed air from the AF diesel-driven pump rooms to supply the Unit 1 and Unit 2 AF diesel engines and a wire mesh screen cap was installed to prevent incidental intrusion of debris that could be present in the proximity of the air intake. On March 7, 2016, following the installation of changes, the AF trains were declared operable. Additionally, compensatory measures were implemented to 1) monitor for a potential radioactive material release from the engine exhaust to the atmosphere, and 2) institute a fire watch due to the configuration change disabling the C02 system and opening the doors for the AF diesel-driven pump rooms. This condition is reportable in accordance with 10CFR50.73(a)(2)(ii)(B), any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety. Additionally, TS LCO 3.7.5 Condition A requires restoring the AF train to OPERABLE status within 72 hours. As the AF combustion air intake was installed per the original plant design, this condition existed for a longer period of time than is allowed by LCO 3.7.5 Condition A. Therefore, this event is also being reported pursuant to 10 CFR 50.73(a)(2)(i)(B), any operation or condition which was prohibited by TSs. Further, as there were multiple times during the past three years where the Unit 1 and Unit 2 A-train AF system were inoperable for surveillance testing, this event is also being reported pursuant to 1O CFR 50.73(a)(2)(v)(B) as a condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat. NRG FORM 366A (11-2015) Page 3 of 4 | ML16119A296
byron station | Unknown Unit | Auxiliary Feedwater Diesel Intake Design Deficiency Related to Turbine Building High Energy Line Break Resulted in an Unanalyzed Condition Due to Insufficient Validation of Vendor Analysis Inputs | 05-03-2076 | On March 4, 2016, during the Braidwood NRC Component Design Basis Inspection, a concern was raised regarding why it was acceptable forthe diesel driven Auxiliary Feedwater (AF) pump engine combustion air intake to be located in the turbine building, a non-safety related structure. On March 7, 2016, the additional evaluations that were completed for Byron determined that the existing configuration did not adequately support diesel engine operation with high energy line break (HELB) conditions in the turbine building, and at 0400 hours Operations entered Technical Specification Limiting Condition for Operation 3.7.5, “Auxiliary Feedwater (AF) System,” Condition A, “One AF train inoperable, for one train (B-train) of AF inoperable for both Units 1 and 2. The AF trains were declared operable following a corrective action to install a temporary configuration change to provide an engine combustion air intake from the auxiliary building. The cause of the event was insufficient validation of vendor analysis inputs in 1993 while reviewing the AF diesel engine’s abilityto function during a turbine building HELB event. The corrective actions planned are to develop and install a permanent modification to re-route the AF diesel engine intakes for Unit 1 and 2. NRCFORM366(11-2015) Page 2 of 4 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY0MB: NO.3150-0104 EXPIRES: 10/31/2018 (11-2015) EstimatedburdenperresponsetocomplyWiththismandatorycollection request:80hours. Reported lessons learned are incorporated into the licensing process and led buck to industry. Send commentsregardingburden estimatetothe FOIA, Pdvacy and Intormation CollectionsBranch (T-5 . LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by Internete-mail to lnfocuiects.Resource@nrc.gov, andtotheDeskOfficer,OfficeoftntormationandRegulatoryAffairs, :; CONTINUATION SHEET NEOB-10202,(3150-0104), OfficeofManagementandBudget, Washington, DC 20503. Ifsmeans usedtoimposeaninformation collection doesnotdisplay acurrentlyvalid0MB control number,the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Byron Stati;on Uni-t 1 05000454 YEAR NUMBER NO. — 2016 001 00 - - | A. Plant Operating Conditions Before the Event: Event Date: March 4, 2016 Unit: 1 Mode: 1 Reactor Power: 100 percent Unit: 2 Mode: 1 Reactor Power: 100 percent Unit 1 Reactor Coolant System (RCS) [AB]: Normal operating temperature and pressure Unit 2 Reactor Coolant System: Normal operating temperature and pressure No structures, systems or components were inoperable at the start of this event that contributed to the event. B. Description of Event: On March 4, 2016, during the Braidwood NRC Component Design Basis Inspection, a concern was raised regarding why it was acceptable forthe diesel driven auxiliary feedwater (AF) [BA] pump engine combustion air intake to be located in the turbine building, a non-safety related structure. Combustion air intake draws air from the turbine building via an intake pipe that enters the safety-related auxiliary building to the AF diesel room. During the review of documentation related to the air intake for Byron Station, it was identified that the existing configuration did not adequately support diesel engine operation with high energy line break (HELB) environmental conditions in the turbine building. Prior evaluations did not fully account forthe combustion air being a steam-air mixture in a post-HELB environment that reduces the available air density during the event. This issue was determined to be applicable to Byron Station and on March 7, 2016 at 0400 hours, Byron Operations entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.5, “Auxiliary Feedwater (AF) System,” Condition A, “One AF train inoperable,” for one train (B-train) of AF inoperable for both Units 1 and 2. NRC Event Notification (ENS) 51772 was made on March 7, 2016 at 1118 hours. A temporary configuration change was implemented to provide engine combustion intake air from the auxiliary building. The change allowed airfrom the AF diesel-driven pump rooms to supply the Unit 1 and Unit 2 AF diesel engines and a wire mesh screen cap was installed to prevent incidental intrusion of debris that could be present in the proximity of the air intake. On March 8, 2016, following the installation of changes, the Byron AF trains were declared operable. Additionally, compensatory measures were implemented to 1) monitor for a potential radioactive material release from the engine exhaust to the atmosphere, and 2) institute a fire watch due to the configuration change disabling the C02 system and opening the doors for the AF diesel rooms. This condition is reportable in accordance with 1OCFR5O.73(a)(2)(ii)(B), any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety. Additionally, TS LCO 3.7.5 Condition A requires restoring the AF train to OPERABLE status within 72 hours. As the AF combustion air intake was installed per the original plant design, this condition existed for a longer period of time than is allowed by LCO 3.7.5 Condition A. Therefore, this event is also being reported pursuantto 10 CFR 50.73(a)(2)(i)(B), any operation or condition which was prohibited byTSs. Further, as there were multiple times during the past three years where the Unit 1 and Unit 2 A-train AF system were inoperable for surveillance testing, this event is also being reported pursuant to 10 CFR 50.73(a)(2)(v)(B) as a condition that could have prevented the fulfillment of a system’s safety function. NRCFORM366A(11-2015) Page 3 of 4 | ML16124A048
Susquehanna Steam Electric Station | Unit 1 | lnoperability of Swing Bus Transfer Switch Due to Deformed Bolt on Linkage | 00-03-2016 | On March 5, 2016 during surveillance testing, Automatic Transfer Switch (ATS), 1ATS229, failed to close in on the alternate supply resulting in a loss of the Division 2 Class 1 E Engineered Safeguards System (ESS) 480V Motor Control Center (MCC) 1 B229 and entry into Technical Specifications 3.3.3.1, 3.5.1, and 3.6.1.3. Based on the cause of the failure, Susquehanna believes that there is firm evidence that the transfer switch would have failed on its next actuation following testing on February 5, 2016. Based on this conclusion, the condition existed for a period longer than allowed by Technical Specifications. As a result, this condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. Susquehanna also determined that work associated with the Division 1 transfer switch (1ATS219) was performed while the Division 2 switch was unknowingly inoperable resulting in simultaneous inoperability of both divisions. Since both divisions were inoperable for a period of time between February 5, 2016 and March 5, 2016, this is also considered a condition that could have prevented fulfillment of a safety function and is reportable in accordance with 10 CFR (a)(2)(v)(D). The direct cause was determined to be a deformed bolt on the upper linkage. The apparent cause was the upper linkage rod being too long causing the deformation of the bolt. Corrective actions include revising the preventive maintenance activities for the transfer switch. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366 (11-2015) Page 2 of 5 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 11-2015) Estimated burden per response to comply with this mandatol)' collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industl)'. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatol)' Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollecls.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatol)' Affairs, CONTINUATION SHEET NEOB-10202, (3150·0104), Office of Management and Budge!, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER I I YEAR SEQUENTIAL REV Susquehanna Steam Electric Station, Unit 1 NUMBER NO. 05000387 2016 -007 -00 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, approximately 87 percent Rated Thermal Power Based upon the failure mode of the transfer switch, the switch is considered to have been inoperable since the last time it was tested on February 5, 2016. EVENT DESCRIPTION Background Information/System Description: Two redundant Class 1 E 480 V Isolation Swing Buses (1 B219 and 1 B229) [EllS System/Function Identifier: ED/BU] provide power for the Residual Heat Removal (RHR) Injection Valves [EllS System/Function Identifier: BO/INV], RHR Minimum Flow Valves [EllS System/Function Identifier: BOIV], Recirculation Loop Bypass Valves [EllS System/Function Identifier: AD/V], and Recirculation Discharge Valves [EllS System/Function Identifier: AD/V]. The preferred power source to the isolation swing bus is from the A and B 480 VAC ESS Bus Load Groups via motor-generator set [EllS Function Identifier: MG], and the alternate power is supplied directly from the C and D 480 VAC ESS Bus Load Groups, respectively. The transfer will occur automatically upon reduction or loss of voltage from the preferred source. Event Timeline: On March 5, 2016 during surveillance testing, Automatic Transfer Switch (ATS) [EllS Function Identifier: ASU], 1ATS229, failed to close in on the alternate supply resulting in a loss of the Division 2 Class 1 E ESS 480V MCC 1 B229 and entry into Technical Specifications 3.3.3.1, 3.5.1, and 3.6.1.3. The detailed timeline is as follows: February 5, 2016 12:00- 1ATS229 was successfully tested. February 8, 2016 01:45- Technical Specification 3.5.1 was entered for a Division 1 RHR system outage window. Work associated with 1ATS219 was performed during this window. February 10,2016 17:43-The RHR system outage window was completed and Technical Specification 3.5.1 was exited. March 5, 2016 21:25- 1ATS229 failed to close in on the alternate supply. Testing was stopped and 1 B229 was de-energized. 21:30-The Field Unit Supervisor (FUS) reported that the ATS transfer motor was very hot to the touch and had an acrid odor. NRC FORM 366 (11-2015) Page 3 of 5 | ML16125A027
River Bend Station -Unit 1 05000 458 1 OF 4 | Unit 1 | Potential Loss of Safety Function of Onsite AC Sources and Operations Prohibited by Technical Specifications Due to Uncorrected Circuit Breaker Control Logic Design Causing Intermittent Failure to Close | 04-25-2016 | On February 24, 2016, with the plant in cold shutdown, the operations shift manager was made aware of a notification regarding a certain model ofMasterpact 480-volt circuit breakers that described a failure mode that could potentially prevent the automatic closure of the breakers. Assessment of this information determined that the susceptible breakers included those powering the emergency ventilation fans in the Division 1 and 2 emergency diesel generator rooms and two auxiliary building unit coolers. This condition required that both diesel generators and both trains of shutdown cooling and to be declared inoperable. This constituted a condition that could potentially prevent fulfillment of the safety function of onsite AC power sources and decay heat removal. The Division 2 residual heat removal loop was operating in shutdown cooling, satisfactorily maintaining reactor coolant temperature. The cause of the event is that station personnel failed to recognize the breakers' vulnerability to this failure mode. This directly resulted in the failure to take corrective action prior to this industry notification. The cause of the untimely corrective actions is that the breakers were incorrectly determined to be operable in 2014 when the condition was discovered. All the affected breakers were modified to eliminate the failure mode prior to the subsequent plant 'startup. NRG FORM 366 (11-2015) Page 1of3 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 ' (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to lnfocollects.Resollrce@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME .I 3. LER NUMBER osooo-1~ oocKET•u::~ DYE AR SEQUENTIAL REV NUMBER NO. u-1 1-0 !Riv" Bond Station -Unit 1 ° I 0s | REPORTED CONDITION On February 24, 2016, with the plant in cold shutdown, the operations shift manager was made aware of a notification regarding a certain model of Masterpact 480-volt s11fety-re(ated circuit breakers (**BKR~*) that described a failure mode that could potentially prevent the automatic closure of the breakers. The initial information regarded the emergency ventilation fans in the Division 1 and 2 emergency diesel generator rooms. These fans are not in Technical Specifications, but they provide a support function to the emergency diesel generators (**DG**). This condition required that both diesel generators to be declared inoperable. This constituted a condition that could potentially prevent fulfillment of the safety function of onsite AC power sources [ED]. Later on the same c:late, further evaluation of the notification identified four other circuit breakers affected by the same condition. These breakers supply power to Division l·and 2 containment unit coolers and the Division 1and2.auxiliary building 141 ft. elevation general area unit coolers. The auxiliary building unit coolers are not in Technical Specifications, but they provide a support function to the electrical distribution system. The required action in Technical Specification is to declare both trains of the residual heat removal system (shutdown cooling mode) [BO] inoperable. This inoperability constituted a condition that could have potentially prevented the fulfillment of the decay heat removal safety function. Division 2 residual heat removal was operating in shutdown cooling, satisfactorily maintaining reactor coolant temperature. The affected breakers can be manually operated to start/stop their associated equipment, if necessary for operation INVESTIGATION AND IMMEDIATE ACTIONS Masterpa'ct breakers were installed at RBS as replacements for obsolete General Electric AKR breakers. Subsequently, at RBS and elsewhere, there were isolated failures ofthe breakers to close upon demand. Failure analyses had beer:i conducted by both the vendor and the utilities, but no such analyses determined that a potentially generic problem existed. · · · In 2014, the breaker vendor issued a non-conformance report that concluded that the closure failures were from intermittent mechanical binding of the anti-pump mechanism. The binding was the result of a "standing close signal," which is the condition where the relay that actuates the closing mechanism remains energized, either indefinitely or for a defined period of time following a closure actuation. The control logic for any given breaker is an inherent design feature of the circuitry of the switchgear, not internal to the breaker itself. It was eventually determined by the vendor that this condition could cause any Masterpact breaker to intermittently fail to close. The vendor indicated that the failure mode could not be predicted, but was repeatable, 'and occurred on both new and old breakers. When RBS evaluated the vendor's nonconformance report, a population of affected circuit breakers was identified, and the served systems were evaluated for adverse effects on their ability to perform their safety functions. The operational history of the. breakers was examined, and it was determined that the observed increase in failure rate was not statistically significant. The affected systems were determined to be operable. The nonconformance report stated that the failure mode could be averted by pressing the PUSH TO OPEN button on the front of the breaker after remote opening. This information was used to develop an Operations Standing Order, and this action was performed after every breaker opening for any of the affected breakers during power operations or hot NRG FORM 366A (11-2015) Page 2 of 3 | ML16126A229
PAGE | Unknown Unit | Unit 2 Zone 3 HVAC unable to maintain Zone 3 differential pressure greater than 0.25 in wg | 03-08-2016 | On March 8, 2016 at 0232 hours Secondary Containment Zone Ill ventilation differential pressure lowered to 0.16" inch of vacuum water gauge (WG) when securing Unit 1 Zone Ill ventilation for a routine preventative maintenance activity. Required differential pressure per Surveillance (SR) 3.6.4.1.1 could not be maintained in he intended alignment and Technical Specification (TS) 3.6.4.1 was entered for Unit 1 and Unit 2. Zone Ill tventilation was restored to the original alignment and Zone Ill differential pressure recovered to> 0.25" WG at 0335 hours. lrhis event is being reported under 10 CFR 50.73(a)(2)(v)(C) and per the guidance of NUREG 1022 Rev 3 section 3.2.7 as an event or condition that could have prevented fulfillment of a safety function. There is no redundant Susquehanna Secondary Containment System. There were no actual or potential consequences to the health and safety of the public as a result of this event. An engineering evaluation concludes no safety system functional failure (SSFF) actually occurred as a result of his event. The apparent cause is less than adequate design of the outside air dampers. The corrective action for this condition is an engineering change that allows the closing of the upper and lower damper sections to be operated separately for the reactor building HVAC supply systems. NRC FORM 366 (11-2015) Page 2 of 3 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 11-2015) Estimated burden per response lo comply with this mandal01y collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollecls.Resource@nrc.gov, and lo the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does nol display a currently valid OMB control number, the NRC may nol conduct or sponsor, and a person is not required lo respond lo, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER l 3. LER NUMBER l YEAR SEQUENTIAL REV Susquehanna Steam Electric Station, Unit 1 NUMBER NO. 05000387 2016 -003 -00 | CONDITIONS PRIOR TO EVENT Unit 1 -Mode 1, 86.6 percent Rated Thermal Power Unit 2- Mode 1, 100 percent Rated Thermal Power There were no other structures, systems, or components that were inoperable at the start of the event that contributed to the event. EVENT DESCRIPTION On March 8, 2016 at 0232 hours, and while securing the Unit 1 Secondary Containment (EllS Code: NG) Zone Ill Heating Ventilation and Air Conditioning (HVAC) for a preventive maintenance activity, Zone Ill (Unit 1 and 2) Reactor Building (RB) differential pressure lowered to 0.16 inch of vacuum water gauge (WG). The required differential pressure per SR 3.6.4.1.1 of 0.25 inch WG could not be maintained in the intended alignment for the RB HVAC and Technical Specification (TS) 3.6.4.1 was entered for Unit 1 and Unit 2. The affected Zone Ill ventilation was restored to the original alignment and differential pressure recovered to > 0.25" inch WG at 0335 hours. On March 8, 2016, at 0937 hours, this condition was reported in accordance with 10 CFR 50.72(b)(3)(v)(C) for any event or condition that, at the time of discovery, could have prevented the fulfillment of the safety function. There is no redundant secondary containment system. In accordance with 10 CFR 50. 73(a)(2)(v)(C), this LER is being submitted for an event or condition that could have prevented the fulfillment of the safety function of Secondary Containment to control the release of radioactive material. CAUSE OF EVENT The direct cause of the event was misalignment between upper and lower damper blades. The outside air dampers were originally designed to be maintained Full Open, but have since initial plant startup been throttled to control Reactor Building differential pressure. Over time, the alignment of the upper and lower blades has become misaligned, such that the top blades are more open than the lower blades, decreasing differential pressure. This misalignment caused a larger gap in the upper blades than was needed to restrict supply flow into Zone Ill when operations swapped the fans. The apparent cause is less than adequate design of the outside air dampers. The manual outside air dampers use a single level to control the entire bank of 13 louver blades. This design puts more stress on the linkages than if it were controlled by multiple levers. NRC FORM 366 (11-2015 Page 3 of 3 | ML16127A083
North Anna Power Station | Unit 1 | Chemical Addition System Outside of Technical Specification Due to Excessive Unseating Thrust on MOVs | 05-05-2016 | On March 9, 2016, at approximately 1034 hours, with Unit 1 at 100 percent power in Mode 1 and Unit 2 at 0 percent power in Mode 6 for a scheduled refueling outage, 2-QS-MOV-202B failed to stroke open when functionally tested due to excessive unseating thrust. An extent of condition review and engineering evaluation determined that 2-QS-MOV-202A maintained its function. An extent of condition review and engineenng evaluation of the Unit 1 valves determined that l-QS-MOV-102B maintained its function and 1-QS-MOV- · 102A did not. Design Changes (DC) (DC NA-16-00023 for Unit 1 and DC NA-16-00021 for Unit 2) were implemented to provide additional valve operating margin prior to returning the valves to service. Based on as- found testing and engineering evaluation, Sodium Hydroxide (NaOH) injection for both units would have been supplied in the event of a Design Basis Accident (DBA) and the safety function of the Chemical Addition System was maintain~d. The health and safety of the public were not affected by this event. .NRC FORM 366 (11-2015) Page 2 of 4 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPR9VED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the )icensing process and fed back to industry. Send. comments' regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR NUMBER- NO. North Anna Power Station, Unit 1 05000338 2016 -002 -00 | 1.0 DESCRIPTION OF THE EVENT Ort March 9, 2016, with Unit 2 at 0 percent power in Mode 6, the Unit 2 Chemical Addition Tank Outlet Valve, 2-QS-MOV-202B (EIIS System-BE, ·component-V) failed to open when functionally tested. The actuator was unable to unseat the disc under normal bus voltage. This resulted in tripping the thermal overload for breaker, 2-EE-BK.R-2Jl-2S-B3 (EIIS System-EE, Component-BKR), due to excessive unseating thrust. The actuator stall thrust was estimated to be approximately 25,000 lbs. The valve would not have been able to open if called upon in a Design Basis Accident (DBA). -In support of continued troubleshooting of 2-QS-MOV-202B, an extent of condition review and an engineering evaluation was conducted on Unit 2 Chemical Addition Tarik Outlet Valve, 2-QS-MOV-202A. Periodic Test, 2-PT-212.34H, "Valve Inservice Inspection (2-QS-MOV-202A)", had been performed prior to evaluation. Therefore, initial unseating thrust was unknown prior to testing. Based on 2-QS-MOV-202A successfully opening during the performance of 2-PT-212.34H, subsequent test data, and engineering evaluation it was determined that 2-QS-MOV-202A would have opened and performed its function if called upon in a DBA. Design Change (DC) NA-16-00021 was implemented to modify the gear ratio to increase the unseating thrust margin to the motor operated valves (MOVs) and valve stroke was changed to limit controlled seating, instead of torque controlled. On March 25, 2016, at approximately 0805 hours, with Unit 1at100 percent power\n Mode 1, the 72 hour Required Action for Technical Specification (TS) 3.6.8 was enter~d to perform an extent of condition review and as-found diagnostic testing on the Unit 1 Chemical Addition Tank Outlet V ;:ilves. While both valves exhibited higher than expected unseating thrust, they both opened on demand. Based on functional testing and engineering evaluation, it was determined that l-QS-MOV-102B would have performed its function. Engineering could p.ot definitively, determine that l-QS-MOV-102A would have performed its function if called upon in a DBA; therefore, it is considered not capable of performing its function. DC NA-16-00023 was implemented to modify the gear ratios to increase the unseating thrust margin for the valves ·and valve stroke was changed to limit controlled seating, instead of torque controlled. The Required Action for Unit 1 was cleared on March 26, 2016, at approximately 0055 hours. NRG FORM 366A (11-2015) Page 3 of 4 | ML16133A335
Limerick Generating Station | Unit 1 | Plant Shutdown Required by Technical Specification Due to a Pressure Boundary Leak | 05-18-2016 | Reactor coolant system pressure boundary leakage was identified by a drywell leak inspection team during a planned shutdown for a Unit 1 refueling outage. This event resulted in a plant shutdown required by Technical Specifications. The Unit 1 ‘A’ RHR Shutdown Cooling Return Check Valve equalizing line developed a crack at the toe of a weld due to high cyclic fatigue induced by vibration from the reactor recirculation system. The Unit 1 welds were reworked to EPRI 2x1 at select locations on the “A” and “B” RHR Shutdown Cooling Return check valve equalizing lines for HV-051-1F050A and 50B. The similar Unit 2 welds on equalizing lines for HV-051-2F050A and 50B will be examined and reinforced. The scope will be added into the next refueling outage (2R14) currently scheduled for April 2017. NRC FORM 366 (01-2014) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 01/31/2017 (01-2014) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by LICENSEE EVENT REPORT (LER) internet e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, CONTINUATION SHEET Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 6. LER NUMBER 3. PAGE SEQUENTIAL REV YEAR NUMBER NO. Limerick Generating Station, Unit 1 05000352 2 OF 3 2016 - 003 - 00 | Unit Conditions Prior to the Event Unit 1 was in Operational Condition (OPCON) 1 (Power Operation) at approximately 14.5 percent power performing a planned Unit 1 shutdown to support a refueling outage. There were no structures, systems or components out of service that contributed to this event. Description of the Event On Sunday March 20, 2016, Limerick Unit 1 was operating at 14.5 percent power performing a planned Unit 1 shutdown to support a refueling outage (1R16). At 2154 hours, the drywell leak inspection team identified a 0.5 gpm pressure boundary leak on the shutdown cooling (BO:EIIS) testable check valve (ISV:EIIS) equalizing line. The control room supervisor (CRS) entered Technical Specification (TS) 3.4.3.2 Reactor Coolant System - Operational Leakage Action “a” which requires being in at least Hot Shutdown within 12 hours and Cold Shutdown within the next 24 hours. The 12 hour Hot Shutdown TS Action was met at 0133 hours and the 24 hour Cold Shutdown Action was met at 1401 hours. An investigation determined that Unit 1 Unidentified Leakage increased from 0.03 gpm to 0.06 gpm between January 16, 2016 and January 18, 2016. Leakage increased to 0.24 gpm on January 19, 2016 and continued to vary with reactor recirculation pump speed for the remainder of the cycle. The maximum leakage recorded was 1.2 gpm which stabilized at 1.0 gpm following power reduction to 95 percent. On March 20, 2016 Maintenance Technicians performed a planned drywell entry at 14.5 percent power and identified a leak on the ¾ inch reactor side equalizing line of the 1A Shutdown Cooling (SDC) Return Line Inboard Testable Check Primary Containment Isolation Valve, HV-051-1F050A. The leak was located approximately ¼ inch from the valve body weld and was determined to be pressure boundary leakage. A 4-hour ENS (#51809) was completed at 2351 hours as required by 10CFR50.72(b)(2)(i) for the initiation of a plant shutdown required by TS. The ENS also reported an event that resulted in the condition of the plant principal safety barriers being seriously degraded per 10CFR50.72(b)(3)(ii). Therefore, this LER is being submitted pursuant to the requirements of 10CFR50.73(a)(2)(i)(A) and 10CFR50.73(a)(2)(ii)(A). Analysis of the Event There was no actual safety consequence associated with this event. The potential safety consequences of this event were minimal. The Unidentified Leakage remained a small fraction of the 5 gpm TS 3.4.3.2 LCO. HPCI was unavailable less than 29 minutes due to testing and RCIC was unavailable for less than 13 hours due to maintenance and testing during the three month period (January, February and March of 2016) of elevated drywell leakage. HPCI is designed to prevent the actuation of the automatic depressurization system (ADS) and ensure that the reactor core remains covered in the event of a small pipe break size of one-inch diameter or less. | ML16139A428
Arkansas Nuclear One | Unit 1 | Non-Functional External Penetration Flood Seals | 05-18-2016 | On March 19, 2016, two block-out penetrations separating the Arkansas Nuclear One, Unit 1 (ANO-1) Turbine Building from the Auxiliary Building were determined to be non-functional. The penetrations are located in the floor of Turbine Building elevation 354 ft. Below the penetrations is the Auxiliary Building, housing safety related equipment. On March 17, 2016, it was identified that two penetration seals did not match approved fire penetration or approved flood seal details. Further investigation, completed on March 19, 2016, revealed that the two block-out penetrations were not grouted and represented a previously unknown vulnerability in a credited external flood barrier. The apparent cause of this event was less than adequate project management control for the size and scope of the External Flood Mitigation Project associated with post Fukushima Dai-ichi resolutions and requirements set forth by the NRC. Mitigating strategies and extent of condition reviews have been implemented for the identified conditions. Permanent repair of the deficient flood barriers is complete minus cure time. Actions to correct programmatic aspects of this condition are in progress. NRC FORM 366 (11-2015) Page 2 of 5 NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information LICENSEE EVENT REPORT (LER) Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555- (See Page 2 for required number of 0001, or by internet e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of digits/characters for each block) Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Arkansas Nuclear One, Unit 1 05000-313 2016 - 001 - 00 | A. Background The design basis flood protection elevation for Arkansas Nuclear One, Units 1 and 2 (ANO-1 and ANO- 2) safety- related components and structures is 361 ft. Mean Sea Level (MSL). The design basis flood is a combination of the probable maximum flood (PMF) (358 ft. MSL), which is based on a 10,000 year probability, and the assumed coincident failure of the upstream Ozark Dam (+3 ft.). The ANO-1 and ANO-2 Safety Analysis Reports (SARs) state that Seismic Class/Category 1 structures are designed for the PMF of 361 ft. MSL and Seismic Class/Category 1 systems and equipment are either located on floors above 361 ft. MSL or protected by walls, waterproof doors, hatches, etc. B. Plant Status At the time the condition was discovered, ANO-1 and ANO-2 were operating in Mode 1 at 100% power. There were no other structures, systems, or components that were inoperable at the time that contributed to the event. C. Event Description ANO conducted walk downs and design verifications as follow-up activities in response to Near-Term Task Force (NTTF) Recommendation 2.3, “Flooding Walk down of the NTTF Review of Insights from the Fukushima Dai-ichi Accident.” As previously reported in LER 50-313/2014-01-00 dated May 5, 2014, multiple instances of ANO-1 and ANO-2 design features that may not have provided adequate external flood protection for safety-related equipment located below the design basis flood elevation of 361 ft. MSL were documented during these walk downs. Examples of the identified deficient design features and procedures included:  Missing or deficient internal conduit seals  Missing or deficient seals  Unsealed removable closure plates  Missing gaskets  Roof leaks  Ground water intrusion through penetrations, building joints and conduits  Degraded hatch gaskets  Floor drain system cross connected between flood protected areas and non-flood areas Due to the lack of designed isolation features on these pathways, the potential existed for flood waters to migrate into the Auxiliary Building where pumps and equipment required for safe shutdown are located. In March 2016, as part of follow-up actions, a list of dual-function penetrations (fire and flood) was being created to determine where there was a detail difference between the Fire Penetration Log and the Flood Features database. Penetrations 00073-01-0034 and 0073-01-0063 were identified on the Fire Penetration Log as sealed with lathe and plaster; however, the Flood Features database indicated the penetrations were sealed with grout and/or cellular concrete. Lathe and plaster is sufficient for fire protection purposes, but unqualified for flood protection. This was documented in Condition Report CR-ANO-1-2016-0985 on March 17, 2016. No recent documentation could be located supporting the assertion that the penetrations were sealed with grout and/or cellular concrete. Follow-up field inspection confirmed the penetrations were sealed with lathe and plaster and the penetrations were declared non- functional for flood protection on March 19, 2016. NRC FORM 366 (11-2015) Page 3 of 5 NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information LICENSEE EVENT REPORT (LER) Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555- (See Page 2 for required number of 0001, or by internet e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of digits/characters for each block) Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Arkansas Nuclear One, Unit 1 05000-313 2016 - 001 - 00 NARRATIVE D. Event Causes The direct cause of the event (failure to identify the lathe and plaster detail in two flood barrier block-out penetrations) is both the vendor preparer and reviewer failed to perform adequate verification of penetration details in drawings and the associated Flood Features database. The apparent cause of this event is less than adequate project management control for the size and scope of the External Flood Mitigation Project. The following contributing causes were also identified:  Oversight personnel did not recognize and correct inadequate monitoring and management of the project as the scope and complexity increased.  Flood design documents did not distinguish between lathe and plaster from grout, other than in the Fire Penetration Log, which was not accessible in the field.  The preparer and reviewer did not follow design verification requirements. Penetration photographs were accepted as sufficient information for assigning incorrect details on architectural drawings and in the Flood Features database for the two block-out penetrations. E. Corrective Actions The following corrective actions have been completed to address this condition:  Carbon steel forms were anchored to the floor around the subject block-out penetrations and sealing materials staged as a contingency until permanent repairs can be completed.  A comprehensive review of the Flood Features database, Fire Protection Penetration Log, and architectural drawings has been performed. No further external flooding vulnerabilities were identified during this review.  A human performance error review has been completed to document inappropriate action analysis. The following corrective actions are being taken to further address this condition (list is not all inclusive):  Entergy personnel and contractors responsible for gaps in oversight and accountability related to the external flooding project will be briefed on the importance of recognition and mitigation of the impacts of schedule pressures and changes in personnel assigned to the project.  A detailed review of the vendor’s root cause evaluation being developed will be performed and important results and actions from the review will be documented in the ANO corrective action plan.  A review of completed external flood barrier walk-down packages is planned to determine if post verification entries in the walk-down package have been made without verification and to document the adequacy of all external flood boundary features (including vendor test data, qualification reports and other supporting documentation).  Permanent repair of the defective block-out penetrations. NRC FORM 366 (11-2015) Page 4 of 5 NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information LICENSEE EVENT REPORT (LER) Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555- (See Page 2 for required number of 0001, or by internet e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of digits/characters for each block) Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Arkansas Nuclear One, Unit 1 05000-313 2016 - 001 - 00 NARRATIVE F. Safety Significance Evaluation Arkansas Nuclear One is required to be protected from flooding within the station’s design and licensing basis. The safety-related equipment required to mitigate the consequences of an accident were potentially affected by this condition. There are several factors which could mitigate the impact of these deficiencies depending on the specific conditions encountered during an actual event including the actual flood height, the capability for the subject block-out penetrations to resist water ingress, the sealing of pathways, and water removal actions. Should mitigating strategies fail, the unanalyzed pathways could permit an indeterminate amount of leakage into the Auxiliary building, potentially challenging the ability of safety-related equipment to perform the specified safety function during an accident. There were no actual consequences. G. Basis for Reportability This event is reported pursuant to the following criteria: 10 CFR 50.73(a)(2)(ii): Any event of condition that resulted in (B) The nuclear power plant being in an unanalyzed condition that significantly degraded plant safety 10 CFR 50.73(a)(2)(v) Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: (B) Remove residual heat (ANO-1 and ANO-2 Decay Heat Removal system) H. Additional Information 10 CFR 50.73(b)(5) states that this report shall contain reference to “any previous similar events at the same plant that are known to the licensee.” NUREG-1022 reporting guidance states that term “previous occurrences” should include previous events or conditions that involved the same underlying concern or reason as this event, such as the same root cause, failure, or sequence of events. A review of the ANO corrective action program and Licensee Event Reports for the previous three years was performed. This review identified conditions that were previously identified deficiencies in the flood barrier program. Two relevant similar events were identified. These events are discussed below. On April 7, 2015, during preparation of walk down packages for flood barrier inspections, two credible flood paths were identified between an unscheduled junction box located in the ANO-2 Turbine Building (floor elevation 329 ft., approximately 4 feet off the floor) and lighting receptacles in the Auxiliary Building elevation 317 ft. The apparent cause of this condition was the failure to recognize a drawing note which identified the junction box seal in addition to the lighting panel seals. In addition to the above, one Licensee Event Report (50-313/2014-001-00) was submitted to the NRC (described in Section C above) on May 5, 2014 (ML14125A483). NRC FORM 366 (11-2015) Page 5 of 5 NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information LICENSEE EVENT REPORT (LER) Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555- (See Page 2 for required number of 0001, or by internet e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of digits/characters for each block) Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Arkansas Nuclear One, Unit 1 05000-313 2016 - 001 - 00 NARRATIVE H. Additional Information (continued) The subject condition associated with this report (failure to identify the lathe and plaster detail in two flood barrier block-out penetrations) was identified as part of the ongoing External Flood Mitigation Project extent of condition review and is not associated with corrective actions intended to prevent recurrence. Additional corrective actions are initiated when further deficiencies are identified, as noted in the partial list provided in Section E above. Energy Industry Identification System (EIIS) codes and component codes are identified in the text of this report as [XX]. NRC FORM 366 (11-2015) | ML16139A795
PAGE | Unknown Unit | Secondary Containment Breach due to Simultaneous Opening of Airlock Doors Due to Degraded Latch Mechanism | 02-04-2016 | On March 29, 2016 at approximately 23:00, two employees leaving the Unit 2 Turbine Building entered the Turbine Building to Reactor Building airlock. Prior to opening the airlock door, employees verified a green light was present, indicating the opposite airlock door was closed. The first employee entered the airlock while the other employee held the Turbine building door. As the second employee entered into the airlock, the airlock alarm was heard. As this time, a rush of air was observed from the Reactor Building side of the airlock, forcing the door open (Door 120A). Both individuals quickly closed the doors. The individuals then proceeded through the Reactor Building door to the nearest phone and informed the Control Room of the event. Having both airlock doors momentarily open simultaneously, results in a potential loss of safety function and requires reporting under 10 CFR 50.73(a)(2)(v)(C). The cause of this event was determined to be normal wear of the Door 120A (Reactor Building airlock door) door latch. Corrective actions to address this issue include repair of the door latch mechanism. NRC FORM 366 (11-2015) PaQe 2 of 4 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and led back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER I I YEAR SEQUENTIAL REV Susquehanna Steam Electric Station, Unit 2 NUMBER NO. 05000388 2016 -001 -00 | CONDITIONS PRIOR TO EVENT Unit 2- Mode 1, 100 percent Rated Thermal Power Unit 1 - Mode 5, 0 percent Rated Thermal Power EVENT DESCRIPTION On March 29, 2016 at approximately 23:00, two employees leaving the Unit 2 Turbine Building [EllS System Identifier: NM] entered the Turbine Building to Reactor Building airlock [EllS Component Identifier: AL] on elevation 676'. Prior to opening the airlock door [EllS Component Identified: DR], employees verified a green light was present, indicating the opposite airlock door was closed. The first employee entered the airlock while the other employee held the Turbine building door. As the second employee entered into the airlock, the airlock alarm was heard. At this time, a rush of air was observed from the Reactor Building [EllS System Identifier: NG] side of the airlock, forcing the door open (Door 120A). Both individuals quickly closed the doors, followed by a peer check to verify each door was properly shut. The individuals then proceeded through the Reactor Building door to the nearest phone and informed the Control Room [EllS System Identifier: NA] of the event. CAUSE OF EVENT The direct cause of this event is normal wear of the airlock door latch. Based on investigation performed, the Door 120A latch was determined to be sticking inside the crash bar. This prevented the Reactor Building airlock door from properly latching and staying latched when differential pressure was applied to the door upon entering the airlock from the Unit 2 Turbine Building side. NRC FORM 366 (11-2015) Paqe 3 of 4 | ML16145A123
Clinton Power Station | Unit 1 | Bypassing Both Divisions of Reactor Water Cleanup Leak Detection System is a Reportable Loss of Safety Function | 05-23-2016 | On March 24, 2016, it was determined that placing both Reactor Water Cleanup System (RT) Leak Detection System (LD) bypass switches in the Bypass position per plant procedure when the RT Filter/Demineralizer (F/D) was placed in service following backwash and pre-coat operations on-January 25, 2016 was a reportable condition. Both divisions of the RT LD were bypassed for seven minutes. Backwashing and pre-coating a RT F/D is a normal system operation and not considered maintenance. A review of the Updated Safety Analysis Report (USAR) determined that the associated isolation functions are credited to mitigate the consequences of an RT pipe break accident described in USAR Chapter 6. Therefore, placing both divisions of RT LD in Bypass a constituted a condition that could have prevented the fulfillment of the safety function of system that is needed to mitigate the consequences of an accident. The direction for bypassing the RT LD system had been included in procedures since 1989 but did not constitute a reportable event until the issuance of NUREG-1022, Rev. 3 in 2013. The failure to report this condition was caused by not revising plant procedures when the Exelon fleet reporting requirements were revised to align with NUREG-1022, Rev. 3. NRG FORM 366 (11-2015) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 01/31/2017 (02-2014) d1'-"""eoll(., Estimated burden per response to comply with this mandatory collection request: 80 hours. .~ ~o,,. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and lnfonnation Collections \~) Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by LICENSEE EVENT REPORT (LER) internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of lnfonnation and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budge~ CONTINUATION SHEET Washington, DC 20503. If a means used to impose an infonnation collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the infonnation collection. 1. FACILITY NAME 2. DOCKET 6. LER NUMBER 3. PAGE I YEAR I SE N Q U U M E B N E T R IA L R N E O V . Clinton Power Station, Unit 1 05000461 2 OF 4 2016 - 003 - 00 | PLANT AND SYSTEM IDENTIFICATION General Electric-Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX] EVENT IDENTIFICATION Bypassing Both Divisions of Reactor Water Cleanup Leak Detection System is a Reportable Loss of Sate ty Function A. Plant Operating Conditions before the Event Unit: 1 Event Date: 03/24/16 Event Time: 1157 Mode: 1 Mode Name: Power Operation Reactor Power: 99 percent B. DESCRIPTION OF EVENT On March 24, 2016, it was determined that placing both Reactor Water Cleanup System (RT) Leak Detection System (LO) bypass switches in the Bypass position per Clinton Power Station (CPS) Procedure 3301.01, "Reactor Water Cleanup" when the RT Filter/Demineralizer (F/D) was placed in service following backwash and pre-coat operations was a reportable condition. It was determined from the Operations Log for January 25, 2016 that both divisions of the RT LD were bypassed for seven minutes. The fol.lowing Operations log entries document the actions taken on January 25, 2016: 0940: Placed 'A' RT F/D in Hold for backwash and pre-coat per procedure CPS 3303.01 section 8.1.3 and procedure CPS 3303.02, "Reactor Water Cleanup Filter Demineralizer Operating Procedure," sections 8.2 and 8.5. 1155: Placed RT F/D 'B' in Hold. 1157: When pressurizing RT F/D 'A' received RT differential flow alarm. Placed both divisions of RT LD in Bypass, this will render both RWCU diffe.rential flow instruments INOPERABLE. Verified Dose Equivalent Iodine 1-131 specific activity is< 1.8 x 10e-3 µCi/gm (actual 1.84 x 1O e-6 µCi/gm) per CPS 3303.01 step 6.9 and Technical Specification (TS) Limiting Condition for Operation (LCO) 3.3.6.1, "Primary Containment and Drywall Isolation Instrumentation." Entered the following action statements: - LCO 3.3.6.1, Required Action D.1 - Place channel in trip in 24 hours and LCO 3.3.6.1 Required Action E.1 - Restore RT isolation capability in 1 hour. | ML16146A543
Susquehanna Steam Electric Station | Unit 2 | Secondary Containment Breach due to Simultaneous Opening of Airlock Doors Due to Degraded Latch Mechanism | 02-06-2016 | On March 29, 2016 at approximately 23:13, an employee leaving the Unit 2 Turbine Building entered the Turbine Building to Reactor Building airlock. Prior to opening the airlock door, employee verified a green light was present, indicating the opposite airlock door was closed. The employee entered the airlock and the airlock alarm was heard. At this time, a rush of air was observed from the Reactor Building side of the airlock, forcing the door open (Door 120A). The individual quickly closed both doors. The individual then proceeded through the Reactor Building door to the nearest phone and informed the Control Room of the event. Having both airlock doors momentarily open simultaneously results in a potential loss of safety function and requires reporting under 10 CFR 50.73(a)(2)(v)(C). The cause of this event was determined to be normal wear of the Door 120A (Reactor Building airlock door) door latch. Corrective actions to address this issue include repair of the door latch mechanism. NRC FORM 366 (11-2015) Pa~e 2 of 4 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555·0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR I SEQUENTIAL I REV Susquehanna Steam Electric Station, Unit 2 NUMBER NO. 05000388 2016 -002 -00 | CONDITIONS PRIOR TO EVENT: Unit 2 - Mode 1, 100 percent Rated Thermal Power Unit 1 -Mode 5, 0 percent Rated Thermal Power There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. EVENT DESCRIPTION: On March 29, 2016 at approximately 23:13, an employee leaving the Unit 2 Turbine Building [EllS System Identifier: NM] entered the Turbine Building to Reactor Building airlock [EllS Component Identifier: AL] on elevation 676'. Prior to opening the airlock door [EllS Component Identified: DR], employee verified a green light was present, indicating the opposite airlock door was closed. The employee entered the airlock and the airlock alarm was heard. At this time, a rush of air was observed from the Reactor Building [EllS System Identifier: NG] side of the airlock, forcing the door open (Door 120A). The individual quickly closed both doors. The individual then proceeded through the Reactor Building door to the nearest phone and informed the Control Room [EllS System Identifier: NA] of the event. CAUSE OF EVENT: The direct cause of this event is normal wear of the airlock door latch. Based on investigation performed, the Door 120A latch was determined to be sticking inside the crash bar. This prevented the Reactor Building airlock door from properly latching and staying latched when differential pressure was applied to the door upon entering the airlock from the Unit 2 Turbine Building side. NRC FORM 366 (11-2015) Page 3 of 4 | ML16147A322
Edwin I. Hatch Nuclear Plant | Unit 1 | Safety Relief Valves As Found Settings Resulted in Not Meeting Tech Spec Surveillance Criteria | 05-26-2016 | On March 30, 2016, Unit 1 was at 10 0 percent rated thermal power (RTP) when "as-found" testing results of the 3-stage main steam safety relief valves (SRVs) indicated two of the eleven Unit 1 SRVs had experienced a setpoint drift during the previous operating cycle which resulted in their failure to meet the Technical Specification (TS) opening setpoint pressure of 1150 +1-34.5 psig as required by TS Surveillance Requirement (SR) 3.4.3.1. The test results showed that two SRVs were slightly out of spec low due to setpoint drift. The SRV pilots were disassembled and inspected while investigating the reason for the drift. SNC has determined that the abutment gap closed pre-maturely. The pre-mature abutment gap closure is most likely due to loose manufacturing tolerances leading to SRV setpoint drift. NRC FORM 366 (11·2015) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMS: NO. 3150·0104 EXPIRES: 10/31/2018 11-2015) ,..,. ...... Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported )\_ lessons learned are incorporated into the licensing process and fed back to industry. Send !~~ comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 \~) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555.0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to !he Desk Officer, Office of lnfomnation and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an infonmation collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the infonmation collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER I I YEAR SEQUENTIAL REV Edwin I. Hatch Nuclear Plant Unit 1 NUMBER NO. 05000-321 2016 -004 -00 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor Energy Industry Identification System codes appear in the text as (EllS Code XX). DESCRIPTION OF EVENT On March 30 2016, with Unit 1 at 100 percent rated thermal power (RTP), "as-found" testing of the 3-stage main steam safety relief valves (SRVs) (EllS Code RV) showed that two of the eleven main steam SRVs that were tested had experienced a drift in pressure lift setpoint during the previous operating cycle such that the allowable technical specification (TS) surveillance requirement (SR) 3.4.3.1 limit of 1150 +1-34.5 (+ 1- 3%) psig had been exceeded. Below is a table illustrating the Unit 1 SRVs that failed as found testing results after being removed from service during the Spring 2016 refueling outage. MPL Lift Pressure Percent Drift 1821-F013D 1113 psig -3.2% 1B21-F013E 1106 psig -3.8% CAUSE OF EVENT The SRV pilots were disassembled and inspected while investigating the reason for the drift. SNC has determined that the linear variable differential transformer (LVDT) used to measure displacement confirmed the abutment gap closed pre- maturely. The pre-mature abutment gap closure is most likely due to loose manufacturing tolerances leading to SRV setpoint drift. REPORTA BILITY ANALYSIS AND SAFETY ASSESSMENT This event is reportable in accordance with 10 CFR 50.7 3(a)(2)(i)(B) because a condition occurred that is prohibited by TS 3.4.3. Specifically, an example of multiple test failures is given in NUREG-10 22, Revision 3, "Event Reporting Guidelines 10 CFR 50.72 and 50.73" which describes the sequential testing of safety valves. This example notes that "Sometimes multiple valves are found to lift with set points outside of technical specification limits." NUREG-1022 further states in the example that "discrepancies found in TS surveillance tests should be assumed to occur at the time of the test unless there is firm evidence, based on a review of relevant information (e.g., the equipment history and the cause of failure), to indicate that the discrepancy occurred earlier. However, the existence of similar discrepancies in multiple valves is an indication that the discrepancies may well have arisen over a period of time and the failure mode should be evaluated to make this determination." Based on this guidance, the determination was made that this "as found" condition is reportable under the reporting requirements of 10 CFR 50.73(a)(2)(i)(B). | ML16147A344
Clinton Power Station | Unit 1 | Trip of Emergency Reserve Auxiliary Transformer Static VAR Compensator Causes Positive Secondary Containment Pressure Following Lightning Strike on 138 kV Offsite Source | 05-26-2016 | On March 30, 2016, at approximately 1545 CDT, the Main Control Room (MGR) received numerous annunciators that indicated a trip of the Emergency Reserve Auxiliary Transformer (!;RAT) Static VAR Compensator (SVC) caused by a voltage transient on the 138 kV supply. Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1, AC Sources-Operating, Required Action A.1 and A.2 were entered. As a result of the voltage transient, the Division 1 Fuel Building ventilation (VF) system isolation dampers closed causing a trip of VF supply and exhaust fans. With no operating VF fans, Secondary Containment (SC) vacuum rose to slightly greater than 0 inches water gauge (WG) which exceeded the TS requirement of greater than 0.25 inches vacuum WG. The MGR entered Emergency Operating Procedure (EOP)-8, Secondary Containment Control and TS LCO 3.6.4.1, Secondary Containment, Required Action A.1. The likely cause of the voltage transient on the 138 kV line was a lightning strike that occurred during thunderstorms in the area on the day of the event. SC vacuum was restored within TS requirements at 1550 CDT by starting the Standby Gas Treatment System. Corrective actions have been initiated to improve reliability of the 138 kV source. This event is being reported as a condition that could have prevented fulfillment of a safety function under 10 CFR 50. 73(a)(2)(v)(C). NRG FORM 366 (11-2015) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 01/31/2017 (02-2014) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. % Send comments regarding burden estimate to the FOJA, Privacy and Information Collections ! Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by ······""· LICENSEE EVENT REPORT (LER) internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202; (3150-0104), Office of Management and Budget, CONTINUATION SHEET Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 6. LER NUMBER 3. PAGE I YEAR I SE N Q U U M E B N E T R IA L R N E O V . Clinton Power Station, Unit 1 05000461 2 OF 4 2016 004 00 | PLANT AND SYSTEM IDENTIFICATION General Electric-Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX] EVENT IDENTIFICATION Trip of Emergency Reserve Auxiliary Transformer Static VAR Compensator Causes Positive Secondary Containment Pressure Following Lightning Strike on 138 kV Offsite Source A. Plant Operating Conditions before the Event Unit: 1 Event Date: 03/30/16 Event Time: 1545 Mode: 1 Mode Name: Power Operation Reactor Power: 99 percent B. DESCRIPTION OF EVENT On March 30, 2016, at 1545 CDT, the Emergency Reserve Auxiliary Transformer (ERAT) Static VAR Compensator (SVC) [COMP] tripped when the 138 kV line cycled open and closed due to a lightning strike. Operations entered CPS procedures 4002.01, Loss of AC, and 4001.02, Automatic Isolation, and Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1, AC Sources - Operating, Required Actions A.1 and A.2. During the event, Division 1 Secondary Containment (SC) isolation dampers went shut due to the momentary loss of power and SC vacuum exceed O inch water gauge (WG). Emergency Operating Procedure (EOP)-8, Secondary Containment Control, and TS LCO 3.6.4.1, Secondary Containment, Required Action A.1 were entered as a result of this abnormal condition. At 1547, the Standby Gas Treatment System (VG) Train A was started per CPS procedure 3319.01, Standby Gas Treatment, Section 8.2.1, due to SC isolation dampers going shut. At 1550, SC vacuum had been restored to TS limits. Procedure EOP-8 and TS LCO 3.6.4.1 Required Action A.1 were exited. The ERAT was restored at 1926 and TS LCO 3.8.1 Required Actions A.1 and A.2 were exited. An investigation determined the cause of the event was most likely due to a lightning strike. During the time frame of the event, a powerful electrical (lightning) storm was moving through the CPS service area. During the event, the ERAT relay scheme worked as designed and ERAT circuit switcher 8018 remained closed allowing the ERAT to re-energize when the 138 kV breakers re-closed. | ML16153A249
Clinton Power Station | Unit 1 | Insulator Failure On the Reserve Auxiliary Transformer Results In A Loss of Secondary Containment Vacuum | 05-31-2016 | On April 2, 2016, at approximately 1257 CDT the Main Control Room (MCA) received numerous annunciators that indicated a trip of the Reserve Auxiliary Transformer (RAT) and associated Static VAR Compensator (SVC). The MCA entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1, AC Sources-Operating, Required Actions A.1 and A.2. The Division 1 Fuel Building ventilation (VF) system isolation dampers closed due to loss of power causing a trip of VF supply and exhaust fans. With the VF fans inoperable, Secondary Containment (SC) vacuum rose to slightly greater than O inches water gauge (WG) which exceeded the TS requirement of greater than 0.25 inches vacuum WG. The MCR entered Emergency Operating Procedure (EOP)-8, Secondary Containment Control, and TS LCO 3.6.4.1 , Secondary Containment, Required Action A.1. SC vacuum was restored within TS requirements at 1300 by starting the Standby Gas Treatment (VG) system. The RAT was successfully returned to service following replacement of the broken 'A' phase insulator stack on the 345 kV Circuit Switcher 4538. The cause of this event was identified as the failure of the 'A' phase 4538, 345 kV Circuit Switcher insulator due to a manufacturing defect. The corrective actions included performing a risk review of all Ohio Brass Insulators for potential failure impact and creating a replacement strategy to replace the high risk and critical insulators. Replacement of the remaining Ohio Brass insulators in the switchyard will be completed by the end of C 1R17. NRC FORM 366 (11-2015) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 01/31/2017 (02-2014) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by LICENSEE EVENT REPORT (LER) internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, CONTINUATION SHEET Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 6. LER NUMBER 3. PAGE I YEAR I SE N Q U U M E B N E T R IA L R N E O V . Clinton Power Station, Unit 1 05000461 2 OF 4 2016 005 00 | PLANT AND SYSTEM IDENTIFICATION General Electric-Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX] EVENT IDENTIFICATION Insulator Failure on the Reserve Auxiliary Transformer Results in a Loss of Secondary Containment Vacuum A. Plant Operating Conditions before the Event Unit: 1 Event Date: 04/02/16 Event Time: 1257 Mode: 1 Mode Name: Power Operation Reactor Power: 99 percent B. DESCRIPTION OF EVENT . . On April 2, 2016, at approximately 1257 CDT the Reserve Auxiliary Transformer (RAT) and Static VAR Compensator (SVC) tripped due a failure of the 'A' phase insulator 345 kV Circuit Switcher 4538 in the switchyard. The Main Control Room (MCR) entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1, AC Sources-Operating, Required Action A.1 and A.2. The CPS area was experiencing very strong winds at the time of the failure. The bus bar connected to the failed insulator has a configuration that is susceptible to wind induced loads. The bus bar is supported at the plant north end by the insulator stack and on the south end by a flexible link attached to the 345 kV Circuit Switcher 4538. In the middle of the bus bar is a wire connection to the overhead 345 kV lines that supply power from the North Bus. This configuration allows the wind to induce loads on the overhead 345 kV lines, the electrical drop connection (wire attached to the bus bar), and on the physical bus bar itself. As a result of the voltage transient, caused by automatic transfer to the Emergency Reserve Auxiliary Transformer (ERAT), the Division 1 Fuel Building Ventilation (VF) system isolation dampers closed causing a trip of VF supply and exhaust fans. The effect of this condition was that Secondary Containment (SC) rose to slightly greater than O inches water gauge (WG) and exceeded the TS limit of 0.25 inch water gauge. Operations personnel entered Emergency Operating Procedure (EOP) -8, Secondary Containment Control, and TS LCO 3.6.4.1, Secondary Containment, Required Action A.1. The Standby Gas Treatment System was started and SC vacuum was restored within TS limits at 1300 hours. NRG FORM 366A (02-2014) | ML16155A080
Quad Cities Nuclear Power Station | Unit 2 | Main Steam Isolation Valve Local Leak Rate Tests Exceed Technical Specification Limits | 05-19-2016 | On March 21, 2016, at 2200 hours, with Unit 2 shutdown for refuel outage Q2R23, the as-found local leak rate tests (LLRT) for the four (4) main steam lines (MSL) were performed following closure of the main steam isolation valves (MSIV). The initial as-found LLRT on the "A" and "C" MSL MSIVs exceeded the minimum pathway criteria (lesser leakage in a line) of the Technical Specifications (TS), and the combined total leakage of all MSLs also exceeded the minimum pathway criteria (lesser leakage in each line when combined for all MSIVs) of the TS. Corrective actions included flushing, disassembling, inspecting, repairing, and retesting the valves. Future corrective actions include installation of an improved spherical nose plug design to the MSIV plug and seat, and installation of an anti-rotation device to the MSIV pilot. Valves 2-0203-2A and 2-0203-1C were disassembled and inspected. The most likely cause for the higher than expected leakages has been determined to be a valve design that is susceptible to a degraded main plug I seat interface during valve closure. A contributing cause was susceptible pilot plug I seat misalignment, due to pilot disc stem nut wear. The safety significance of this event was minimal. The total primary containment leakage of 315.866 scfh was well within the allowed leakage limit of 1372.99 scfh (La). However, since the "A", "B", "C" and "D" MSL MSIV as-found leakage exceeded the TS limit, and the combined total leakage of all MSLs exceeded the TS limit, this report is submitted in accordance with the requirements of 10 CFR 50.73(a)(2)(i)(B), which requires the reporting of a past operation or condition which was prohibited by the plant Technical Specifications. NRG FORM 366 (11-2015) Page 2 of 6 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV Quad Cities Nuclear Power Station Unit 2 05000265 YEAR NUMBER NO. 2016 - 001 - 00 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Main Steam Isolation Valve local leak rate testing resulted in two (2) MSIVs exceeding the individual Technical Specification limit and the combined minimum path MSIV leakage exceeding the Technical Specifications Limit. A. CONDITION PRIOR TO EVENT Unit: 2 Event Date: March 21, 2016 Event Time: 2200 hours Reactor Mode: 4 Mode Name: Cold Shutdown Power Level: 0% B. DESCRIPTION OF EVENT On March 21, 2016, at 2200 hours, with Unit 2 shutdown for refuel outage Q2R23, the as-found local leak rate tests (LLRT) for the four (4) main steam [SB] lines (MSL) were performed following closure of the main steam isolation valves [ISV] (MSIV). Two (2) MSIV leakage paths; "A" MSL inboard valve 2-0203-1A (65.5 scfh) and "C" MSL outboard valve 2-0203-2C (45 scfh), when tested at~ 25 psig; exceeded the allowed limit for leakage as specified by Technical Specifications (TS) Surveillance Requirement (SR) 3.6.1.3.10 criteria for the as-found min path (lesser leakage in a line) criteria of 34 scfh at ~ 25 psig. In addition, the combined total leakage of all MSLs, 118.8 scfh at ~ 25 psig, exceeded the allowed limit for leakage as specified by TS SR 3.6.1.3.10 criteria of s 86 scfh at ~ 25 psig for all MSIVs combined minimum path leakage limit (i.e., lesser leakage in each line when combined for all MSIVs). Following the completion of the individual as-found results, the "A", "B", and "D" MSLs were flushed. On March 22, 2016, following the flushing of the MSIVs and the subsequent re-draining of the test volumes, an additional LLRT was performed on each MSL. Post-flushing LLRTs resulted in successful leakage rates on the 2-0203-1A, 2-0203-1B, and 2-0203-20 MSIVs, while the 2-0203-2A MSIV continued to show significant seat leakage. The "C" MSL was not flushed due to the decision to repair valve 2-0203-1C. Valves 2-0203-2A and 2-0203-1C were originally scoped into Q2R23 based on results from the previous Unit 2 refuel outage (Q2R22). Valves 2-0203-2A and 2-0203-1 C were disassembled and inspected, and MSIV pilot and disc stem nut wear associated with the 2-0203-2A and 2-0203-1C MSIVs was identified as causing the seat leakage. Valves 2-0203-2A and 2-0203-1 C were subsequently repaired and satisfactorily retested. Valve 2-0203-2C was not worked due to a successful combined as-left LLRT, following 2-0203-1C valve repair. The as-found leakage on valve 2-0203-1C masked 2-0203-2C as-found leakage and as such, repairs to valve 2-0203-2C were not required. Given the impact that the "A" and "C" MSL isolation valves as-found leakage exceeded the TS limit for minimum path leakage in its MSL, and the combined total leakage of all MSLs exceeded the TS limit for min-path leakage for all MSIVs, this report is submitted in accordance with the requirements of 1O CFR 50.73(a)(2)(i)(B), which requires the reporting of a past operation or condition which was prohibited by the plant Technical Specifications. NRG FORM 366A (11-2015) Page 3 of 6 | ML16155A128
Browns Ferry Nuclear Plant | Unit 3 | Main Steam Relief Valves Lift Settings Outside of Technical Specifications Required Setpoints | 06-06-2016 | On April 6, 2016, the Tennessee Valley Authority was presented with as-found testing results indicating that three of the thirteen Main Steam Relief Valves (MSRVs) from Browns Ferry Nuclear, Unit 3, exceeded the +/- 3 percent setpoint required for their operability. Troubleshooting determined that the MSRV discs failed by corrosion bonding to their valve seats. The valve discs were previously platinum coated to prevent this, but the valve seat's rough Stellite surface caused the coating to flake off. It was determined that the MSRVs were inoperable from March 19, 2014 to February 20, 2016. The affected valves remained capable of maintaining reactor pressure within American Society of Mechanical Engineers code limits. Additionally, the valves' ability to open under remote-manual operation, or activation through the !Automatic Depressurization System or MSRV Automatic Actuation Logics was not affected. The valves remained capable of performing their required safety function. Corrective Actions were to replace all Unit 3 MSRVs, to analyze the pilot valves of the inoperable MSRVs, and to revise procedures to verify the pilot disc finish meets its requirements prior to valve assembly. NRG FORM 366A (11-2015) Page 2 of 8 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Browns Ferry Nuclear Plant, Unit 3 05000296 YEAR NUMBER NO. 2016 - 004 00 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Unit 3, was in Mode 1 at 100 percent power. II. Description of Events A. Event: On April 6, 2016, National Technical Systems (NTS) Laboratories provided Tennessee Valley Authority (TVA) with the as-found testing results of the thirteen Main Steam Relief Valves (MSRVs) [RV] which were removed from BFN, Unit 3 during its Spring 2016 refueling outage (U3R18). Three of the Main Steam Line A, B, and D Relief Valves (BFN-3-PCV-001-0004, BFN-3- PCV-001-0023, and BFN-3-PCV-001-0041) had as-found lift settings which exceeded the +/- 3 percent setpoint required for their operability. Technical Specification (TS) 3.4.3 requires twelve of the thirteen Safety/Relief Valves (S/RVs) to be operable for S/RV system operability. The three failed MSRVs rendered the entire S/RV system inoperable for the duration of the fuel cycle, from March 19, 2014 to February 20, 2016. MSRV operability was restored on March 28, 2016, upon completion of a Work Order (WO) 116592810, for the biennial scheduled replacement of the MSRVs with refurbished valves which were certified to lift within +/- 1 percent of their setpoints. Throughout this event, the two-stage MSRVs remained capable of maintaining the reactor pressure below 1375 psig, which is the American Society of Mechanical Engineers (ASME) code limit of 110 percent of the vessel design pressure. The valves remained capable of performing their required safety function. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event: There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. NRG FORM 366A (11-2015) Page 3 of 8 | ML16158A139
Clinton Power Station | Unit 1 | Missed Surveillance Results in a Condition Prohibited by Technical Specifications | 06-10-2016 | On April 21, 2016, in preparation to reduce power in order to restore the 'B' turbine driven reactor feed pump (TDRFP) Operations detected that Technical Specification (TS) Surveillance Requirement (SR) 3.3.2.1.2 had not been performed eight days earlier. On April 13, 2016 Operations lowered reactor power below the Control Rod Withdrawal Limiter (RWL) High Power Setpoint (HPSP) to remove 'B' TDRFP from service due to high vibrations. TS SR 3.3.2.1.2 requires a functional test of the 4-Notch Control Rod Withdraw Limit of the RWL within one hour of resetting the HPSP during a power reduction; if it has not been completed within the previous 92 days. The SR was last performed on April 26th, 2015 and was required to be performed on April 13, 2016. TS 3.3.2.1 Required Action A.1 requires with one or more RWL channels inoperable, to immediately suspend control rod withdrawal. Contrary to this requirement, control rods were withdrawn to restore power above the HPSP following restoration of the 'B' TDRFP to service. The cause of the event was that the SRO responsible for the down power on April 13, 2016 did not validate, by preventative maintenance identifier (PMID), that the required surveillance was current. Corrective actions included applying Management Associated Results Company, Inc. (MARC) principles to the individuals involved. NRC FORM 366 (11-2015) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 01/31/2017. (02-2014) Estimated burden per response to comply with this mandatory collection request: 80 hours . •~ ¢VP.•£011"'~q,. Reported lessons learned are incorporated into the licensing process and fed back to industry. ! i Send comments regarding burden estimate to the FOIA, Privacy and Information Collections ~ Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by ..... / LICENSEE EVENT REPORT {LER) internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, CONTINUATION SHEET Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 6. I.ER NUMBER 3. PAGE I YEAR I SE N Q U U M E B N E T R IA L R N E O V . Clinton Power Station, Unit 1 05000461 2 OF 4 2016 - 006 - 00 | PLANT AND SYSTEM IDENTIFICATION General Electric-Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX] EVENT IDENTIFICATION Missed Surveillance Results in a Condition Prohibited by Technical Specifications A. Plant Operating Conditions before the Event Unit: 1 Event Date: 04/21/16 Event Time: 1709 Mode: 1 Mode Name: Power Operation Reactor Power: 85 percent B. DESCRIPTION OF EVENT At 1709 hours (CDT) on April 21, 2016, in preparation to reduce power in order to restore the 'B' turbine driven reactor feed pump (TDRFP) to service, Operations discovered that Technical Specification (TS) Surveillance Requirement (SR) 3.3.2.1.2 had not been performed eight days earlier. On April 13, 2016 Operations lowered reactor power below the Control Rod Withdrawal Limiter (RWL) High Power Setpoint (HPSP) (approximately 66% rated thermal power)'to remove 'B' TDRFP from service due to high vibrations. TS SR 3.3.2.1.2 requires a functional test of the 4-Notch Control Rod Withdraw Limit of the RWL within one hour of resetting the HPSP during a power reduction; if it has not been completed within the previous 92 days. The SR was last performed on April 25th, 2015 and, therefore, was required to be performed, TS 3.3.2.1 Required Action A.1 requires with one or more RWL channels inoperable, to immediately suspend control rod withdrawal. Contrary to this requirement, control rods were withdrawn to restore reactor power above the HPSP following restoration of the 'B' TDRFP to service. The RWL provides protection from control rod withdrawal errors above the Low Power Setpoint (LPSP) {29.2% rated thermal power). Above the LPSP and below the HPSP, the RWL initiates a control rod withdrawal block every 4 notches. Above the HPSP, the RWL initiates a control rod withdrawal block every 2 notches. TS SR 3.3.2.1.2 requires a functional test every 92 days of the 4-Notch Control Rod Withdraw Limit when operating above the LPSP but below the HPSP, and TS SR 3.3.2.1.1 requires a functional test of the 2-Notch Control Rod Withdraw Limit every 92 days when operating above the HPSP. Both of the RWL Functional tests are performed by Clinton Power Station (CPS) surveillance procedure CPS 9014.01, RPC System Withdrawal Limitation Test. However each SR has a unique Preventative Maintenance Identification Number (PMI D) which is listed in the integrated operating procedures to support determining whether the SR had been performed within the last 92 days when reactor power is lowered below the HPSP. NRG FORM 366A {02-2014) | ML16165A491
PAGE | Unknown Unit | Secondary Containment Declared Inoperable Due to Airlock Doors Open Due to a Human Performance Error | 01-05-2016 | On April 22, 2016 at approximately 11 :30, a Nuclear Plant Operator (NPO) was entering a Unit 1 Reactor Building access door and noticed another worker entering the airlock door behind him with a cart. The NPO stated that he was trying to be helpful and opened the reactor building side (inner) door. The NPO stated that they did not notice that the turbine building side (outer) door was still open. Both doors were open at the same time for approximately one second. This airlock serves as a se.condary containment boundary; as such, having both doors open at the same time results in failure to meet Technical Specification 3.6.4.1 as a result of not satisfying Surveillance Requirement 3.6.4.1.3. The condition requires a Licensee Event Report (LER) in accordance with 10 CFR 50. 73(a)(2)(v)(C). The direct cause of the event was less than adequate verification practices to ensure compliance with Secondary Containment door requirements. Corrective actions include holding the individual accountable for less than adequate verification practices. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366 (11-2015) Page 2 of 3 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and led back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555·0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150·0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER I I YEAR SEQUENTIAL REV Susquehanna Steam Electric Station, Unit 1 NUMBER NO. 05000387 2016 -015 -00 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, approximately 10 percent Rated Thermal Power Unit 2 - Mode 1, approximately 100 percent Rated Thermal Power There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. EVENT DESCRIPTION On April 22, 2016 at approximately 11:30, a Nuclear Plant Operator (NPO) was entering a Unit 1 Reactor Building [EllS System Identifier: NG] access door [EllS Component Identifier: DR] and noticed another worker entering the airlock door behind him with a cart. The NPO stated that he was trying to be helpful and opened the reactor building side (inner) door. The NPO stated that they did not notice that the turbine building side (outer) door was still open. Both doors were open at the same time for approximately one second. This airlock serves as a secondary containment boundary [EllS System Identifier: NG]; as such, having both doors open at the same time results in failure to meet Technical Specification 3.6.4.1 as a result of not satisfying Surveillance Requirement 3.6.4.1.3. The condition requires a Licensee Event Report (LER) in accordance with 10 CFR 50. 73(a)(2)(v)(C). CAUSE OF EVENT The direct cause of the event was less than adequate verification practices to ensure compliance with Secondary Containment door requirements. ANALYSIS/SAFETY SIGNIFICANCE An engineering evaluation was performed and concluded that secondary containment could have performed its safety function of isolating, as assumed in the accident analysis, and also of re-establishing 0.25 inches vacuum (drawdown) within the assumed accident analysis time (1 0 minutes). Therefore, the subject event did not cause a loss of safety function. This event will not be counted as a safety system functional failure (SSFF) for the NRC performance indicator based on the engineering analysis that shows there was no loss of ability to fulfill the safety function. CORRECTIVE ACTIONS Corrective actions include holding the individual accountable for less than adequate verification practices. NRC FORM 366 (11-2015) Page 3 of 3 | ML16167A301
Pilgrim Nuclear Power Station | Unknown Unit | Both Emergency Diesel Generators Inoperable | 06-09-2016 | On April 12, 2016 at 0050 hours, with the reactor at 100% power and the mode switch in RUN, Pilgrim Nuclear Power Station (PNPS) entered an unplanned 24-hour Limiting Condition for Operation (LCO) Action Statement per Technical Specification 3.5.F.1 due to both emergency diesel generators (EOG) being inoperable. With EOG B out of service for a planned LCO maintenance window, EOG A was declared inoperable due to identification of an approximate leak of 130 drops per minute (dpm) from the line to the jacket water pressure indication. The apparent cause of the EOG A jacket water pressure boundary leak was stress corrosion cracking (SCC) that eventually led to failure of a bulkhead pipe fitting. The apparent cause was confirmed by the failure analysis performed. Corrective action was taken to replace the leaking bulkhead pipe fitting on EOG A to restore EOG Operability. An aditional corrective action is planned to replace the opposite train EOG jacket water bulkhead pipe fitting. There was no impact to public health and safety. NRG FORM 366A (11-2015) Page 2 of 4 U.S. NUCLEAR REGULATORY COMMISSION APPR.OVED BY OMS: NO. 3150-0104 EXPIRES: 10/31/2018 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means CONTINUATION SHEET used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR NUMBER NO. Pilgrim Nuclear Power Station 05000293 2016 001 00 | BACKGROUND The standby alternating current (AC) power source provides two independent diesel generators as the onsite source of AC power to the emergency service portions of the station Auxiliary Power Distribution System. Each onsite source provides AC power to safely shut down the reactor, maintain the safe shutdown condition, and operate all auxiliaries necessary for station safety. On April 10, 2016 at 1900 hours, Emergency Diesel Generator (EOG) B was tagged out of service for planned preventative maintenance. EVENT DESCRIPTION At approximately 2130 hours on April 11, 2016, as part of the Operators outside tour of the EOG building, the Operator on tour reported a water leak from the C103C panel trailing across the EOG A floor towards the floor = drain. This leak was evaluated and determined to 'be a leak in the EOG A Cooling Water System (EllS code LB) pressure boundary. The leak rate was determined to be approximately 130 drops per minute (dpm). At 0050 hours on April 12, 2016, EOG A was declared inoperable due to the jacket water pressure boundary leak. PNPS entered an unplanned 24-hour LCO Action Statement per Technical Specification 3.5.F.1 because both EDGs were Inoperable. · The pipe fitting was replaced and EOG A was restored to operable status at 1059 hours on April 12, 2016. CAUSE OF THE EVENT The apparent cause of the EOG A jacket water pressure boundary leak was identified to be stress corrosion cracking (SCC) of the bulkhead pipe fitting. The pipe fitting was original plant equipment manufactured by = Imperial-Eastman Corp (EllS code 1027), and was identified on plant drawings as Part #1298 Anchor = Coupling (EllS Code PSF). CORRECTIVE ACTIONS The leaking anchor coupling bulkhead fitting on EOG A was replaced to restore EOG A operability. Additional corrective actions were issued to mitigate the likelihood of event recurrence. These additional actions include: Procedure enhancement to inspect. the opposite train EOG cabinets prior to performing scheduled maintenance on either EOG; and action to replace both EOG A and B anchor coupling pipe fittings associated with the jacket water pressure instruments with new fittings. NRG FORM 366A (11-2015) Page 3 of 4 NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) .............. Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported /\. lessons learned are incorporated into the licensing process and fed back to industry. Send \~ ~'rt) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to •s-tit• LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and. Budget, Washington, DC 20503. If a means CONTINUATION SHEET used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR NUMBER NO. Pilgrim Nuclear Power Station 05000293 2016 001 00 NARRATIVE SAFETY CONSEQUENCES The standby AC power source provides two independent diesel generators as the onsite source of AC power to the emergency service portions of the station Auxiliary Power Distribution System. Each onsite source provides AC power to safely shut down the reactor, maintain the safe shutdown condition, and operate all auxiliaries necessary for station safety. The safety objective of the standby AC power source is to provide a single failure proof source of onsite AC power adequate for the safe shutdown of the reactor following abnormal operational transients and postulated accidents. ' The unit AC power source provides AC power to all station auxiliaries and is the normal station AC power I source when the main generator is operating. The station preferred (offsite) AC power source provides AC power to all station auxiliaries required for startup and shutdown and is normally in use when the unit AC power source is unavailable. The secondary (o ffsite) AC power source provides AC power to essential station auxiliaries. It is used to supply essential station auxiliary loads only when the main generator is shut down, there is a failure of the preferred AC power source, and failure of a standby AC power source. The Station Blackout AC Power Source provides an independent diesel generator as the onsite source of AC power to the emergency service portions of the Auxiliary Power Distribution System in the unlikely event of a loss of preferred and secondary offsite power sources combined with a complete failure of the Standby AC Power System. · At the time of the event, the preferred AC and the secondary AC power sources were Operable and available to perform their intended safety function. In addition, the Station Blackout AC Power Source was Functional and available as the onsite source of AC power to the emergency service portions of the Auxiliary Power Distribution System. Based on the operable and available preferred and secondary power sources, there was no adverse impact on the public health or safety. REPORTA BILITY This report is submitted in accordance with 1O CFR 50. 73(a)(2)(v)(A), 50. 73(a)(2)(v)(B), and 50. 73(a)(2)(v)(D) for a condition that could have prevented the fulfillment of the safety function of a system needed to shut down the reactor and maintain it in a safe shutdown condition, remove residual heat, and mitigate the consequences of an accident. NRG FORM 366A (11-2015) Page 4 of 4 NRC FO,R.M. 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) ....... Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send \~. w..r ~t) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, •t&t• NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means CONTINUATION SHEET used to impose an information collection does not display a curren~y valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR NUMBER NO. Pilgrim Nuclear Power Station 05000293 2016 001 00 NARRATIVE PREVIOUS EVENTS Events involving LERs where both EDGs were inoperable were reviewed. These LERs are summarized as follows: · LER 99-006-00, LER 97-021-00, and LER 97-027-00 involved events where both emergency diesel generators were declared inoperable due to high ambient air temperatures. LER 98-004-00 and LER 98-002-00 involved events where both EDGs were declared inoperable due to low ambient temperatures. These prior LERs involved events where both EDGs were declared inoperable at the same time; however, the events are different because equipment failure and EOG maintenance was not involved. ENERGY INDUSTRY IDENTIFICATION SYSTEM (EllS) CODES The EllS codes for Components and Systems referenced in this report are as follows: COMPONENTS CODES Pipe Fitting PSF SYSTEMS CODES Diesel Cooling Water System LB REFERENCES: Condition Report CR-PNP-2016-2537 | ML16168A030
Browns Ferry Nuclear Plant | Unit 3 | !Automatic Depressurization System Valve lnoperability Exceeded Technical Specification Limits 5. EVENT DAT E 6. LER NUMBER 7. REPORT DATE 8. OTHER FACILITIES INVOLVED I SEQUENTIAL I REV FACILITY NAME DOCKET NUMBER MONTH DAY YEAR YEAR NUMBER NO. MONTH DAY YEAR N/A N/A - - FACILITY NAME DOCKET NUMBER 04 18 2016 2016 005 00 06 17 2016 11.1/!1 N/A 9. OPERATING MODE 11. THIS REPORT IS SUBMITIED PURSUANT TO THE REQUIREMENTS OF 10 CFR §: (Check all that apply) D D D D 20.2201 (b) 20.2203(a)(3)(i) 50. 73(a)(2)(ii)(A) 50.7 3(a)(2)(viii)(A) D D D D 20.2201(d) 20.2203(a)(3)(ii) 50.7 3(a)(2)(ii)(B) 50.7 3(a)(2)(viii)(B) 1 D D D D 20.2203(a)(1) 20.2203(a)(4) 50.73(a)(2)(iii) 50.73(a)(2)(ix)(A) D D D D 20.2203(a)(2)(i) 50.36(c)(1 )(i)(A) 50.73(a)(2)(iv)(A) 50. 73(a)(2)(x) 10. POWER LEVEL D 20.2203(a)(2)(iil D 50.36(c)(1 )(ii)(A) D 50. 73(a)(2)(v)(A) D 73.7 1 (a)(4) D D D D 20.2203(a)(2)(iii) 5o.36(c)(2) 50.73(a)(2)(v)(B) 13.11(a)(5) D D D D 20.2203(a)(2)(iv) 50.46(a)(3)(ii) 50. 73(a)(2)(v)(C) 73. 77(a)(1) 100 D D D D 20.2203(a)(2)(v) 50.7 3(a)(2)(i)(A) 50.7 3(a)(2)(v)(D) 73.77(a)(2)(i) D D D 20.2203(a)(2)(vi) ~ 50. 73(a)(2)(i)(B) 50. 73(a)(2)(vii) 73.77(a)(2)(ii) D D 50.7 3(a)(2)(i)(C) OTHER Specify in Abstract below or in NRG Form 366A 12. LICENSEE CONTACT FOR THIS LER LICENSEE CONTACT I TELEPHONE NUMBER (Include Area Code) Ryan Coons, Licensing Engineer 256-729-2070 13. COMPLETE ONE LINE FOR EACH COMPONENT FAILURE DESCRIBED IN THIS REPORT CAUSE SYSTEM COMPONENT MANU- REPORTABLE CAUSE SYSTEM COMPONENT MANU- REPORTABLE FACTURER TO EPIX FACTURER TO EPIX x SB RV T020 y D SB BKR G080 y I I 14. SUPPLEMENTAL REPORT EXPECTED 15.EXPECTED MONTH DAY YEAR D YES (If yes, complete 15. EXPECTED SUBMISSION DA TE) ~NO SUBMISSION DATE N/A I N/A I N/A ABSTRACT (Limit to 1400 spaces, i.e., approximately 15 single-spaced typewritten lines) On April 18, 2016, during a scheduled surveillance, the power to the Main Steam Line (MSL) B Relief Valve failed to transfer to its alternate feeder breaker when the normal feeder breaker was opened. The Automatic Depressurization System (ADS) function of the MSL B Relief Valve was declared inoperable. It was determined that the ADS valve was inoperable from March 26, 2016 to April 19, 2016. The valve's ability to open under normal power was not affected. Five of the six ADS valves remained operable. Only four ADS valves are required to meet the ADS function in the Loss of Coolant Analysis described in the Final Safety Accident Report. The unavailability of the ADS alternate power source was directly caused by a bus stab on the back of the Molded Case Circuit (MCC) breaker not fully engaging with the bus. This was apparently caused by improper performance of previous post-maintenance testing. The stab was adjusted, the MCC breaker was returned to service, and the MSL B Relief Valve's ADS function was declared operable upon verification of its alternate power supply. Corrective actions were to determine which load-feeding MCC breakers have a normal and alternate power source, and revise their preventative maintenance procedures to verify that post-maintenance testing includes power source isolation prior to closing the breaker under load. Breaker bus stabs will be replaced. NRG FORM 366A (11-2015) Page 2 of 7 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Browns Ferry Nuclear Plant, Unit 3 05000296 YEAR NUMBER NO. 2016 - 005 00 NARRATIVE I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Unit 3, was in Mode 1 at 100 percent power. II. Description of Events A. Event: On April 18, 2016, during a scheduled surveillance of the Automatic Depressurization System (ADS) [SB] Logic System, the power to the Main Steam Line (MSL)[SB] B Relief Valve [RV] (3-PCV-001-0022) failed to transfer to the alternate feeder breaker when the normal feeder breaker was opened. Operations subsequently declared the ADS function of the MSL B Relief Valve inoperable, and entered Technical Specification (TS) Limiting Condition of Operability (LCO) 3.5.1 Condition E, a 14 day shutdown LCO action statement. Troubleshooting determined that the bus stab on the back of the alternate feeder Molded Case Circuit (MCC) breaker [BKR] (3-BKR-001-0022A) was not properly engaged with the bus. The stab was adjusted, the MCC breaker was returned to service, and MSL B Relief Valve was verified to have proper power. The valve's ADS function was declared operable on April 19, 2016 at 1400 Central Daylight Time (CDT). Since the failure was discovered during surveillance testing, a past operability evaluation (POE) was performed to determine the duration of inoperability. The POE determined that the breaker was working properly until it was racked out for preventative maintenance (PM) performed during the previous Unit 3 refueling outage in March 2016. This failure went undetected due to improper post-maintenance testing (PMT). Prior to the outage, the associated breaker passed all required surveillances. The POE concluded that the time of inoperability began on March 26, 2016 at 2300 CDT and ended on April 19, 2016 at 1400 CDT. Since the BFN, Unit 3 ADS system only requires four of the six ADS valves to remain operable, the ADS system was operable throughout this entire event. MSL B Relief Valve actuation through the ADS or Main Steam Relief Valve (MSRV) Automatic Actuation Logics were not affected under normal power. The valve's mechanical setpoints were unaffected by this event, and they remained capable of lifting. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event: There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. NRC FORM 366A (11-2015) Page 3 of 7 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Browns Ferry Nuclear Plant, Unit 3 05000296 YEAR NUMBER NO. 2016 - 005 00 NARRATIVE C. Dates and approximate times of occurrences: Dates and Approximate Times Occurrence April 22, 2014 Last successful performance of 3-SR-3.3.5.1.6(ADS A), ADS Logic System Functional Test. March 9, 2016 Performed breaker inspection and PM on 250V DC Motor Operated Valve Board 3A. March 26, 2016 at 2300 CDT Plant mode and conditions require ADS valve operability. April 18, 2016 During scheduled performance of 3-SR-3.3.5.1.6(ADS A), Power to the MSL B Relief Valve failed to transfer to its alternate feeder breaker when the normal feeder breaker was opened. The ADS valve was declared inoperable. April 19, 2016 at 1400 CDT Troubleshooting found a stab on the back of the MCC breaker which required adjustment. Following adjustment, the ADS valve was returned to operable status. D. Manufacturer and model number (or other identification) of each component that failed during the event: The inoperable valve was a Target Rock Corporation two-stage pressure control valve, model number 7567F. The breaker was manufactured by General Electric, model number THEF136015. E. Other systems or secondary functions affected: No other systems or secondary functions were affected by this event. F. Method of discovery of each component or system failure or procedural error: Valve inoperability was discovered during the scheduled performance of 3-SR-3.3.5.1.6(ADS A), ADS Logic System Functional Test, when Operations opened the normal feeder breaker for the MSL B Relief Valve on 250V DC Motor-Operated Valve Board 3A, and its associated green light did not remain illuminated. Breaker inoperability was discovered during troubleshooting for the inoperable ADS valve. G. The failure mode, mechanism, and effect of each failed component, if known: The MSL B Relief Valve failed when its associated MCC breaker, which supplied alternate power from 250V DC Motor-Operated Valve Board 3A, became unavailable. The MCC breaker failed because the bus stabs were not properly engaged with the bus. NRG FORM 366A (11-2015) Page 4 of 7 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Offce of Management and Budget, Washington, DC 20503. If a means used to impose an information oollection does not display a currently valid OMS control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Browns Ferry Nuclear Plant, Unit 3 05000296 YEAR NUMBER NO. 2016 - 005 00 NARRATIVE H. Operator actions: There were no operator actions associated with this event. I. Automatically and manually initiated safety system responses: There were no automatic or manual safety system responses associated with this event. Ill. Cause of the event A. The cause of each component or system failure or personnel error, if known: The direct cause for the ADS valve failure was the unavailability of its alternate power source due to a bus stab on the back of the MCC breaker not fully engaging with the bus. The most apparent cause for the valve failure was improper implementation of previous PMT. 8. The cause(s) and circumstances for each human performance related root cause: Previous PMT was not properly performed, and failed to check if load operation was transferred upon breaker closure. IV. Analysis of the event: The Tennessee Valley Authority (TVA) is submitting this report in accordance with Title 10 of the Code of Federal Regulations 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant's TS. It was determined that the ADS valve was inoperable from March 26, 2016 to April 19, 2016, due the failure of the valve's associated MCC breaker to supply alternate power because of a misaligned bus stab. BFN, Unit 3, TS LCO 3.5.1 requires six Operable ADS Safety/Relief Valves (S/RVs) during Modes 1, and in Modes 2 and 3 when reactor steam dome pressure exceeds 150 psig. If one or more required ADS valve becomes inoperable, Required Action E.1 requires that valve to be restored to operability within 14 days. Based on this evaluation, BFN, Unit 3, operated with an inoperable ADS valve for longer than allowed by TS. The condition was assumed to have begun on March 9, 2016, during routine breaker inspection, as part of refueling outage maintenance activities. ADS valve operability was not required until March 26, 2016, when BFN, Unit 3 entered Mode 2 and reactor dome pressure exceeded 150 psig. Therefore, the ADS valve was considered inoperable from March 26, 2016 to April 19, 2016, when the breaker stabs were readjusted. The duration of ADS system inoperability was longer than allowed by plant TS LCO 3.5.1. NRC FORM 366A (11-2015) Page 5 of 7 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Browns Ferry Nuclear Plant, Unit 3 05000296 YEAR NUMBER NO. 2016 - 005 00 NARRATIVE V. Assessment of Safety Consequences System availability was not impacted by this event. While one ADS valve was inoperable, the remaining five ADS valves remained operable for the duration of this event. Only four ADS valves are required to meet the ADS function in the Loss of Coolant Accident analysis described in the Final Safety Accident Report. This condition did not affect the Appendix R Function. However, due to the failure of its alternate power source, the MSL B Relief Valve was not able to perform its specified safety function under all conditions. The MSL B Relief Valve remained operable for its required "Overpressure safety and relief protection for the nuclear system" function. The lack of reliable alternate power, from the MCC breaker had no effect on the mechanical setpoint of the valve, and it would have opened if reactor pressure exceeded 1145 psig. The MSL B Relief Valve was inoperable for its "Automatic nuclear system depressurization" function. All ADS valves are equipped with a logic circuit to automatically open the valve on concurrent high drywell pressure and low reactor water level or sustained reactor low water level when one of the Residual Heat Removal pumps is available in the Low Pressure Coolant Injection mode or two of the appropriate core spray pumps are available. Additionally, four of the six ADS valves have alternate power sources for manual actuation. The MSL B Relief Valve normal power source was aligned and operating as designed. However, during testing it was found that the alternate power source was not working as designed. The fuel vendor analyses of record assume between four and six available ADS valves, depending upon the applicable assumed single failure. A single failure of 250V DC Motor Operated Valve Board 3A, which feeds the MSL B Relief Valve normal power supply would still have resulted in all six S/RVs remaining available for their ADS function. The Main Steam system is required by TS 3.5.1 to have six operating S/RVs for ADS. TS Bases 3.5.1 states that each of the ADS S/RVs must be equipped with one air accumulator and associated inlet check valves, in order to provide pneumatic actuation. TS Bases 3.5.1 cites NEDC-32484P, "Browns Ferry Nuclear Plant Units 1, 2, and 3, SAFER/GESTR-LOCA Loss-of-Coolant Accident Analysis," which evaluated the effect of one ADS valve being out of service. Based on this analysis, five operable ADS valves will provide the required depressurization. However, the overall reliability of the ADS system is reduced, because any further valve failure could result in a reduction of depressurization capability. Therefore, operation is only allowed for a limited time. The 14 day completion time was based on a reliability study cited in "Recommended Interim Revisions to LCOs for ECCS Components" and has been found to be acceptable through operating experience. A. Availability of systems or components that could have performed the same function as the components and systems that failed during the event: The ADS system consists of six S/RVs as a defense-in-depth measure; only four of the six ADS valves are required for system operability. The five remaining S/RVs were unaffected by this event and were operable throughout the duration of this event. MSL B Relief Valve actuation NRG FORM 366A (11-2015) Page 6 of 7 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMS: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Offce of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Browns Ferry Nuclear Plant, Unit 3 05000296 YEAR NUMBER NO. 2016 - 005 00 NARRATIVE through the ADS or MSRV Automatic Actuation Logics were not affected under normal power. The valve's mechanical setpoints were unaffected by this event, and they remained capable of lifting. 8. For events that occurred when the reactor was shut down, availability of systems or components needed to shut down the reactor and maintain safe shutdown conditions, remove residual heat, control the release of radioactive material, or mitigate the consequences of an accident: This event did not occur when the reactor was shutdown. C. For failure that rendered a train of a safety system inoperable, an estimate of the elapsed time from discovery of the failure until the train was returned to service: While one ADS valve was inoperable for longer than permitted by TS, the ADS system itself remained operable throughout the duration of this event. Approximately one day elapsed between the time of discovery and returning the valve to service. VI. Corrective Actions: Corrective Actions are being managed by TVA's corrective action program under Condition Report (CR) 1161911. A. Immediate Corrective Actions A troubleshooting work order was initiated, which found a stab on the back of the MCC breaker cubicle that required adjustment. After adjusting the MCC bucket stab, the green light operated as designed. 8. Corrective Actions to Prevent Recurrence Corrective actions to prevent recurrence include determining the scope of MCC breakers that feed loads that have a normal and alternate power source. Preventative Maintenance Change Requests were initiated for these MCC Breakers to revise their maintenance PMs to verify PMT includes power source isolation prior to closing the breaker under load. Additionally, a work order will be generated to replace the breaker bus stabs. Finally, a Performance Analysis and Training Needs Analysis will be prepared to develop targeted needs that will close the apparent knowledge gap associated with the implementation of breaker PMT. NRC FORM 366A (11-2015) Page 7 of 7 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMS control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Browns Ferry Nuclear Plant, Unit 3 05000296 YEAR NUMBER NO. 2016 005 00 NARRATIVE VII. Additional Information: A. Previous Similar Events: There were no previous similar events. B. Additional Information: There is no additional information. C. Safety System Functional Failure Consideration: In accordance with NUREG-1022, this event is not considered a safety system functional failure. While one ADS valve was inoperable for longer than permitted by TS, the remaining five ADS valves remained operable throughout this event. D. Scram with Complications Consideration: This event did not result in a reactor scram. VIII. COMMITMENTS There are no new commitments. NRG FORM 366A (11-2015) | 06-17-2016 | On April 18, 2016, during a scheduled surveillance, the power to the Main Steam Line (MSL) B Relief Valve failed to transfer to its alternate feeder breaker when the normal feeder breaker was opened. The Automatic Depressurization System (ADS) function of the MSL B Relief Valve was declared inoperable. It was determined that the ADS valve was inoperable from March 26, 2016 to April 19, 2016. The valve's ability to open under normal power was not affected. Five of the six ADS valves remained operable. Only four ADS valves are required to meet the ADS function in the Loss of Coolant Analysis described in the Final Safety Accident Report. The unavailability of the ADS alternate power source was directly caused by a bus stab on the back of the Molded Case Circuit (MCC) breaker not fully engaging with the bus. This was apparently caused by improper performance of previous post-maintenance testing. The stab was adjusted, the MCC breaker was returned to service, and the MSL B Relief Valve's ADS function was declared operable upon verification of its alternate power supply. Corrective actions were to determine which load-feeding MCC breakers have a normal and alternate power source, and revise their preventative maintenance procedures to verify that post-maintenance testing includes power source isolation prior to closing the breaker under load. Breaker bus stabs will be replaced. NRG FORM 366A (11-2015) Page 2 of 7 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Browns Ferry Nuclear Plant, Unit 3 05000296 YEAR NUMBER NO. 2016 - 005 00 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Unit 3, was in Mode 1 at 100 percent power. II. Description of Events A. Event: On April 18, 2016, during a scheduled surveillance of the Automatic Depressurization System (ADS) [SB] Logic System, the power to the Main Steam Line (MSL)[SB] B Relief Valve [RV] (3-PCV-001-0022) failed to transfer to the alternate feeder breaker when the normal feeder breaker was opened. Operations subsequently declared the ADS function of the MSL B Relief Valve inoperable, and entered Technical Specification (TS) Limiting Condition of Operability (LCO) 3.5.1 Condition E, a 14 day shutdown LCO action statement. Troubleshooting determined that the bus stab on the back of the alternate feeder Molded Case Circuit (MCC) breaker [BKR] (3-BKR-001-0022A) was not properly engaged with the bus. The stab was adjusted, the MCC breaker was returned to service, and MSL B Relief Valve was verified to have proper power. The valve's ADS function was declared operable on April 19, 2016 at 1400 Central Daylight Time (CDT). Since the failure was discovered during surveillance testing, a past operability evaluation (POE) was performed to determine the duration of inoperability. The POE determined that the breaker was working properly until it was racked out for preventative maintenance (PM) performed during the previous Unit 3 refueling outage in March 2016. This failure went undetected due to improper post-maintenance testing (PMT). Prior to the outage, the associated breaker passed all required surveillances. The POE concluded that the time of inoperability began on March 26, 2016 at 2300 CDT and ended on April 19, 2016 at 1400 CDT. Since the BFN, Unit 3 ADS system only requires four of the six ADS valves to remain operable, the ADS system was operable throughout this entire event. MSL B Relief Valve actuation through the ADS or Main Steam Relief Valve (MSRV) Automatic Actuation Logics were not affected under normal power. The valve's mechanical setpoints were unaffected by this event, and they remained capable of lifting. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event: There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML16169A066
Nine Mile Point | Unit 2 | Secondary Containment Inoperable Due to Simultaneous Opening of Airlock Doors | 06-06-2016 | On April 7, 2016, at approximately 1730 hours, the secondary containment of the Nine Mile Point Unit 2 (NMP2) Reactor Building was breached when workers opened both inner and outer airlock doors, SA262-2 and SA262-3, simultaneously. The integrity of the airlock was re-established within 4 to 5 seconds when one of the doors was closed and latched. This resulted in a momentary loss of Secondary Containment Operability (TS 3.4.3). Secondary containment differential pressure never exceeded the minimum Technical Specification limit of 0.25 inch of vacuum water gauge. The causal analysis identified that the existing notice providing airlock door usage instructions is not effective in preventing doors being opened simultaneously in all situations. Corrective actions taken include revising the notice signage at all airlock doors to increase wait time from 5 seconds to 10 seconds to allow personnel traversing the airlock to exit. NMP2 has submitted LER 2014-007, Revision 1 for similar conditions. NRC FORM 366 (11-2015) ._.-- Page 2 of 5 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LEA) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150·0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Nine Mile Point Unit 2 05000-410 YEAR NUMBER NO. 2016 - 001 - 00 | I. DESCRIPTION OF EVENT A. PRE-EVENT PLANT CONDITIONS: Prior to the event, Nine Mile Point Unit 2 (NMP2) was in Mode 1 and operating at 100% reactor power. B. EVENT: On April 7, 2016, at approximately 1730 hours, the simultaneous opening of Reactor Building airlock doors resulted in a momentary loss of secondary containment safety function. NMP2 was in Mode 1 and operating at 100%. The incident occurred when individuals were attempting to utilize the Unit 2 outer South Auxiliary Bay airlock (doors SA262-2 and SA262-3) on elevation 261 from opposite directions. An Operator was entering the airlock from RP access into the Reactor Building through door SA262-3. The Operator carded in, opened door, and started to step into the airlock. Concurrently, two supplemental workforce personnel were exiting the Reactor Building to RP Access through door SA262-2. The breach of secondary containment was immediately realized and the supplemental workforce personnel immediately closed door SA262-2 without entering the airlock. The control room was contacted and in response to this condition, operators entered Technical Specification (TS) action statement 3.6.4.1, Condition C then promptly exited this action statement when the inner airlock door was closed. During the event, both the operator and the supplemental workforce personnel were attempting to utilize the airlock doors in accordance with the posted Notice. However, the requirement to wait 5 seconds to allow personnel who may be traversing to exit, does not reduce the chances of an event when personnel are attempting to enter the airlock from outside opposing airlock doors (not actually traversing). Nine Mile Point Unit 1 (NMP1) was unaffected by both airlock doors being open at NMP2. The event has been entered into the plant's corrective action program as IR 2652511. C. INOPERABLE STRUCTURES, COMPONENTS, OR SYSTEMS THAT CONTRIBUTED TO THE EVENT: No other systems, structures, or components contributed to this event. NRG FORM 366A (11-2015) o/ Page 3 of 5 | ML16172A020
Susquehanna Steam Electric Station | Unit 2 | Secondary Containment lnoperability due to Failure to Meet Surveillance Requirement 3.6.4.1.1 | 04-19-2016 | On April 19, 2016, at 2159 hours, Secondary Containment became inoperable, requiring an action of Technical Specification (TS) 3.6.4.1 to restore the system to an operable status in four hours. The TS 3.6.4.1 Condition A for an inoperable Secondary Containment was entered because Reactor Building (RB) Zone II differential pressure (dP) was below the required TS limit of>/= 0.25 inches of vacuum water gauge (in. w.g.), which does not meet the Surveillance Requirement (SR) 3.6.4.1.1. The Zone II supply system outside air (intake) louver XD-27586 was then adjusted and the Zone II dP returned to a steady 0.29 in. w.g. of vacuum, which was above the required TS limit. The TS 3.6.4.1, Condition A for inoperable Secondary Containment was exited at 2222 hours. The event was reported to the NRC on April20, 2016 in accordance with 10 CFR 50.72(b)(3)(v)(C) under Event Notification 51872, for the loss of a safety function. There is no redundant Secondary Containment system. This LER is being submitted in accordance with 10 CFR 50.73(a)(2)(v)(C), for an event or condition that could have prevented the fulfillment of the safety function of Secondary Containment to control the release of radioactive material. No actual consequences to the health and safety of the public occurred and this event will not be counted as a safety system functional failure (SSFF) for the NRC performance indicator. The cause of this event was determined to be less than adequate Operating Procedure instructions for the RB HVAC systems, for instructions that follow fan swaps. Planned corrective action includes revising Operating Procedure instructions for the Units 1 and 2 RB HVAC systems. NRC FORM 366 (11-2015) Page 2 of 4 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 11-2015) Estimated burden per response to comply with this mandala!)' collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to indusll)'. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatol)' Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and RegulaloJY Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR I SEQUENTIAL I REV Susquehanna Steam Electric Station, Unit 2 NUMBER NO. 05000388 2016 -003 -00 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 4, 0 percent Rated Thermal Power Unit 2 - Mode 1, 100 percent Rated Thermal Power There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. On April 19, at 1606 hours, supply and exhaust fan swaps were completed for the Reactor Building (RB) Heating Ventilation and Air Conditioning (HVAC) systems [EllS System Identifier: VA]. The fan swaps were associated with equipment maintaining Zone II of Secondary Containment (Unit 2 RB [EllS System Identifier: NG]). EVENT DESCRIPTION On April 19, 2016 at 2159 hours, Secondary Containment became inoperable, requiring an action of Technical Specification (TS) 3.6.4.1 to restore the system to an operable status in four hours. The TS 3.6.4.1, Condition A for an inoperable Secondary Containment was entered because RB Zone II differential pressure (dP) was below the required TS required limit of>/= 0.25 inches of vacuum water gauge (in. w.g.), which does not meet the Surveillance Requirement (SR) 3.6.4.1.1. The Zone II supply system outside air (intake) louver XD-27586 [EllS Identifier: LV] was then adjusted and the Zone II dP returned to a steady 0.29 in. w.g. of vacuum, which was above the required TS limit. The TS 3.6.4.1, Condition A for inoperable Secondary Containment was exited at 2222 hours. The event was reported to the NRC on April20, 2016 in accordance with 10 CFR 50.72(b)(3)(v)(C) under Event Notification 51872, and per the guidance of NUREG-1022, Revision 3, Section 3.2.7, for applicable reporting criteria on the loss of a safety function. There is no redundant Secondary Containment system. This LER is being submitted in accordance with 10 CFR 50.73(a)(2)(v)(C), for an event or condition that could have prevented the fulfillment of the safety function of Secondary Containment to control the release of radioactive material. NRC FORM 366 (11-2015) Page 3 of 4 | ML16172A177
Browns Ferry Nuclear Plant (BFN) | Unit 1 | Failure of 4kV Shutdown Board Normal Feeder Breaker Results in Actuations of Emergency Diesel Generators and Containment Isolation Valves | 06-21-2016 | On April 22, 2016, at 1358 Central Daylight Time (CDT), during transfer of the 4160 V (4kV) Shutdown Bus from Alternate to Normal, the Normal Feeder Breaker (BKR 1722) failed to close when the Alternate Feeder Breaker was manually tripped. 4kV SD Bus 2 de-energized, resulting in the loss of 1B and 2B Reactor Protection System (RPS) as well as Steam Jet Air Ejector 1B. Emergency Diesel Generators (EDG) C and D started, but did not tie to the 4kV Shutdown Boards due to Operations personnel immediately re-closing the Alternate breaker and re-energizing 4kV Shutdown Bus 2. Invalid actuations of several Containment Isolation Valves also occurred during this event due to the loss of RPS. At 1530 CDT, EDG C and D were shut down. BFN, Unit 1, was returned to normal operating conditions. The cause of this event was loose wires in the closing control circuit for BKR 1722 due to work in the vicinity of the control circuit termination points. Corrective actions were to terminate loose wires, using a ring type lug instead of a forked spade type lug, in the closing control circuit for BKR 1722; and to verify Shutdown Bus 2 transferred successfully to BKR 1722. A briefing was provided to Electrical personnel who perform modifications to discuss the potential consequences of installing tie wraps and performing other activities that could adversely affect existing wiring. NRC FORM 366A (11-2015) Page 2 of 6 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Browns Ferry Nuclear Plant, Unit 1 05000259 YEAR NUMBER NO. 2016 - 001 - 00 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Unit 1, was operating in Mode 1 at approximately 100 percent rated thermal power. BFN, Units 2 and 3, were unaffected by this event. A. Event: On April 22, 2016, at 1358 Central Daylight Time (CDT), during transfer of the 4160 V (4kV) Shutdown Bus [BU](SD Bus) from Alternate to Normal, the Normal Feeder Breaker BFN-0-BKR-211-000C/026 [BKR](BKR 1722) failed to close when the Alternate Feeder Breaker (BKR 1712) was manually tripped. 4kV SD Bus 2 de-energized, resulting in the loss of 1B and 2B Reactor Protection System [JC](RPS) as well as Steam Jet Air Ejector [EJR][SH](SJAE) 1B. Emergency Diesel Generators (EDG)[DG] C and D started, but did not tie to the 4kV Shutdown Boards (SD BD) due to Operations personnel immediately closing BKR 1712 and re-energizing 4kV SD Bus 2. Upon loss of 4kV SD Bus 2, Primary Containment Isolation System [JM](PCIS) Group 2 outboard valves [ISV] isolated and BFN, Unit 1, entered Technical Requirement Manual (TRM) Limiting Condition for Operation (LCO) 3.4.1 which requires sampling of reactor coolant conductivity every four hours. PCIS Group 3 Reactor Water Cleanup [CE](RWCU) and PCIS Group 6 isolated; BFN, Unit 1, entered Technical Specification (TS) LCO 3.4.5 Condition D and TRM LCO 3.3.10 with required action to enter TS LCO 3.0.3 immediately. Operations personnel entered Abnormal Operating Instructions 1-AOI-99-1 (Loss of Power to One RPS Bus), 1-AOI-57-5B (Loss of I&C Bus B), and 1-AOI-47-3 (Loss of Condenser Vacuum) [COND]. On April 22, 2016, at 1436 CDT, Operations personnel noted that Drywell to Suppression Chamber differential pressure was reading 0.95 pounds per square inch differential (psid). BFN, Unit 1, entered TS LCO 3.6.2.6 Condition A.1 which requires Drywell to Suppression Chamber differential pressure to be restored to greater than 1.1 psid within eight hours. Operations personnel returned BFN, Unit 1, to normal operating conditions and exited all TS LCOs, TRM LCOs, and AOIs. On April 22, 2016, at 1530 CDT, EDG C and D were shut down. On April 22, 2015, at 1722 CDT, Event Notification (EN) 51878 was made to the NRC in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.72(b)(3)(iv)(A). II. Description of Events B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event: No inoperable systems, structures, or components contributed to this event. | ML16173A251
Prairie Island Nuclear Generating Plant | Unit 1 | Missina Fire Barrier Between Fire Area (FA) 59 and 85/ Fire Hazard Analvsis Drawinas Do Not Match Boundarv Descriotion | 06-21-2016 | On April21, 2016, during a walkdown of fire barriers for the National Fire Protection Association (NFPA) 805 project, it was determined that the fire barrier between Fire Area (FA) 59 (Auxiliary Building Mezzanine Unit 1) and FA 85 (Holdup Tank/ Demineralizer Area) is not a rated barrier due to unsealed combustible pathway penetrations in the barrier. The walkdown also identified that penetrations in the fire barriers between FA 68 (Unit 1 Annulus) and FA 60 (Auxiliary Building Operating Level Unit 1) , FA 68 and FA 61A (Auxiliary Building Hatch Area), FA 72 (Unit 2 Annulus) and FA 75 (Auxiliary Building Operating Level Unit 2), and FA 72 and 61A are not sealed with fire rated materials. Both conditions were reported under 10 CFR 50. 73(a)(2)(ii)(B) as an unanalyzed condition that significantly degrades plant safety due to the missing fire barrier between redundant Appendix R safe shutdown trains. The apparent cause was determined to be that the Engineering Manual 3.4.2 does not require Appendix R program owner review of Fire Protection Engineering Evaluations that depend on Appendix R Safe Shutdown analysis. The corrective action is to revise the Engineering Manual 3.4.2 to require Appendix R review when the program is impacted. NRC FORM 366 (11-2015) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BYOMB: NO. 3150-0104 EXPIRES: 10/31/2018 11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LERNUMBER I YEAR I SEQUENTIAL REV Prairie Island Nuclear Generating Plant 05000-282 NUMBER NO. Unit 1 2016 -004 -00 | BACKGROUND The original Fire Hazards Analysis (FHA) was submitted to the NRC with drawings that show the walls (between Fire Area (FA) 59 & 85, 74 & 85, FA 68 & 60, FA 72 & 75, 68 & 61A, 72 & 61A) are fire area boundaries. [Northern States Power (NSP)-NRC Fire Hazards Analysis report dated March 11, 1977] Sections 3.1.1 (2) through (4) of the Fire Protection Safety Evaluation Report (SER) require fire barrier modifications to upgrade penetration seals in various plant areas, to install qualified seal designs in the future, and to replace or modify existing seals which contain polyurethane foam. [NRC Safety Evaluation Report dated September 6, 1979] In response to the requirements above from the September 6, 1979, NRC SER, NSP committed to review and upgrade seals as necessary, to use 3-hour rated seal designs for new seals and to upgrade seals in specific areas. Among the areas listed were the Elevation 735' Auxiliary Building barriers shared with Turbine Building and Hatch Area (FA 61) barriers shared with parts of the Auxiliary Building. The barriers that are the subject of this event were not included in the list of areas where seals would be upgraded. The details of the penetration seal upgrades laid out in the November 30, 1979, letter was accepted in NRC SER dated April21, 1980. [NSP letter to the NRC dated November 30, 1979; NRC Safety Evaluation Report dated April21, 1980] Revision 12 to the FHA updated the FHA Boundary drawings to reflect boundaries discussed in licensing correspondence and the results of the Safe Shutdown Analysis (GEN-PI-026 Rev.1 dated December 15, 1997, and F5 App E Rev. 4). The FHA drawings were updated to remove and add Appendix R barriers. The barriers between FA 59 & 85, FA 74 & 85, FA 68 & 60, FA 72 & 75, FA 68 & 61A and FA 72 & 61A were not addressed in the FHA or Safety Evaluation 502. [Safety Evaluation (SE) 502, F5 Appendix F Rev.12- Fire Hazards Analysis dated March 12, 1999] On August 16, 2012, Fire Protection Engineering Evaluation (FPEE) 12-006 Rev. 1 was completed. The FPEE evaluated the fire area boundaries between FA 85 and FA 59. The evaluation concludes that the fire area boundary is not required for separation of safe shutdown equipment therefore the barrier is acceptable as is. The safe shutdown analysis section of the FPEE states, "All the cabling for required equipment in FA 85, except for CV- 31198, is also routed in FA 59. FA 59 does not contain cabling for the component redundant to CV-31198. As such, fire safe shutdown capability is identical between FA 59 and FA 85 for the identified components and there is no impact on fire safe shutdown capability should a fire spread between FA 59 and FA 85." The methodology used to justify the condition was inappropriate because it considered availability of safe shutdown components in the fire area instead of availability of the entire safe shutdown train. The evaluation was prepared in accordance with Engineering Manual 3.4.2 which provides guidelines for completing FPEEs in accordance with NRC Generic Letter 86-10. The preparer and reviewer were assigned in accordance with the procedure which does not require an Appendix R program owner to review FPEEs. An Appendix R program owner review would have identified that the evaluation was not consistent with the Appendix R Safe Shutdown Analysis. [FPEE 12-006; AR 1311038-03 Evaluate change to F5 App K barrier] NRC FORM 366 (11-2015) | ML16173A434
Quad Cities Nuclear Power Station | Unit 2 | High Pressure Coolant Injection System Declared Inoperable Due to Valve Packing Leak | 06-24-2016 | On April 25, 2016, at 06:07 hours, the High Pressure Coolant Injection (HPCI) System was isolated to stop a packing leak on the Motor Operated (MO) HPCI Outboard Main Steam Isolation Valve (MO 2-2301-5). The packing leak was causing a two (2) foot steam plume to impinge on the valve limit switch compartment, potentially impacting the motor operator for the MO 2-2301-5 valve. Due to the uncertainty on how the steam impingement would affect the valve limit switch compartment, Operations conservatively isolated the steam leak by closing the HPCI Inboard Main Steam Isolation Valve (MO 2-2301-4). With the steam supply isolated, HPCI was declared inoperable and Technical Specification (TS) 3.5.1 Condition G was entered. The cause of the packing leak was a non-modern style packing installed in 2007 to repack valve MO 2-2301-5. This packing material was susceptible to premature degradation. Corrective actions included repacking the valve with modern packing and performance of valve diagnostic testing. The safety significance of this event was minimal. Given the impact on the HPCI system, this report is submitted for Unit 2 in accordance with the requirements of 10 CFR 50.73 (a)(2)(v)(D), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information LICENSEE EVENT REPORT (LER) Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of CONTINUATION SHEET Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 6. LEA NUMBER I 3. PAGE YEAR I ::>t:UUt:l'l I IAL REV NO. Quad Cities Nuclear Power Station Unit 2 NUMBER 2 OF 5 05000265 2016 002 00 | PLANT AND SYSTEM IDENTIFICATION General Electric -Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX]. EVENT IDENTIFICATION High Pressure Coolant Injection System Declared Inoperable Due to Valve Packing Leak A. CONDITION PRIOR TO EVENT Unit: 2 Event Date: April 25, 2016 Event Time: 06:07 hours Reactor Mode: 1 Mode Name: Power Operation Power Level: 100% B. DESCRIPTION OF EVENT On April 25, 2016 at 04:50, while performing Reactor Building basement rounds, an Equipment Operator (EO) identified a small puddle of water in Bay 2 of the Unit 2 Torus area with water actively leaking from the overhead area at 2 drops per minute (dpm). An additional, much larger, puddle was discovered in Bay 3 with approximately 15 dpm leaking from the overhead area. A second EO was dispatched to the top of the Unit 2 Torus to inspect for leaks. The EO on top of the Torus reported a two foot steam plume coming from the packing of the MO 2-2301-5, Unit 2 HPCI Outboard Main Steam Isolation Valve. It was noted that the steam was impinging on the MO 2-2301-5 limit switch compartment, but not directly on any other components. At 06:07, Operations isolated the identified steam leak by closing the MO 2-2301-4, Unit 2 HPCI Inboard Main Steam Isolation Valve. Operations declared Unit 2 HPCI inoperable and unavailable at this time and entered TS 3.5.1 Condition G. At 12:05, Operations closed the MO 2-2301-5 valve as part of the Clearance Order (CO) boundary. The valve closed as expected and no ground alarms were received. At 12:39, ENS #51880 was made to the NRC under 10 CFR 50.72(b)(3)(v)(D) to report this event as an event or condition that could have prevented the fulfillment of a safety function. On April 27, 2016 at 05:44, after repacking the valve with a modern packing set (AP Services 6000/6300J) and diagnostic testing, Unit 2 HPCI was returned to the standby line-up and declared operable; TS LCO 3.5.1 Condition G was exited. C. CAUSE OF EVENT Non-modern style packing (Crane 387-1) was used in 2007 to repack the MO 2-2301-5 valve. This packing material wa~ susceptible to premature degradation and hardening. At the time of installation, the long term temperature effects on Crane 387-1 packing were not yet discovered. Crane 387-1 (non-modern style) packing has a history of drying out and becoming very hard. This typically happens when Crane 387-1 packing is used in high temperature and pressure systems. The materials used in this pac~ing are | ML16183A262
Oyster Creek | Unit 1 | Manual SCRAM Inserted due to Leakage from the 'D' Reactor Recirculation Pump Seal | 06-29-2016 | On April 30, 2016, at 1804 hours, during the plant startup following the 1M 38 maintenance outage, a reactor SCRAM was manually inserted by the Control Room Operators during post maintenance testing following work on the 'D' Reactor Recirculation Pump (RRP) mechanical seal. The SCRAM was initiated since leakage was discovered by a rising trend in drywell unidentified leakage during plant startup. The seal had been replaced during the maintenance outage. The SCRAM was selected as the preferred method of shutting down the reactor due to low decay heat conditions following the outage. ENS 51895 was submitted on April 30, 2016, as required by 10 CFR 50.72 (b)(2)(iv)(B). This issue is reportable under 10 CFR 50. 73(a)(2)(iv)(A), for any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph 1O CFR 50. 73(a)(2)(iv)(B). NRG FORM 366 (11-2015) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 01/31/2017 (01-2014) .. Estimated burden per response to comply with this mandatoiy collection request: BO hours . ~oY·°'~ Reported lessons learned are incorporated into the licensing process and fed back to industry. ~ Send comments regarding burden estimate to the FOIA, Privacy and Information Collections ~. .l Branch (T-5 F53), U.S. Nuclear Regulatoiy Commission, Washington, DC 20555-0001, or by ····· LICENSEE EVENT REPORT (LER) internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatoiy Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, CONTINUATION SHEET Washington, DC 20503. If a means used to impose an information collection does not display a currenijy valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 6. LER NUMBER 3. PAGE I YEAR I SE N Q U U M EN BE T R IA L REV NO. Oyster Creek, Unit 1 05000219 2 OF 3 2015 002 00 | Description of Event On April 30, 2016, during the plant startup from 1 M38 at approximately 1422 hours, the station identified a rise in Unidentified Leak Rate (UILR). UILR rose from 0.21 gpm to 1.62 gpm at 1545 hours. During this time reactor pressure was increased from 335 psi to 450 psi. As part of the troubleshooting for the unexpected rise in UILR, inspections in the drywell were performed and identified primary coolant leaking from the pump 'Shaft of the 'D' · Reactor Recirculation pump (RRP). At 1804 hours, Control Room Operators initiated a manual SCRAM of the reactor to place the plant in a safe condition due to the leakage ori the 'D' RRP. Assessment of Safety Consequences Following the manual SCRAM actuation, all systems responded as expected; therefore, this event is of low safety significance. Cause of Event In mid- 2015, unidentified drywell leak rate along with temperature and pressure trends on the 'D' RRP indicated degradation of the pump seal. The leakage was monitored for several months and remained within the limitations delineated by the Station's Technical Specifications {TS). In order to ensure that the condition did not degrade further, a maintenance outage (1 M38) was scheduled to commence on April 25, 2016, with the replacement of the 'D' RRP seal as the main focus of the scope of work. During 1 M38 on April 27, 2016, the old 'D' RRP seal was removed and the new replacement seal was installed. During the installation, the technicians discovered that the pump coupling could not be installed because it was too tall to fit onto the seal. The pump vendor then recommended machining the coupling and that minor machining is part of the normal fit-up process when installing new seal components. Additionally, the pump installation procedure specifically states that machining of up to 0.060" is permitted. Engineering prepared, approved and issued a technical evaluation to maintenance to machine the coupling to 0.060". The backing ring functions as a keeper for the 0-ring on. the shaft sleeve. Following this machining, the coupling fit and reassembly of the pump was completed. Following completion of the maintenance work on the 'D' RRP and during the startup from 1 M38, Control Room Operators identified a rising trend in UILR. UILR rose from 0.21 gpm to 1.62 gpm as reactor pressure was increased from 335 psi to 450 psi. Inspections conducted inside the drywall, identified primary coolant leaking from around the pump shaft of the 'D' RRP. At 1804 hours, a manual SCRAM of the reactor was initiated to place the ~plant in a safe condition due to the leakage on the 'D' RRP. Following the SCRAM and during the disassembly of the 'D' RRP, when removing the pump half coupling keys the shaft sleeve 0-ring was found extruding on top of the back-up ring. Upon further disassembly the 0-ring was found to be cut, and an approximately one-inch piece of the 0-ring was found sitting on top of the back-up ring, which lead to the leakage from the seal cavity. The Root Cause of the event was determined to be that the seal rebuild procedure was not properly revised in 2012 to prevent this failure from occurring. Corrective Actions NRG FORM 366A (01-2014) | ML16187A322
Cooper Nuclear Station 05000298 1of4 | Unknown Unit | De-Energized High Pressure Coolant Injection Auxiliary Lube Oil Pump Caused By Light Bulb Failure Results in Loss of Safety Function | 06-27-2016 | On April 26, 2016, it was noted that the green off light for High Pressure Coolant Injection (HPCI) auxiliary lube oil pump (ALOP) in the Control Room, was not illuminated. A non-licensed operator was dispatched to the HPCI ALOP starter and reported the green bulb appeared to have shattered in the socket. HPCI was declared inoperable at 1754 Central Daylight Time (CDT) resulting in entry into Technical Specifications Limiting Condition of Operation 3.5.1, Condition C, HPCI System Inoperable. Investigation found the 125 volts direct current fuse open circuited and the local indication green light and socket were damaged. The cause of the failure was determined to be a lack of engineering knowledge which led to a design change in 1984 in the HPCI ALOP starter circuitry that diminished the robustness of the circuit with respect to a specific failure modality; direct short circuiting within the indication bulb itself. The HPCI system was restored to operable status on April 28, 2016, at 1245 CDT. This event is being reported as a loss of safety function due to HPCI being a single-train safety system. The potential safety consequences of this event were minimal due to the limited duration the condition existed and the redundant/diverse core cooling systems which remained operable. Page 2of4 APPROVED BYOMB: NO. 3150-0104 EXPIRES: 10/31/2018 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION Estimated burden per response to comply with this mandatory collection request: 80 hours. (11-2015) Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch l"'"~ (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e \~) LICENSEE EVENT REPORT (LER) mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a "'····· CONTINUATION SHEET means used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Cooper Nuclear Station 05000- 298 2016 -002 -00 | PLANT STATUS Cooper Nuclear Station (CNS) was in Mode 1, Power Operation, at 100 percent, steady-state power at the time the condition was identified. Service Water Pump "B" and Service Water Booster Pump "B" were inoperable when HPCI (High Pressure Coolant Injection) was inoperable. No other emergency core cooling systems were inoperable during the event. BACKGROUND The HPCI System (EllS:BJ) provides protection to the core for the case of a small break in th~; reactor coolant pressure boundary which does not result in rapid depressurization of the reactor vessel. (EllS:RPV). The HPCI System permits the nuclear piant to be shutdown while maintaining sufficient reactor vessel water inventory until the reactor vessel is depressurized. The HPCI System continues to operate until reactor vessel pressure is below the pressure at which Low Pressure Coolant Injection (EllS:BO) operation or Core Spray System (EllS:BM) operation can be used to maintain core cooling. HPCI consists of a steam turbine assembly (EllS:TRB) driving a multi-stage booster and main pump ... .....; assembly (EllS:P) and system piping, valves, controls and instrumentation. The HPCI turbine is driven -;:=''· by steam from the reactor which is generated by decay and residual heat. ..:'-t, A control governor (EllS:65) receives a HPCI flow signal and adjusts the turbine steam controf'yalve (EllS:SCV) so that HPCI design pump discharge flow rate is obtained. The flow signal usedfor automatic control of the turbine is derived from a differential pressure measurement across a 'flow element (EllS:FE) in the HPCI pump discharge pipeline. The governor controls the pressure applied to the hydraulic operator of the turbine control valve, which, in turn, controls the steam flow to the turbine. Upon receipt of the actuation signal, the auxiliary oil pump starts, providing hydraulic pressure for the turbine stop valve and turbine control valve hydraulic operator. The flow signal will ramp the control governor until rated flow is achieved. As hydraulic oil pressure is developed, the turbine stop valve and the turbine control valve open simultaneously and the turbine accelerates toward the speed setting of the control governor. As HPCI flow increases, the flow signal adjusts the control governor setting so that design flow is maintained. EVENT DESCRIPTION On April 26, 2016, while performing a walkdown of Control Room panels, it was noted that the green off light for HPCI auxiliary lube oil pump (ALOP) was not illuminated. The bulb was replaced and the replacement bulb did not illuminate. A non-licensed operator was dispatched to the HPCI ALOP starter and reported the green bulb was broken and appeared to have shattered in the socket. An attempt was made to start the ALOP with the control switch and the pump did not start. The ALOP is required to start in order to open the steam admission valves for the HPCI turbine.The HPCI system was declared inoperable at 1754 Central Daylight Time (CDT) resulting in entry into Technical Specifications (TS) Limiting Condition of Operation 3.5.1, Condition C, HPCI System Inoperable. NRC FORM 366 (11-2015) Page 3of4 APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 NRC F0RM 366A U.S. NUCLEAR REGULATORY COMMISSION Estimated burden per response to comply with this mandatory collection request: 80 hours. (11-2015) Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch \...¥........).1 \. (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e LICENSEE EVENT REPORT (LER) mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a ••••• CONTINUATION SHEET means used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Cooper Nuclear Station 05000- 298 2016 -002 -00 NARRATIVE Investigation found the 125 volts direct current (VDC) fuse open circuited and the local indication green light and socket were damaged. The green bulb and socket were replaced as well as the red bulb. The 125 VDC fuses were also replaced. The HPCI system was restored to operable status on April 28, 2016, at 1245 CDT after post work testing had been satisfactorily completed. Examination of the local green indication bulb and socket, and a review of the circuit schematic found that the light did not have a dropping resistor. In this circuit, a dropping resistor helps prevent the fuse in the HPCI ALOP control circuit from opening by limiting current in the indication bulb side of the circuit if a short circuit in the bulb were to occur. .. The original HPCI starter circuit utilized a local indication light with a dropping resistor. The cir.cuit was modified in 1984 by the vendor to accommodate environmental requirements. A direct voltage light and socket were substituted for the dropping resistor and light combination. Consequently, if the indication light were to short it would open circuit the 125 VDC portion of the starter circuit. The commercial grade bulb that failed was a 3 watt bulb with a 120MB base style. BASIS FOR REPORT .. ·, : The HPCI System is a single train safety system. This condition is reportable in accordance with 10 --'\~ CFR 50. 73(a)(2)(v) as "any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to ... (D) Mitigate the consequences of an ~~cident." The event was reported as Event Notification Number 51886. SAFETY SIGNIFICANCE This is a Safety System Functional Failure. There were no actual safety consequences associated with this event. The potential safety consequences of this event were minimal due to the limited duration the condition existed and the redundant/diverse core cooling systems which remained operable. The HPCI ALOP performance had been previously tested satisfactory at 1312 CDT on the day of the failure. The HPCI system is an emergency core cooling system designed to inject water into the reactor vessel to provide core cooling. The total duration of inoperability, including the time prior to discovery of the condition was less than the 14 day Technical Specification Completion Time. During the time period of inoperability, other core cooling systems (Automatic Depressurization System, Core Spray, and Low Pressure Coolant Injection) were operable and would have adequately responded to a design basis event. The Reactor Core Isolation Cooling system was also operable during this event. CAUSE A lack of engineering knowledge led to a design change in 1984 in the HPCI ALOP starter circuitry that diminished the robustness of the circuit with respect to a specific failure modality; direct short circuiting within the indication bulb itself. NRC FORM 366 (11-2015) Page 4of4 APPROVED BYOMB: NO. 3150-0104 EXPIRES: 10/31/2018 | ML16190A112
Susquehanna Steam Electric Station | Unit 2 | Unit 2 HPCI Manually Overridden Prior to a Manual Scram During a Plant Transient | 01-02-2016 | On 5/13/2016 at 0055, the Unit 2 Unit Supervisor directed manually overriding High Pressure Coolant Injection HPCI (HPCI) immediately prior to a manual scram during a plant transient. [This event is being reported under 10 CFR 50. 73(a)(2)(v) [There were two causes of this event. First, the Unit Supervisor made a decision to prematurely override HPCI o minimize distractions later in the shutdown without procedural guidance to do so. Second, weaknesses in eamwork and oversight prevented the mistake from being corrected by the crew. Immediate corrective actions include removing qualifications from the individuals involved and communicating expectations with the remaining crews. Additional corrective actions being taken include incorporating this event into initial licensed operator training and a Human Performance Improvement Plan will be created to address gap noted in the crew's performance. NRC FORM 366 (11-2015) Page 2 of 3 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150·0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER I I YEAR SEQUENTIAL REV Susquehanna Steam Electric Station, Unit 2 NUMBER NO. 05000388 2016 -005 -00 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, 10 0 percent Rated Thermal Power Unit 2- Mode 1, 069 percent Rated Thermal Power At 23:55 on 5/12/16, Unit 2 experienced an electrical transient resulting in a loss of 2B246 Reactor Building Engineered Safeguard System (ESS) Division 480 volt Motor Control Center (MCC) (EllS: B) and 2Y246 208/120 Volt Alternate Current (AC) Instrument Panel (EIIS:JL). With the loss of the Reactor Building ESS Division 480 volt MCC, several drywell cooling fans were lost leading to an increase in drywell pressure. EVENT DESCRIPTION On 5/12/16 at 2355, Unit 2 experienced an electrical transient caused by a loss of 480VAC MCC 2B246 breaker. Operations reduced reactor power by reducing reactor recirculation flow. Drywell pressure and temperature began to rise and it was reported by Maintenance that the 2B246 bus faulted and was not able to be re-energized. Operations determined that a manual scram was required based upon a loss of drywell cooling. On 5/23/2016 at 0055 HPCI (EllS code: BJ) was overridden prior to the manual scram to prevent the trip of all feedwater pumps on reactor pressure vessel high water level alarm (EllS: JB). Technical specification 3.5.1 was entered for HPCI inoperable due to manual override. At 0110, Unit 2 was manually scrammed and HPCI was restored to AUTO at 0122. The Unit Supervisor directed the override of HPCI without following station procedures which require adequate core cooling to be assured by at least two independent indicators. The Reactor Operator at the HPCI controls did not question the Unit Supervisor's decision. The Unit 2 scram event will be addressed under LER 388/ 2016-004-00. CAUSE OF EVENT There were two causes of this event. First, the Unit Supervisor made a decision to prematurely override HPCI to minimize distractions later in the shutdown without procedural guidance to do so. OP-AD-300, Administration of Operations, provides direction for overriding ECCS systems and clearly defines when such a system may be placed in manual. This procedure was not followed. Second, weaknesses in teamwork and oversight prevented the mistake from being corrected by the crew. A crew update was not conducted to announce the placing of HPCI in manual override, preventing the crew from providing a peer check of the Unit Supervisor's decision. NRC FORM 366 (11-2015) Page 3 of 3 | ML16194A251
rPAGE | Unknown Unit | Grouo I Isolation Received Durina Turbine Testing | 07-13-2016 | On May 23,2016, at 1009 EDT, while personnel were performing turbine testing with Unit 2 offline for planned maintenance, an event resulted in the actuation of containment isolation valves in more than one system. In response to this unexpected signal, 2821-F016 (Steam Line Drain Line Inboard Isolation Valve), 2821-F019 (Steam Line Drain Line Outboard Isolation Valve), and 2831-F019 (Reactor Water Sample Inboard Isolation Valve) went closed, all of which are primary containment isolation valves actuated by Group !Isolation. The Group I Isolation signal initiated based on low condenser vacuum during the turbine testing procedure, a valid condition for actuation that was expected to have been bypassed in the logic during the performance of this procedure. Inadequate procedure usage caused these systems to actuate in a way that was not part of the planned evolution. Although the Unit was shut down when this signal was received, and primary containment isolation was not required to mitigate the consequences of an event, this isolation signal has been determined to have been valid due to the initiation in response to actual plant conditions or parameters which satisfy the requirements for initiation of the system As a corrective action, the operating procedure will be revised to clarify the required conditions to perform Turbine Trip Testing. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMS: NO. 3150..0104 EXPIRES: 1al3112018 11·2015) Eslimaled bunfen per response to comply with this mandatory collection request 80 hauls. Reponed le$sons teamed are incorp018ted iniO the licansing process and lad back to industry. Send convneniS regardng burden estimate to the FOIA. Privacy and lntormation Colledions Branch IT-S F53). U.S. Nuclear Rl!glllatory Convnission, Waslington, DC 2055S-0001, or by inlemet e-mai to LICENSEE EVENT REPORT (LER) lnfocolltcts.ResourceOnrc.gov, and to the Desk Officer, Office ci lnlonnation and R~IOiy Affairs. CONTINUATION SHEET NEOB-10202, (3150-0tQ.4), Office ol Management and Budge~ Washington. OC 20503. II a means U5ed to impose an inlonnalion collection does not dsplay a currently valid OMB oontrol number, the NRC may not oonduct or sponsor, and a person is nOI required to respond to, the inlonnation collection. 1. FACIUTY NAME 2. DOCKET NUMBER 3. LERNUMBER I I YEAR SEQUENTIAL REV Edwin I. Hatch Nuclear Plant Unit 2 NUMBER NO. 05000-366 2016 -002 -00 | PLANT AND SYSTEM IDENTIFICATION General Electric-Boiling Water Reactor (BWR) Energy Industry Identification System codes appear in the text as (EllS Code XX) DESCRIPTION OF EVENT On May 23,2016, at 1009 EDT, with Unit 2 at zero percent rated thermal power, a full Group I Isolation signal was received during the performance of a turbine operability test [EllS Code TA; Main Turbine System]. In response to this unexpected signal, 2B21-F016 (Steam Line Drain Line Inboard Isolation Valve), 2B21-F019 (Steam Line Drain Line Outboard Isolation Valve), and 2B31-F019 (Reactor Water Sample Inboard Isolation Valve) [EllS Code TF; Turbine Drains and Miscellaneous Piping System] went closed. The turbine testing evolution was stopped and investigation commenced to determine the cause of the Group I isolation. Investigation revealed the Condenser Low Vacuum trip was not bypassed as expected prior to the test performance per the Turbine Testing Trip Overrides and Valve Stroking procedure. There were no inoperable structures, systems, or components (SSCs) which contributed to this event. CAUSE OF EVENT The cause of the actuation of the Group I isolation signal during Turbine Testing was due to inadequate procedure usage. Poor communications between maintenance and operations personnel resulted in false assumptions that the Group I isolation trips were bypassed. Causal factors included procedure weaknesses which resulted in improper interpretation of critical steps. CORRECTIVE ACTIONS Immediately following the Group I isolation, Turbine Testing was halted. The operating procedure is being revised to clarify the required conditions to perform Turbine Trip Testing. Lessons learned were communicated among the Operations department. Additional training and qualification actions were taken to address the human performance aspects of this event. NRC FORM 386A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150.0104 EXPIRES: 1013112018 11·2015) Eslimaled burden per response 10 comply with !his manda!Oiy collection request: 80 hours. Repolled ............." - IIISSOilS leamed are incorporaled into lhe licensing process and fed back to indusby. Send \¥) commeniS regarding burden estimate lo lhe FOIA. Privacy and lnf0111131ion Cdledions Branch (T·S ..... F53), U.S. Nuclear RagulaiOI'f Commission, Wuhinglon, DC 20555-0001, or by inlemel e-mail to LICENSEE EVENT REPORT (LEA) lnfocdii!CIS.ResouroeOnrc.gav, and lo the Desk Officer, Office of Information and Regula!ory Alfairs, CONTINUATION SHEET NEOB·10202, (3150-0104), Office of Management and Budgel Washington, DC 20503. II a 11181115 used lo impose an information collection does not display a CUIIllndy valid OMB c:ontro1 number, !he NRC may nOI condue1 or sponsor, and a person is nol required lo respond to, lhe lnformalion collldion. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER J I YEAR SEQUENTIAL REV Edwin I. Hatch Nuclear Plant Unit 2 NUMBER NO. 05000-366 2016 -002 -00 NARRATIVE REPORT ABILITY ANALYSIS AND SAFETY ASSESSMENT This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in automatic actuation of general containment isolation signals affecting containment isolation valves in more than one system or multiple main steam isolation valves (MSIVs). This isolation signal was valid in response to actual plant conditions induced by testing, and impacted isolation valves in the Nuclear Boiler System and the Reactor Recirculation System. This turbine testing was being conducted with the reactor offline when the drywall was open for maintenance activities. The received Group I isolation signal was valid due to conditions measured by the appropriate instruments, however the isolation was not necessary to protect against an actual radiological event in progress. The main steam isolation valves were already closed prior to the start of the testing. Based on this information this reported condition had low safety consequence. ADDITIONAL INFORMATION Other Systems Affected: Isolation valves in the Nuclear Boiler System and the Reactor Recirculation System automatically went closed. Failed Components Information: None. Commitment Information: This report does not created any new licensing commitments. Previous Similar Events: LEA 2009-005-0 On May 15, 2009 at 05:19 EDT, Unit I was in the cold shutdown mode with reactor power at 0 CMWT. At that time a Group I isolation signal on actual low condenser vacuum was generated when Operations personnel moved the reactor mode switch to the run position per subsection 7.1 of special purpose procedure 42SP-05-1209-PI-I-I. "Test of Nuclear Instrumentation Response to Diverse Logic System Actuations." Because the Main Steam Isolation Valves (MSIVs) were open at the time the Group I isolation signal was generated, they closed per design resulting in a reactor scram trip signal on MSIVs less than 90 percent open with the mode switch in the run position. Since the unit was in the cold shutdown condition at the time of the event, all controls rods were already inserted fully and therefore no rod motion occurred. However, the Main Steam Line Drain and Reactor Water Sample Line isolation valves also closed per design on the Group I isolation signal. Operations personnel returned the reactor mode switch to the shutdown position and reset the isolation and scram signals. Operations personnel left the MSIVs in the closed position. This event was caused by a personnel error resulting in the development of an inadequate procedure. The cause was that the test procedure was developed without the necessary steps to defeat the lower condenser vacuum isolation logic. The event in May 2016 was due to human performance of not following a procedure as written; therefore, the corrective actions from the 2009 event would not be expected to have prevented the condition reported in this LEA. | ML16196A350
i | Unknown Unit | Emergency Diesel Generator Manual Start Due to Loss of Voltage on the 6.9kV Shutdown Board 1B-B | 07-15-2016 | On May 17,2016, at 1630 hours while restoring from a plant modification related to installation of new protective relays designed to detect open phase conditions on the 6.gkv shutdown boards, the feeder breakers for the 6.9kV Shutdown Board 1B-B tripped resulting in a loss of bus voltage. The feeder breakers tripped due to actuation of the loss of voltage relays in the shutdown board protective relay trip logic circuit resulting in separation of offsite power from the 6.9kV Shutdown Board 'lB-8. The 1B-B emergency diesel generator did not auto start during this event because it was out of service due to planned maintenance. ln response to the loss of power on the 6.9kV Shutdown Board 1B-B, the operators immediately entered Abnormal Operating lnstruction, 0-A0143.02, Loss of Unit 1 Train B Shutdown Boards, and manually started emergency diesel generators 1A-4, 2A-A, and 2B-8. Allequipment operated properly. The emergency dieselgenerators were not required to be paralleled to their respective boards because offsite power was available. Offsite power was restored to the 6.9kV Shutdown Board 1B-B at 1802 hours on May '17,2016. Event Notification 51 940 was issued May 17 , 2016. This event is being reported pursuant to 1 0 CFR 50.73(aX2Xiv)(A). NRC FORM 365 (1 1-201s) Paaoe 2 oof 6 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 1013112018 (1 1-2015) Estimated burden per response to comply with his mandatory collection request 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send ' - a 3 , 4 { i * i r ',, . f - ^ r ; , 'o * I " . t , 6 . I :o o r , ^ i - L TcENSEE EVENr REpoRT (LER) c F ln o 5 f m o 3 c ) m , o e l U le n . c B S t s . . r R N eg e u a s c o r le d u a i r n r c g e R @ b e u n g r r u d c l e . a g n t o o v r e y , s ti C a m n o a d m t e m t o i t s o t s h i t e o h n e D , e F W s 0 k a ! A s ff h , i i c n P e g ri t r v o , a n c , O y f D f a c C n e d 2 o 0 l f n 5 l f n 5 o f 5 r o m - r 0 m a 0 t a 0 io t 1 i n o , n C o r a o n l b le d y c R t i i n o e t n g e u s r l n a B e to t r r a y e n - c m A h f f a a ( i i T l r s - t 5 , o CONTINUATION SHEET NE0&10202, (315O0104), Ofice of Management and Budget, Washington, DC 20503. lf a means used to impose an information oollection does not display a cunently valid OMB confol number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Watts Bar Nuclear Plant, Units 1 and 2 05000390 NUMBER NO. - -00 2016 008 | t. PLANT OPERATING CONDITIONS BEFORE THE EVENT Watts Bar Nuclear Plant (WBN) Unit 1 was in Mode 1 at 100 percent rated thermal power. Unit 2 was in Mode 3 at zero percent rated thermal power. il. DESCRIPTION OF EVENT A. Event On May 17 ,2016, a clearance was issued in preparation of installing new protective relays designed to detect open phase (OP) conditions on the 6.9 kV Shutdown Board 1B-B {EllS:BU}, which is part of the on- site electrical distribution system [EllS:EA]. The work scope required that the OP relays {EllS:46} be tied in parallel with the existing loss of voltage (LOV), degraded voltage (DV), and overvoltage (OV) relays. The OP relays, including the LOV, DV, and the OV relays are electronic relays that sense the 3 phase 6.9kV bus voltage through a common step down potentialtransformer (PT). The electronic relays require dc power to operate. This power is provided by the vital dc control circuit which is the same power supply that is used to energize the protective relay trip logic circuit for the 6.9kV Shutdown Board 1B-B. Upon completion of work, the 6.9kV Shutdown Board 1B-B clearance was approved for removal. During restoration of dc control power, it was noted that the B-phase relays for the LOV (phase B-C), DV (phase B- C) and OV (phase A-C), did not reset while the other relays did. After trouble shooting, the decision was made to pull PK Test Block 1-PK-211-81714 to isolate the ac sensing voltage from the newly installed OP relays and eliminate any associated wiring as a possible cause for inability to reset the above relays. The PK test block is an isolation device for disconnecting the new OP relays from the PT secondary circuit. Upon removal of the PK test block at 1630, the 6.9kV Shutdown Board 1B-B immediately de-energized. The loss of power was caused by the LOV relays that initiate the trip sequence to separate offsite power from the 6.9kV Shutdown Board. The 1B-B emergency diesel generator (EDG) did not auto start during this event because it was out of service due to planned maintenance. ln response to the loss of power on the 6.9kV Shutdown Board 1B-8, the operators immediately entered Technical Specifications (TS) Limiting Condition of Operation (LCO) 3.8.9, Distribution System - Operating, Action Condition A. The operators also entered Abnormal Operating lnstruction, 0-AOl 43.02, Loss of Unit 1 Train B Shutdown Boards, and manually started EDGs 1A-A, 2A-A, and 2B-8. All equipment operated properly. The EDGs were not required to be paralleled to the boards because offsite power was available. Offsite power was restored to the 6.9kV Shutdown Board 1B-B at 1802 hours on May 17, 2016. This event is being reported pursuant to 10 CFR 50.73(aX2Xiv)(A),for any event or condition that resulted in manual or automatic actuation of the emergency ac electrical power system as listed in 10 CFR 50.73(aX2Xiv)(B), paragraph (8). B. lnoperable Structures, Components, or Systems that Contributed to the Event There were no additional structures, components or systems that contributed to this event. | ML16197A556
Clinton Power Station | Unit 1 | Main Steam Line Flexible Hose lntergranular Stress Corrosion Cracking Identified During Refueling Outage | 07-15-2016 | On May 17, 2016 with the plant in Mode 4 during Refueling Outage C1R16 personnel entered the drywell to perform a system walkdown. At 0945 CDT water was identified leaking from flexible hoses located at the inner elbows of main steam line (MSL) B and MSL C. It was determined that the leakage was from the flexible hoses associated with the MSL flow instrumentation. The degraded flexible hose on MSL B was previously replaced in 2008 and on MSL C in 2007. An analysis determined the failure mechanism of the degraded flexible hoses as lntergranular Stress Corrosion Cracking (IGSCC). Main Steam Line C flexible hose had previously failed in 2007 due to IGSCC. Corrective actions taken for that event did not prevent a recurrence of the condition identified during C1R16. The leaking flexible main steam line hoses and the remaining flexible hoses on the MS Ls B and C were replaced during C1R16. The remaining inner elbow flexible hoses on MS Ls A and D have been scheduled for replacement during the next refueling outage C1R17. This condition is reportable under 1 O CFR 50.73(a)(2)(ii)(A), as a condition that resulted in the condition of the nuclear power plant, including its principal safety barriers being seriously degraded. NRG FORM 366 (11-2015) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 01/31/2017 (02·2014) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and led back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by LICENSEE EVENT REPORT (LER) internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, CONTINUATION SHEET Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 6. LER NUMBER 3. PAGE I YEAR I SE N Q U U M E B N E T R IA L R N E O V . Clinton Power Station, Unit 1 05000461 2 OF 4 2016 007 00 | PLANT AND SYSTEM IDENTIFICATION General Electric-Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX] EVENT IDENTIFICATION Main Steam Line Flexible Hose lntergranular Stress Corrosion Cracking Identified During Refueling Outage A. Plant Operating Conditions before the Event Unit: 1 Event Date: May 17, 2016 Event Time: 0945 Mode: 4 Mode Name: Cold Shutdown Reactor Power: O percent B. DESCRIPTION OF EVENT On May 17, 2016 at 0945 while the plant was in Mode 4 (Cold Shutdown) during refueling outage C1R16, it was discovered that water was leaking from two separate flexible hoses connecting the main steam line (MSL) to flow instrumentation. Steam flow during power operations is measured in each MSL using instrument taps off the inside and outside of the respective piping elbow. Pressure sensed in each of the lines is used to derive the steam flow. Flexible hose 1B21-D372C - located at the inner elbow on MSL 'B' had water leaking slowly in a thin, steady stream. The leak originated from the collar on the end of the hose closest to MSL 'B'. No mechanical damage was noted on the flexible hose or attached insulation. The vacuum port protective jacket was in place. Flexible hose 1B 21-D372E - located at the inner elbow on MSL 'C' had water dripping out slowly, less than 5 dpm. The leak was coming from the area of the vacuum port near the top of the hose, going down the side, and dripping off the bottom. A failure analysis of the flexible hose failures identified the failure mechanism as lntergranular Stress Corrosion Cracking (IGSCC). Both leaking flexible hoses 1B 21-D372C and 1B 21-D372E were replaced during the refueling outage and their respective high side flexible connections were also replaced. No additional leaks were found during an inspection of other flexible hoses connected to MSLs and the reactor recirculation system. An examination of monitored drywell points prior to plant shutdown for C1R16 showed no change in temperature, pressure or airborne radiation levels. NRG FORM 366A (02-2014) | ML16201A232
Braidwood Station | Unit 1 | Inadequate Protection from Tornado Missiles Identified Due to Non-Conforming Design Conditions | 07-19-2016 | On May 25, 2016, during evaluation of protection for Technical Specification (TS) equipment from the damaging effects of tornadoes, Braidwood identified non-conforming conditions in the plant design such that specific TS equipment on both units was considered to not be adequately protected from tornado missiles. On May 25, 2016 at 1415 Operations declared the affected equipment inoperable, implemented Enforcement Guidance Memorandum (EGM) 15-002, "Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance" and the required compensatory measures, and then declared the affected equipment operable but non-conforming. The cause of this issue was a lack of clarity and changing requirements during the original licensing of the plants which led to inadequate understanding of the original NRC regulatory guidance. The corrective actions planned are to complete the EGM 60-day comprehensive compensatory measures to demonstrate a discernable change from its pre-discovery actions, to modify the refueling water storage tank hatches to eliminate the tornado missile vulnerability, and to obtain and implement a license amendment for an analytical solution dispositioning tornado generated missile nonconforming conditions. NRC FORM 366 (11-2015) Page 2 of 4 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the inlormation collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR NUMBER NO. Braidwood Station, Unit 1 05000456 2016 - 002 - 00 | A. Plant Operating Conditions Before the Event: Event Date: May 25, 2016 Unit: 1 Mode: 1 Reactor Power: 100 percent Unit: 2 Mode: 1 Reactor Power: 100 percent Unit 1 Reactor Coolant System (RCS) [AB]: Normal operating temperature and pressure Unit 2 Reactor Coolant System: Normal operating temperature and pressure No structures, systems or components were inoperable at the start of this event that contributed to the event. Background NRC Documents Enforcement Guidance Memorandum (EGM) 15-002, "Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance," provides guidance to exercise enforcement discretion when an operating power reactor licensee does not comply with a plant's current site-specific licensing basis for tornado-generated missile protection. Specifically, discretion would apply to the applicable Technical Specification (TS) Limiting Condition(s) for Operation (LCO) which would require a reactor shutdown or mode change, if a licensee could not meet TS LCO required action(s) within the TS completion time. Interim Staff Guidance DSS-ISG-2016-01, "Clarification of Licensee Actions in Receipt of Enforcement Discretion Per Enforcement Guidance Memorandum EGM 15-002," provides interim staff guidance (ISG) to provide clarifying guidance to facilitate staff understanding of expectations for consistent oversight associated with implementing enforcement discretion for tornado missile protection noncompliance(s) per EGM 15-002. Appendix A to DSS-ISG-2016-01 provides guidance for acceptable initial and comprehensive compensatory measures for licensee use in implementing the enforcement discretion outlined in EGM 15-002. The licensee should declare (log) the utilization of EGM 15-002, inform the resident inspector, and enter the issue into the corrective action program. For initial compensatory measures, it is expected that the measures listed are already in place at sites that may be affected by severe weather, such as tornadoes and/or hurricane force winds. The measures provided should be verified as current and readily deployable within a very short timeframe (the shortest timeframe could, in some scenarios, be dictated by a TS 3.0.3 completion time of one hour). B. Description of Event: On May 25, 2016, during evaluation of protection for TS equipment from the damaging effects of tornadoes, Braidwood identified non-conforming conditions in the plant design such that specific TS equipment on both units was considered to not be adequately protected from tornado missiles. These included ventilation openings in the wall that separates the non-safety related turbine building and the safety related auxiliary building. Additionally, the auxiliary feedwater (AF) [BA] diesel exterior exhaust stacks, which extend from the roofline, could be impacted by tornado missiles. While there are analyses on these impacts, they do not use an NRC accepted methodology to evaluate the impact and affects. Further, the refueling water storage tank (RWST) roof access opening Sileo hatch is fabricated from sheet metal that is not designed to prevent all postulated tornado missiles from entering the tank. The following piping, located NRG FORM 366A (11·2015) Page 3 of 4 | ML16201A336
Pilgrim Nuclear Power Station | Unknown Unit | Salt Service Water Pump B Past Operability- Operation or Condition Prohibited by Technical Specifications | 07-11-2016 | On May 10, 2016 with the reactor at 100% power and the mode switch in RUN; a condition report was written to evaluate past operability of the Salt Service Water (SSW) Pump P-2088 power supply breaker overload relay based on thermography results obtained on October 25, 2013. A similar high temperature condition was identified during the February 29, 2016 thermography surveillance that resulted in declaring the pump inoperable on March 4, 2016 and completing the replacement of the overload relay on March 5, 2016. SSW Pump P-2088 is currently operable. The past operability review covers the period of time between the 2013 thermography surveillance and March 5, 2016 when the pump breaker overload relay was replaced. Based on the lack of detailed information in the 2013 surveillance, past operability of the pump could not be assured. A review of out-of-service time for SSW Pumps P208A and P208C indicates that one instance occurred where less than two SSW pumps were Operable to feed the SSW A L.::oop Header for a period in excess of SSW Technical Specification requirements. This represents a reportable condition. The cause of the overload relay high temperature readings was evaluated and determined to be a high resistance connection on the overload relay heater assembly. Inadequate predictive maintenance monitoring was identified as the apparent cause for not periodically assessing breaker status or replacing the breaker overload relay prior to March 5, 2016. Testing the overload relay that was removed from service is planned. This testing is expected to be completed by· · August 15, 2016. Results will be reported in a supplement to this report. There was no impact to public health and safety. NRC FORM 366A(11-2015) Page 2 of 5 NRC FO,R,M 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) ...... Estimated burden per response to comply with this mandatory collection request 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send commenls regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 i F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, I .,, ••• NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means CONTINUATION SHEET used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR NUMBER NO. Pilgrim Nuclear Power Station 05000293 2016 004 00 | BACKGROUND The safety objective of the SSW system is to provide a heat sink for the Reactor Building Closed Cooling Water (RBCCW) system under normal, transient, and accident conditions. The SSW system has five SSW pumps and is designed with sufficient redundancy so that no single active system component failure can prevent the system from achieving the safety objective. The system is designed to continuously provide a supply of cooling water to the secondary side of the RBCCW heat exchangers adequate to meet the requirements of the RBCCW system under all conditions. The RBCCW system provides the necessary cooling requirements for the residual heat removal (RHR) system and ultimately the reactor and primary containment. The SSW pumps are separated into two loops. Two pumps are connected to each loop and the fifth pump can feed either loop. Initiation of standby AC power following loss of the preferred AC power source will automatically start at least one pump in each loop during normal conditions. Following a Loss of Coolant Accident (LOCA) and loss-of-offsite power, one pump will start in each loop because of diesel load limitations. Additional pumps are started manually by the operator as additional cooling loads are established and diesel 1 capacity is available. Technical Specification (TS) Limiting Condition For Operation (LCO) 3.5.B.4 requires two SSW loops to be operable whenever fuel is in the vessel and reactor coolant temperature is greater than 212 degrees F. Operability of each loop requires at least two SSW pumps to be operable in the loop along with the associated / controls to demonstrate SSW loop operability. Thermography is part of the SSW pump breaker predictive maintenance program. SSW system TS surveillances do not require use of thermography to determine system or pump operability. The site thermography procedure requires conditio~ reports to be written if high temperature conditions exist. EVENT DESCRIPTION On May 10, 2016, Condition Report CR-PNP-2016-3308 was written to perform a past operability review on the SSW Pump P-2088 ·power supply breaker overload relay based on thermography surveillance results obtained on October 25, 2013. The 2013 thermography surveillance indicated the breaker was in the Level II -Warning Range (a temperature rise of greater than 25 degrees F and less than 50 degrees F for 480 Volt equipment). Procedure instruction for 480 Volt breakers is to take action recorllmended by the Preventative Maintenance Team. Condition Report CR-PNP-2013-7196 was issued and the pump was identified as operable. No follow-up maintenance work was performed to address the potential high temperature condition. Work Order (WO) 366187 to replace the overload relay was created on October 28, 2013 but not worked until after the SSW pump was declared inoperable in March 2016. SSW Pump P2088 TS operability surveillances during the 2013 to 2016 time frame were performed with acceptable results. No actions were taken or believed necessary to replace the overload relay to demonstrate TS operability. | ML16202A053
Nine Mile Point | Unit 1 | Secondary Containment Inoperable Due to Simultaneous Opening of Airlock Doors | 07-12-2016 | On Wednesday June 1, 2016, at approximately 1046, the secondary containment of the Nine Mile Point Unit 1 (NMP1) Reactor Building was momentarjly breached when workers opened both airlock doors on elevation 261 simultaneously. The integrity of the airlock was re-established within 5 seconds when one of the doors was closed and latched. The cause of this event is personal accountability. With clear understanding of the expectations for using the airlock doors in conjunction with all mechanical barriers (lights, buzzers, monitors) functioning properly, the individual failed to use human performance tools to verify the airlock was not already being used by other individuals. This condition is reportable under 1O CFR 50.72(b)(3)(v)(C) and 10 CFR 50.73(a)(2)(v)(C). NRC FORM 366 (11-2015) Page 2 of 5 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatmy Affairs, CONTINUATION SHEET NEOB· 10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR NUMBER NO. Nine Mile Point Unit 1 05000-220 2016 - 001 00 | I. DESCRIPTION OF EVENT A. PRE-EVENT PLANT CONDITIONS: Prior to the event, Nine Mile Point Unit 1 (NMP1) was operating at 100% reactor power. B. EVENT: On Wednesday June 1, 2016, at approximately 1046, the secondary containment of the Unit 1 Reactor Building was breached when workers opened both airlock doors on elevation 261 simultaneously. The integrity of the airlock was re-established within 5 seconds when one of the doors was closed and latched. During the event, two groups of individuals were attempting to use the Unit 1 airlock doors D-52 and D-53 simultaneously while exiting the Reactor Building. The cause of this event is personal accountability. With clear understanding of the expectations for using the airlock doors in conjunction with all mechanical barriers (lights, buzzers, monitors) functioning properly, the individual failed to use human performance tools to verify the airlock was not already being used by other individuals. Operations review determined that the simultaneous opening of both secondary containment airlock doors constituted a momentary loss of secondary containment per Technical Specification 3.4.3 and NU REG 1022, Revision 3 .. This event represents a potential loss of secondary containment safety function as presented in Technical Specification 3.4.3, Access Control. This condition is reportable under 1O CFR 50.72(b)(3)(v)(C) and 1O CFR 50.73(a)(2)(v)(C) as any_ event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. Nine Mile Point Unit 2 (NMP2) was unaffected by both airlock doors being open at NMP1. The event has. been entered into the plant's corrective action program as IR 2676493. C. INOPERABLE STRUCTURES, COMPONENTS, OR SYSTEMS THAT CONTRIBUTED TO THE EVENT: No other systems, structures, or components contributed to this event. NRG FORM 366A (11-2015) Page 3 of 5 | ML16202A148
Columbia Generating Station 05000 397 1 OF 3 | Unknown Unit | MANUAL REACTOR SCRAM FOLLOWING LOSS OF REACTOR CLOSED COOLING | 07-25-2016 | At 1322 PDT on March 28, 2016, a manual reactor scram was initiated in response to a loss of Reactor Closed Cooling (RCC). The loss of RCC was due to the opening of a Service Water (SW) valve at the inlet side of the Fuel Pool Cooling heat exchanger during performance of a partial surveillance without proper isolation of the RCC system piping from the heat exchanger. The cross-connection of the two systems caused depressurization and loss of flow from the RCC system into the non-pressurized SW piping. The SW valve was closed and the reactor was scrammed. Safety system responses to the scram signal were normal, with all control rods being fully inserted. Reactor decay heat was removed via bypass valves to the Main Condenser. No safety relief valves lifted and no emergency core cooling systems injected following the reactor scram. The root cause was determined to be that plant Operators did not properly evaluate plant configuration when performing a partial surveillance including the marking as “N/A” (not applicable) of procedural steps, in accordance with plant procedures. Human performance aspects of the event were quickly addressed and additional corrective actions include reinforcing and monitoring procedure standards, and updating work control procedures at the station. 26158 R6 NRC Form 366 (01-2014) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 01/31/2017 (01-2014) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections LICENSEE EVENT REPORT (LER) Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information CONTINUATION SHEET and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 6. LER NUMBER 3. PAGE Columbia Generating Station SEQUENTIAL REV YEAR NUMBER NO. 05000 397 2 OF 3 2016 − 001 − 01 | Plant Conditions The reactor was at 100% power before the event. There were no structures, systems or components that malfunctioned or that were out of service that contributed to this event. One of the four reactor source range detectors failed to insert during the scram, with no impact on safety functions. Event Description On March 28, 2016, Operators performed a partial surveillance of the Fuel Pool Cooling (FPC) System [DA] to satisfy Post Maintenance Testing (PMT) for a Service Water (SW) [BI] to FPC isolation valve. Per PMT instructions, sections of the surveillance procedure had been marked as Not Applicable (N/A) for steps not considered necessary for the partial surveillance. The steps marked as N/A included closing Reactor Closed Cooling (RCC) [CC] isolation valves on the downstream side of the heat exchanger that isolate SW from RCC. Opening the SW valve without isolating RCC resulted in loss of pressurized RCC inventory into depressurized SW piping. Operators recognized the loss of RCC from Control Room indications and took appropriate actions to manually scram the reactor as required by abnormal operating procedures. All plant systems responded as expected during the scram transient. The SW valve was closed after approximately 2 minutes of being opened and RCC inventory recovered quickly. This event was reported (EN # 51826 – 4 hour notification) under criterion 10 CFR 50.72(b)(2)(iv)(B) – Actuation of Reactor Protection System (RPS) [JC] when the reactor is critical. The event also requires a 60-day report, or Licensee Event Report (LER), under criterion 10 CFR 50.73(a)(2)(iv)(A) as applicable to condition 50.73(a)(2)(iv)(B)(1) – An event or condition that resulted in manual or automatic actuation of the RPS system including: reactor scram or reactor trip. Event Precursors The SW valve maintenance was originally scheduled to be performed concurrent with the quarterly surveillance of FPC. A change to the schedule moved the maintenance to after the surveillance. As a result a partial surveillance was performed. Work control reviews and pre-job briefs failed to recognize the significance of some of the steps being bypassed (N/A’d) in the partial surveillance such as closing the RCC isolation valves. Cause The root cause was determined to be that plant Operators did not properly evaluate plant configuration when performing a partial surveillance including the marking as “N/A” (not applicable) of procedural steps, in accordance with plant’s Procedure and Work Instruction Use and Adherence requirements. | ML16207A708
River Bend Station -Unit 1 05000 458 1 OF 3 | Unit 1 | Potential Loss of Safety Function of Multiple Systems Due to Design Deficiency in 480-volt Circuit Breakers | 07-12-2016 | At 1200 CDT on May 13, 2016, while the plant was operating at 100 percent power, the shift manager was notified of a design inadequacy that could potentially prevent both divisions of the standby gas treatment system (GTS) from performing its design function. Under certain specific conditions, the 480-volt circuit breakers supplying the GTS fans may not re-close following a trip signal. In the postulated condition in which a start signal is followed by an immediate (within 0.075 seconds) trip signal, the breaker could fail to close at the next attempt. As a result of this condition, both divisions of GTS were declared inoperable. The initial investigation of this condition determined that circuit breakers in the main control building air conditioning system (HVC) and the diesel generator building ventilation system (HVP) are also susceptible to this postulated failure mechanism. This defect has the potential to similarly cause the HVC and HVP systems to be incapable of performing their safety function. The affected circuit breakers in those systems have been modified to correct the deficiency. This condition is being reported in accordance with IO CFR 50.73(a)(2)(i)(B) and (a)(2)(v)(D) as operations prohibited by Technical Specifications and an event that could have caused a loss of safety functions of the affected systems. The specific scenario in which this failure mechanism could plausibly have occurred is a highly unlikely e_vent. Adqitionally, standing _ orders were already in place at the time of this -event that directed the operators to take compensatory actions to preserve the safety function of the affected systems. Those orders will remain in effect until ·an modifications are complete. Thus, this condition does not represent a significant challenge to the health and safety of the public. - NRG FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and lnfonmation Collections Branch (T-5 CONTINUATION SHEET F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of lnfonmation and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an infonmation collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the infonmation b.t!p://www,.ill.IUJ_Qv/readin~d..QC-collec..ti.Qlls.l!l.!J.re.gfil..1filflfil192.2Lr.3Ll collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER DYEA R SEQUENTIAL REV River Bend Station - Unit 1 05000-1 458 Iu -1 NU ° MBER 1- NO 0 . 06 | REPORTED CONDITION At 1200 CDT on May 13, 2016, while the plant was operating at 100% power, the shift manager was notified of a design inadequacy that could potentially prevent both divisions of the standby gas treatment system (GTS) [BH] from performing its design function. Under certain specific conditions, the 480-volt circuit breakers (**BKR**) Sl.Jpplying the GTS fans may not re-close following a trip signal. In the postulated condition in which a start signal is followed by an immediate (within 0.075 seconds) trip signal, the breaker could fail to close at the next attempt. As a result of this condition, both divisions of GTS were declared inoperable. The initial investigation of this condition determined that circuit breakers in the main control building air conditioning system (HVC) [VI] and the diesel generator building ventilation system (HVP) [VJ] are also susceptible to this postulated failure mechanism. This defect has the potential to similarly cause the HVC and HVP systems to be incapable of performing their safety function. This condition is being reported in accordance with 10 CFR 50. 73(a)(2)(i)(B) and (a)(2)(v)(D) as operations prohibited by Technical Specifications, and an event that could have caused a loss of safety functions of the GTS, HVC, and HVP systems. INVESTIGATION and IMMEDIATE ACTIONS At 1240, the Division 1 GTS subsystem was manually started. Since the postulated breaker failure mechanism js precluded when the breaker is closed, this action allowed the Division 1 subsystem to be restored to an operable status. BACKGROUND The safety-related 480-volt switchgears were originally constructed with GE AKR breakers. Due to age and obsolescence, the GE breakers were replaced with Square D Masterpact breakers. A notable design difference between the two designs is in how the "anti-pumping" functionality is achieved. Pumping is the rapid, repeated opening and closing of the breaker when "open" and "close" signals are applied simultaneously. In the AKR design, the anti-pumping function was accomplished electrically using relays. In the Masterpact design, the function is accomplished mechanically by the breaker operating mechanism. This mechanical mechanism of the Masterpact breakers has a documented failure history. After several failures at RBS and at another utility, the vendor released a Part 21 notification describing a failure mode for Masterpact breakers. When a susceptible breaker receives an "open" signal when standing close signal is present, the closing mechanism has the potential to bind. This can cause the breaker to be incapable of responding to any subsequent "close" signal. The binding can be corrected by the operator action to depress the "open" pushbutton on the front of the breaker. CAUSAL ANALY SlS The reported condition was precipitated by RBS' evaluation of a failure analysis report from the circuit breaker vendor. RBS engineering personnel had witnessed offsite testing of Masterpact breakers for the purposes of evaluating the effectiveness of the vendor-provided solution for the anti-pump mechanism malfunction. This testing determined that even with the vendor-recommended solution implemented, the reported failure mode can still occur if a "close" signal is followed within 0.075 .seconds by an "open" signal. In this highly unlikely sequence of events, the breaker will trip as expected, bl!t_ it may not successfully respond tO the next "close" signal. - - - | ML16208A056
Limerick Generating Station | Unit 2 | Manual Actuation of the Reactor Protection System When Critical Due to Wiring Design Error | 07-27-2016 | A manual actuation of the reactor protection system (RPS) when the reactor was critical was initiated during Plant Process Computer (PPC) modification testing at power. A modification wiring design error caused an actuation of both reactor recirculation pump (RRP) trip relays when a circuit isolation switch was closed. The direct cause of the event was a circuit wiring design error implemented in the field that caused energization of the RRP adjustable speed drive (ASD) trip coils. The root cause of the event was a failure of station personnel to appropriately apply Technical Human Performance (THU) error prevention techniques to identify the design error and prevent its installation and testing as part of the modification. The isolation switch for the mis-wired circuit was opened to enable reset of the ASD trip coils. The 2A and 2B ASDs were returned to service. The corrective actions are to change the circuit design to correct the design error. The human performance aspects of the event will be addressed through several management actions that include reinforcement of proper standards and behaviors related to THU error techniques with station personnel. NRC FORM 366 (01-2014) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 01/31/2017 (01-2014) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by LICENSEE EVENT REPORT (LER) internet e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, CONTINUATION SHEET Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 6. LER NUMBER 3. PAGE SEQUENTIAL REV YEAR NUMBER NO. Limerick Generating Station, Unit 2 05000353 2 OF 3 2016 - 001 - 00 | Unit Conditions Prior to the Event Unit 2 was in Operational Condition (OPCON) 1 (Run) at approximately 100 percent power with PPC modification testing in progress. There were no structures, systems or components out of service that contributed to this event. Description of the Event On Wednesday, June 1, 2016, Limerick Unit 2 was operating at 100 percent power with PPC (EIIS:CPU) modification testing in progress. The modification testing directed closure of a circuit isolation switch which resulted in the trip of both RRPs (EIIS:P) due to an error in the modification wiring design. The control room supervisor (CRS) entered the procedure for an unexpected/unexplained change in core flow (OT-112) due to the trip of both RRPs. The procedure directed a manual actuation of RPS. All control rods inserted and safety significant systems functioned as expected. Reactor level initially increased then decreased to approximately +0 inches which is less than the +12.5 inch low level setpoint for RPS. Level then stabilized at normal level. Nuclear Steam Supply Shutoff System Groups IIA and IIB isolations actuated on low level at +12.5 inches. The digital feedwater level control system functioned as designed. Reactor pressure vessel pressure was controlled by the main steam bypass valves. The investigation of the event identified that a wiring design error caused an unplanned actuation of both RRP trip relays when a circuit isolation switch was closed as directed by the modification acceptance test procedure. A four-hour ENS notification (#51968) was completed on Wednesday, June 1, 2016, at 1041 hours as required by 10CFR50.72(b)(2)(iv)(B) for an actuation of RPS when the reactor is critical. This LER is being submitted pursuant to the requirements of 10CFR50.73(a)(2)(iv)(A) for a manual actuation of RPS. Analysis of the Event There was no actual safety consequence associated with this event. The potential safety consequences of this event were minimal. All control rods were verified to be fully inserted following the RPS actuation. The 2A RRP was restarted at 1548 hours on June 1, 2016 and the 2B RRP was restarted at 0326 hours on June 2, 2016. The PPC replacement modification was in progress and computer input points were being transferred from the original computer to the new computer. When the second RRP related computer point was placed in service by closure of a circuit isolation switch both 2A and 2B RRP trip relays were energized due to an error in the wiring design. | ML16209A265
Surry Power Station | Unit 1 | Emergency Service Water Pump Inoperable Due to Corrosion of Valve Support | 07-11-2016 | On April 7, 2016 at 0638 hours, with Surry Power Station Units 1 and 2 operating at 100% power, the Emergency Service Water Pump (ESWP) 1 B cooling water discharge valve flange was found to be cracked, and the pump was declared inoperable. During flange and valve support repair activities, four bolts on the cooling water discharge valve support base plate were found to be failed due to corrosion. The flange was replaced and the support base plates were anchored with stainless steel bolts. ESWP 1 B was returned to operable status on April 9, 2016 at 1105 hours. The cause of the flange and support failure was corrosion of the base plate and anchor bolts from repetitive exposure to service water. On May 11, 2016, an Engineering evaluation determined that the piping and support had been non-functional for prior operability based on the potential for lateral displacement during a seismic event. Therefore, this report is being submitted, pursuant to 1O CFR 50. 73(a)(2)(i)(B), for operations prohibited by Technical Specifications, and pursuant to 1O CFR 50. 73(a)(2)(v)(B), an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat. Based on the risk assessment of this event, the risk impact was determined to be of very low significance, and, as a result, the health and safety of the public were not affected. NRG FORM 366 (11-2015) Page 2 of4 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: BO hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an infonllation collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR NUMBER NO. Surry Power Station, Unit 1 05000 - 280 2016 001 00 | 1.0 DESCRIPTION OF THE EVENT Three diesel-driven vertical Emergency Service Water Pumps (ESWPs) [EllS-Bl-P] are provided at the James River intake structure [EllS-KE-NN] to deliver required service water makeup to the intake canal [EllS-KE-NN] in case of a total loss of station power. In the event of a Loss of Coolant Accident (LOCA) and a total loss of station power, with the requirement that the pon-LOCA unit must also be cooled down, two of the three ESWPs would be required to provide the design service water makeup. Technical Specification (TS) 3.14.A.4 states that when the reactor coolant system temperature or pressure exceeds 350°F or 450 psig, three emergency service water pumps shall be operable. TS 3.14.B allows one ESWP to remain inoperable for a period not to exceed 7 days. On April 7, 2016, during a walk-down of the ESWP house [El IS-Bl-MK], the ESWP 1 B cooling water discharge valve piping flange [EllS-81-LB-PSF] was found to be cracked. A follow on Engineering and Maintenance inspection confirmed the cracked flange and observed a cooling water discharge valve support [EllS-81-LB-SPT] was raised due to corrosion buildup under the support base plate. With Units 1 and 2 operating at 100% power, ESWP 1 B was declared inoperable as of 0638 hours, based on the deteriorated condition of the flange. During flange repair activities, the valve support, consisting of two stanchions and two base plates, was removed to install stainless steel anchor bolts. On the north base plate, the existing carbon steel anchor bolts were found to be failed due to corrosion. The cracked flange was repaired, the valve support base plate anchor bolts were replaced, and ESWP 1 B was returned to operable status on April 9, 2016 at 1105 hours. The elapsed time from discovery until the ESWP 1B was returned to service was 52 hours and 27 minutes. On May 11, 2016, an engineering review determined that the piping and support were non functional for prior operability based on the potential for lateral displacement during a seismic event. If this were to occur, cooling water would discharge to the ESWP house. It is expected that since ESWPs are operated locally, the ESWP 1 B would be shut down to minimize water intrusion into the ESWP pump house. Based upon the as-found conditions of the failed valve support anchor bolts, the condition of the ESWP 1B was determined to be present for a time greater than the 7 day limiting condition. Therefore, this report is being submitted pursuant to 10 CFR 50.73 (a)(2)(i)(B), an operation or condition that was prohibited by the plant's Technical Specifications. In addition, during the prior 7-day period when ESVVP 18 was determined to be inoperable, ESWP 1C was removed from service for maintenance. Therefore, this report is also being submitted pursuant to 10 CFR 50. 73(a)(2)(v)(B), an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat. 2.0 SIGNIFICANT SAFETY CONSEQUENCES AND IMPLICATIONS The duration of the ESWP 1 B flange and valve support failure is undetermined due to the nature of | ML16216A150
i | Unknown Unit | Concurrent Opening of Reactor Building Airlock Doors 8. OTHERFACILITIESINVOLVED DOCKETNUMBER N/A DOCKETNUMBER N/A 9. OPERATING MODE 11. THIS REPORTISSUBMITTED PURSUANTTOTHE REQUIREMENTS OF10 CFR§: (Checkallthatapply) 20.2201(b) 20.2203(a)(3)(i) 50.73fa)(2)(ii)(A) 50.73(a)f2)(viii)(A) 20.2201(d) 20.2203(a)(3)(ii) 50.73(a)(2)(ii)(B) 50.73(a)(2)(v0i)(B) 20.2203(a)(1) 20.2203(a)(4) 50.73(a)(2)(Bi) 50.73(a)(2)Øx)(A) 20.2203(a)(2)(i) 50.36(c)(1)(i)(A) 50.73(a)(2)(iv)(A) 50.73(a)(2)(x) 10. POWER LEVEL 20.2203(a)(2)(ii) 50.36(c)(1)(0)(A) 50.73(a)(2)(v)(A) 73.71(a)(4) 20.2203(a)(2)(iN) 50.36(c)(2) 50.73(a)(2)(v)(B) 73.71(a)(5) 20.2203(a)(2)(iv) 50.46(a)(3)(ii) 50.73(a)f2)(v)(c) 73.77(a)(1) 100 20.2203(a)(2)(v) 50.73(a)(2)Q)(A) 50.73(a)(2)(v)(D) 73.77(a)(2)(i) 20.2203(a)(2)(vi) 50.73(a)(2)(i)(B) 50.73(a)(2)(vh) 73.77(a)(2)(0) 50.73(a)(2)(i)(c) OTHER SpecifyinAbstractbeloworin NRCForm3eeA 12. LICENSEECONTACT FORTHIS LER LICENSEECONTACT TELEPHONENUMBER(IncludeAreaCode) Mr. William Drews, RegulatoryAssurance Manager 315-349-6562 13. COMPLETE ONE LINE FOR EACHCOMPONENTFAILURE DESCRIBED INTHIS REPORT MANU- REPORTABLE MANU- REPORTABLE CAUSE SYSTEM COMPONENT FACTURER TOEPIX CAUSE SYSTEM COMPONENT FACTURER TOEPIX X NG N/A N/A N 14. SUPPLEMENTAI REPORTEXPECTED 15. EXPECTED MONTH DAY YEAR SUBMISSION YES (Ifyes, complete 75. EXPECTED SUBMISSIONDATE) NO DATE ABSTRACT (Limitto 1400spaces, i.e., approximately15single-spacedtypewrittenlines) On the morning of June 7, 2016, while operating at 100% power, workers opened doors concurrently when entering a secondary containment access airlock. The individuals involved each closed their respective doors upon encountering this unexpected condition; however, the result was a brief inoperability of secondary containment. This resulted in an 8 hour reportable event. The Resident Inspector was notified, and an Event Notification was made pursuant to 10 CFR 50.72(b)(3)(v)(C) due to a condition at the time of discovery that prevented the fulfillment of the Secondary Containment safety function (Reference ENS 51985). Following the event, the doors functioned properly, and no deficiencies were noted with either door. There were no radiological releases associated with this event. NRCFORM366(11-2015) Page 2 of 3 NRC FORM 366A U.S. NUCLEAR REGULATORYCOMMISSION APPROVED BY0MB: NO. 3150-0104 EXPIRES: 1013112018 (11-2015) Eshmated burden perresponsetocomplywiththis mandatorycollechon request. 80hours. Reported ‘•, lessonslearned areincorporatedintothelicensing processandfed backtoinduslry.Send comments LICENSEE EVENT REPORT (LER) regarding burden esbmateto the FOIA, Privacy and Information Collections Branch (T-5 F53). US. •. “ -‘—)‘.j CONTINUATION SHEET N ln u f c o l c e o ar llec R ts e . g R u e la s t o o u ry rcen C r o c m .g m ov is , si a o n n d . to W th as e hi D ng es to k n. Offi D ce C r, O 2 f 0 fi 5 c 5 e 5 o - f 00 I 0 nf 1 o , rma o t r ion by and in R te e r g n u e l t ato e r - y m A ai f l fair t s o , , j,... NEOB-10202, (3150-0104), Officeof Management and Budget, Washington, DC 20503. If a means used to impose an information collection does notdisplay acurrentlyvalid 0MB control number,the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKETNUMBER 3. LERNUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 333 NUMBER NO. — 2016 —003 —00 NARRATIVE Background The Secondary Containment [EIIS identifier: NGJ boundary surrounds the primary containment and refueling equipment. The boundary forms a control volume to contain, dilute, and hold up fission products. The Secondary Containment consists of four systems which include the Reactor Building, the Reactor Building Isolation and Control System, the Standby Gas Treatment System, and the Main Stack. Secondary Containment is designed to provide containment for postulated design basis accident scenarios: loss-of- coolant accident and refueling (fuel handling) accident. Since pressure may increase in Secondary Containment relative to the environmental pressure, support systems are required to maintain a differential pressure vacuum such that external atmosphere would leak into containment rather than fission products leak out. The systems which maintain a differential pressure vacuum inside Secondary Containment include the normal Reactor Building Ventilation and Cooling (RBV) System [VA] (during normal plant operations) and the safety- related Standby Gas Treatment (SBGT) System [BHJ for post-accident conditions. Technical Specification (TS) Surveillance Requirement(SR) 3.6.4.1.3 requires one Secondary Containment access door in each access opening to remain closed. Failure to meet this SR results in the Secondary Containment Limiting Condition for Operation (LCO) not being met, and requires the Secondary Containment to be declared Inoperable. Event Description On June 7, 2016, with the James A. FitzPatrick Nuclear Power Plant (JAF) operating at 100 percent power, members ofthe Maintenance and Security departments simultaneously entered the northeast Secondary Containment airlock on Reactor Building Elevation 272’. This resulted in the concurrent opening ofthe airlock doors. This condition was corrected within approximately two (2) seconds. At the time ofthe closure of either door, secondary containment integrity was restored as the SR for one door closed was met, and no other SRs (such as negative pressure) were being exceeded. For the condition in which Secondary Containment did not meet the Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.3 for at least one door in secondary containment access opening being closed, the TS Limiting Condition of Operation (LCO) 3.6.4.1 required action was to restore secondary containment to Operable status in 4 hours. An NRC notification was made via ENS 51985. This Licensing Event Report (LER) is being submitted per 10 CFR 50.73(a)(2)(v)(C) as a condition that could have prevented the fulfillment of safety function to control the release of radioactive material. Event Analysis Timeline of Events on 6/712016 1030 Personnel entered the northeast Reactor Building Elevation 272’ airlock simultaneously, and the condition was corrected within approximately two (2) seconds. 1110 Condition Report (CR-JAF-2016-01996) initiated. 1307 NRC notified via ENS 51985 NRCFORM366A(11-20151 Page 3 of 3 NRC FORM 366A U.S. NUCLEARREGULATORYCOMMISSION APPROVED BY0MB: NO. 3150-0104 EXPIRES: 1013112018 (11-2015) , Estimatedburden perresponsetocomplywiththis mandatory collection request: 80hours, Reported lessonslearnedareiecorporaledintothelicensingprocessandfed backtoindustry.Send comments “,, LICENSEE EVENT REPORT (LER) regarding burdenestimateto the FOIA, Privacy and Information CollectionsBranch (T-5 P53), U.S. -., ,.../,? CONTINUPITION SHEET N ln u f c o l c e o a l r lec R to e . g R s e )a o t o or u y rcen C r o c m .g m o i v s , si a o n n d , to W th a e shi D n e g s to k n O , ffi D ce C r. O 2 f 0 fi 5 c 5 e 5 o - f 00 I 0 nf 1 o , rma o t r ion by and in R te e r g n u e l t ato e ry -m A ai f l fair t s o . ‘, ‘ NEOB-10202, (3150-0104), OfficeofManagementand Budget, Washington, DC 20503. Ifa means used to imposean informationcollechon does notdisplay acurrentlyvalid 0MB controlnumber, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKETNUMBER 3. LER NUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 333 NUMBER NO. — 2016 —003 —00 Cause Secondary Containment access openings are equipped with green indicating lights that are lit when the opposing access opening door is fully shut. None of the parties involved indicated they observed the green indicating light not being lit prior to opening the airlock door. Therefore, the cause ofthis condition was determined to be simultaneous opening of the doors. Similar Events Internal Events LER 2015-004-00, Concurrent Opening of Reactor Building Airlock Doors; Condition Report: CR-JAF-2015-04146, September 17, 2015 External events: Quad Cities Nuclear Generating Station: LER 2015-008, Interlock Doors Opened Simultaneously Cause Loss of Secondary Containment Duane Arnold Energy Center: LER 2015-003-01, Both Doors in Secondary Containment Airlock Opened Concurrently Corrective Actions Completed Actions • Both airlock doors (24R-272-5 & -6) on the northeast Reactor Building Elevation 272’ Secondary Containment airlock were closed within approximately two (2) seconds. • Condition Report initiated (CR-JAF-2016-01996); NRC notified via ENS 51985. • Installed cameras and monitors on both sides of the northeast Reactor Building Elevation 272’ Secondary Containment airlock. This will allow verification that the opposing door will not be simultaneously opened. Safety Consequence and Implications Actual Consequences There were no actual consequences of this event relative to nuclear, industrial, or radiological safety. Potential Consequences The Secondary Containment differential pressure remained more negative than 0.25 inches of water vacuum while this condition existed. Therefore, there are no potential consequences of this event relative to nuclear, industrial, or radiological safety. References • Condition Report: CR-JAF-2016-01996, June 7,2016, Concurrent Opening of Secondary Containment Access Airlocks • Technical Specification 3.6.4.1 NRCFORM366A(11-2015) | 08-03-2016 | On the morning of June 7, 2016, while operating at 100% power, workers opened doors concurrently when entering a secondary containment access airlock. The individuals involved each closed their respective doors upon encountering this unexpected condition; however, the result was a brief inoperability of secondary containment. This resulted in an 8 hour reportable event. The Resident Inspector was notified, and an Event Notification was made pursuant to 10 CFR 50.72(b)(3)(v)(C) due to a condition at the time of discovery that prevented the fulfillment of the Secondary Containment safety function (Reference ENS 51985). Following the event, the doors functioned properly, and no deficiencies were noted with either door. There were no radiological releases associated with this event. NRCFORM366(11-2015) Page 2 of 3 NRC FORM 366A U.S. NUCLEAR REGULATORYCOMMISSION APPROVED BY0MB: NO. 3150-0104 EXPIRES: 1013112018 (11-2015) Eshmated burden perresponsetocomplywiththis mandatorycollechon request. 80hours. Reported ‘•, lessonslearned areincorporatedintothelicensing processandfed backtoinduslry.Send comments LICENSEE EVENT REPORT (LER) regarding burden esbmateto the FOIA, Privacy and Information Collections Branch (T-5 F53). US. •. “ -‘—)‘.j CONTINUATION SHEET N ln u f c o l c e o ar llec R ts e . g R u e la s t o o u ry rcen C r o c m .g m ov is , si a o n n d . to W th as e hi D ng es to k n. Offi D ce C r, O 2 f 0 fi 5 c 5 e 5 o - f 00 I 0 nf 1 o , rma o t r ion by and in R te e r g n u e l t ato e r - y m A ai f l fair t s o , , j,... NEOB-10202, (3150-0104), Officeof Management and Budget, Washington, DC 20503. If a means used to impose an information collection does notdisplay acurrentlyvalid 0MB control number,the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKETNUMBER 3. LERNUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 333 NUMBER NO. — 2016 —003 —00 | Background The Secondary Containment [EIIS identifier: NGJ boundary surrounds the primary containment and refueling equipment. The boundary forms a control volume to contain, dilute, and hold up fission products. The Secondary Containment consists of four systems which include the Reactor Building, the Reactor Building Isolation and Control System, the Standby Gas Treatment System, and the Main Stack. Secondary Containment is designed to provide containment for postulated design basis accident scenarios: loss-of- coolant accident and refueling (fuel handling) accident. Since pressure may increase in Secondary Containment relative to the environmental pressure, support systems are required to maintain a differential pressure vacuum such that external atmosphere would leak into containment rather than fission products leak out. The systems which maintain a differential pressure vacuum inside Secondary Containment include the normal Reactor Building Ventilation and Cooling (RBV) System [VA] (during normal plant operations) and the safety- related Standby Gas Treatment (SBGT) System [BHJ for post-accident conditions. Technical Specification (TS) Surveillance Requirement(SR) 3.6.4.1.3 requires one Secondary Containment access door in each access opening to remain closed. Failure to meet this SR results in the Secondary Containment Limiting Condition for Operation (LCO) not being met, and requires the Secondary Containment to be declared Inoperable. Event Description On June 7, 2016, with the James A. FitzPatrick Nuclear Power Plant (JAF) operating at 100 percent power, members ofthe Maintenance and Security departments simultaneously entered the northeast Secondary Containment airlock on Reactor Building Elevation 272’. This resulted in the concurrent opening ofthe airlock doors. This condition was corrected within approximately two (2) seconds. At the time ofthe closure of either door, secondary containment integrity was restored as the SR for one door closed was met, and no other SRs (such as negative pressure) were being exceeded. For the condition in which Secondary Containment did not meet the Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.3 for at least one door in secondary containment access opening being closed, the TS Limiting Condition of Operation (LCO) 3.6.4.1 required action was to restore secondary containment to Operable status in 4 hours. An NRC notification was made via ENS 51985. This Licensing Event Report (LER) is being submitted per 10 CFR 50.73(a)(2)(v)(C) as a condition that could have prevented the fulfillment of safety function to control the release of radioactive material. Event Analysis Timeline of Events on 6/712016 1030 Personnel entered the northeast Reactor Building Elevation 272’ airlock simultaneously, and the condition was corrected within approximately two (2) seconds. 1110 Condition Report (CR-JAF-2016-01996) initiated. 1307 NRC notified via ENS 51985 NRCFORM366A(11-20151 Page 3 of 3 | ML16216A162
Susquehanna Steam Electric Station | Unit 1 | Pressure Boundary Leakage from an Inadequate Weld Repair in Small Bore Pump Seal Vent Piping l | 00-03-2016 | On June 6, 2016, at 0556 hours during a drywell entry, a leak was reported on the Unit 1 B Reactor Recirculation Pump Lower Seal Vent Line. The leak was identified at the inboard pipe-to-union weld and required replacement prior o returning to service. The affected piping weld is for 3/4-inch piping, Quality Class Q (ASME Class 2) and is part of he Reactor Coolant Pressure Boundary. ifhe cause of the event was determined to be the result of a crack in the pipe-to-union weld on the pump side pf the connection. The crack was determined to have initiated and propagated as a result of an undetectable lack of fusion at the weld root along with an unrecognized cyclic or vibratory loading. A complete replacement of the pump seal cooler assembly to remove the welded connection was completed prior to the restart of Unit 1. The condition was immediately reported as a plant shutdown required by Technical Specifications (TS) pursuant o 10 CFR 50.72(b)(2)(i) and degraded condition pursuant to 10 CFR 50.72(b)(3)(ii)(A) (EN 51983). This event is being reported pursuant to 10 CFR 50. 73(a)(2)(ii)(A), 10 CFR 50. 73(a)(2)(i)(A), and 10 CFR 50. 73(a)(2)(i)(B), as a condition resulting in a principal safety barrier degradation, plant shutdown required by Technical Specifications, and as a condition prohibited by Technical Specifications. NRC FORM 366 (11-2015) Page 2 of 4 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and led back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555·0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Olficer, Olfice of Information and Regulatory Aflairs, CONTINUATION SHEET NEOB-10202. (3150-0104). Olfice of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER I I YEAR SEQUENTIAL REV Susquehanna Steam Electric Station, Unit 1 NUMBER NO. 05000387 2016 -019 -00 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 2, 9 percent Rated Thermal Power Unit 2 - Mode 1, 100 percent Rated Thermal Power There were no other structures, systems, or components that were inoperable at the start of the event that contributed to the event. EVENT DESCRIPTION Susquehanna Unit 1 commenced a manual shutdown on June 5, 2016 for a maintenance outage to investigate an increasing trend in unidentified drywellleakage. On June 6, 2016, at approximately 0556, with Unit 1 in Mode 2, leakage was identified from the inboard (pump-side) pipe-to-union weld on the Lower Seal Vent Line [EllS Component Identifier: PSP] for Unit 1 Reactor Recirculation [EllS System Identifier: AD] Pump [EllS Component Identifier: P] 1 B. The piping is classified as American Society of Mechanical Engineers (ASME) Class 2 and is part of the Reactor Coolant Pressure Boundary. The leak location is within the Reactor Recirculation loop isolation valves and is isolable from the reactor vessel [EllS Component Identifier: RPV]. The reactor was in Mode 2 at the time of discovery. A timeline of relevant events follows: November 2015 Unit 1 Scram as a result of a Main Steam Isolation Valve (MSIV) [EllS Component Identifier: ISV] closure. During drywell walk-downs, a leak was identified on the Reactor Recirculation Pump BLower Seal Vent Line. The pipe-to-union connection was replaced. March-April 2016 During Unit 1 Refueling and Inspection Outage (RIO), follow-up pipe support inspections were conducted and a welded shim was installed to prevent movement of Lower Seal Vent Line. June 2016 Unit 1 was down-powered to investigate an increasing trend in unidentified drywell leakage. Actual unidentified drywellleakage prior to shutdown was approximately 0.53 GPM. The inboard (pump-side) pipe-to-union weld on Lower Seal Vent Line for the Reactor Recirculation Pump B was identified as leaking. This event was reported pursuant to 10 CFR 50.72(b)(2)(i) and 10 CFR 50.72(b)(3)(ii)(A) (EN 51983). This Licensee Event Report (LER) is being communicated pursuant to 10 CFR 50. 73(a)(2)(ii)(A), 10 CFR 50. 73(a)(2)(i)(A), and 10 CFR 50. 73(a)(2)(i)(B), as a condition resulting in a principal safety barrier degradation, plant shutdown required by Technical Specifications, and as a condition prohibited by Technical Specifications. Page 3 of 4 | ML16216A374
PAGE | Unknown Unit | Reactor Coolant Pressure Boundary Leakage at LPRM Housing as a result of IGSCC | 10-31-2018 | On June 8, 2016 at approximately 02:26, while performing under vessel inspections, a Reactor Coolant Pressure Boundary (RCPB) leak was found at the Local Power Range Monitor (LPRM) 24-09 housing above the housing flange, on the LPRM housing tube. The leakage was determined to be non-isolable from the reactor vessel. The cause of the RCPB leakage was determined to be lntergranular Stress Corrosion Cracking (IGSCC). Corrective actions to repair the leak have been completed. In addition, a visual inspection was performed on all the Unit 1 LPRM, Intermediate Range Monitor (IRM), and Source Range Monitor (SRM) In-core monitor housings and no further issues were identified. There was no operational impact as a result of this event due to the plant being in Mode 4 at the time of discovery. This event resulted in an eight (8) hour Emergency Notification System (ENS) communication pursuant to 10 CFR 50.72(b)(3)(ii)(A). This Licensee Event Report (LER) is being communicated pursuant to 10 CFR 50.73(a)(2)(i)(B) and 10 CFR 50.73(a)(2)(ii)(A) as a condition prohibited by Technical Specifications and as degradation of a principal safety barrier. NRC FORM 366 (11-2015) Page 2 of 3 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and lnlormation Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office ol Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITYNAME 2. DOCKET NUMBER 3. LER NUMBER I I YEAR SEQUENTIAL REV Susquehanna Steam Electric Station, Unit 1 NUMBER NO. 05000387 2016 -020 -00 | CONDITIONS PRIOR TO EVENT Unit 1 -Mode 4, 0 percent Rated Thermal Power Unit 2- Mode 1, 100 percent Rated Thermal Power There were no systems, structures or components that were inoperable at the start of the event that contributed to the event. EVENT DESCRIPTION On June 8, 2016 at approximately 02:26, while performing under vessel inspections during a plant maintenance outage, a Reactor Coolant Pressure Boundary (RCPB) leak was found at the Local Power Range Monitor (LPRM) 24-09 housing [EllS Code: PEN] above the housing flange, on the LPRM stub housing. The leakage was determined to be about 2 drops per minute (DPM) with the reactor [EllS Code: RPV] de-pressurized and non-isolable from the reactor vessel. Further investigation, including Non Destructive Examination (NDE) was performed. The through-wall crack was characterized as tight, linear and approximately 1" in length, running parallel with the adjacent weld. The location of the crack was about 0.25 inches from the LPRM housing to flange weld in the heat affected zone (HAZ). This location is also considered not fully mitigated by Hydrogen Water Chemistry (HWC) due to configuration allowing the presence of stagnant water. Although formal laboratory analysis could not be performed on the crack, the cause of the RCPB leakage was determined to be lntergranular Stress Corrosion Cracking (IGSCC). The LPRM housing is fabricated of · SA 182- 304 Stainless Steel, which is susceptible to IGSCC. Additionally, this location is subject to reactor pressures, resulting in tensile stresses on the LPRM housing. There was no operational impact as a result of this event due to the plant being in Mode 4 at the time of discovery. This event resulted in an eight (8) hour Emergency Notification System (ENS) communication pursuant to 10 CFR 50. 72(b )(3)(ii)(A). This Licensee Event Report (LER) is being communicated pursuant to 10 CFR 50.73(a)(2)(i)(B) and 10 CFR 50.73(a)(2)(ii)(A) as a condition prohibited by Technical Specifications and as degradation of a principal safety barrier. CAUSE OF EVENT The cause of the RCPB leakage was the determined to be lntergranular Stress Corrosion Cracking (IGSCC). NRC FORM 366 (11-2015) PaQe 3 of 3 | ML16216A378
Browns Ferry Nuclear Plant | Unit 3 | High Pressure Coolant Injection System Found to be Inoperable During Testing | 08-05-2016 | During a surveillance test on June 8, 2016, the BFN, Unit 3, High Pressure Coolant Injection (HPCI) Turbine Stop Valve Mechanical Trip Valve behaved erratically upon turbine start. Troubleshooting and maintenance on the valve led to discovery of a condition that could have resulted in the HPCI system being unable to perform its required safety function in a Mode where HPCI Operability was required. The inoperability was caused by the HPCI Turbine Stop Valve Mechanical Trip Valve's Reset Spring, which was deformed and weakened from years of continuous compression. The spring was replaced and the system was returned to service on June 10, 2016. Corrective actions to prevent recurrence include revising preventive maintenance procedures to specify replacement of the Trip Tappet, Piston, and Reset Spring on a defined periodicity. Additionally, procedures will be revised to require testing the as-left breakaway force a minimum of three times to ensure repeatability. Preventative maintenance procedures will also be revised to clarify that lift force checks after spring compression adjustments shall be conducted with the auxiliary oil pump running. NRC FORM 366A (11-2015) Page 2 of 8 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send ~..)c,..._'-"'\' Rl:C'lu'-1,..1')1> comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to (fiffl~} LICENSEE EVENT REPORT (LER) ....... lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Browns Ferry Nuclear Plant, Unit 3 05000296 YEAR NUMBER NO. 2016 - 006 00 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Unit 3, was in Mode 1 at 100 percent power. II. Description of Events A. Event: On June 8, 2016 at 1037 Central Daylight Time (CDT), the BFN, Unit 3, High Pressure Coolant Injection (HPCI) system [BJ] was manually tripped following erratic operation upon turbine [TRB] start during a surveillance. In accordance with the surveillance procedures, the turbine steam supply valve (3-FCV-73-16) [FCV] was opened to supply steam to the turbine. Both the HPCI stop valve (3-FCV-73-18) [FCV] and control valve (3-FCV-73-19) [FCV] operated slowly and erratically. The HPCI turbine steam supply valve open signal, which also starts the auxiliary HPCI oil pump [P], was given at 1026 CDT. The expected system response was that the HPCI turbine stop valve would begin to open approximately 10 to 13 seconds later. However, the stop valve did not begin moving until 63 seconds after the start signal was given. The stop valve stayed open for 14 seconds before spuriously closing. The stop valve then remained closed for 8 seconds, then reopened, and the system appeared to operate normally. Troubleshooting identified that the HPCI Turbine Stop Valve Mechanical Trip Valve (i.e. "HPCI mechanical trip valve," 3-XCV-73-18) [XCV] was operating erratically. The HPCI mechanical trip valve must remain in its normal "stand-by" position during HPCI operation to allow the HPCI stop valve to remain open. If the HPCI mechanical trip valve is re-positioned, either by manually lifting its reset knob, or by the overspeed (OS) trip weight striking the bottom of the tappet assembly, then the control oil to the HPCI stop valve is dumped, closing the HPCI stop valve under spring pressure. The failure of this reset spring resulted in erratic HPCI stop valve operation during the system start on June 8, 2016. Because of this degradation in system reliability, Operations declared the HPCI system inoperable. The Unit 3 HPCI system had been declared inoperable prior to the event, on June 8, 2016 at 0925, to perform a routine surveillance. Operability was restored on June 10, 2016 at 0555 CDT, following a HPCI oil system check. The maintenance associated with the HPCI mechanical trip valve was not part of pre-planned maintenance activities. This event was determined to be reportable as a safety system functional failure in accordance with NUREG-1022, because the HPCI system, a single-train safety system, could have been prevented from performing its safety function in a Mode where HPCI Operability is required. NRG FORM 366A (11-2015) Page 3of8 | ML16218A477
St. Lucie | Unit 1 | Inadequate Legacy Evaluation for Containment High Range Radiation Monitor Nonconformance with Design Accuracy Requirements Resulted in Latent lnoper-ability and Operation Prohibited by Technical Specifications | 06-02-2016 | On June 2, 2016, St. Lucie Units 1 and 2 were in Mode 1 at 100% power. At 1500 hours FPL declared the containment high. range radiation monitors (CHRRMs) inoperable on both Units. FPL determined that the resolution of the-.NRC Information Notice (IN) 97-45 industry Operating Experience (OE) concerning CHRRMs cabling was less than adequate. The assumed CHRRMs design accuracy could not be assured during some postulated design basis accidents due to the errors introduced by thermal induced currents and water intrusion/cable blistering within the associated detectors' cabling, resulting in inoperable CHRRMs. The Technical Specifications (TSs) require pre- planned alternate means for containment radiation monitoring for inoperable CHRRMs; these requirements were not implemented until June 2016. FPL also submitted a TS 6.9.2 Special Report for two channels of inoperable CHRRMs. This legacy event was caused by the inadequate evaluation and improper tracking of actions required to fully close the nonconformance identified in the 1997 Information Notice. CHRRMs are used for information, they are not used to control radioactive releases or mitigate accidents. Their inoperability had no significant impact on the health and safety of the public. FPL plans to replace the CHRRMs cabling susceptible to the phenomenon identified in NRG Information Notice 97-45 and its supplement 1. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 01/31/2017 (02-2014) Estimated burden per response to comply with this mandatory collection request 80 hours. ,, Reported lessons learned are incorporated into the licensing process and fed back to industry . . ; Send comments regarding burden estimate to the FOIA, Privacy and Information Collections ..•... Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by LICENSEE EVENT REPORT (LER} internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budge~ CONTINUATION SHEET Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB conbol number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 6. LER NUMBER I 3. PAGE YEAR I SE N Q U U M E B N E T R IA L R N E O V . St. Lucie Unit 1 05000335 2 OF 4 2016 001 0 | · Description of the Event On June 2, 2016, St. Lucie Units 1 and 2 were in Mode 1 at 100% power. As discussed in the NRG design basis inspection report 05000335/2016010 and 05000389/2016010, FPL's 1997 evaluation of previous containment high range radiation monitor (CHRRM) [EllS:IL:RM] industry Operating Experience (OE) had incorrectly evaluated the impact of thermally induced currents (TIC) and moisture intrusion/cabl.e blistering on Rockbe~tos/Raychem coaxial cable [EllS:IL:CBL 1] and their effect on CHRRMs operability. At 1500 hours, FPL declared the CHRRMs inoperable and entered the appropriate action statements for each Unit. The limiting condition for operation (LCO) for Technical Specification (TS) 3.3.3.1, Action b, Table 3.3-6, Action 15 (Unit 1) and Action 27 (Unit 2), are essentially the same and state that: "With the number of channels OPERABLE [OPERABLE Channels - Unit 2] less than required by the Minimum Channels OPERABLE requirement, either restore the inoperable Channel(s) to OPERABLE status within 72 hours, or: 1) Initiate the preplanned alternate method of monitoring the appropriate parameter(s), and 2) Prepare and submit a Special Report to the Commission pursuant to Specification 6.9.2 within 14 days following the event outlining the action taken, the cause of the inoperability and the plans and schedule for restoring the system to OPERABLE status." · On June 4, 2016 the preplanned alternate methods for monitoring containment radiation levels were implemented in accordance with operator night orders and enhancements made to plant procedure EPG-08, "Monitoring Plant Equipment Important to the Radiological Emergency Plan," Attachment 2, "Alternate Monitoring Method with the CHRRM Channels Inoperable." The CHRRMs are used as one of several diverse methods for evaluating emergency action levels (EALs) for the Loss of Fuel Clad Barrier and for the Potential Loss of Primary Containment Barrier in the St. Lucie Emergency Plan (EPlan). Unit differences necessitate different strategies for the Loss of Fuel Clad Barrier EAL determined by CHRRMs indication. These preplanned alternate methods use: • the containment isolation radiation monitors (Unit 1), or • the diverse indications as defined in the EAL table to evaluate the loss of the fu13l clad barrier (Unit 2) (e.g. core exit thermocouples, Dose Equivalent 1-131, loss of the core heat removal safety function and entry into emergency operating procedure EOP-15) The Potential Loss of Primary Containment Barrier EAL determined by CHRRMs indication will be provided in part by the use of the post-LOCA radiation monitors with outside containment radiation levels that correlate to the radiation levels inside containment. Two inoperable CHRRMs require that the NRG be notified of this condition in accordance with TS 6.9.2. FPL submitted the special report on July 16, 2016, in FPL letter L-2016-127. Cause of the Event In 1997 and 1998, NRG Information Notice (IN) 97-45 and its !)upplement 1 notified the industry that the CHRRMs were subject to erratic behavior and possible failure because the expected post-accident environmental conditions within containment could adversely affect the cabling system. FPL's initial disposition of the issue considered the CHRRMs operable due to the short time period the effects lasted, the bounded containment LOCA temperature profiles, and the consideration of the diverse means available for accomplishing post-accident dose assessment, core damage assessment, and emergency plan (EPlan) actions. FPL intended | ML16230A000
PAGE | Unknown Unit | Secondary Containment Declared Inoperable Due to Airlock Doors Open Due to a Human Performance Error | 01-07-2016 | On June 22, 2016 at approximately 15:01, an engineer passing through a Unit 1 Reactor Building airlock inadvertently unlatched an outside airlock door, resulting in an airlock alarm indicating both doors were open simultaneously. This airlock serves as a secondary containment boundary; as such, having both doors open at the same time results in failure to meet Technical Specification 3.6.4.1 as a result of not satisfying Surveillance Requirement 3.6.4.1.3. The condition requires a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(v)(C). The cause of the event was the individual inadvertently utilized their key card for the wrong door and when opening the intended door, differential pressure caused a momentary violation of secondary containment. Corrective actions included coaching the engineer and reinforcing to all Engineering personnel the expectations for passing through airlocks. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366 (11-2015) Page 2 of 3 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated inlo the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555·0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER j I YEAR SEQUENTIAL REV Susquehanna Steam Electric Station, Unit 1 NUMBER NO. 05000387 2016 -021 -00 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 4, 0 percent Rated Thermal Power Unit 2- Mode 1, approximately 100 percent Rated Thermal Power There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. EVENT DESCRIPTION On June 22, 2016 at approximately 15:01, an engineer working with a team was passing through a Unit 1 Reactor Building [EllS System Code: NG] airlock [EllS Component Code: AL] to access the Unit 1 train bay. Once inside the airlock, the individual inadvertently unlatched the Reactor Building airlock door [EllS Component Code: DR], resulting in an airlock alarm [EllS Component Code: ALM], indicating both Reactor Building and train bay doors were open simultaneously. This airlock serves as a secondary containment [EllS System Code: VA] boundary; as such, having both doors open at the same time results in failure to meet Technical Specification 3.6.4.1 as a result of not satisfying Surveillance Requirement 3.6.4.1.3. The following is a time line of the event that occurred on June 22, 2016: 14:55 Engineering personnel arrived at Unit 1 Reactor Building airlock with the intent of passing through to the Unit 1 train bay. Individuals ensured they were in the correct location and discussed expectations for traversing through airlock. 14:59 Engineering personnel proceeded to key-card into the airlock through the Reactor Building door. 15:00 Once inside the airlock, one individual used the card reader inside the airlock, incorrectly assuming the card reader operated the train bay door. This unlatched the Reactor Building door; personnel were unaware the Reactor Building door had been unlatched 15:01 When the inner door was opened, differential pressure cause the unlatched Reactor Building door to open, resulting in an airlock alarm. The train bay door was then immediately closed. The individual self-identified that they had inadvertently assumed the need to key-card through the inner door to access the Unit 1 train bay. Upon receiving the airlock alarm, the train bay door was immediately closed. The condition requires a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(v)(C). CAUSE OF EVENT The cause of the event was the individual inadvertently utilized their key card for the wrong door and when opening the intended door, differential pressure caused a momentary violation of secondary containment. NRC FORM 366 (11-2015) Page 3 of 3 | ML16230A121
Quad Cities Nuclear Power Station | Unit 2 | Drywell/Suppression Chamber Differential Pressure, Primary Containment Oxygen Concentration Technical Specification Compliance | 07-25-2016 | On 05/23/16 Low Level Alarm 2A Recirc Motor occurred due to a low oil level condition for the 2A recirculation pump motor. As a result, the Station determined that a drywall entry was required to investigate the condition, make any needed repairs, and refill the oil reservoir. NRC provided that Station personnel did not comply with Technical Specifications (TS) 3.6.2.5 {OW to Suppression Chamber DP) and 3.6.3.1 (Primary Containment 02 concentration) since while in MODE 1, at the end of the 32 hour Completion Time {24 hour Action A, plus the 8 hour Action B) during the actual plant evolutions for power ascension, these Required Actions were not met because the associated Applicability for each TS were not met since the Unit remained in MODE 1. The cause of the issue was Station personnel understanding and application of the subject TS as used in context under this infrequent plant condition, differed from the NRC's understanding and application of the subject TS. The specific difference is with the application of the term, "start-up," as used in the LCO Applicability. Corrective actions included issuance of an Operations Standing Order, and revision of pertinent Operating procedures to ensure these Tech Specs are properly implemented. The safety significance of this event was minimal. Given the impact on the Drywall/Suppression Chamber Differential Pressure, and Primary Containment Oxygen Concentration Technical Specifications, this report is submitted for Unit 2 in accordance with the requirements of 10 CFR 50.73{a)(2)(i)(B), which requires the reporting of a past operation or condition which was prohibited by the olant Technical Soecifications. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) ~<l><;Pnatavi.,,c- ! . . ; .~ E R s e t p im or a te te d d l b e u s r s d o e n n s p l e e r a r r n e e s d p o a n r s e e t in o c c o o rp m o p ra ly t e w d i th in t t h o i s t h m e a n lic d e a n to s r i y n g c o p lle ro c c ti e o s n s re a q n u d e s fe t: d B O b a h c o k u r t s o . ~ Industry. Send comments regarding burden estimate to the FOIA, Privacy and Information •••• .I' LICENSEE EVENT REPORT (LER) Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by Internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of CONTINUATION SHEET Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 6. LER NUMBER I 3. PAGE YEAR I t;t:l.!Ut:NllAL REV Quad Cities Nuclear Power Station Unit 2 NUMBER NO. 2 OF 5 05000265 2016 003 00 | PLANT AND SYSTEM IDENTIFICATION General Electric -Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Compliance Issue with the Drywall/Suppression Chamber Differential Pressure, and Primary Containment Oxygen Concentration Technical Specifications A. CONDITION PRIOR TO EVENT Unit: 2 Event Date: May 25, 2016 Event Time: 11 :1 O hours Reactor Mode: 1 Mode Name: Power Operation Power Level: 100% B. DESCRIPTION OF EVENT On 05/23/16 Low Level Alarm [LA] 2A Recirc [AD] Motor [MO] occurred due to a low oil level condition for the 2A recirculation pump [P] motor. As a result, the Station determined that a drywall [NH] entry was required to investigate the condition, make any needed repairs, and refill the oil reservoir [TK]. NRC provided that Station personnel did not comply with TS 3.6.2.5 (DW to Suppression Chamber DP) and 3.6.3.1 (Primary Containment 02 concentration [BB]) since while in MODE 1, at the end of the 32 hour Completion Time {24 hour Action A, plus the 8 hour Action B) during the actual plant evolutions for power ascension, the Required Actions B for TS 3.6.2.5 and TS 3.6.3.1 were not met (at 1110 on 5/25/16, and 1123 on 5/25/16, respectively), because the Unit 2 LCO Applicability for establishing OW/Torus differential pressure and being fully inerted were not met since the Unit remained in MODE 1. NRC provided that these TS were not met when the Station improperly used the LCO Applicability (a), 24 hour "clock reset" allowance to proceed above 15% power "following startup" without setting the OW/Torus differential pressure (Dp) > 1 psid, and oxygen concentration < 4% (inerted), during the Unit 2 power ascension. NRC provided this is contrary to the NRC's "plain language" interpretation of this associated TS Applicability, in that "following startup" was intended to mean "following MODE 2." Furthermore, the NRC provided that the Unit did not exit the Mode of Applicability just by dropping below 15% Rated Thermal Power {RTP), since the Unit was still in MODE 1, and a total of only 32 hours was available to re-achieve OW/Torus Dp and reinert while remaining in MODE 1. While under this interpretation, the resulting available options during this drywall entry were to either: 1) re-establish OW/Torus Dp and inerting prior to reaching 15% RTP during the power ascension, or 2) to exit MODE 1 to reset the 24 hour clock (meaning to start power ascension from MODE 2). In this situation, the TS LCO Applicability is not clear, does not coincide with the Bases intent, and may be overly restrictive in that it uses the terms, "startup" and "shutdown." The cause of the issue was Station personnel understanding and application of the subject TS as used in context under this this infrequent plant condition, differed from the NRC's understanding and application of the subject TS. The specific difference is with the application of the term, "start-up," as used in the LCO Applicability. | ML16230A233
Brunswick Steam Electric Plant (BSEP) | Unit 2 | Mispositioned Valves Result in Residual Heat Removal Service Water System lnoperability | 10-31-2018 | On June 15, 2016, at 05:15 Eastern Daylight Time, Unit 2 was in Mode 1 (i.e., Run mode) at 100 percent of rated thermal power. At that time, Opera1ions personnel were preparing to run the Resid,ual Heat Removal Service Water (RHRSW) system in the spppression pool cooling mode. While performing the valve lineup, an alarm was received on low RHRSW suction pressure. Two instrument valves connected to the "B" and "D" RHRSW pump suctions were found closed. This resulted in the pump start logic being unable to sense RHRSW pump suction pressure, which prevented the pumps from being able to start. With the pumps unable to start, the associated RHRSW division was inoperable. It is most likely that the valves were mispositioned during a previous operation of the "B" RHRSW division. The event resulted from procedures which did not adequately control the position of the instrument valves. Corrective actions for this event included repositioning the valves to their correct configuration and revising applicable procedures. NRG FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150·0104 EXPIRES: 10/31/2018 . (06-2016)) Estimated burden per response to comply with this mandatory collection request: BO hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r30 collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant (BSEP) YEAR NUMBER NO. 05000-324 Unit 2 2016 - 001 000 | Energy Industry Identification System (EllS) codes are identified in the text as [XX]. Background Initial Conditions On June 15, 2016, at 05:15 Eastern Daylight Time (EDT), Unit 2 was in Mode 1 (i.e., Run mode) at 100 percent of rated thermal power. No out-of-service equipment contributed to, or affected the course of, this event. Reportability Criteria This event is being reported in accordance with 10 CFR 50.73{a)(2)(i)(B) because Unit 2 was operated in a condition prohibited by the Technical Specifications (TS). Specifically, one division of the Residual Heat Removal (RHR) [BO] Service Water (RHRSW) [Bl] system was found to be inoperable. The duration of the inoperability was based on the last successful operation of the RHRSW system, or June 4, 2016, at 14:41 EDT. TS Limiting Condition for Operation (LCO) 3.7.1 Condition B says that with one RHRSW subsystem inoperable for reasons other than Condition A (i.e., one pump inoperable), the system must be restored within 7 days or be in Mode 3 (i.e. shut down) within the following 12 hours. The plant was operated until June 15, 2016, at 05:45 EDT in this condition (i.e., 1O days, 15 hours, 4 minutes). Therefore, the plant was operated in a condition prohibited by the TS. Event Description On June 15, 2016, at 05:15 EDT, Unit 2 was in Mode 1 (i.e., Run mode) at 100 percent of rated thermal power. Operations personnel were preparing to start the RHRSW system in the suppression pool cooling mode. While opening Nuclear Service Water (NSW) system [Bl] valves to supply RHRSW, operators received an annunciator for RHRSW pump suction pressure being low. Personnel then identified two RHRSW instrument valves which were closed and should have been open. The associated instrument lines feed pressure instruments for the suction of the "B" and "D" RHRSW pumps. With the valves closed, suction pressure from NSW could not be sensed, and the RHRSW pumps could not start. Both instrument valves were immediately opened. This restored the affected RHRSW subsystem to operable status at 05:45 EDT on June 15, 2016. J ; ) ) Event Causes It is most likely that the instrument valve mispositioning occurred during a previous operation of the "B" division of RHRSW on April 6, 2016. Investigators found no evidence of tampering. The RHRSW suction valves were opened on June 4, 2016, at 14:41 EDT, and the low pressure annunciator did not alarm. The absence of the low pressure alarm confirms the "B" and "D" RHRSW pumps could have started. Therefore, the duration of inoperability is conservatively assumed to have begun on June 4, 2016, at 14:41 EDT. | ML16231A019
Duane Arnold Energy Center 05000-331 1 OF 5 | Unknown Unit | Two Instances of Both Doors in Secondary Containment Airlock Opened Concurrently - . | 08-18-2016 | On June 19, 2016, while operating at 82% power, two secondary containment access airlock doors were briefly opened simultaneously during a surveillance test. This event was a momentary inoperability of secondary containment integrity, which is an 8 hour reportable event. The Resident Inspector was notified, and an Event Notification made pursuant to 10 CFR 50.72(b)(3)(v)(C). (Reference EN#52022). Following the event, the door· controls were adjusted and verified to function properly. On June 29, 2016, at 100% power, workers opened two doors concurrently when entering a secondary containment access airlock. The individuals promptly closed their respective doors. The event was a brief inoperability of secondary containment integrity as above, notifications were made, and repairs completed. (Reference EN#52053) The root causes were determined to be inadequate procedural guidance and equipment design not being able to prevent the simultaneous opening of an inner and outer door at all times, under all possible conditions. Corrective actions include modification of the interlock tests, and replacement of key door interlock components. These events did not result in a safety system functional failure. There were no radiological releases associated with these events. NRC FORM 366 (02-2014) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 01/31/2017 (02-2014) . Estimated burden per response to comply with this mandatory collection request: 80 hours . e ., .:P"'«lto"<,..>o.. . Reported lessons learned are incorporated into the licensing process and fed back to industry. = .•~ Send comments regarding burden estimate to the FOIA, Privacy and Information Collections v.• .•••• I LICENSEE EVENT REPORT (LER) B in r t a e n rn c e h t ( e T -m -5 a F il 5 to 3 ), l n U fo . c S o . lle N c u ts c . le R a e r s o R u e r g c u e l @ ato n r r y c .g C o o v m , m an is d s i t o o n t , h e W a D s e h s in k g O to f n fic , e D r, C O 2 ff 0 ic 5 e 5 5 o - f 0 I 0 n 0 fo 1 r , m o a r t io b n y and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, CONTINUATION SHEET Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2; DOCKET 6. LER NUMBER 3. PAGE I YEAR I SEQUENTIAL REV NUMBER NO. Duane Arnold Energy Center 05000-331 2 OF 5 2016 001 00 | I. Description of Event: On June 19, 2016 at 1533, while operating at 82% power, the Control Room Supervisor (CRS) was notified that Door-281 and Door-282, both in Secondary Containment Airlock 153, had been opened concurrently during performance of STP 3.6.4.1-02, "Secondary Containment Airlock Verification," Revision 15, Step 7.1.1.e. This step directed the technician to attempt to open the inner door while the outer door was open The doors being open at the same time caused a failure.to meet SR · 3.6.4.1.2 to verify that either the outer door(s) or the inner door(s) in each Secondary Containment access opening are closed. The identified condition caused Secondary Containment to be considered inoperable per TS LCO 3.6.4.1. The technician involved immediately closed the doors upon encountering this unexpected condition. This action allowed SR 3.6.4.1.2 to be met, and restored Secondary Containment to ari operable status. On June 29, 2016 at 0940, while operating at 100% power, the CRS was notified that Door- 239A and Door-246, botli in Secondary Containment Airlock 222, the Reactor Building Railroad Airlock, had been opened concurrently. The doors being open at the same time caused a failure to meet SR 3.6.4.1.2 to verify that either the outer door(s) or the inner door(s) in each Secondary Containment access opening are closed. The identified condition caused Secondary Containment to be considered inoperable per TS LCO 3.6.4.1. The individuals involved· immediately closed their respective doors upon encountering this unexpected condition. This action allowed SR 3.6.4.1.2 to be met, and restored Secondary Containment to an operable status. Each of the above events resulted in an 8 hour reportable event. In both cases, the Resident Inspector was notified, and an Event Notification was made pursuant to 10 CFR 50.72(b)(3)(v)(C). (References EN #52022 and EN #52053). Secondary containment leak tightness is required to ensure that the release of radioactive materials from the primary containment is restricted to those leakage paths and associated leakage rates assumed in the accident analysis and that fission products entrapped within the secondary containment structure will be treated by the Standby Gas Treatment System prior to discharge to the environment. A Secondary Containment door airlock utilizes an interlock device with an adjustable permanent magnet (mounted on the door), and an electromagnet (on the door frame) arranged in an electrical circuit so that door(s) are held closed and/or are allowed to open · after a pushbutton is depressed. · Immediately following the event on June 19, troubleshooting adjusted an interlock magnet and by 1651 hours post-maintenance testing had been performed satisfactorily per Surveillance Test Procedure (STP) 3.6.4.1-02, Secondary Containment Airlock Verification. | ML16232A600
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Transformer Fault Results in Manual Scram and Secondary Containment Vacuum Below Technical Specification Limit | 10-31-2018 | On June 24, 2016, at 1205, several 600V electrical busses lost power when James A. FitzPatrick Nuclear Power Plant was operating at 100% power. A fault in transformer 71T-5 caused a trip of circuit breaker 71-10340. Power was lost to 2 of 3 Reactor Building Closed Loop Cooling (RBCLC) pumps and 2 of 3 lube oil pumps for the Motor-Generator (MG) Set for ‘A’ Reactor Water Recirculation (RWR). The ‘A’ RWR pump tripped immediately causing reactor power to reduce to approximately 50%. The remaining RBCLC pump was inadequate to maintain the MG Set fluid drive oil temperature for the ‘B’ RWR pump so Operators initiated a manual scram at 1236. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A). The power loss also affected Reactor Building Ventilation (RBV). This system supports the requirement of Technical Specification Surveillance Requirement 3.6.4.1.1 for a differential pressure in Secondary Containment. At the loss of RBV, Secondary Containment automatically isolated and the Standby Gas Treatment system was manually initiated. However, during this short transition the differential pressure requirement was not met. This report is being submitted per 10 CFR 50.73(a)(2)(v)(C). The apparent cause of the 71T-5 fault was inadequate preventative maintenance which allowed the transformer to remain in service beyond expected service life. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 – 333 NUMBER N0. 2016 – 004 – 00 | Background James A. FitzPatrick Nuclear Power Plant (JAF) 600V electrical distribution system [EIIS identifier: EC] is supplied by stepping down 4160V to 600V through one of twelve transformers (T-5 to T-16). Nonsafety-related electrical busses are supplied by T-5 to T-12 and safety-related electrical buses by T-13 to T16. (See Figure: Electrical Distribution). A transformer uses a type of cellulose paper insulation between windings. The insulator material must have a large enough dielectric property to prevent electrical breakdown under high voltages. Electrical faults can occur if the insulator material degrades or becomes damaged. Many outdoor transformers are liquid-immersed using a highly refined mineral oil that cools and insulates the windings. Since electrical faults could breakdown the oil into combustible gases, extra fire protection measures are needed when using them indoors. Dry-type transformers use air cooling instead of oil. Both dry-type and liquid-immersed transformers are often self- cooled by natural convection. As power ratings increase, transformers are often cooled by forced-air cooling, forced-oil cooling, water-cooling, or combinations of these. All twelve 4160V to 600V transformers at JAF are dry-type and force-air cooled except T-5 and T-13 which are dry-type and convection cooled. This licensee event report (LER) addresses an electrical fault in T-5 caused by insulation breakdown. Event Description On June 24, 2016, at 12:05, when JAF was operating at 100% power, several 600V electrical busses lost power. A fault in 71T-5 caused breaker 10340 to trip. This breaker connects 4160V to four transformers which each provide power to a 600V bus: 11300 (L-13), 12300 (L-23), 13300 (L-33), and 14300 (L-43). These electric buses provide power to a variety of nonsafety-related plant loads; notable equipment include:  Reactor Water Recirculation (RWR) [AD], 2 of 3 Motor-Generator (MG) Set lube oil pumps for “A” recirc pump and 1 of 3 MG Set lube oil pumps for “B” recirc pump.  Reactor Building Closed Loop Cooling (RBCLC) [CC], 2 of 3 pumps  Fuel Pool Cooling [DA], 1 of 2 recirculation pumps  Reactor Building Ventilation (RBV) [VA], 2 of 3 supply fans and 2 of 4 exhaust fans  Service Air [LF], Instrument Air [LD], and Breathing Air [LH], 2 of 3 air compressors  Reactor Water Cleanup [CE], 1 of 2 pumps Immediately following breaker 10340 trip “A” RWR pump tripped causing reactor power to decrease to approximately 50%. MG Set fluid drive oil temperature for the “B” RWR pump began to rise because the single RBCLC pump was insufficient to maintain its temperature. Three of four nonsafety-related 600V electric buses affected by this event were crossed tied to the other four nonsafety-related 600V electric buses. This was not done for L-13 since the source of the fault was not known during the event. When power was lost to RBV fans, Secondary Containment [NG] automatically isolated and differential pressure began to degrade. Standby Gas Treatment (SBGT) [BH] was manually initiated and differential pressure was restored by 12:19. At 12:36, Operators initiated a manual scram. The event was reported to the NRC as ENS 52042. Page 2 of 5 | ML16236A390
Clinton Power Station | Unit 1 | Trip of Fuel Building Fans Due to Damper Failure Results in Loss of Secondary Containment | 08-22-2016 | On June 24, 2016 at 1511 (CST) Clinton Power Station (CPS) was operating at 99 percent reactor power when the MCR received two Fuel Building (VF) trouble alarms. An unexpected damper closure resulted in Secondary Containment (SC) vacuum degrading, eventually exceeding the Technical Specification {TS) limit of 0.25 inch vacuum water gauge. TS Limiting Condition for Operation (LCO) 3.6'.4.1, Secondary Containment, Required Action A.1 and Emergency Operating Procedure (EOP) - 08, Secondary Containment Control were entered. At 1512, SC vacuum was restored within TS limits with the auto start of VF supply fan 1 VF03CB and exhaust fan 1 VF04CB. An initial Investigation determined that the 'A' Exhaust Fan Isolation Damper 1VF11VA had failed to the closed position on loss of air due to failure of the associated air supply solenoid, 1 FSVVF005. The apparent cause of this event is the failure of the ASCO solenoid valve, 1 FSVVF005, due to a slightly deformed and worn core which resulted in sticking. The failed solenoid valve 1 FSVVF005 was replaced and the VF system ventilation was restored. In addition, parts quality testing, and preventative maintenance programs are being established to replace VF solenoid operated valves on a periodic basis. The temporary loss of SC is reportable under 1O CFR 50. 73{a){2){v)(C) as an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material. NRG FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016)) Estimated burden per response to comply with this mandatory collection request: 80 hours .. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555·0001, or by e-mail to lnfocollects.Resource@nrc.gov. and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150·0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Clinton Power Station, Unit 1 05000461 YEAR NUMBER NO. 2016 - 009 - 00 | PLANT AND SYSTEM IDENTIFICATION General Electric-Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX] EVENT IDENTIFICATION Trip of Fuel Building Fans Due to Damper Failure Results in Loss of Secondary Containment A. Plant Operating Conditions before the Event Unit: 1 Event Date: 06/24/16 Event Time: 1511 Mode: 1 Mode Name: Power Operation Reactor Power: 99 percent B. DESCRIPTION OF EVENT On June 24, 2016 at 1511-(CST) Clinton Power Station (CPS) was operating at 99 percent reactor power when the MCA received two unexpected annunciators associated with the Fuel Building ventilation system (VF), 5042-4D {Trouble VF system local panel 1 PL44J) and 5042-5D (Hi Diff Press Fuel Bldg). Subsequent investigation determined that VF exhaust fan isolation damper . 1V F11 YA had failed closed as a result of a failure of solenoid 1 FSVVF005. As a result, Secondary Containment (SC) vacuum degraded, eventually exceeding the Technical Specification {TS) limit of 0.25 inch vacuum water gauge (WG). Both the Fuel Building (FB) 'B' supply and exhaust fans auto started as designed, to restore SC vacuum, however, the sequence was not timely enough to prevent the FB differential pressure from exceeding the TS requirement. TS Limiting Condition for Operation (LCO) 3.6.4.1, Secondary Containment, Required Action A.1 and Emergency Operating Procedure (EOP) - 08, Secondary Containment Control were entered. The momentary loss of the VF fans also resulted in no flow through the VF exhaust ductwork and; therefore, duct monitors 1 RIX-PR006A-D were declared inoperable. The lack of monitored VF exhaust flow associated with LCO 3.3.6.2, Secondary Containment Isolation Instrumentation, Fuel Building exhaust radiation resulted in a momentary loss of SC isolation capability and Standby Gas Treatment System (SGTS) initiation capability on VF exhaust high radiation. As a result of this condition, LCO 3.3.6.2 Required Actions A.1 and Action B.1 were entered. At 1512, SC vacuum was restored within TS limits following the auto start of supply fan 1V F03CB and exhaust fan 1V F04CB. TS LCO 3.6.4.1 Required Action A.1-and TS LCO 3.3.6.2 Required Actions A.1 and B.1 were subsequently exited. At 1602, EOP-08 was exited. CPS replaced failed solenoid valve 1 FSVVF005. In addition, Exelon Powerlabs evaluated a similar failed ASCO solenoid valve in determining a cause of component failure. The failure conditions of this valve were similar based on observations by field technicians. CPS concluded the apparent cause of ASCO solenoid valve 1 FSVVF005 failure was due to sticking as a result of a slightly deformed and worn core .. The Powerlabs evaluation further attributed the most likely cause of the initiating event to a manufacturing defect in the solenoid valve due to its low inservice time (11 months). NAG FORM 366A (06-2016) Page_2_ of_.!__ | ML16238A478
Dresden Nuclear Power Station | Unit 3 | Alert Declared from Unit 3 HPCI Auxiliary Oil Pump Motor Fire | 08-25-2016 | On 6/27/16 at approximately 1042 CDT, the High Pressure Coolant Injection (HPCI) Auxiliary Oil Pump (AOP) motor failed and was discovered on fire during the performance of the quarterly operability run of the HPCI system. The fire was extinguished manually at 1045 CDT with a carbon dioxide fire extinguisher. At 1050 CDT, an ALERT was declared. The fire did not adversely impact the operation of any system other than HPCI which was inoperable prior to the fire due to the operability run. At 1319 CDT, the ALERT was terminated. The unit remained at full power throughout the evolution. This event is reportable under 1 O CFR 50.73(a)(2)(v)(D), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident." NRG FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and led back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/@l} collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR NUMBER NO. Dresden Nuclear Power Station, Unit 3 05000-249 2016 - 001 - 00 | PLANT AND SYSTEM IDENTIFICATION Dresden Nuclear Power Station (DNPS), Unit 3, is a General Electric Company Boiling Water Reactor with a licensed maximum power level of 2957 megawatts thermal. The Energy Industry Identification System codes used in the text are identified as [XX]. A. Plant Conditions Prior to Event: Unit: 03 Event Date: 06/27/16 Event Time: 1042 CDT Reactor Mode: 1 Mode Name: Power Operation Power Level: 100 percent 8. Description of Event: On 6/27/16 at approximately 1042 CDT, the High Pressure Coolant Injection (HPCI) [BJ] Auxiliary Oil Pump (AOP) motor failed during the performance of the quarterly operability run of the HPCI system. HPCI was the only system inoperable at the time. Alarms were received in the Main Control Room (MCR), and the HPCI turbine was immediately tripped. The HPCI steam inlet inboard isolation valve (3-2301-4) and HPCI main pump torus discharge minimum flow valve were closed (3-2301-14). The AOP motor was secured, and Equipment Operators standing by in an adjacent room were dispatched to investigate the AOP. Upon opening the door, active flames were visible at the top and bottom of the AOP motor along with light smoke in the room. This observation was immediately communicated to the MCR, and the fire was extinguished manually at 1045 CDT with a carbon dioxide fire extinguisher. At 1046 CDT, the Incident Commander and the fire brigade were contacted to report to the Unit 3 HPCI Room, and the Unit 2/3 Diesel Fire Pump automatically started due to the HPCI Room Fire Protection [KP] piping filling with water in anticipation of initiating the sprinkler system. However, initiation of the sprinkler system was not required since the fire was quickly extinguished. At 1050 CDT, an ALERT was declared. At 1319 CDT, the ALERT was terminated. The unit remained at full power throughout the evolution. On 7/7/16 at 1625 CDT, HPCI was returned to service. This event is reportable under 10 CFR 50.73(a)(2)(v)(D), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident." C. Cause of Event: The Root Cause of the HPCI AOP motor failure is inadequate control of critical parameters when installing a DC shunt wound motor. The Failure Mechanism was high armature current with a stalled rotor. The Contributing Cause of the HPCI AOP motor failure is historical motor procurement evaluation standards were not rigorous enough. | ML16239A393
Brunswick Steam Electric Plant (BSEP) | Unit 2 | High Pressure Coolant Injection System Inoperable due to Failed Relay Coil | 02-09-2016 | On July 5, 2016, at 1640 Eastern Daylight Time (EDT), the Unit 2 High Pressure Coolant Injection (HPCI) system was declared inoperable due to apparent failure of the HPCI Auxiliary Oil Pump. The HPCI Auxiliary Oil Pump provides hydraulic pressure required to open the HPCI Turbine Stop Valve and the HPCI Turbine Control Valve during initial HPCI startup. Failure of the HPCI Auxiliary Oil Pump prevents the HPCI system from performing its safety function. This condition is being reported in accordance with 1O CFR 50. 73(a)(2)(v)(D), as an event or condition that could have prevented the fulfillment of the safety function of a system that is needed to mitigate the consequences of an accident. The HPCI system inoperability was due to loss of control power for the Auxiliary Oil Pump. The loss of control power was caused by a failed motor overload alarm relay coil; which caused current flow in excess of the control power fuse rating. The HPCI system was restored on July 6, 2016, at 1050 EDT. The alarm relay coil failure was age related. The corrective actions include creation of preventive maintenance tasks to replace the Unit 1 and 2 HPCI motor overload alarm relay coils on an appropriate frequency. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06·2016)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send ~~.,_,"1-flill.£011'-t>o comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T·5 { ? <'. ~'"i LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555·0001, or by e-mail to ~ . ~ ..... , ..~... . · l CONTINUATION SHEET N ln E fo O co B l - le 10 ct 2 s 0 .R 2, e s (3 o 1 u 5 rc 0 e -0 @ 10 n 4 rc ), . g O o f v fi , c e a n o d f t M o a th n e a g D em es e k n O t a ff n ic d e r B , u O d f g fi e c t e , W of a In sh fo in rm gt a o t n io , n D a C n d 2 0 R 5 e 0 g 3 u . lat I o f r a y A m f e fa a ir n s s , used to impose an information collection does not display a currently valid OMB control number, the {See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant (BSEP), YEAR NUMBER NO. 05000-324 Unit 2 2016 - 002 00 | Energy Industry Identification System (EllS) codes are identified in the text as [XX]. Background Initial Conditions At the time of this event, Unit 2 was in Mode 1 at approximately 100 percent of rated thermal power. The Reactor Core Isolation Cooling (RCIC) system [BN], Automatic Depressurization System (ADS), Low Pressure Coolant Injection (LPCI) system [BO], and Core Spray (CS) system [BM] were operable at the time of the event. Reportability Criteria This condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D), as an event or condition that could have prevented the fulfillment of the safety function of a system that is needed to mitigate the consequences of an accident. The NRC was initially notified of this event on July 5, 2016 (i.e., Event Number 52064). Event Description On July 5, 2016, at 1640 Eastern Daylight Time (EDT), the Unit 2 High Pressure Coolant Injection (HPCI) system [BJ] was declared inoperable after the control room received annunciator 2-A-1 (3-3), 11HPCI Aux Oil Pump Motor Overload.11 Upon further investigation, it was determined that the HPCI Auxiliary Oil Pump motor overload alarm relay (i.e., 2-2XDA-B11-74) had failed and blown the associated control circuit fuse (i.e., 2-2XDA-B11-2FU). The HPCI Auxiliary Oil Pump provides hydraulic pressure required to open the HPCI Turbine Stop Valve and the HPCI Turbine Control Valve during initial HPCI startup. With failure of the relay, the HPCI Auxiliary Oil Pump was incapable of starting; rendering the HPCI system inoperable. Operability of the HPCI system was restored on July 6, 2016, at 1050 EDT. Event Cause The cause of the Unit 2 HPCI inoperability was determined to be age related failure of HPCI Auxiliary Oil Pump motor overload alarm relay (i.e., 2-2XDA-B11-74) coil. The failed relay is normally energized and was original plant equipment. The equipment reliability classification was 11lmportant" as opposed to "Critical." Based on this classification, preventive maintenance had not been performed to replace the Unit 2 relay. The Unit 1 HPCI Auxiliary Oil Pump motor overload alarm relay was last replaced in January 1995. | ML16242A191
Pilgrim Nuclear Power Station | Unknown Unit | Online Maintenance Test Configuration Prohibited By Technical Specifications | 10-31-2018 | On April 19, 2016, at approximately 1450 hours, it was discovered that a maintenance activity performed between 2010 hours on August 26, 2014 and 0143 hours on August 27, 2014, had rendered the Startup Transformer (X4) and the standby Emergency Diesel Generators (EDG) (X-107 A&B) unable to automatically supply power to Buses A5 and A6, due to the breaker interlock that would prevent Startup Transformer breakers (152-504 and 152-604) and standby EDG breakers (152-509 and 152-609) from closing, when Bus AB to Bus A5 breaker (152-501) and Bus AB to Bus A6 breaker (52-601) are in the TEST position and CLOSED. During the maintenance activity, the plant was operating at 100 percent power and the_ Unit Auxiliary Transformer (X3) was providing power to Emergency Buses A5/A6. The functional testing of negative sequence relays (146-600/A and B) and 23kV feed undervoltage relays (127-600A/1 and 2, and 127-600B/1 and 2) created a test configuration, lasting less than 1-hour, whereby power to Buses A5 and A6 was not automatically available from either the startup transformer or from the EDGs. As a result, Limiting Conditions for Operation (LCO) Action Statement 3.9.B.2 was not met. The root cause is that the decision to perform the described surveillance testing online, instead of during cold shutdown, lacked sufficient rigor to ensure compliance with Technical Specifications. Corrective actions will establish and ' institutionalize expectations and accountability for station leadership regarding consequence-biased decision-making and effective risk manaaement. There was no imoact to nublic health and safetv. NRC FORM 366A (06-2016) Page 2of7 NRC FORM366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send ~ ~ .... ' .r t) c F o 5 m 3) m , en U ts .S r . e g N ar u d c in le g a r b ur R d e e g n u e la s t t o im ry a te C t o o m t m he is s F io O n I , A , W P a r s iv h a in cy g to a n n , d ln D f C o nn 2 a 0 t 5 io 5 n 5 -0 C 0 o 0 ll 1 e , c tio o n r s b B y r a e n - c m h ai ( l T - to 5 LICENSEE EVENT REPORT (LER) lnfocollects.Resoun:e@nrc.gov, and to the Desk Officer, Office of lnfonnation and Regulatory Affairs, NEOB-10202, (315().0104), Office of Management and Budget, Washington, DC 20503. If a means CONTINUATION SHEET used to impose an infonnation collection does not display a currenUy valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the infonnation collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR NUMBER NO. Pilgrim Nuclear Power Station 05000293 2016· 002 01 | BACKGROUND There are six 4, 160 volt alternating current (AC) buses (A 1, A2, A3, A4, AS, and A6) in the station auxiliary power distribution system. The six buses are divided into emergency service and normal service buses. The two emergency service buses, AS and A6, supply power to essential loads required during abnormal operational transients and accidents. The four normal service buses, "A 1, A2, A3, and A4, supply power to other station auxiliaries requiring AC power during planned operations. The maintenance activity had no effect on the normal service buses. · When the Pilgrim Nuclear Power Station (PNPS) is on line and buses AS and A6 are powered from the Unit Auxiliary Transformer, on a turbine trip or reactor scram, Buses AS and A6 should fast transfer to the startup transformer or dead bus transfer to EDGs if the startup transformer is unavailable or dead bus transfer to the shutdown transformer if both the startup transformer and EDGs are unavailable. Another 4160 volt bus, Bus A8, is powered from either the shutdown transformer through Breaker A802 or the Station Blackout Diesel Generator (SBODG) through Breaker A801. Bus A8 provides power to Emergency Bus AS through Breakers A600 and AS01 and to Emergency Bus A6 through Breaker A600 and A601. Relays in the Bus A8 to Bus AS and Bus A8 to Bus A6 control circuits are tested while the plant is online, at a two year interval, in accordance with Procedure 3.M.3-1, AS/A6 Buses 4kV Protective Relay Calibration/Functional Test and Annunciator Verification, Attachment 10, Bus A8 to AS & A6 Relays. See Figure 1 for bus and breaker arrangement. ' Procedure 3.M.3-1, Revision 136, step 6.2[S] and Attachment 10, provide a caution that during the performance of Attachment 10, with breakers 1S 2-S01 and 1S 2-601 in the TEST position and CLOSED, in the presence of a plant Scram neither AS nor A6 would automatically transfer to the Startup Transformer rendering both buses unavailable. Based upon this caution, activity risk compensatory measures for the August 2014 maintenance activity included a compensatory measure for operators to be briefed such that in the event of a plant trip the 1S 2-S01 and1 S2-601 breakers would be tripped to restore the automatic load transfer function. The compensatory measure is a simple single control switch manipulation for each of the two buses. Procedure 3.M.3-29, Shutdown Transformer and 23kV Relay Calibration and Functional Test, Revision 23, included, Prerequisite step 7.1[4], which states: "With permission from the Shift Manager (depending on weather conditions), the relays in Attachment 1 Step [2] may be calibrated with the Shutdown Transformer on line. The relays are to be calibrated one at a time. If plant electrical distribution will require the Shutdown Transformer to be loaded, the relay will be installed in an expeditious manner." Consistent with this prerequisite, a Control Room Narrative Log entry on February 20, 2014, at 1200 hours 17 seconds, indicates that a Pre~Evolution Brief (PEB) was conducted for 3.M.3-29 to bring attention to the following: the limiting condition for operation (LCO) for shutdown transformer (SOT) will be entered but SOT will remain available; and per procedure, the associated protection relays will be removed from service for functional test and calibration, one at a time, with procedures in place to return to service expeditiously in the event that plant electrical distribution requires the SOT to be loaded; and that E-lab personnel have been briefed and will remain on-site with no concurrent duties while the relays are out of service (OOS)." NRG FORM 366A (06-2016) Page 3of7 NRC FORM366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 , (06-2016) ...... Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported \¥)~ lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and lnfonmation Collections Branch (T-5 ..... F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of lnfonmation and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means CONTINUATION SHEET used to impose an infonmation collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person. is not required to respond to, the infonmation collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR NUMBER NO. Pilgrim Nuclear Power Station 05000293 2016 002 01 NARRATIVE For general information, when a 4160 volt breaker is required to be in TEST position, the breaker shall have been racked down, test position spindle inserted, test position cable assembly in place, 125 volt direct current (DC) control knife blade disconnect in closed position, and 4160 volt breaker springs charged. As specified under Limiting Conditions for Operations (LCO) Action Statement 3.9.B.2, "From and after the date that incoming power is not available from both startup and shutdown transformers, continued operation is permissible, provided both diesel generators and associated emergency buses remain operable, all core and containment cooling systems are operable, and reactor power level is reduced to 25 percent of design". EVENT DESCRIPTION On April 19, 2016, at approximately 1450 hours, it was discovered, and documented in the Corrective Action Program under Condition Report CR-PNP-2016-02735, that maintenance activities performed on protective relays between 2010 hours on August 26, 2014 and 0143 hours on August 27, 2014, had rendered the Startup Transformer (X4) and the standby EDGs (X-107A&B) unable to automatically supply power to Buses A5 and A6, due to the breaker interlock that prevents Startup Transformer breakers (152-504 and 152-604) and Standby EOG breakers (152-509 and 152-609) from closing when Bus A5 breaker (152-501) and Bus A6 breaker (52-601) are in the TEST position and CLOSED. With incoming power unavailable from the shutdown transformer and power not automatically available from the startup transformer or the standby EDGs, the Limiting Conditions for Operation (LCO) 3.9.B.2 was not met. See Figure 1 for bus and breaker configuration. During functional testing of negative sequence relays 146-600/A and B undervoltage relays 127-600A/1 and 2 and 127-600B/1 and 2, breakers 152-501 (shutdown transformer supply to Bus A5) and 152-601 (shutdown transformer supply to A6) are closed briefly and tripped on three different occasions in accordance with Procedure 3.M.3-1, Attachment 10. Based on a review of associated alarm data, operator logs, and interviews with maintenance personnel, the longest single duration when the buses were not operable was approximately 13 minutes; the combined duration is estimated to be approximately 33 minutes. Since this event occurred in the past, no immediate actions were required. Work Order (W0-52581_885) for the next scheduled functional test has been placed on administrative hold pending implementation of associated corrective actions. CAUSE OF THE EVENT While performing the extent of condition review for this event it was discovered, and entered into the Corrective Action Program under CR-PNP-2016-04139, that surveillance procedure 3.M.3-29, Shutdown Transformer and 23kV Relay Calibration and Functional Test, places the 4160V AC System in similar test configurations and operating conditions as procedure 3.M.3-1, Attachment 10. When the four year interval functional test required by procedure 3.M.3-29 was performed in February of 2014 it placed the plant in a configuration where both 4kV Emergency Buses A5 and A6 would have been prevented from automatically transferring to back-up power sources for approximately 26 minutes. Accordingly, the scope of the causal evaluation addresses the surveillance test configurations established by procedure 3.M.3-1, Attachment 10, and procedure 3.M.3-29. NRG FORM 366A (06-2016) Page 4of7 NRC FORM366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150--0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send ~~ comments regarding burden estimate to the FOIA, Privacy and lnfonnation Collections Branch (T-5 ~ ....~. } I F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of lnfonnation and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means CONTINUATION SHEET used to impose an infonnation collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the infonnation collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR NUMBER NO. Pilgrim Nuclear Power Station 05000293 2016 002 01 NARRATIVE The root cause for placing the plant in a configuration where both Emergency Buses A5 and A6 would have been prevented from automatically transferring to back-up power sources is that the decision to perform 3.M.3-1, Attachment 10, and 3.M.3-29 online, instead of during cold shutdown, lacked sufficient rigor to ensure compliance with Technical Specifications. A contributing cause of this condition is corrective actions were ineffective in resolving identified risks with the online performance of 3.M.3-1Attachment10 and 3.M.3-29 protective relay functional tests. Another contributing cause is that Senior Reactor Operators have.less than adequate task specific knowledge of Limited Conditions.for Operation. CORRECTIVE ACTIONS The corrective action to prevent recurrence is to establish and institutionalize expectations and accompanying accountability for station leadership (i.e., supervisor and above) regarding consequence-biased decision making and effective risk management. Other correction actions include: • Revising procedures 3.M.3-1, Attachment 10, and 3.M.3-29 so that they may only be performed while in 1 the cold shutdown condition • Providing training to personnel on condition report initiation (Problem Identification) and corrective action closure quality (Evaluation and Resolution) • Developing and presenting training to SROs on integrated knowledge of operability, availability, risk mitigation, and LCO requirements SAFETY CONSEQUENCES The actual consequences of the procedure 3.M.3-1, Attachment 10, and procedure 3.M.3-29 surveillance test configurations placed the plant in a condition not allowed by Technical Specifications. As there was no initiating event, there were no actual safety consequences. The performance of procedure 3.M.3-1 and procedure 3.M.3-29 surveillance testing placed the plant in a configuration where both 4KV Emergency Buses A5 & A6 would have been prevented from automatically transferring to back-up power sources upon a plant scram. This testing placed the plant in a condition not allowed by Technical Specifications. Had there been an initiating event (plant scram) during the performance of procedure 3.M.3-1, both Emergency Buses A5 and A6 would be inoperable immediately and until the recovery action (tripping of breakers 152-501 and 152-601) took place. The recovery action is a simple action, capable of being performed in the main control room or locally, and was part of the pre-job brief. Because the test configuration was brief and because qualified, dedicated operators were briefed and available to perform simple compensatory measures, the potential safety consequence was considered minimal. | ML16250A013
Brunswick Steam Electric Plant (BSEP) | Unit 1 | Tornado Missile Vulnerability Results in Condition Prohibited by Technical Specifications | 10-31-2018 | On July 21, 2016, Units 1 and 2 were in Mode 1 (i.e., Run mode) at 100 percent of rated thermal power. At that time, Engineering personnel determined that a conduit in the Emergency Diesel Generator building was vulnerable to a tornado missile. The conduit contains cables associated with Unit 2 Nuclear Service Water (NSW) pump "B". If the cables were disabled by a tornado missile, NSW pump 2B would be inoperable. The plants' Technical Specifications (TS) require three of the site's four NSW pumps to be operable. Thus, any of the other NSW pumps removed from service for longer than the TS-allowed out of service time would be a condition prohibited by the TS. It has been found that this condition occurred. Enforcement Guidance Memorandum (EGM) 15-002 was implemented, and NSW pump 2B was considered operable but nonconforming. The tornado missile vulnerability has existed since original plant construction. Immediate compensatory measures included verifying that station procedures address tornadoes, high winds, and potential loss of vulnerable equipment, and confirming or receiving training on procedures to be used if a tornado watch or warning is issued. Planned corrective actions include implementing more comprehensive compensatory actions and permanently eliminating the vulnerability to a tornado missile. NRG FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send l .:l•~ R£o"<-.-""o comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 11.. . LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to ~ ?: CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, -e... ~. .., ........ NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMS control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant (BSEP) 05000-325 YEAR NUMBER NO. Unit 1 2016 - 004 000 | Energy Industry Identification System (EllS) codes are identified in the text as [XX]. Background Initial Conditions On July 21, 2016, Unit 1 and Unit 2 were both in Mode 1 (i.e., Run mode) at 100 percent of rated thermal power. Except as described below, no out-of-service equipment contributed to, or affected the course of, this event. Reportability Criteria This event is being reported in accordance with 1O CFR 50.73(a)(2){i)(B) because Units 1 and 2 were operated in a condition prohibited by the Technical Specifications (TS). Specifically, the Unit 2 "B" Nuclear Service Water (NSW) [Bl] pump was inoperable because some of its control cables were vulnerable to a postulated tornado missile. Both units' TS require at least three of four site NSW pumps to be operable when the units are at power. Therefore, inoperability of the Unit 2 "B" NSW pump alone did not require entry into a TS condition. lnoperability of a second NSW pump constitutes a loss of one required pump. In both units' TS, Limiting Condition for Operation (LCO) 3.7.2, Condition B, says that with one NSW subsystem inoperable for reasons other than Condition A (i.e., one required NSW pump inoperable due to header inoperable on the opposite unit), the system must be restored within seven days or be in Mode 3 (i.e., Hot Shutdown) within the following 12 hours. When the affected Unit 2 NSW pump was considered inoperable due to tornado missile vulnerability, and an additional site NSW pump became unavailable, then the plant entered Condition Bas described above. In the past three years, two instances were identified in which the plant entered this condition, and the time to restore compliance with the LCO exceeded seven days, twelve hours. Therefore, the plant was operated in a condition prohibited by the TS. The two instances occurred as shown below. Pumps Out of Service Beginning of Condition End of Condition Duration 2B and 1B NSW Jul 8, 2013 at 2:05 EDT Jul 19, 2013 at 1: OO EDT 10.95 days 2Band 1B NSW Aug 26, 2013 at 1: 39 EIDT Sep 5, 2013 at 5:43 EDT 10.17 days This event did not result in the safety function of NSW being lost because sufficient NSW capacity remained available in the two pumps that remained unaffected on each occasion. Additional cooling capacity available via Conventional Service Water (CSW) [KG] pumps which can be aligned to supply the NSW header. NRG FORM 366A (06-2016) Page _2_ of _4_ | ML16271A187
Susquehanna Steam Electric Station | Unit 2 | Unit 2 experienced an electrical transient resulting in a manual SCRAM | 07-12-2016 | At 23:55 on 5/12/16, Unit 2 experienced an electrical transient resulting in a loss of 2B246 Reactor Building Engineered Safeguard System (ESS) Division 480 volt Motor Control Center (MCC) and 2Y246 208/120 Volt Alternate Current (AC) Instrument Panel. With the loss of the Reactor Building ESS Division 480 volt MCC, several drywell cooling fans were lost leading to an increase in drywell pressure. At 0110 on 5/13/16 Unit 2 was manually scrammed. All rods inserted as expected. Reactor water level lowered to -27 inches and was immediately restored by normal feedwater level control. Level 3 (+13 inch) Primary Containment Isolation System (PCIS) isolations occurred, along with an initiation of the Reactor Core Isolation Cooling (RCIC). The direct cause of the transient was found to be a phase to ground short between a cable and a protruding screw in MCC bucket 2B246091, Drywell Area Unit Cooler 2V411 B Breaker. The apparent cause is the vendor did not comply with Specification E1116, Rev 3 with this order of buckets. Immediate corrective actions included the repair of 2B246 which has been completed. A plan has been developed to review a sample of the 480 VAC MCC breakers and is being tracked by maintenance and system engineering. NRC FORM 366 (11-2015) Page 2 of 3 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR I SEQUENTIAL I REV Susquehanna Steam Electric Station, Unit 2 NUMBER NO. 05000388 2016 -004 -01 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, 100 percent Rated Thermal Power Unit 2- Mode 1, 100 percent Rated Thermal Power 2B246 Reactor Building Engineered Safeguard System (ESS) Division 2 480 volt Motor Control Center (MCC) (EIIS:B) and 2Y246 208/120 Volt Alternate Current (AC) Instrument Panel (EIIS:JL) were inoperable at the time of the scram. It was discovered that the Manual Bypass Switch 2D666SW1 (EIIS:HS) was set to its alternate power source, via 2B246 AC ESS Bus (EIIS:JL). When the loss of 2B246 (EIIS:JL) occurred, power could not be swapped back over to its primary power source via 2D666 vital uninterruptable power supply (UPS) since the Manual Bypass Switch (EIIS:HS) was degraded. This led to the loss of power to panel 2Y629, which challenged operator response. The Manual Bypass Switch (EIIS:HS) had been in its degraded condition since May 61 h 2015 when the UPS was being taken out of service and power was placed on its alternate supply via the Manual Bypass Switch (EIIS:HS). This event was reported under the NRC Pis as a Scram with Complications. EVENT DESCRIPTION At 23:55 on 5/12/16, Unit 2 experienced an electrical transient resulting in a loss of 2B246 Reactor Building Engineered Safeguard System (ESS) Division 2 480 volt Motor Control Center (MCC) (EIIS:B) and 2Y246 208/120 Volt Alternate Current (AC) Instrument Panel (EIIS:JL). With the loss of the Reactor Building ESS Division 480 volt MCC, several drywell cooling fans were lost leading to an increase in drywell pressure. Drywell pressure increased to 1.3 psig when operators placed the mode switch to the shutdown position to manually scram the reactor. At 0110 on 5/13 Unit 2 was manually scrammed. The automatic start signal on high drywell pressure was received at 0312 for the A, C, and D Emergency Diesel Generators (EIIS:EK). The B Emergency Diesel Generator was manually started from the control room. It did not automatically start in emergency mode due to the Unit 2 division 2 core spray not reaching an initiation signal on 1. 72 psig. All rods inserted as expected. Reactor water level lowered to -27 inches and was immediately restored by normal feedwater level control. Level 3 (+13 inch) Primary Containment Isolation System isolations occurred, along with an initiation of the Reactor Core Isolation Cooling (RCIC) {EIIS:KI) system(- 30 inches). The 'A' and 'B' Emergency Service Water pumps were manually started. Once adequate level was verified, RCIC was overridden. Pressure was controlled with turbine bypass valves, and subsequently Main Steam Line Drains. All safety systems functioned as expected. The power loss also tripped Reactor Building HVAC (EIIS:VA), causing a loss of secondary containment differential pressure resulting in a loss of safety function. Due to the loss of drywell cooling, high drywell pressure actuations and a second reactor scram signal occurred at 0314 hours. High Pressure Coolant Injection (EllS code:BJ) was subsequently overridden and declared inoperable, resulting in a Loss of Safety Function. Page 3 of 3 | ML16273A157
Fermi 2 05000 341 1 OF 5 | Unknown Unit | Secondary Containment Pressure Exceeded Technical Specification Due to Reactor Building HVAC Restart During High Winds | 09-30-2016 | On August 2, 2016, at 1015 EDT, while restoring the east train of Reactor Building Heating Ventilation and Air Conditioning (RBHVAC) after a surveillance test on Division 2 Standby Gas Treatment System (SGTS), the Technical Specification (TS) for the Secondary Containment (SC) pressure boundary was not met for approximately I second. The maximum SC pressure observed was approximately 0.120 inches of vacuum water column. The TS requirement is to maintain SC vacuum greater than or equal to 0.125 inches of vacuum water column for SC operability. All plant equipment responded as required to the changing conditions and RBHVAC and SGTS already in operation returned the SC pressure to within the TS limits; therefore, the Limiting Condition for Operation was met. There were no safety consequences or radiological releases associated with this event. The cause of this momentary loss of SC was determined to be the combined effect of the RBHVAC startup sequence with high winds outside the Reactor Building (RB). For corrective actions, Fermi 2 has implemented a plant modification to the RBHVAC system to improve its ability to maintain RB pressure negative during the RBHVAC startup sequence. In addition, Fermi 2 will adopt Technical Specification Task Force Traveler (TSTF) 551, "Revise Secondary Containment Surveillance Requirements," when it is approved, to eliminate the need to declare SC inoperable due to momentarily exceeding the TS vacuum limit. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY MB: NO. 3150-0104 EXPIRES: 10131/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 I C N T SHEET F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to -CONTINUAinfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Managemeanntd B udgeWt, ashingtoDnC, 2 0503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form u N s R e C d to m a im y p n o o s t e c a o n n d in u f c o t r m o a r ti s o p n o c n o s l o le r c , ti a o n n d d a oe p s e n rs o o t n d is is p la n y o t a r e cu qu rr i e re n d tl y t v o a l r i e d s O po M n B d c to o , n t t r h o e l n i u n m fo b rm er a , t t i h o e n http://www.nrc.gov/readingrr/doCcollections/lnuregs/staff/Sr1022/r3/h collection. 1. FACILITY NAME 2. DOCKET NUMBER YAR 3 S . E L Q E U R E N N U TI M A B L E R REV 05000- NUMBER NO. Fermi 2 341 2016-r 005r - 00 | INITIAL PLANT CONDITIONS: Mode - 1 Reactor Power - 100 percent There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT: On August 2, 2016, at 1015 EDT, while restoring the east train of Reactor Building Heating Ventilation and Air Conditioning (RBHVAC) [[VA]] after a surveillance test on Division 2 Standby Gas Treatment System (SGTS) [[BH]], the Technical Specification (TS) for the Secondary Containment (SC) [[NH]] pressure boundary was not met for a duration of approximately 1 second. The maximum SC pressure observed during the event was approximately 0.120 inches of vacuum water column. In addition to the restart of RBHVAC, high winds were noted at the time that SC was lost. There are two recorder [[PR]] divisions to monitor SC pressure. The Division 2 recorder indicated 0.120 inches of vacuum water column. The Division 1 recorder indication was within TS limits throughout this event, with a maximum SC pressure of 0.150 inches of vacuum water column. SC pressure was immediately returned to within the TS limit by RBHVAC and SGTS already in operation. There were no equipment failures or abnormal equipment indications observed during the RBHVAC startup sequence. There were no radiological releases associated with this event. The TS requirement is to maintain secondary containment vacuum greater than or equal to 0.125 inches of vacuum water column (TS Surveillance Requirement 3.6.4.1.1) for SC operability. An 8-hour event notification (EN 52146) was made to the NRC based on meeting the reporting criteria of Title 10 Code of Federal Regulations (10 CFR) 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. This Licensee Event Report (LER) is being made under the corresponding requirement in 10 CFR 50.73(a)(2)(v)(C). SIGNIFICANT SAFETY CONSEQUENCES AND IMPLICATIONS: There were no safety consequences or radiological releases associated with this event. At no time during this event was there a potential for endangering the public health and safety. The specified safety function of the SC is to contain, dilute, and hold up fission products that may leak from primary containment following a Design Basis Accident (DBA). In conjunction with operation of the SGTS and closure of certain valves [[V]] whose lines penetrate the SC, the SC is designed to reduce the activity level of the fission products prior to release to the environment and to isolate and contain fission products that are released during certain operations that take place inside primary containment, when primary containment is not required to be OPERABLE, or that take place outside primary containment. It is possible for the pressure in the control volume to rise relative to the environmental pressure (e.g., due to pump [[P]] and motor [[MO]] heat load additions). To prevent ground level exfiltration while allowing the SC to be designed as a conventional structure, the SC requires support systems to maintain the control volume pressure at less than the external pressure. For the SC to be considered OPERABLE, it must have adequate leak tightness to ensure that the required vacuum can be established and maintained. | ML16274A060
Browns Ferry Nuclear Plant (BFN) | Unknown Unit | Fire Safe Shutdown Procedures Do Not Consider Potential for Fire-Induced Failure of 4kV Shutdown Board Under-Voltage Trip Functions | 10-03-2016 | On August 3, 2016, at 1300 Central Daylight Time (CDT), during reviews to respond to a NRC information request for the 2016 NRC Triennial Fire Protection Inspection regarding Emergency Diesel Generator A (EDG) alignment in Fire Safe Shutdown (FSS) procedure 0-FSS-9 (Electrical Battery Board Room 2A and 250V Battery Rooms EL 621’), it was discovered that the National Fire Protection Association (NFPA) 805 analysis and FSS procedures do not consider the potential for fire-induced failure of the 4kV Shutdown Board under-voltage trip function for EDG power supply alignments. Fire-induced failure of the board under- voltage trip function may result in the need for Operations personnel to perform additional actions. These actions, to trip board loads, are currently not included in the FSS procedures. The cause of this condition was a human error which occurred during the transition of the fire protection program from Appendix R to NFPA 805. Corrective actions are to revise fire protection calculations, update fire protection models, provide coaching to the individuals involved, and add interim compensatory measures to FSS procedures in order to account for this condition. The risk significance of this condition was determined to be very low. NRC FORM 366A (11-2015) Page 2 of 6 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported (11-2015) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, LICENSEE EVENT REPORT (LER) NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the CONTINUATION SHEET NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Browns Ferry Nuclear Plant, Units 1, 2, 05000259 YEAR NUMBER NO. and 3 2016 - 003 - 00 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Unit 1, was operating in Mode 1 at approximately 84 percent rated thermal power. BFN Units 2 and 3 were operating in Mode 1 at approximately 100 percent rated thermal power. II. Description of Events A. Event: On August 3, 2016, at 1300 Central Daylight Time (CDT), during reviews to respond to a NRC information request for the 2016 NRC Triennial Fire Protection Inspection regarding Emergency Diesel Generator (EDG)[DG] A alignment in Fire Safe Shutdown (FSS) procedure 0-FSS-9 (Electrical Battery Board Room 2A and 250V Battery Rooms EL 621’), it was discovered that the National Fire Protection Association (NFPA) 805 analysis and FSS procedures do not consider the potential for fire-induced failure of the 4kV Shutdown Board (SDBD)[ECBD] under-voltage trip function for EDG power supply alignments. Fire-induced failure of the board under-voltage trip function may result in the need for Operations personnel to perform additional actions, to trip board loads, that are currently not included in the FSS procedures. On August 3, 2016, at 2038 CDT, Event Notification 52150 was made to the NRC. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event: No inoperable systems, structures, or components contributed to the event. C. Dates and approximate times of occurrences: June 24, 2016 BFN Transitioned to NFPA 805 August 3, 2016, Unanalyzed condition discovered during reviews to respond to a NRC 1300 CDT information request. August 3, 2016, Event Notification 52150 made to the NRC 2038 CDT D. Manufacturer and model number (or other identification) of each component that failed during the event: No component failures were identified that occurred during the event. E. Other systems or secondary functions affected: There were no other systems or secondary functions affected. | ML16277A095
Nine Mile Point | Unit 1 | Isolation of both Emergency Condensers due to loss of UPS 1628 | 09-26-2016 | On Thursday July 28, 2016, at approximately 2357 hours with power level at approximately 100 percent, Nine Mile Point Unit 1 (NMP1) experienced a loss of Uninterruptible Power Supply (UPS), UPS 1628 which resulted in loss of Reactor Protection System (RPS) Bus 11. Numerous half scram and half isolation signals were generated in addition to the isolation of both# 11 and# 12 Emergency Condensers (ECs). EC# 12 was returned to standby on 7/29/2016 at 0041 hours and EC# 11 was returned to standby on 7/29/2016 at 0045 hours. The causes of this event were the failure of a UPS capacitor and the bypass power transfer set point being set too low for the type of transient. Corrective actions include immediate replacement of the failed capacitor, installation of new higher temperature rated capacitors and adjusting the low voltage bypass power transfer set point. This event is reportable under 1O CFR50.73(a)(2)(v)(B). NRG FORM 366 (11-2015) Page 2 of 5 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Nine Mile Point Unit 1 05000-220 YEAR NUMBER NO. 2016 - 002 00 | I. DESCRIPTION OF EVENT A. PRE-EVENT PLANT CONDITIONS: Unit 1 was in Run operating at approximately 100% rated thermal power when the event occurred. There were no structures, systems or components out of service that contributed to this event. B. EVENT: On July 28, 2016, at approximately 23;57 hours, UPS 162B unexpectedly transferred to its bypass power supply. Contrary to the expectation that the output loads remain energized during a transfer, the RPS Channel 11 Instrument Bus de-energized resulting in numerous half scram and half isolation signals. In addition, both # 11 and# 12 ECs isolated. The EC System was declared inoperable and the appropriate Technical Specification Action was entered. This condition was reported to the NRG on July 29, 2016 at approximately 0651 hours pursuant to the requirements of 10 CFR 50.72(b)(3)(v)(B) (Event Notification #52133). Subsequent troubleshooting of UPS 162B determined that a capacitor in the UPS Constant Voltage Transformer shorted. When the capacitor initially shorted, UPS voltage dropped but remained higher than the 60 VAC bypass power supply transfer set point. The UPS's protective relaying logic tripped the UPS loads prior to reaching the 60 VAC setpoint, resulting in de-energization of RPS Channel 11 Instrument Bus before the transfer could occur. Upon the trip of the Instrument Bus, the low voltage setpoint was reached and the UPS transferred to bypass power supply thereby re-engerizing the loads. The voltage transient on the Bus afffected the pressure transmiters for the EC high steam flow isolation signal resulting in the isolation of both EC trains. Nine Mile Point Unit 2 (NMP2) was unaffected. The event has been entered into the plant's corrective action program as IR 2698136. C. INOPERABLE STRUCTURES, COMPONENTS, OR SYSTEMS THAT CONTRIBUTED TO THE EVENT: No other systems, structures, or components contributed to this event. NRG FORM 366A (11-2015) ·. -·-. ... - Page 3 of 5 | ML16277A145
Dresden Nuclear Power Station | Unit 2 | Unit 2 HPCI Inlet Steam Drain Pot Piping Leak Resulting in HPCI lnoperability | 09-30-2016 | On 5/16/2016 at approximately 1120 CDT during planned maintenance on Division II of the Low Pressure Coolant Injection (LPCI} system, a through-wall steam leak was observed in the Unit 2 High Pressure Coolant Injection (HPCI) inlet drain pot drain piping. The leak was identified to be on the Inlet Drain Pot line leading to the Main Condenser upstream of the HPCI Inlet Drain Pot 2A Inboard Drain Valve, Air Operated Valve (AOV) 2-2301-29, which is ASME Code Class 2 piping. The cause of the through-wall leak was liquid droplet impingement erosion thinning of chrome moly piping. HPCI was declared inoperable following isolation of the degraded piping per Technical Requirements Manual (TRM) 3.4.a. This event is of low safety significance. Corrective Actions included replacing the piping with stainless steel, ensuring similar sections of piping are replaced or scheduled for replacement, and reviewing Extent of Condition. This event is reportable under 1O CFR 50.73(a)(2)(v)(D), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident." NRC FORM 366 (06-2016) Page 2 of 4 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2011 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-ma~ to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV Dresden Nuclear Power Station, Unit 2 05000-237 YEAR NUMBER NO. ______________________________. ..._ _________________________. ._ 2 _ 0 _ 1 _ 6 _ _ - _____ 00 _ 2 _ _______ 0 _ 1 - --t I | PLANT AND SYSTEM IDENTIFICATION Dresden Nuclear Power Station (DNPS), Unit 2, is a General Electric Company Boiling Water Reactor with a licensed maximum power level of 2957 megawatts thermal. The Energy Industry Identification System codes used in the text are identified as [XX]. A. Plant Conditions Prior to Event: Unit: 02 Event Date: 05/16/16 Event Time: 1120 CDT Reactor Mode: 1 Mode Name: Power Operation Power Level: 100 percent B. Description of Event: On 5/16/2016 at approximately 1120 CDT, a through-wall steam leak was observed in the Unit 2 High Pressure Coolant Injection (HPCI) [BJ] inlet drain pot drain piping during planned maintenance on Division II of the Low Pressure Coolant Injection (LPCI) [BO] system. The leak was identified to be on the Inlet Drain Pot line upstream of the HPCI Inlet Drain Pot 2A Inboard Drain Valve, Air Operated Valve (AOV) 2-2301-29, which is ASME Code Class 2 piping. At 1157 CDT, the station entered the Action Statement in the Technical Requirements Manual (TRM) 3.4.a to isolate the adversely affected ASME Code Class 2 component. At 1457 CDT, the flow path containing the leaking pipe was isolated and HPCI was declared inoperable. At this time, the station entered Technical Specification (TS} 3.5.1 Condition K due to the inoperability of HPCI and a division of LPCI. Condition K directed entry into TS Limiting Condition for Operation (LCO) 3.0.3. At 171 O CDT, the LPCI system was restored and TS LCO 3.0.3 was exited but the unit remained in TS 3.5.1 Condition G. At 0042 CDT on 5/18/2016, the adversely affected piping was replaced with stainless steel and HPCI was declared operable which allowed for TS 3.5.1 Condition G to be exited. This event is reportable under 10 CFR 50.73(a)(2}(v)(D), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident." C. Cause of Event: The cause of the failure was local internal thinning from a mechanical erosion mechanism. Based on the cratered appearance of the eroded surface, the thinning was due to liquid droplet impingement erosion. The through-wall leak occurred toward the downstream side of the elbow where the droplet impact angle was high (close to 90 degrees). The susceptible pipe was scheduled to be replaced in 2013, but the work package was inadvertently revised to remove the replacement from the scope of work. D. Safety Analysis: The safety significance of this condition is low and did not adversely impact the health and safety of the public. During the evolution redundant systems remained capable of I Page _2_ of _4_ I J Page 3 of 4 | ML16278A007
Hope Creek Generating Station 05000354 1 OF4 | Unknown Unit | High Pressure Coolant Injection System Found to be Inoperable During Testing | 00-04-2016 | A review of plant conditions from April 2016, revealed a condition that could have prevented the fulfillment of a safety function. On April 7, 2016, at 0352, with the Hope Creek reactor operating at 100% power, the High Pressure Coolant Injection (HPCI) system turbine over-speed assembly did not respond as expected during post maintenance testing. The HPCI system was in the process of post maintenance testing following a planned maintenance window, and was inoperable at the time of the event. During system testing, the HPCI turbine was momentarily tripped by the over-speed assembly, and then reset itself with no operator action. Subsequent investigation found that the HPCI over-speed assembly reset spring did not have the correct preload. A review of the maintenance completed during the scheduled system outage determined that there was no maintenance performed on the over-speed assembly. Therefore, the condition could have been present prior to the start of the maintenance window on April 5, 2016 at 0205. This report is being submitted under 10 CFR 50.73(a)(2)(v)(D), as an event or condition that could have prevented the fulfillment of a safety function of systems that are needed to mitigate the consequences of an accident. No specific cause was identified; however there is industry operating experience that the reset spring will relax over time, reducing the preload. NRC FORM 366 (02-2014). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 01/31/2017 (02-2014) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are Incorporated Into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and LICENSEE EVENT REPORT (LER) Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to lnfocollects.Resource@nrc.gov, and to CONTINUATION SHEET the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-01 04), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the Information collection. 1. FACILITY NAME 2. DOCKET 6. LER NUMBER 3. PAGE YEAR I SEQUENTIAL I REVISION Hope Creek Generating Station 05000354 NUMBER NUMBER 2 OF4 2016 • 001 . 000 | PLANT AND SYSTEM IDENTIFICATION General Electric- Boiling Water Reactor (BWR/4) Reactor Protection System- EllS Identifier {BJ/XCV}* *Energy Industry Identification System {EllS} codes and component function identifier codes appear as {SS/CCC} IDENTIFICATION OF OCCURRENCE Event Date: 04/07/2016 Discovery Date: 09/07/2016 CONDITIONS PRIOR TO OCCURRENCE Hope Creek was in Operational Condition 1 at 100 percent rated thermal power (RTP). HPCI System {BJ} post maintenance testing was in progress. The HPCI system was inoperable following planned maintenance. DESCRIPTION OF OCCURRENCE On April 7, 2016, while performing a post maintenance test of the HPCI turbine and pump, the system did not respond as expected. Following startup, the HPCI turbine tripped and reset in an approximate 5 second time span. The HPCI turbine and pump then continued to accelerate to normal speed with proper pressure and flow rates. Because the turbine tripped and reset, station operators considered the system to remain inoperable, although all other test results were satisfactory. The HPCI system ensures that the reactor core is not uncovered if there is a small break in the reactor coolant pressure boundary (RCPB) that does not result in rapid depressurization of the reactor vessel. The HPCI system controls automatically start the system and bring it to design flow rate within 35 seconds from receipt of a reactor pressure vessel (RPV) low water level signal or a primary containment (drywell) high pressure signal. During the trip and reset event, plant data indicates that the 35 second response time from system initiation to full flow would not have been accomplished, because the event delayed the development of full system flow rate, discharge pressure, and pump/turbine speed. Troubleshooting determined that the reset spring was set at 1 pound (lb.), which is outside the prescribed range of 2 to 5 lbs. The spring preload was adjusted to 3.5 lbs. and the system was retested satisfactorily. There was no record of any maintenance performed on the trip mechanism or reset spring during the system maintenance window on April 5, 2016 at 0205 through April 7, 2016 at 0352. The last maintenance performed on the trip mechanism was during the previous refueling outage which completed in May, 2015. At that time the spring was set to 3.5 lbs. The HPCI system was run for testing on March 1, 2016, approximately five weeks prior to the trip and reset event. The HPCI system is tested quarterly as part of system surveillance testing. It was successfully run in June, September, and December, 2015 and March, 2016 with no abnormal operation of the trip mechanism. Based on this, it was concluded that the reset spring preload most likely relaxed to less than the required preload during the period between March 1, 2016, at 1427, when HPCI was last operated successfully, and April 7, 2016 at 0352 when the event occurred. Based on the suspected failure mode, the HPCI system could have been unavailable for a period of time prior to April 5, 2016, at 0205, when the system was required to be operable. This meets the reporting criterion of 10 CFR 50.73 (a)(2)(v)(D), a condition that could have prevented the fulfillment of a safety function to mitigate the consequences of an accident. The condition was also reviewed under 10 CFR 50.73 (a)(2)(i)(B), as a condition prohibited by Technical Specifications. However, because there is no firm evidence that the system would not have worked, the event is not required to be reported under that section. | ML16278A094
Sequoyah Nuclear Plant | Unit 1 | Emergency Diesel Generator Fire Dampers and Crankcase Pressure Switches Not Analyzed for Withstanding the Effects ofa Tornado 5. EVENTDATE 6. LER NUMBER 7. REPORT DATE 8. OTHER FACILITIES INVOLVED FACILITYNAME DOCKETNUMBER SEQUENTIAL REV MONTH NUMBER NO MONTH Sequoyah Nuclear Plant Unit 2 05000328 FACILITYNAME DOCKETNUMBER 05 16 2016 2016 - 004 - 01 10 03 2016 NA 9.OPERATING MODE 11.THIS REPORT ISSUBMITTED PURSUANTTO THE REQUIREMENTSOF 10 CFR§: (Checkallthatapply) • 20.2201(b) • 20.2203(a)(3)(i) • 50.73(a)(2)(ii)(A) • 50.73(a)(2)(viii)(A) • 20.2201(d) • 20.2203(a)(3)(i E3 50.73(a)(2)(ii)(B) • 50.73(a)(2)(viii)(B) • 20.2203(a)(1) • 20.2203(a)(4) • 50.73(a)(2)(iii) • 50.73(a)(2)(ix)(A) • 20.2203(a)(2)(i) • 50.36(c)(1)(i)(A) • 50.73(a)(2)(iv)(A) • 50.73(a)(2)(x) 10. POWERLEVEL • 20.2203(a)(2)(ii) • 50.36(c)(1)(ii)(A) • 50.73(a)(2)(v)(A) • 73.71(a)(4) • 20.2203(a)(2)(iii) • 50.36(c)(2) • 50.73(a)(2)(v)(B) • 73.71(a)(5) • 20.2203(a)(2)(iv) • 50.46(a)(3)(H) • 50.73(a)(2)(v)(C) • 73.77(a)(1) 100 • 20.2203(a)(2)(v) • 50.73(a)(2)(i)(A) • 50.73(a)(2)(v)(D) • 73.77(a)(2)(i) • 20.2203(a)(2)(vi) • 50.73(a)(2)(i)(B) • 50.73(a)(2)(vii) • 73.77(a)(2)(H) • 50.73(a)(2)(i)(C) ¦ ¦ OTHER SpecifyinAbstractbeloworinNRCForm366A 12. LICENSEECONTACT FORTHIS LER LICENSEECONTACT TELEPHONENUMBER (IncludeAreaCode) Rebecca L. Travis 423-843-8335 13. COMPLETE ONELINE FOR EACH COMPONENT FAILURE DESCRIBED INTHIS REPORT CAUSE SYSTEM COMPONENT FA M C A T N U U RER REP T O O R E T P A IX BLE CAUSE SYSTEM COMPONENT FA M C A T N U U RER REP T O O R E T P A IX BLE 14. SUPPLEMENTAL REPORTEXPECTED 15. EXPECTED MONTH DAY YEAR SUBMISSION • YES (Ifyes, complete 15. EXPECTEDSUBMISSIONDATE) [X] NO DATE ABSTRACT (Limitto1400spaces, i.e., approximately15single-spacedtypewrittenlines) On May16, 2016, at 2105 Eastern DaylightTime (EDT),Sequoyah Nuclear Plant (SQN) identified a nonconforming condition involvingthe Emergency Diesel Generator (EDG) firedampers installed for Units 1and 2. Specifically, ithas been identified that ifa tornado causes a differential pressure across the east and west sides of the EDG Building, the associated ventilation fire dampers have not been analyzed to withstand the corresponding high airflow rate that could result from this condition and could possibly failina way that impedes airflow for EDG cooling. On June 8, 2016, at 1526 EDT, SQN determined that a tornado could potentially cause actuation of the EDG crankcase pressure trip due to a low barometriccondition thatcould result in an EDG lockout condition. The EDG lockout condition prevents subsequent EDGstarts (normal or emergency) untiloperators manually reset the lockout condition locallyat the EDG. Correctiveactions include establishing compensatory measures to block the fire dampers inthe open position inthe eventthata Tornado Watch/Warning is issued for the Hamilton County, Tennesseearea. Inaddition, a compensatory measure has been established, that upon notification ofa Tornado Warning, the EDGs will be emergency started and operated during the time the Tornado Warning is ineffect to bypass the crankcase pressure tripfunction and allowthe EDGs to perform their required safetyfunction. The apparentcause ofthese events is misjudgment regarding the intent ofthe Regulatory Issue Summary2006-23. The corrective actions developed in response to the RIS were too narrowlyfocused on ductwork and ventilating dampers withstanding the effects ofa tornado. NRCFORM366(11-2015) Page2 of 6 NRCFORM366A U.S.NUCLEARREGULATORYCOMMISSION APPROVEDBYOMB: NO.3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimatedburdenperresponsetocomplywiththismandatorycollectionrequest80hours.Reported lessonslearned are incorporated into the licensing processandfed backto industry. Send commentsregardingburdenestimatetotheFOIA,PrivacyandInformationCollectionsBranch(T-5 vw/ F53), U.S. NuclearRegulatoryCommission, Washington, DC20555-0001,orbyinternete-mailto LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov,andtotheDeskOfficer,OfficeofInformationandRegulatoryAffairs, NEOB-10202,(3150-0104),OfficeofManagementandBudgetWashington, DC20503.Ifameans CONTINUATION SHEET usedtoimposeaninformationcollectiondoesnotdisplayacurrentlyvaldOMBcontrolnumber,the NRC maynotconductorsponsor,anda personis notrequired torespondto,theinformation collection. 1.FACILITYNAME 2. DOCKETNUMBER 3. LERNUMBER SEQUENTIAL REV YEAR NUMBER NO. Sequoyah NuclearPlantUnit1 05000327 2016 004 01 NARRATIVE PLANT OPERATING CONDITIONS BEFORE THE EVENT Atthe time ofthe events, Sequoyah Nuclear Plant (SQN) Unit1 and Unit2 were in Mode 1 at 100 percent rated thermal power. DESCRIPTION OF EVENTS A. Event: On May16, 2016, at 2105 Eastern DaylightTime(EDT), Sequoyah Nuclear Plant (SQN) identifieda nonconforming condition involving the Emergency Diesel Generator(EDG)[ElIS Code EKand DG]firedampers [ElISCode DMP] installedfor Units1and 2. Specifically,ithas been identifiedthat ifa tornado causes a differential pressure across the east and west sides of the EDGBuilding, this couldcreate a highairflow rate through the EDGBuilding ventilationpath. The firedampers foreach EDGbay have notbeen analyzed to withstand highairflowsresulting from a tornado and could possibly failina waythat impedes airflowfor EDGcooling. This isan unanalyzed condition that potentially significantlydegrades plantsafety and couldprevent all EDGsfromsupplyingelectrical poweras designed duringa tornado orother similarweather events. On June 8, 2016, at 1526 EDT,anotherissue was identifiedinvolving the potential impact ofa tornado on the EDGs. The EDGs are designed witha crankcase pressuretrip[EMS Code PS], which isbypassed during an emergencystart. Atornadocould potentially cause actuation ofthe crankcase pressuretripdue to a low barometriccondition. Ifan emergency start signalhas not previously occurred,then during a tornado,actuation ofthe crankcase pressure trip would energizethe shutdownrelaycausing an EDG lockout condition. The EDG lockout condition prevents subsequent EDG starts (normal oremergency) until operators manuallyresetthe lockout condition locally at the EDG. Thiscondition places bothunitsinan unanalyzed condition that potentially significantly degrades plantsafetyand could potentially affectall fourEDGs simultaneously. B. Status ofstructures, components, orsystems that were inoperable at the start ofthe event and contributed to the event: Noinoperablestructures, components, orsystems contributedtothis event. NRCFORM366A(11-2015) Page 3 of 6 NRC FORM366A U.S. NUCLEARREGULATORYCOMMISSION (11-2015) LICENSEE EVENT REPORT (LER) CONTINUATION SHEET 1.FACILITYNAME 2. DOCKET 6. LERNUMBER SEQUENTIAL REV YEAR NUMBER NO. Sequoyah NuclearPlant Unit 1 05000327 2016 004 01 NARRATIVE C. Dates and approximatetimes of occurrences: Dateffime (EDT) Description May 16, 2016 at SQN determined that a tornado could potentially causefailure of the EDG 2105 EDT building fire dampers. May 16, 2016 at An 8-hour non-emergency notification was madeto the NRC to reportthe 2217 EDT event as an unanalyzed condition that significantly degrades plant safety per 10 CFR 50.72(b)(3)(ii)(B). June 8, 2016 at SQN determined that a tornado could potentially cause actuation of the 1526 EDT EDG crankcase pressure trip. June 8, 2016 at An 8-hournon-emergency notification was made to the NRC to report the 1710 EDT event as an unanalyzed condition that significantly degrades plantsafety per 10 CFR 50.72(b)(3)(ii)(B). D. Manufacturer and model numberof each componentthatfailed during the event: There were no componentfailures. E. Othersystems or secondaryfunctions affected: There were no othersystems or secondaryfunctions affected by this event. F. Method ofdiscovery of each component or system failure or procedural error: The unanalyzed conditions were discovered as a result ofquestions asked during the NRC Component Design Bases Inspection. G. Thefailure mode, mechanism, and effect of each failed component, ifknown: Therewere no componentfailures. H. Operatoractions: Upon determination ofeach unanalyzed condition, operators promptlymade NRC notifications. I. Automatically and manually initiated safety system responses: There were no automatic or manual system responses associated with this event. NRCFORM366A(11-2015) Page 4 of 6 NRC FORM366A U.S. NUCLEARREGULATORYCOMMISSION (11-2015) LICENSEE EVENT REPORT (LER) CONTINUATION SHEET 1.FACILITYNAME 2. DOCKET 6. LERNUMBER SEQUENTIAL REV YEAR NUMBER NO. Sequoyah NuclearPlant Unit1 05000327 2016 004 01 NARRATIVE II. CAUSE OFTHE EVENT A. The cause of each component orsystem failure or personnel error, ifknown: The apparent cause ofthese events is misjudgment regarding the intent of Regulatory Issue Summary (RIS) 2006-23, "Post-Tornado Operability ofVentilating and Air-Conditioning Systems Housed in Emergency Diesel Generator Rooms." The corrective actions developed in response to RIS 2006-23were too narrowlyfocused on ductwork and ventilating dampers withstanding the effects ofa tornado, and did not conservatively expand the analysis limitsto include all safety related components within the ventilating system. B. The cause(s) and circumstancesfor each human performance related root cause: The human performance issuethat contributed to the cause was a wrong assumption or preconceived idea. The decision to analyze the ductwork and dampers, as opposedto all components ofthe ventilation system, appearsto have been a non-conservative decision; however, the decision also appears to have been more of a misunderstanding ofthe intent ofthe RIS. Sincethe licensee response that prompted RIS 2006-23 only analyzed vulnerable duct segments, itled to a predisposition ofthe initiatorofthe CR to suggestthat onlythe ductwork and dampers needed to be analyzed. These precursors led to a faultyscope. The decision does not appearto be deliberately non-conservative. The personnel involvedwiththe response to the CR were adequatelytrained inboth general engineering principles and workgroup specific training. IV. ANALYSIS OF THE EVENT All 4 EDGs are required to be operable by both units' Technical Specifications to provide electrical powerto safe shutdown/safety related equipmentfollowing accident conditions coincident witha loss ofoffsite power. The Current Licensing Basis (CLB) requires thattornado effects be considered in the design ofsafety related structures, systems, and components. Itcould not be demonstrated at the time ofthe eventsthatthe fire dampers and crankcase pressure switches would withstand the design basis tornado. The EDGs are operable, but degraded and have successfully passed their required surveillances within the appropriate frequency. The occurrence ofsuch an event involvingfailureofthe fire dampers orthe crankcase pressure switches is highly unlikely and there was no imminentconcern regarding severeweatherinvolving tornadoes. Inorderto prevent any operabilityissues with the EDGdue totornado damageto the EDGbuilding or components, compensatory measures have been developed to address the associated nonconformance. These compensatory measures will be accomplished by physically blockingopen the firedampers, and removingan access portdownstream ofone ofeach pairofthe EDGexhaust fan dampers. Itwill be implemented promptly upon site notification ofa Tornado Watch orWarning. Acompensatory measure has also been established, that upon notification ofa TornadoWarning,the EDGswill be emergencystarted and operated duringthe timethe Tornado Warning is ineffect to NRCFORM366A(11-2015) Page 5 of 6 NRCFORM366A U.S. NUCLEARREGULATORYCOMMISSION (11-2015) LICENSEE EVENT REPORT (LER) CONTINUATION SHEET 1.FACILITYNAME 2. DOCKET 6. LERNUMBER SEQUENTIAL REV YEAR NUMBER NO. Sequoyah NuclearPlantUnit1 05000327 2016 004 01 NARRATIVE bypass the crankcase pressure tripfunction and allow the EDGs to be able to perform their required safetyfunction. V. ASSESSMENT OF SAFETY CONSEQUENCES The EDGs are located inside the power plant structure and are capable of performing their safetyfunction. The occurrence ofsuch an event involvingfailure ofthe fire dampers or the crankcase pressure switches is highly unlikely and there was no imminent concern regarding severe weather involving tornadoes atthe time ofthe events. A risk assessment has been completed and has determined thatthe change in core damage frequency is less than 1E-6for failures of both the EDG fire dampers and crankcase pressure switches, which is of very low safety significance. A. Availabilityof systems orcomponents that could have performed the samefunction as the components and systems thatfailed during the event: There were no componentfailures. B. Forevents that occurred when the reactorwas shut down, availability of systems or components needed to shutdown the reactor and maintain safe shutdown conditions, remove residual heat, control the release of radioactive material, or mitigate the consequences of an accident: These events did not occurwhen the reactorwas shutdown. C. Forfailure that rendered a train of a safety system inoperable, an estimate of the elapsed timefrom discovery ofthe failure until the train was returned to service: Withthe compensatory measures in place, the EDGs will remain capable offulfilling theirdesign basisfunction following a tornado. VI. CORRECTIVEACTIONS This eventwas entered into the Tennessee ValleyAuthority CorrectiveAction Program under Condition Reports (CR) 1170545, 1178891, and 1181710. A. Immediate CorrectiveActions: 8-hour non-emergency notifications were made to the NRC to report the events as unanalyzed conditions that significantly degrade plant safety per 10 CFR 50.72(b)(3)(ii)(B). B. Corrective actions to reduce probability of similarevents occurring inthe future: Corrective actions include establishing compensatory measures to blockthe fire dampers inthe open position inthe eventthat a Tornado Watch/Warning is issued for the Hamilton NRCFORM366A(11-2015) Page 6 of 6 NRC FORM366A U.S. NUCLEARREGULATORYCOMMISSION (11-2015) LICENSEE EVENT REPORT (LER) CONTINUATION SHEET 1.FACILITYNAME 2. DOCKET 6. LERNUMBER SEQUENTIAL REV YEAR NUMBER NO. Sequoyah NuclearPlantUnit 1 05000327 2016 004 01 NARRATIVE County, Tennessee area. Inaddition, a compensatory measure has been established, that upon notification of a TornadoWarning, the EDGs willbe emergency started and operated during the time the TornadoWarning is ineffectto bypass the crankcase pressure trip function and allow the EDGs to perform their required safety function. Furthercorrective actions include establishing the bounding criteria for evaluation of other componentsthat are subjectto the effects of a tornado that could impactthe safe operation of safety related equipment inCategory Istructures, fullyevaluating the components ofthe EDG building ventilation system, and fullyevaluating the components inthe EDG building that are subjectto the effects of a tornado that could impactthe operation ofthe EDGs. VII. ADDITIONAL INFORMATION A. Previous similarevents atthe same plant: There have been no similarevents at SQN inthe pastthree years that resulted in an unanalyzed condition on the EDGs due to a tornado. B. Additional Information: None. C. SafetySystem Functional Failure Consideration: These events did not result in a safety system functional failure in accordance with 10CFR50.73(a)(2)(v). D. Scramswith Complications Consideration: There were no scrams associated with these events. VIII. COMMITMENTS None. NRCFORM366A(11-2015) | 10-03-2016 | On May16, 2016, at 2105 Eastern DaylightTime (EDT),Sequoyah Nuclear Plant (SQN) identified a nonconforming condition involvingthe Emergency Diesel Generator (EDG) firedampers installed for Units 1and 2. Specifically, ithas been identified that ifa tornado causes a differential pressure across the east and west sides of the EDG Building, the associated ventilation fire dampers have not been analyzed to withstand the corresponding high airflow rate that could result from this condition and could possibly failina way that impedes airflow for EDG cooling. On June 8, 2016, at 1526 EDT, SQN determined that a tornado could potentially cause actuation of the EDG crankcase pressure trip due to a low barometriccondition thatcould result in an EDG lockout condition. The EDG lockout condition prevents subsequent EDGstarts (normal or emergency) untiloperators manually reset the lockout condition locallyat the EDG. Correctiveactions include establishing compensatory measures to block the fire dampers inthe open position inthe eventthata Tornado Watch/Warning is issued for the Hamilton County, Tennesseearea. Inaddition, a compensatory measure has been established, that upon notification ofa Tornado Warning, the EDGs will be emergency started and operated during the time the Tornado Warning is ineffect to bypass the crankcase pressure tripfunction and allowthe EDGs to perform their required safetyfunction. The apparentcause ofthese events is misjudgment regarding the intent ofthe Regulatory Issue Summary2006-23. The corrective actions developed in response to the RIS were too narrowlyfocused on ductwork and ventilating dampers withstanding the effects ofa tornado. NRCFORM366(11-2015) Page2 of 6 NRCFORM366A U.S.NUCLEARREGULATORYCOMMISSION APPROVEDBYOMB: NO.3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimatedburdenperresponsetocomplywiththismandatorycollectionrequest80hours.Reported lessonslearned are incorporated into the licensing processandfed backto industry. Send commentsregardingburdenestimatetotheFOIA,PrivacyandInformationCollectionsBranch(T-5 vw/ F53), U.S. NuclearRegulatoryCommission, Washington, DC20555-0001,orbyinternete-mailto LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov,andtotheDeskOfficer,OfficeofInformationandRegulatoryAffairs, NEOB-10202,(3150-0104),OfficeofManagementandBudgetWashington, DC20503.Ifameans CONTINUATION SHEET usedtoimposeaninformationcollectiondoesnotdisplayacurrentlyvaldOMBcontrolnumber,the NRC maynotconductorsponsor,anda personis notrequired torespondto,theinformation collection. 1.FACILITYNAME 2. DOCKETNUMBER 3. LERNUMBER SEQUENTIAL REV YEAR NUMBER NO. Sequoyah NuclearPlantUnit1 05000327 2016 004 01 | PLANT OPERATING CONDITIONS BEFORE THE EVENT Atthe time ofthe events, Sequoyah Nuclear Plant (SQN) Unit1 and Unit2 were in Mode 1 at 100 percent rated thermal power. DESCRIPTION OF EVENTS A. Event: On May16, 2016, at 2105 Eastern DaylightTime(EDT), Sequoyah Nuclear Plant (SQN) identifieda nonconforming condition involving the Emergency Diesel Generator(EDG)[ElIS Code EKand DG]firedampers [ElISCode DMP] installedfor Units1and 2. Specifically,ithas been identifiedthat ifa tornado causes a differential pressure across the east and west sides of the EDGBuilding, this couldcreate a highairflow rate through the EDGBuilding ventilationpath. The firedampers foreach EDGbay have notbeen analyzed to withstand highairflowsresulting from a tornado and could possibly failina waythat impedes airflowfor EDGcooling. This isan unanalyzed condition that potentially significantlydegrades plantsafety and couldprevent all EDGsfromsupplyingelectrical poweras designed duringa tornado orother similarweather events. On June 8, 2016, at 1526 EDT,anotherissue was identifiedinvolving the potential impact ofa tornado on the EDGs. The EDGs are designed witha crankcase pressuretrip[EMS Code PS], which isbypassed during an emergencystart. Atornadocould potentially cause actuation ofthe crankcase pressuretripdue to a low barometriccondition. Ifan emergency start signalhas not previously occurred,then during a tornado,actuation ofthe crankcase pressure trip would energizethe shutdownrelaycausing an EDG lockout condition. The EDG lockout condition prevents subsequent EDG starts (normal oremergency) until operators manuallyresetthe lockout condition locally at the EDG. Thiscondition places bothunitsinan unanalyzed condition that potentially significantly degrades plantsafetyand could potentially affectall fourEDGs simultaneously. B. Status ofstructures, components, orsystems that were inoperable at the start ofthe event and contributed to the event: Noinoperablestructures, components, orsystems contributedtothis event. NRCFORM366A(11-2015) Page 3 of 6 NRC FORM366A U.S. NUCLEARREGULATORYCOMMISSION (11-2015) LICENSEE EVENT REPORT (LER) CONTINUATION SHEET 1.FACILITYNAME 2. DOCKET 6. LERNUMBER SEQUENTIAL REV YEAR NUMBER NO. Sequoyah NuclearPlant Unit 1 05000327 2016 004 01 NARRATIVE C. Dates and approximatetimes of occurrences: Dateffime (EDT) Description May 16, 2016 at SQN determined that a tornado could potentially causefailure of the EDG 2105 EDT building fire dampers. May 16, 2016 at An 8-hour non-emergency notification was madeto the NRC to reportthe 2217 EDT event as an unanalyzed condition that significantly degrades plant safety per 10 CFR 50.72(b)(3)(ii)(B). June 8, 2016 at SQN determined that a tornado could potentially cause actuation of the 1526 EDT EDG crankcase pressure trip. June 8, 2016 at An 8-hournon-emergency notification was made to the NRC to report the 1710 EDT event as an unanalyzed condition that significantly degrades plantsafety per 10 CFR 50.72(b)(3)(ii)(B). D. Manufacturer and model numberof each componentthatfailed during the event: There were no componentfailures. E. Othersystems or secondaryfunctions affected: There were no othersystems or secondaryfunctions affected by this event. F. Method ofdiscovery of each component or system failure or procedural error: The unanalyzed conditions were discovered as a result ofquestions asked during the NRC Component Design Bases Inspection. G. Thefailure mode, mechanism, and effect of each failed component, ifknown: Therewere no componentfailures. H. Operatoractions: Upon determination ofeach unanalyzed condition, operators promptlymade NRC notifications. I. Automatically and manually initiated safety system responses: There were no automatic or manual system responses associated with this event. NRCFORM366A(11-2015) Page 4 of 6 NRC FORM366A U.S. NUCLEARREGULATORYCOMMISSION (11-2015) LICENSEE EVENT REPORT (LER) CONTINUATION SHEET 1.FACILITYNAME 2. DOCKET 6. LERNUMBER SEQUENTIAL REV YEAR NUMBER NO. Sequoyah NuclearPlant Unit1 05000327 2016 004 01 NARRATIVE II. CAUSE OFTHE EVENT A. The cause of each component orsystem failure or personnel error, ifknown: The apparent cause ofthese events is misjudgment regarding the intent of Regulatory Issue Summary (RIS) 2006-23, "Post-Tornado Operability ofVentilating and Air-Conditioning Systems Housed in Emergency Diesel Generator Rooms." The corrective actions developed in response to RIS 2006-23were too narrowlyfocused on ductwork and ventilating dampers withstanding the effects ofa tornado, and did not conservatively expand the analysis limitsto include all safety related components within the ventilating system. B. The cause(s) and circumstancesfor each human performance related root cause: The human performance issuethat contributed to the cause was a wrong assumption or preconceived idea. The decision to analyze the ductwork and dampers, as opposedto all components ofthe ventilation system, appearsto have been a non-conservative decision; however, the decision also appears to have been more of a misunderstanding ofthe intent ofthe RIS. Sincethe licensee response that prompted RIS 2006-23 only analyzed vulnerable duct segments, itled to a predisposition ofthe initiatorofthe CR to suggestthat onlythe ductwork and dampers needed to be analyzed. These precursors led to a faultyscope. The decision does not appearto be deliberately non-conservative. The personnel involvedwiththe response to the CR were adequatelytrained inboth general engineering principles and workgroup specific training. IV. ANALYSIS OF THE EVENT All 4 EDGs are required to be operable by both units' Technical Specifications to provide electrical powerto safe shutdown/safety related equipmentfollowing accident conditions coincident witha loss ofoffsite power. The Current Licensing Basis (CLB) requires thattornado effects be considered in the design ofsafety related structures, systems, and components. Itcould not be demonstrated at the time ofthe eventsthatthe fire dampers and crankcase pressure switches would withstand the design basis tornado. The EDGs are operable, but degraded and have successfully passed their required surveillances within the appropriate frequency. The occurrence ofsuch an event involvingfailureofthe fire dampers orthe crankcase pressure switches is highly unlikely and there was no imminentconcern regarding severeweatherinvolving tornadoes. Inorderto prevent any operabilityissues with the EDGdue totornado damageto the EDGbuilding or components, compensatory measures have been developed to address the associated nonconformance. These compensatory measures will be accomplished by physically blockingopen the firedampers, and removingan access portdownstream ofone ofeach pairofthe EDGexhaust fan dampers. Itwill be implemented promptly upon site notification ofa Tornado Watch orWarning. Acompensatory measure has also been established, that upon notification ofa TornadoWarning,the EDGswill be emergencystarted and operated duringthe timethe Tornado Warning is ineffect to NRCFORM366A(11-2015) Page 5 of 6 NRCFORM366A U.S. NUCLEARREGULATORYCOMMISSION (11-2015) LICENSEE EVENT REPORT (LER) CONTINUATION SHEET 1.FACILITYNAME 2. DOCKET 6. LERNUMBER SEQUENTIAL REV YEAR NUMBER NO. Sequoyah NuclearPlantUnit1 05000327 2016 004 01 NARRATIVE bypass the crankcase pressure tripfunction and allow the EDGs to be able to perform their required safetyfunction. V. ASSESSMENT OF SAFETY CONSEQUENCES The EDGs are located inside the power plant structure and are capable of performing their safetyfunction. The occurrence ofsuch an event involvingfailure ofthe fire dampers or the crankcase pressure switches is highly unlikely and there was no imminent concern regarding severe weather involving tornadoes atthe time ofthe events. A risk assessment has been completed and has determined thatthe change in core damage frequency is less than 1E-6for failures of both the EDG fire dampers and crankcase pressure switches, which is of very low safety significance. A. Availabilityof systems orcomponents that could have performed the samefunction as the components and systems thatfailed during the event: There were no componentfailures. B. Forevents that occurred when the reactorwas shut down, availability of systems or components needed to shutdown the reactor and maintain safe shutdown conditions, remove residual heat, control the release of radioactive material, or mitigate the consequences of an accident: These events did not occurwhen the reactorwas shutdown. C. Forfailure that rendered a train of a safety system inoperable, an estimate of the elapsed timefrom discovery ofthe failure until the train was returned to service: Withthe compensatory measures in place, the EDGs will remain capable offulfilling theirdesign basisfunction following a tornado. VI. CORRECTIVEACTIONS This eventwas entered into the Tennessee ValleyAuthority CorrectiveAction Program under Condition Reports (CR) 1170545, 1178891, and 1181710. A. Immediate CorrectiveActions: 8-hour non-emergency notifications were made to the NRC to report the events as unanalyzed conditions that significantly degrade plant safety per 10 CFR 50.72(b)(3)(ii)(B). B. Corrective actions to reduce probability of similarevents occurring inthe future: Corrective actions include establishing compensatory measures to blockthe fire dampers inthe open position inthe eventthat a Tornado Watch/Warning is issued for the Hamilton NRCFORM366A(11-2015) Page 6 of 6 NRC FORM366A U.S. NUCLEARREGULATORYCOMMISSION (11-2015) LICENSEE EVENT REPORT (LER) CONTINUATION SHEET 1.FACILITYNAME 2. DOCKET 6. LERNUMBER SEQUENTIAL REV YEAR NUMBER NO. Sequoyah NuclearPlantUnit 1 05000327 2016 004 01 NARRATIVE County, Tennessee area. Inaddition, a compensatory measure has been established, that upon notification of a TornadoWarning, the EDGs willbe emergency started and operated during the time the TornadoWarning is ineffectto bypass the crankcase pressure trip function and allow the EDGs to perform their required safety function. Furthercorrective actions include establishing the bounding criteria for evaluation of other componentsthat are subjectto the effects of a tornado that could impactthe safe operation of safety related equipment inCategory Istructures, fullyevaluating the components ofthe EDG building ventilation system, and fullyevaluating the components inthe EDG building that are subjectto the effects of a tornado that could impactthe operation ofthe EDGs. VII. ADDITIONAL INFORMATION A. Previous similarevents atthe same plant: There have been no similarevents at SQN inthe pastthree years that resulted in an unanalyzed condition on the EDGs due to a tornado. B. Additional Information: None. C. SafetySystem Functional Failure Consideration: These events did not result in a safety system functional failure in accordance with 10CFR50.73(a)(2)(v). D. Scramswith Complications Consideration: There were no scrams associated with these events. VIII. COMMITMENTS None. NRCFORM366A(11-2015) | ML16281A109
Sequoyah Nuclear Plant | Unit 1 | Closed Fire Damper Renders Both Trains of the Control Room Emergency Ventilation System Inoperable | 10-31-2018 | On August 10, 2016, at 1000 Eastern Daylight Time (EDT), the Maintenance Instrument Group (MIG) performed a surveillance instruction (SI) that resulted in a fire protection damper associated with the Control Room Emergency Ventilation System (CREVS) actuating to a closed position. On August 11, at 1015 EDT, the fire damper was discovered in the closed position. The closure of the fire protection damper resulted in both trains of CREVS being inoperable due to the loss of air circulation and habitability of the Technical Support Center and Relay Room. Both units entered Technical Specification Limiting Condition for Operation (LCO) 3.7.10, Conditions A and G. Condition G requires immediate entry into LCO 3.0.3. At 1159 EDT, on August 11, actions were taken to open the fire damper and both trains of CREVS were declared operable. This allowed both units to exit LCO 3.0.3 and LCO 3.7.10, Conditions A and G. The cause of the event was determined to be inadequate breaker alignment instructions in the SI. Corrective actions include revising the SI to require the associated breaker to be open prior to performance of the SI. NRC FORM 366 (11-2015) Page 2 of 6 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means CONTINUATION SHEET used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR NUMBER NO. Sequoyah Nuclear Plant Unit 1 05000327 2016 - 008 - 00 | I. PLANT OPERATING CONDITIONS BEFORE THE EVENT At the time of the event, Sequoyah Nuclear Plant (SQN) Unit 1 and Unit 2 were in Mode 1 at 100 percent rated thermal power. II. DESCRIPTION OF EVENTS A. Event: On August 10, 2016, at 1000 Eastern Daylight Time (EDT),the Maintenance Instrument Group (MIG) began performing a surveillance instruction (SI) associated with a functional test of the fire detection system [EIIS: IC] and peripheral devices. During performance of the SI, MIG received the expected response from the test, which was an alarm [EIIS: ALM]. Multiple times during the test, MIG was instructed by the SI to acknowledge the alarm (by pressing the “send” key) and continue with testing. At some point during performance of the SI, a fire protection damper [EIIS: DMP] associated with the Control Room Emergency Ventilation System (CREVS) [EIIS: VI] received an actuation signal and actuated to a closed position. While closing, the damper actuator broke its associated fusible links, as designed. This was not an anticipated result of the SI, and therefore, went undiscovered. On August 11, 2016, at 1015 EDT, while performing a walkdown of the Relay Room, the fire protection damper was discovered in the closed position. The closure resulted in both trains of CREVS being inoperable due to the loss of air circulation and habitability of the Technical Support Center (TSC) and Relay Room. Both units entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.10, Conditions A and G. Condition G requires immediate entry into LCO 3.0.3. At 1159 EDT, on August 11, actions were taken to block open the fire damper and both trains of CREVS were declared operable. This allowed both units to exit LCO 3.0.3 and LCO 3.7.10, Conditions A and G. An 8-hour non-emergency event notification (EN 52172) was made to the NRC in accordance with 10 CFR 50.72(b)(3)(xiii), as any event that results in a major loss of emergency assessment capability, offsite response capability, or offsite communications capability, and 10 CFR 50.72(b)(3)(v)(D), as an event or condition that could have prevented fulfillment of a safety function of structures or systems that are needed to mitigate the consequences of an accident. This LER documents the reportable event under 10 CFR 50.73(a)(2)(v)(D). Additionally, it was determined that both trains of CREVS were inoperable from August 10, 2016, at 1000 to August 11, 2016, at 1159. LCO 3.7.10, Condition G, Required Action G.1 requires immediate entry into LCO 3.0.3. LCO 3.0.3 requires the unit to be in MODE 3 within 7 hours and MODE 4 within 13 hours. Because both trains of CREVS were inoperable for approximately 26 hours and remained in MODE 1, this is a condition prohibited by TS and is therefore being | ML16281A424
River Bend Station -Unit 1 05000 . 458 1 OF 3 | Unit 1 | ' ) Operations Prohibited by Technical Specifications Due to Failure to Implement Required Actions Within Completion Time | 10-04-2016 | On May 25, 2016, it was determined that there had been a violation of Technical Specifications during a recent planned maintenance outage of the Division 1 diesel generator (DG). During that outage, three material deficiencies of various subcomponents were discovered while conducting maintenance tasks. The initial operability screening of each deficiency determined that the as-found condition did not, by itself, cause the DG to be inoperable. However, the associated condition report for each item was flagged as "inoperable." These determinations should have, thus, caused the operators to invoke the requirements of the TS to perform common cause evaluations to assure that the same conditions did not exist on the operable Division 2 DG. This action was not performed. Human performance evaluations of the operators involved in the condition report screening concluded that a cognitive, undocumented decision was made that the individual deficiencies did not meet the threshold of requiring a common cause evaluation. This event constituted operations prohibited by Technical Specifications, and is being reported in accordance with 10 CFR 50.73 (a)(2)(i)(B). The investigation of this event discovered a previous similar occurrence during a planned maintenance outage of the Division 2 DG in February 2014 which constituted operations prohibited by Technical Specifications, but which was not reported at the time. That event was later determined to have not defeated the safety function of the DG, and was, thus, of minimal significance with respect to the health and safety of the public NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 CONTINUATION SHEET F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to ........ lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, " NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the b1!p.-:.Llwww na.;.gov/reai:Jing-rm/doc-collectio_n.filmm~,m;L.s~21QL). NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER DYE AR SEQUENTIAL REV River Bend Station - Unit 1 05000-1 458 NUMBER 1-NO0. I ~-I 007 | REPORTED CONDITION On May 25, 2016, it was determined that there had been a violation of Technical Specifications during a recent planned maintenance outage of the Division 1 diesel generator (DG)[EK]. During that outage, three material deficiencies of various subcomponents were discovered while conducting maintenance tasks. These discoveries should have caused the operators to invoke the requirements of the TS to perform common, cause evaluations to assure that the same conditions did not exist on the operable Division 2 DG. This action was not performed. This condition constituted operations prohibited by Technical Specifications, and is being reported in accordance with 10 CFR 50.73 (a)(2)(i)(B). INVES~IGATION The material deficiencies found during the DG outage involved two minor air leaks on pressure switches in the engine air start subsystem and a DG governor drive coupling that was not in compliance with design drawings. Condition Reports were initiated in accordance with the corrective action program, and these CRs underwent the initial operability assessment. The CRs were individually flagged by the operations shift managers (OSM) as conditions that would cause the DG to be inoperable. Since the DG was already inoperable for the planned maintenance outage, the CRs were added to the work tracking system to assure that the conditions would be corrected prior to restoring the DG to an operable status. Limiting Condition for Operation (LCO) 3.8.1 was already in effect for the maintenance outage. One of the Required Actions of this LCO specifies that a common cause evaluation will be performed for material defects discovered to potentially have an adverse effect on the operability of the DG. This evaluation is meant to assure that the same condition does not exist on the other DG. The TS requires that this evaluation be completed within 24 hours. Although there were discussions between OSM and the maintenance staff at the time, there was no, documentation of the cor:iclusions. Human performance evaluations were conducted with the OS Ms involved in the processing of the Condition Reports written on each of the deficiencies. Following are the conclusions: / • With regard to the air leaks, the OSM reasoned that the leaks had likely been induced by the maintenance activities, since the system had been depressurized and then restored to normal pressure prior to discovery of the leak. No leakage had been reported prior to this activity. • Regarding the condition of the DG governor drive coupling, the initial assessment concluded that the coupling had been in the as-found configuration since the DGs were installed during plant construction. This was seen as significant evidence that the as-found condition did not adversely affect the ability of the DG to perform its design safety function. CORRECTIVE ACTIONS TO PREVENT RECURRENCE The causal analysis of this event has been reviewed as operational experience by each of the active OS Ms. A training analysis is being conducted to define and correct knowledge gaps that contributed to this event. NRG FORM 366A (06-2016) Page · 2 of 3 | ML16285A401
Edwin I. Hatch Nuclear Plant | Unit 2 | 2C Emergency Diesel Generator Inoperable Due to Low Lube Oil Pressure | 10-13-2016 | On August 18, 2016 at 1006, while performing the monthly Emergency Diesel Generator (EDG) surveillance, the 2C EDG tripped on low lube oil pressure. The station entered a 72 hour Required Action Statement (RAS) for Unit 2 Limiting Condition of Operation (LCO) 3.8.1.b. The other four EDGs were successfully started for surveillance testing in accordance with Tech Specs to preclude a common cause failure mode. Further inspections were performed and the cross drive shaft between the pump flexible drive gear and the engine driven lube oil pump was found sheared. The cross drive shaft assembly was replaced and the 2C EDG was declared operable on August 24, 2016 after subsequent functional and post maintenance testing. Investigations into the failure revealed that the initial cross drive shaft fracture existed prior to the monthly surveillance performed on August 18. The time frame for which the 2C EDG was able to perform its safety function for its 7-day mission time is indeterminable due to the failure mechanism of the cross drive shaft. A loss of safety function is being reported due to the 2C EDG being potentially inoperable during a time in which either the 1 8 swing EDG was inhibited from Unit 2 or the 1B /2A EDG was inoperable due to normal equipment maintenance and testing. Additionally, this report constitutes a Part 21 notification per 10 CFR 21.21 (d). NRC FORM 366 (02·2014) NRC FORM 366A (1·2001) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSIOI\ APPROVED BY OMB: NO. 3150-0104 EXPIRES: 1/31/2017 (02·2014) Estimated burden per response to comply with this mandatory collection request: 80 hours. # ........ Reported lessons learned are incorporated into the licensing process and led back to industry. F \ Send comments regarding burden estimate to the FOIA, Privacy and lnfonmation Collections ~~~ LICENSEE EVENT REPORT (LER) Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555·0001, or by t' ....~.. .l internet e-mail to lnlocollects.Resource@nrc.gov, and to the Desk Officer, Office of lnfonmation CONTINUATION SHEET and Regulatory Affairs, NEOB-10202, {3150·0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an infonmation collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the infonmation collection. 1. FACILITY NAME 2. DOCKET 6I. LEA NUMBERI 3. PAGE YEAR SEQUENTIAL REV. Edwin I. Hatch Nuclear Plant Unit 2 05000 366 NUMBER NO. 2 OF 6 2016 •• 003 •• 00 | PLANT AND SYSTEM IDENTIFICATION General Electric-Boiling Water Reactor Energy Industry Identification System codes appear in the text as (EllS Code XX) DESCRIPTION OF EVENT On August 18, 2016 at 1006 with Unit 2 at approximately 100 percent thermal power, the 2C Emergency Diesel Generator (EDG) (EllS Code DG) tripped due to low lube oil pressure about 30 minutes into the surveillance run. The station entered a 72 hour Required Action Statement (RAS) for Limiting Condition of Operation (LCO) 3.8.1.b of Hatch Unit 2 Technical Specifications, which requires two (2) Unit 2 EDGs to be operable. The other four (4) EDGs were successfully started in accordance with Tech Specs to preclude a common cause failure mode, and no issues were identified. All four EDGs were also successfully loaded, which exceeded the requirement of the required action. The 1 B EDG was inhibited from automatically aligning to Unit 1 on August 19, 2016 at 1157 in order to allow 14 days to restore the 2C EDG to operable status. Further inspections of the 2C EDG were performed and the cross drive shaft between the pump flexible drive gear and the engine driven lube oil pump was found sheared. As part of further troubleshooting and inspection, the cross drive assembly was inspected and excessive bearing wear was identified in the cross drive indicated by excessive movement in the shaft. Upon the installation of a new cross drive assembly, as well as the replacement of associated damaged parts, the 2C EDG was declared operable on August 24, 2016 at 2334 following successful completion of post maintenance testing. CAUSE OF EVENT Based on physical indications and failure analysis taken from the damaged cross drive shaft, associated drive gears, and cylindrical roller bearing, the shaft failed due to rotational bending fatigue caused by premature bearing failure. The most likely cause of bearing failure was due to an overload condition such that the bearing was no longer able to adequately support the shaft to reduce rotational friction and support radial and axial loads. The overloaded bearing condition most likely existed from the EDG manufacturer. All preventative maintenance activities have been appropriately completed in accordance with vendor recommendations. Additionally, as-found failure analyses did not find indications of foreign material or inadequate lubrication. A search through Southern Nuclear Operating Company (SNC) maintenance records has not revealed any maintenance performed on the cross drive assembly by SNC beyond the vendor recommended visual inspection since the 2C EDG was installed. Therefore, based on the aforementioned information, this event is also reportable per 10 CFR 21.21 (d) for reporting manufacturing defects that could create a substantial safety hazard. Premature wear of the cylindrical roller bearing located on the cross drive shaft initiated and propagated the cross drive shaft failure. Bearing life expectancy is dependent upon the load and speed imposed on the bearing. Based on the maximum speeds seen by Fairbanks Morse 38TD 8-1/8 Opposed Piston Diesel Engines and the amount of run-time hours accumulated by the 2C EDG, the bearing failed prematurely due to being overloaded. This overload caused fatigue on the bearing inner and outer races and on the bearing rollers, such that the shaft was no longer adequately supported. This resulted in the bending of the shaft and initiated cracks at multiple locations on the outer diameter. The cracks then continued to propagate inward towards the center of the shaft due to continued bending fatigue. When the remaining cross-sectional area of the shaft could no longer support the applied bending and torsional loads, the shaft failed. | ML16287A788
Fermi 2 05000 341 1 OF 11 | Unknown Unit | Inadequate Interpretation of Technical Specifications Related to Mechanical Draft Cooling Tower Fan Brake System Leads to Condition Prohibited by Technical Specifications, Loss of Safety Function, and Unanalyzed Condition | 10-20-2016 | At 1629 EDT on August 25, 2016, it was determined that an inadequate interpretation of Fermi 2 Technical Specification (TS) 3.7.2 was being utilized. For an Ultimate Heat Sink (UHS) divisional reservoir to be operable, two Mechanical Draft Cooling Tower (MDCT) fans in that division are required to be operable. The MDCT fans have a brake system to prevent fan overspeed during a tornado. Fermi 2 procedures had directed personnel to declare the MDCT fans and UHS reservoir inoperable due to nonfunctionality of the brake system only if a tornado watch or warning was in effect for the area near Fermi 2. The correct interpretation of TS 3.7.2 would be to declare the MDCT fans and UHS reservoir inoperable any time the brake system was nonfunctional. Following discovery of the inadequate interpretation of TS, a review of the brake system for the past three years was performed. The review identified 15 occurrences where the brake system was nonfunctional and should have resulted in entry to TS 3.7.2. These 15 occurrences resulted in operations or conditions prohibited by TS since TS Required Actions were not completed within their Completion Times. In addition, 5 of the 15 were also instances where the plant configuration was such that it could have prevented the fulfillment of the safety function of structures or systems. Finally, 4 of the 15 were instances where the plant was in an unanalyzed condition. There were no radiological releases associated with this event. There was no credible threat of a tornado during any of the 15 occurrences. The safety significance was determined to be very low. The cause of the event was an incorrect proceduralized TS interpretation. Corrective actions were taken to revise the procedure. NRC FORM 366 (06-20161 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY MB: NO. 31w50-0104 EXPIRES: 1013112018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 CONTINUATION SHEET F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management andB udgeWt,a shington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form u N s R e C d t m o a im y p n o o s t e c a o n n d in u fo c r t m o a r t i s o p n o c n o s l o le r c , ti a o n n d d a oe p s e n rs o o t n d is i p s la n y o t a r c e u q r u r i e r n ed tl y t v o a l r i e d s O po M n B d c to o , n t t r h o e l nu in m fo b r e m r a , t t io h n e htlp://w .nrc gov/reading-rm/doc-collections/nuregs/staff/sr10221r31) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER IYEAR SEQUENTIAL REV - NUMBER NO. S05000 Fermi 2 341 2016 - 06 - 0 | INITIAL PLANT CONDITIONS Mode - 1 Reactor Power - 53 percent There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT At 1629 EDT on August 25, 2016, while operating in Mode 1 at 53 percent power, it was determined that DTE Electric Company (DTE) had been utilizing an inadequate interpretation of Technical Specifications (TS) pertaining to the Mechanical Draft Cooling Tower (MDCT) [[CTW]] fan [[FAN]] brake [[BRK]] system. TS 3.7.2 requires the Ultimate Heat Sink (UHS) [[BS]] reservoir to be operable in Modes 1, 2 and 3. The UHS operability requirements in Modes 4 and 5 are determined by the systems the UHS supports. The UHS reservoir is divided into two one-half capacity reservoirs, corresponding to Division 1 and Division 2. Each reservoir is the cooling source for that division's service water subsystems, including the service water for the Emergency Diesel Generators (EDGs) [[DG]]. A two-cell MDCT is located above each of the one-half capacity reservoirs. Each cell is equipped with a MDCT fan. Two MDCT fans above each one-half capacity reservoir are required for it to be considered operable. The "A" and "C" MDCT fans are in Division 1 and the "B" and "D" fans are in Division 2. The MDCT fans have a brake system to prevent overspeed from a design basis tornado as described in the Updated Final Safety Analysis Report (UFSAR) Section 9.2.5.2.2. Thus the fan brakes are a design feature of the fans and their functionality impacts the operability of the MDCT fans and therefore the UHS. Contrary to this, a DTE procedure directed personnel to declare the MDCT fan and associated reservoir inoperable per TS 3.7.2 due to nonfunctionality of the brake system only if a tornado watch or tornado warning had been issued for the area surrounding Fermi 2. This inadequate interpretation of TS was discovered during an NRC Component Design Basis Inspection (CDBI). At the time of discovery on August 25, 2016, all of the MDCT fan brakes were functional and the associated fans were operable. The fan brake system for each of the four trains is actuated by nitrogen which is supplied by three nitrogen stages (bottles [[GBM]]) arranged in series. The nitrogen source is the main bottle which supplies the other two bottles through pressure reducing valves [[V]]. Each of the three nitrogen bottles is rated at a different pressure and has procedurally specified lower and upper limits. The nitrogen pressures of all twelve bottles are recorded daily as part of operator rounds. If any of the nitrogen bottles is outside of its specified limits, the fan brake system is considered nonfunctional. The main nitrogen bottle for each train is replaced on an as-needed basis when it is out-of-specification or a trend indicates that it is approaching its lower limit. The replacement of a nitrogen bottle is performed per plant procedures. With a correct understanding of the applicable TS, a past operability review was performed for the three years prior to the date of discovery. This review identified multiple occurrences where the MDCT fan brakes were nonfunctional. General descriptions applicable to one or more of the occurrences are provided below and then followed by the details of the specific occurrences. For each occurrence, the associated MDCT fan and reservoir was considered operable at the time and no entry to TS 3.7.2 was made based on the fan brake nonfunctionality. Limiting Condition for Operation (LCO) 3.7.2 Condition B Required Action B.1 requires restoration of the reservoir within 72 hours. LCO 3.7.2 Condition D Required Actions D.1 and D.2 require the reactor to be in Mode 3 in. 12 hours and Mode 4 in 36 hours if the Required Action and associated Completion Time of Condition B are not met. Page 2 of 11 | ML16295A107
Pilorim Nuclear Power Station 05000293 1 OF5 | Unknown Unit | Ultimate Heat Sink and Salt Service Water System Declared Inoperable | 10-13-2016 | On August 15, 2016 at 1552 EDT, with the reactor at about 70 percent core thermal power (CTP), Pilgrim Nuclear Power Station (PNPS) declared the ultimate heat sink (UHS) and salt service water (SSW) system inoperable due to high sea water inlet temperatures greater than 75 degrees Fahrenheit (F). PNPS had already taken action, in accordance with plant procedures, to reduce power from 100 percent in an effort to keep from exceeding the Technical Specification (TS) Limit. PNPS entered a 24-hour shutdown Limiting Condition for Operation Action Statement (LCO-AS) for Salt Service Water (SSW) inlet temperature exceeding the TS limit in TS 3.5.B.4. The LCO-AS was subsequently exited at 1651 hours when the temperature of SSW trended to below the TS limit. Under certain design conditions, the SSW system is required to provide cooling· water to various heat exchangers such as the Reactor Building Closed Cooling Water (RBCCW) and Turbine Building Closed Cooling Water (TBCCW) systems. When the inlet temperature to these supplied loads exceeds the 75 degree F limit established in the TS, the SSW system is conservatively declared inoperable until the temperature trends below this value. This condition existed for 59 minutes reaching a maximum of 75.1 degrees F. The cause of the sea water inlet temperature exceeding the 75 degree F TS criterion was sustained increased sea water surface temperature in Cape Cod Bay due to summer weather conditions and recirculation of water from the plant's discharge due to wind and tidal conditions. There was no imDact to public health and safetv from this condition. NRC FORM 366A (11-2015) p age 2 0 f 5 NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported "'"'~,..,~ lessons learned are incorporated into the licensing process and fed back to industry. Send .;. comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 'f: F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to *•••· LICENSEE EVENT REPORT lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (LER) CONTINUATION used to impose an information collection does not display a currently valid OMB control number, the SHEET NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR NUMBER NO. Pilgrim Nuclear Power Station 05000293 2016 005 00 | BACKGROUND Cape Cod Bay is the Ultimate Heat Sink (UHS) for PNPS. The circulating water system and the Salt Service Water (SSW) system take sea water from Cape Cod Bay via the plant intake canal and intake structure and . ( provide cooling water for various plant heat loads. These systems discharge the heated cooling water back into Cape Cod Bay via system discharge piping and the plant discharge canal. The safety objective of the SSW system is to provide a heat sink for the Reactor Building Closed Cooling Water (RBCCW) system under normal, transient, and accident conditions. The SSW system has five SSW pumps and is designed with sufficient redundancy so that no single active system component failure can prevent the system from achieving the safety objective. The system is designed to continuously provide a supply of cooling water to· the secondary side of the RBCCW heat exchangers adequate to meet the requirements of the RBCCW system under all conditions. The RBCCW system provides the necessary cooling requirements for the Residual Heat Removal (RHR) system and ultimately the reactor and primary containment. The SSW pumps are separated into two loops. Two pumps are connected to each loop and the fifth pump can feed either loop. Initiation of standby AC power following loss of the preferred AC power source will automatically start at least one pump in each loop during normal conditions. Following a Loss of Coolant Accident (LOCA) and loss-of-offsite power, one pump will start in each loop because of diesel load limitations. Additional pumps are started manually by the operator as additional cooling loads are established and diesel capacity is available. Technical Specification (TS) Limiting Condition For Operation (LCO) 3.5.B.4 requires that two SSW subsystems shall be operable whenever irradiated fuel is in the reactor vessel, reactor coolant temperature is greater than 212 degrees F and prior to startup from a cold condition. A subsystem is considered OPERABLE when it has an OPERABLE UHS and two OPERABLE pumps with associated controls and instrumentation. The OPERABILITY of the UHS is based on having a minimum water level in the pump well of the intake structure of greater than 13 ft. 9 in. below mean sea level and a maximum water temperature of 75 degrees F. One of the TS Surveillance Requirements for the SSW System is 4.5.B.4.2 which is to verify the average sea water temperature is less than or equal to 75 degrees F every 24 hours. If the UHS is inoperable, the unit must be placed in a MODE in which the Specification does not apply. To achieve this status, the unit must be in Cold Shutdown within 24 hours. The allowed completion times are reasonable, based on operating experience, to reach the required unit conditions from full power conditions in an orderly manner and without challenging unit systems. EVENT DESCRIPTION On August 15, 2016 at 1552 EDT, with the reactor at about 70 percent core thermal power (CTP), Pilgrim Nuclear Power Station (PNPS) declared the ultimate heat sink (UHS) and salt service water (SSW) system inoperable due to high sea water inlet temperatures greater than 75 degrees F. PNPS had already taken action, in accordance with plant procedures, to reduce power from 100 percent in an effort to keep from exceeding the Technical Specification (TS) Limit. PNPS entered a 24-hour shutdown Limiting Condition for NRG FORM 366A (11-2015) Pa e 3 of 5 NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (LER) CONTINUATION used to impose an information collection does not display a currently valid OMB control number, the SHEET NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR NUMBER NO. Pilgrim Nuclear Power Station 05000293 2016 005 00 NARRATIVE Operation Action Statement (LCO-AS) for Salt Service Water (SSW) inlet temperature exceeding the TS limit in TS 3.5.B.4. The LCO-AS was subsequently exited at 1651 hours when the temperature of SSW trended to below the TS limit. Under certain design conditions, the SSW system is required to provide cooling water to various heat exchangers such as the Reactor Building Closed Cooling Water (RBCCW) and Turbine Building Closed Cooling Water (TBCCW) systems. When the inlet temperature to these supplied loads exceeds the 75 degree F limit established in the TS, the SSW system is conservatively declared inoperable until the temperature trends below this value. On August 16, 2016 this condition existed for 59 minutes with the maximum temperature documented at 75.1 degrees F. CAUSE OF THE EVENT The cause of the sea water inlet temperature exceeding the 75 degree F TS criterion was sustained increased sea water surface temperature in Cape Cod Bay due to summer weatper conditions and recirculation of water from the plant's discharge due to wind and tidal conditions. The lack of margin available between the possible maximum sea water temperature and the design analytical limit influenced the plant's response. The possibility that both loops of containment cooling might be declared inoperable because of high UHS temperature was recognized when the 75 degree F Technical Specification limit was established in 1997. However, at that time based on historical temperature data and knowledge of the behavioral characteristics of the bay and local meteorology, it was considered highly improbable that the plant would ever be shut down because of high UHS temperature with the limit set at 75 degrees F. On these bases, the UHS temperature limit of 75 degrees F was considered acceptable. CORRECTIVE ACTIONS To increase the margin between the Salt Service Water (SSW) design basis inlet temperature and expected environmental operating conditions an engineering eval,uation that supports increasing the margin between the Salt Service Water (SSW) design basis inlet temperature and expected environmental operating conditions is being performed. Appropriate regulatory actions will be taken based on the results of that evaluation. · As an interim action, procedural enhancements to deal with elevated salt service water temperature will be implemented. Additional corrective actions will be implemented as necessary within the corrective action program. SAFETY CONSEQUENCES | ML16298A389
Peach Bottom Atomic Power Station | Unit 2 | Leak in High Pressure Service Water Pipe Results in Condition Prohibited by Technical Specifications | 11-11-2016 | On 9/12/16, an engineering evaluation concluded that a flaw identified on a 1" diameter stainless steel pipe associated with the High Pressure Service Water (HPSW) System could have failed during a seismic event. Failure of the pipe would cause flooding of the '2C' Residual Heat Removal (RHR) pump room and impact operation of equipment in the room if needed during a design basis event. The 1" diameter pipe supplies sample water to the '2C' HPSW radiation monitor sample pump. The flaw was identified on 8/16/16 when a 120 drop per minute leak was observed. The leak was the result of a crack located in the pipe at the toe of a fillet weld connecting the pipe to a coupling on an 18" diameter pipe that returns HPSW water to the plant discharge canal. There were no actual consequences as a result of the leak. The pipe was replaced and the equipment was returned to service. NRC FORM 366 (06-20161 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016)) Estimated burden per response to comply with this mandatory collection request 80 hours Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden es Iim ate lo lhe FOIA, Privacy and Information Collections Branch (T- 5 LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulalory Commission, Washington, DC 20555-0001, or by e-mail lo lnfocollects.Resource@nrc.gov, and to lhe Desk Officer, Office of Information and Regulalory Alfa rs CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Managemenl and Budget, Washington, DC 20503. If a means used lo impose an information colleclion does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conducl or sponsor, and a person is not required to respond to, lhe informalion http://www.nrc.gov/reading-rm/doc-colleclions/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Peach Bottom Atomic Power Station Unit 2 05000-277 YEAR NUMBER NO. 2016 - 001 0 | Unit Conditions Prior to the Event Unit 2 and Unit 3 were both operating in Mode 1 at approximately 100% rated thermal power. There were no structures, systems or components out of service that contributed to this event. Description of Event The High Pressure Service Water (HPSW) system (EllS: Bl) is a safety-related system that provides cooling water to four heat exchangers in the Residual Heat Removal (RHR) system (EllS: BO) during post-accident conditions. The HPSW system consists of four 4,500 gpm pumps that normally draw water from the Conowingo Pond. The system can also be lined up to draw water from the Emergency Cooling Tower (ECT} (EllS: BS) in the event that suction from the pond becomes unavailable. Water is pumped to the RHR heat exchangers, each of which is located in a watertight room. Water exits the heat exchangers through 14" diameter pipes. Those pipes from the 'A' and 'C' heat exchangers combine into an 18" diameter line, which later combines with an 18" diameter line from the 'B' and 'D' heat exchanger into a 24" diameter line that goes to the plant discharge canal. On the 18" diameter return line from the 'A' and 'C' heat exchangers, there is a pipe connection for a line to the HPSW radiation monitor sample pump. The line is a 1" diameter Schedule 40S (0. 133" wall thickness) Type 304 stainless steel pipe that was installed as part of a 1994 modification. The line is connected to the 18" diameter HPSW line with a socket weld connection to a half-coupling. The 1" pipe has a short span from the half-coupling to a rigid support on the wall, with two small valves in the span. On 8/16/16, at approximately 0830 hours, in PBAPS Unit 2, a 120 drop per minute leak was identified on the 1" pipe to the '2C' HPSW radiation monitor sample pump. Inspection determined that the leak was from a crack in the pipe located at the toe of the weld to the half-coupling on the 18" diameter HPSW return line from the 'A' and 'C' RHR heat exchangers. The crack was approximately 1" long and located between the 11 :00 o'clock and 2:00 o'clock positions on the pipe. Due to the length of the crack, the structural integrity of the pipe was questionable. If the pipe were to shear at the crack location, it was estimated that 77 gpm would flow through the opening into the 'C' RHR room. As a result of the identified condition, the following equipment was declared inoperable at 1500 hours on 8/16/16: • One low pressure ECCS injection subsystem per TS 3.5.1.A due to flooding potential in the 'C' RHR room • One RHR suppression pool cooling subsystem per TS 3.6.2.3.A due to flooding potential in the 'C' RHR room • One RHR suppression pool spray subsystem per TS 3.6.2.4.A due to flooding potential in the 'C' RHR room • One RHR drywell spray subsystem per TS 3.6.2.5.A due to flooding potential in the 'C' RHR room • One HPSW subsystem per TS 3.7.1.A due to through-wall leak in ASME Class 3 piping | ML16316A114
PAGE | Unknown Unit | Manual Reactor Scram Due To Feedwater Regulating Valve Malfunction | 11-04-2016 | On September 6, 2016 at 0827 EDT, with the reactor at approximately 91 percent core thermal power, operators manually scrammed the reactor when the benchmark for a reactor water level of +42 inches increasing was reached. Following the scram, all rods fully inserted and the Average Power Range Monitors were downscale, indicating the reactor was shut down. The Main Steam Isolation Valves closed on a Primary Containment Isolation Signal Group 1 isolation and were subsequently reopened to maintain reactor pressure. The reason for the increasing reactor water level was the malfunction of Feedwater Regulating Valve 'A' (FRV 'A'). The reactor operator at the control panel placed FRV 'A' in remote manual in an attempt to stabilize the feedwater flow oscillations. This had no effect on the performance of FRV 'A'. The operators experienced feedwater flow oscillations from FRV 'A' that resulted in reactor water level high and low level alarms on the control panel. Shortly after this, the benchmark reactor water level of +42 inches increasing was reached and operators manually scrammed the reactor. There was no impact to public health and safety. NRG FORM 366 (02-2014) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 01/31/2017 (02-2014) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information LICENSEE EVENT REPORT (LER) Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to lnfocollects.Resource@nrc.gov. and to the Desk Officer, CONTINUATION SHEET Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget. Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 6. LER NUMBER 3. PAGE I I YEAR SEQUENTIAL REVISION Pilgrim Nuclear Power Station 05000293 NUMBER NUMBER 2 OF4 2016 -007 -00 BACKGROUND The purpose of the feedwater level control system (FWLC) is to automatically control feedwater flow to the reactor vessel, maintaining vessel water level within a small range during all operating modes. During power generation, the FWLC system regulates feedwater flow maintaining proper water level in the reactor vessel according to the requirements for steam separator carryover and carry under through the entire reactor operating range. The FWLC system ensures sufficient sub-cooled water to the reactor vessel for jet pump and recirculation pump net positive suction head (NPSH) and to maintain normal operating temperatures during power operation. The primary FWLC system purpose is to maintain reactor vessel water level within a small range during all operational modes. FWLC instrumentation measures reactor vessel water level, feedwater flowrate and exit steam flowrate. During automatic operation these three measurements are used to control feedwater flow. The ability to maintain vessel level within a small range during load changes is accomplished by the three element control signal. The total steam flow signal and the total feedwater flow signal are fed into a proportional amplifier. The output from this amplifier is the mismatch between the input signals (steam flow-feedwater flow error signal). If steam flow is greater than feedwater flow, the amplifier output is increased from its normal value, causing the system to increase feed flow to balance with steam flow. This amplifier output is fed to a second proportional amplifier that also receives a reactor vessel water level signal. Adding the reactor vessel water level signal to the steam flow-feedwater flow error signal results in a three-element control signal, which is fed to the level controller. In May of 2015, during the refueling outage, new connectors on the encoder were installed. The new connectors were crimped onto the existing wires and inserted into the connection on the encoder. The valve was successfully post-work tested and returned to service. During the refueling outage, valve testing on the FRV 'A' was completed, including a pressure drop test on the actuator. However, due to a poorly written test procedure, anomalies were not properly identified or addressed as described below. During a reactor downpower on October 20 and 21, 2015, a packing leak was identified on FRV 'A'. This resulted in exposing the valve manual locking device to unfavorable conditions which eventually led to degradation of the valve locking mechanism couplings and bearings. The valve packing was adjusted to reduce the packing leak. EVENT DESCRIPTION At 07:55 on September 6, 2016, the control room received an instantaneous core thermal power (CTP) blinking annunciator light. This was the first indication to the control room operators that there was a problem. At 08:00 operations received an alarm for thermal power due to suspect value (feedwater flow). At 08: 10 operators placed FRV 'A' in remote manual. Three unsuccessful attempts were made to manually control the valve. · At 08: 14 operators were dispatched to the Condenser Bay to lockup FRV 'A' in accordance with procedure. The control room operators established scram benchmarks of +15 inches lowering, +42 inches increasing reactor NRC FORM 366A (02-2014) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION LICENSEE EVENT REPORT (LER) (02-2014) CONTINUATION SHEET 1. FACILITY NAME 2. DOCKET 6. LERNUMBER 3. PAGE I I YEAR SEQUENTIAL REVISION Pilgrim Nuclear Power Station 05000293 NUMBER NUMBER 3 OF4 2016 -007 -00 water level, or +/- 10 percent power swings. ~t 08: 19 the control room operators received reactor water high level alarm. ~t 08:20 an operator at the local digital control panel identified Error message for Friction Warnings and proceeds to FRV 'A' to lockup the valve. ~t 08:21 operators at FRV 'A' cannot operate the mechanical operator due to degraded condition of the actuator. ~t 08:25 FRV 'A' goes full open while operators are located at the valve. ~t 08:26:12, a "Friction Failure" error message was received at the local digital control panel. ~t 08:26:28 operators in the control room received an alarm for reactor water level high. ~t 08:27 operators manually scrammed the reactor at a water level of +42 inches increasing and received ~PRM downscale with all rods in. CAUSE OF THE EVENT rrhe direct cause of this event is the neutral common wire lost connection to the encoder stab on the stepper motor resulting in a loss of feedback to the control system for the valve. lrhe causes of the event are that the work package quality standards for critical maintenance work order package planning were not known or understood by some planning personnel. This resulted in the inadequate installation, during the May 2015 refueling outage, of the neutral common wire that became loose and lost connection between the encoder and the digital controller. In addition, the air operated valve testing procedure for the FRVs did not contain criteria for valve packing friction or stem load evaluation. This resulted in a missed opportunity to identify and correct the valve packing leakage condition and the degraded condition of the mechanical locking device prior to the event. CORRECTIVE ACTIONS lrhe following corrective actions were performed: 1) Replaced the FRV 'A' valve stem 2) Replaced the FRV 'A' and FRV 'B' valve packing 3) Refurbished the FRV 'A' manual actuator 4) Reassembled the encoder electrical connector 5) Performed a pull test of each individual wire in the encoder electrical connection satisfactorily before the connector was reinstalled and sealed in place for both FRV 'A' and 'B'. lrhe following corrective actions are currently planned to be performed: 1) Generate a maintenance planning standards checklist for critical maintenance work package quality and train maintenance planners on use of the new checklist. 2) Train station personnel in problem identification and resolution. 3) Train operating crews and station leadership on the event, causes and corrective actions. ' NRC FORM 366A (02-2014) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION LICENSEE EVENT REPORT (LER) (02-2014) CONTINUATION SHEET 1. FACILITY NAME 2. DOCKET 6. LERNUMBER 3. PAGE I I YEAR SEQUENTIAL REVISION Pilgrim Nuclear Power Station 05000293 NUMBER NUMBER 4 OF4 2016 -007 -00 | SAFETY CONSEQUENCES The actual consequences were a loss of ability to control FRV 'A' which resulted in increasing reactor water level and an operator-initiated manual scram. There were no other actual consequences to general safety of ~he public, nuclear safety, industrial safety, and radiological safety for this event. The potential consequences to general safety of the public, nuclear safety, industrial safety, and radiological safety of this event if the operator-initiated manual scram did not occur were minimal. Had the manual scram not been initiated, in a short time there would have been an automatic turbine trip, feedwater pump trip, and Primary Containment Isolation Signal Group 1 isolation from the high reactor water level condition. These automatic actions would have immediately caused an automatic reactor Scram. rThe conditional core damage probability of this event has been estimated to be 3.49E-06. This is the value associated with a Main Steam Isolation Valve (MSIV) isolation initiator. The risk from the actµal event was less than this calculated value because the Scram was manually initiated prior to the turbine trip and other automatic actions. The scram was considered uncomplicated as defined in Nuclear Energy Institute 99-02. Therefore, based on the above there was no adverse impact on the public health or safety. REPORTA BILITY ifhis report is submitted in accordance with 10 CFR 50. 73(a)(2)(iv)(A). Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section including 50.73(a)(2)(iv)(B)(2), general containment isolation signals c;iffecting containment isolation valves in more than one system or multiple MSIVs. PREVIOUS EVENTS IA review of Pilgrim Nuclear Power Station Licensee Even't Reports for the past five years did not identify any $imilar occurrences of manual scrams being initiated by feedwater oscillations. ENERGY INDUSTRY IDENTIFICATION SYSTEM (EllS) CODES ifhe EllS codes for Components and Systems referenced in this report are as follows: SYSTEMS CODES Feedwater System SJ REFERENCES: CR-PNP-2016-6635 | ML16320A006
Susquehanna Steam Electric Station | Unit 2 | Loss of Secondary Containment Due to Damper Controller Sticking | 10-31-2018 | On September 22, 2016 at 03:20, a Nuclear Plant Operator (NPO) reported that Reactor Building Zone II differential pressure (dP) was steady at 0.15 inches water gauge (WG) resulting in entry into Technical Specification 3.6.4.1. Operations determined that the flow control damper (PDD27522A) for the "A" Zone II equipment exhaust fan (2V206A) was sticking, resulting in Zone II dP not being properly controlled. The linkage for the damper was agitated and the damper moved to control dP as designed. Operations placed the "B" division fan (2V206B) in service. Following the fan swap, dP held steady at 0.31 inches WG with 2V206B in service and 2V206A in standby. Technical Specification 3.6.4.1 was cleared at 03:42. This event was reported in accordance with 10 CFR 50. 72(b )(3)(v)(C) as a condition that could have prevented fulfillment of a safety function (EN 52255). The condition also requires a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(v)(C). The cause of the event was age related degradation of the brass bushing and grease hardening in the damper linkage. Corrective actions include initiating work orders to disassemble, inspect, and replace the brass bushings for the remaining similar dampers. A Preventive Maintenance strategy will be evaluated following completion of the inspections of the remaining dampers. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366A (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and led back to industry. LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53). U.S. Nuclear Regulatory Commission, Washington, DC 20555·0001, or by e-mail CONTINUATION SHEET to lnlocollects.Resource@nrc.gov, and to the Desk Ollicer, Olfice ol Information and Regulatory Alfairs, NEOB-10202, (3150-0104), Ollice ol Management and Budget, Washington, DC 20503. II a (See NUREG-10 22, R.3 for instruction and guidance for completing this form means used to impose an information collection does not display a currently valid OMB control http://'NI/If'N. nrc.g ov/readi nq-rm/doc-collections/nureos/staff/sr1 022/r3/) number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITYNAME 2. DOCKETNUMBER 3. LER NUMBER I I YEAR SEQUENTIAL REV Susquehanna Steam Electric Station 05000-388 NUMBER NO. Unit 2 2016 -006 -00 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, approximately 100 percent Rated Thermal Power Unit 2 - Mode 1, approximately 100 percent Rated Thermal Power EVENT DESCRIPTION On September 22, 2016 at 03:20, a Nuclear Plant Operator (NPO) reported that Reactor Building Zone II differential pressure (dP) was steady at 0.15 inches water gauge (WG) resulting in entry into Technical Specification 3.6.4.1. Operations determined that the flow control damper (PDD27522A) [EllS System/Component Identifier: VAIDMP] for the "A" Zone II equipment exhaust fan (2V206A) [EllS System/Component Identifier: VA/FAN] was sticking, resulting in Zone II dP not being properly controlled. The linkage for the damper was agitated and the damper moved to control dP as designed. Operations placed the "B" division fan (2V206B) in service. Following the fan swap, dP held steady at 0.31 inches WG with 2V206B in service and 2V206A in standby. Technical Specification 3.6.4.1 was cleared at 03:42. During troubleshooting for this event, the linkage was disassembled and the damper was manually stroked with the linkage arm. The damper stroked smoothly with no binding. Internal inspection identified no issues. The pivot point for the linkage arm was disassembled and replaced. When the pivot point was disassembled, Maintenance discovered that the brass bushing and pins were worn and the grease was hardened and sticky. This event was reported in accordance with 10 CFR 50.72(b)(3)(v)(C) as a condition that could have prevented fulfillment of a safety function (EN 52255). The condition also requires a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(v)(C). CAUSE OF EVENT The cause of the event was age related degradation of the brass bushing and grease hardening. ANALYSIS/SAFETY SIGNIFICANCE An engineering evaluation was performed and concluded that secondary containment could have performed its safety function of isolating as assumed in the accident analysis and also of re-establishing 0.25 inches vacuum (drawdown) within the assumed accident analysis time (1 0 minutes). Therefore, the subject event did not cause a loss of safety function. This event will not be counted as a safety system functional failure (SSFF) for the NRC performance indicator based on the engineering analysis that shows there was no loss of ability to fulfill the safety function. | ML16323A007
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Degraded Damper Actuator Prevented Control Room Ventilation Exhaust Fan Start | 11-17-2016 | On September 19, 2016, the Control Room Ventilation exhaust fan 70FN-4A did not start when it was being placed into service. The fan outlet isolation damper actuator 70MOD-108A(OP) failed to give the fully-open permissive signal to start the fan. Gentle pressure on the actuator linkage allowed the fan to start. Prior to this, on August 16, 2016, during post-maintenance testing, 70FN-4A did not start. Troubleshooting adjusted the linkage and the fan started as appropriate. However, the intermittent fan start issue was caused by the degraded damper actuator 70MOD-108A(OP). Corrective action replaced 70MOD-108A(OP). This event is reportable per 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 – 333 NUMBER N0. 2016 – 005 – 00 | Background The James A. FitzPatrick Nuclear Power Plant (JAF) Control Room Air Conditioning (AC) System [EIIS identifier: VI] and the Control Room Emergency Ventilation Air Supply (CREVAS) System [VI] (a mode of the Control Room AC) provides a protected environment from which occupants can control the plant during normal conditions and following an uncontrolled release of radioactivity, hazardous chemicals, or smoke. The Control Room AC System and CREVAS System consists of two redundant subsystems that provide recirculated control room air. A single subsystem is sufficient to maintain a suitable control room environment for a sustained occupancy of 20 persons. Each subsystem consists of air handling units, recirculation exhaust fans, air handling unit fans, ductwork, dampers, and associated Instrumentation and controls; and, each CREVAS subsystem consists of a series of filters, a control room emergency air supply fan, valves or dampers, doors, barriers and instrumentation. The recirculation / exhaust fans consist of two full capacity fans for the Control Room. The intake air supply is mixed with air from one of the recirculation / exhaust fans before it is recirculated back to the room. One Control Room exhaust fan runs at all times to support the normal or emergency mode while the other fan is on standby. Normally these exhaust fans are swapped manually. An automatic start function occurs only if the running exhaust fan stops. This Licensee Event Report (LER) addresses the ability to start one of the Control Room recirculation / exhaust fans (70FN-4A). Event Description On September 19, 2016, JAF was at 54 percent power when the Control Room Ventilation recirculation / exhaust fan lineup was being changed to place 70FN-4A inservice when it did not start as expected. A second attempt to start the fan was successful when gentle pressure was applied to assist the linkage between the damper (70MOD-108A) and motor actuator (70MOD-108A(OP)). This damper is located on the outlet to 70FN-4A. To maintain the operability of 70FN-4A, it was placed in service as the lead fan with 70FN-4B in standby. In addition, a manual Operator compensatory action was developed to have an Operator dispatched to assist the damper linkage in the event that an exhaust fan does not start. This compensatory action requires a short transit from the Control Room to the Control Room Ventilation Equipment room. Event Analysis The switch in the Control Room begins the sequence to start the fan (70FN-4A) by opening its associated damper (70MOD-108A). The circuit logic starts the fan after a time delay so the damper has time to open; but, it only starts the fan if there is a permissive signal that the damper has fully opened. The open permissive signal originates from a position switch integral / internal to the damper actuator (70MOD-108A(OP)) itself. When gentle pressure was applied to assist the damper linkage during the event, it caused the actuator to complete its motion and close the contact for the permissive signal and initiate the fan start. Prior to this event, on August 16, 2016, 70FN-4A did not start during post maintenance testing. In addition, the time delay start logic relay (70-62-1CRVA04) was found out-of-tolerance and damper position indication in the Control Room was dual. Indication in the Control Room for damper position comes from position switches 70PNS-108A1 and 70PNS-108A2. However, these position switches are for indication only and they do not Page 2 of 4 | ML16323A201
Susquehanna Steam Electric Station | Unit 1 | Secondary Containment Declared Inoperable Due to Airlock Doors Open Due to a Human Performance Error | 10-31-2018 | On September 26, 2016 at approximately 11:55, the Control Room was informed of an airlock violation on the Refuel Floor. This violation resulted when an escorted individual who was part of a group opened the airlock exit door while the remainder of the group was still entering the airlock. This airlock serves as a secondary containment boundary; as such, having both doors open at the same time results in failure to meet Technical Specification 3.6.4.1 as a result of not satisfying Surveillance Requirement 3.6.4.1.3. The condition requires a Licensee Event Report (LER) in accordance with 10 CFR 50. 73(a)(2)(v)(C). The cause of the event was less than adequate verification practices to ensure that Secondary Containment door requirements were utilized. Corrective actions included coaching of the group of escorted individuals and the escorting individual. Additionally, direction for communication of airlock expectations will be added to plant escort expectations. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366A (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06·2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail CONTINUATION SHEET to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. II a (See NUREG-1022, R.3 for instruction and guidance for completing this form means used to impose an information collection does not display a currently valid OMB control http://www.nrc.gov/reading-rm/doc-colleclions/nuregs/staff/sr10221r3D number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER I I YEAR SEQUENTIAL REV Susquehanna Steam Electric Station, Unit 1 05000387 NUMBER NO. 2016 -023 -00 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, approximately 100 percent Rated Thermal Power Unit 2- Mode 1, approximately 100 percent Rated Thermal Power There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. EVENT DESCRIPTION On September 26, 2016 at approximately 11:55, a tour group entered an airlock [EllS Component Code: AL] while the escort held the entrance door [EllS Component Code: DR] open. One of the tour group members went in the airlock and immediately opened the exit door. As soon as the alarm [EllS Component Code: ALM] sounded, the escort directed the visitor to reclose the exit door. The exit door was opened about 6 inches and immediately reclosed. This airlock serves as a secondary containment [EllS System Code: VA] boundary; as such, having both doors open at the same time results in failure to meet Technical Specification 3.6.4.1 as a result of not satisfying Surveillance Requirement 3.6.4.1.3. The individuals were coached again on the air lock door expectations and there were no further issues. The escort was also coached on escorting responsibilities relative to secondary containment doors. The condition requires a Licensee Event Report (LER) in accordance with 10 CFR 50. 73(a)(2)(v)(C). CAUSE OF EVENT The cause of this event was less than adequate verification practices to ensure that Secondary Containment door requirements were utilized. ANALYSIS/SAFETY SIGNIFICANCE Technical Specification 3.6.4.1 Surveillance Requirement 3.6.4.1.3 requires that one secondary containment access door in each access opening is closed. This event is being reported pursuant to 10 CFR 50. 73(a)(2)(v)(C) as having both Secondary Containment airlock doors momentarily open simultaneously resulting in a condition that could have prevented fulfillment of a safety function to mitigate the consequences of an accident by controlling the release of radioactive material. There was no actual safety consequence as a result of this event. Engineering analysis of this event has determined that secondary containment could have performed its safety function of isolating, as assumed in the accident analysis, and also of re-establishing 0.25 in w.g. vacuum (drawdown) within the assumed accident analysis time (1 0 minutes). Therefore, the subject event did not cause a loss of safety function. This event will not be counted as a safety system functional failure (SSFF) for the NRC performance indicator based on the Engineering analysis supporting the system's ability to fulfill the safety function. CORRECTIVE ACTIONS Corrective actions completed include coaching of the group of escorted individuals and the escorting individual. Additionally, direction for communication of airlock expectations will be added to plant escort expectations. | ML16326A238
Cooper Nuclear Station 05000298 1of4 | Unknown Unit | Scaffold Construction Places Plant in a Condition Prohibited by Technical Specifications | 11-09-2016 | On September 14, 2016, during testing of the Reactor Recirculation Motor Generator Ventilation Air Operated Isolation Valves (AOV), HV-AOV-265 failed to close as required by Technical Specifications. Operations declared HV-AOV-265 inoperable and entered Limiting Condition for Operation (LCO) 3.6.4.2, Condition A, and commenced preparations to transition the plant to single loop operation, including reducing the plant to approximately 50 percent power. Upon investigation, it was discovered that the air supply line to the valve was pinched between the valve actuator and a scaffold that was erected to support work on a nearby component. After modifying the scaffold and replacing the pinched airline, the valve was tested satisfactorily and Operations exited the LCO and activities to prepare for transition to single loop operation were terminated. The root cause of the event is that personnel involved in the planning, construction, and inspection of the scaffold built for a nearby component were not aware of the unique external movement path of the valve actuator. To prevent recurrence, the procedure will be revised to include specific guidance for the planning, building and inspection of scaffolds in the vicinity of HV-AOV-265 and other AOVs having actuators of similar design. Signage has been installed to warn personnel of the external movement of these AOVs. NRC FORM 366 (06-2016) Page 2 of 4 NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to LICENSEE EVENT REPORT (LER) industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC (See Page 2 for required number of digits/characters for each 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of block) Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not (See NUREG-1022, R 3 for instruction and guidance for completing this form display a currently valid OMB control number, the NRG may not conduct or sponsor, and a http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Cooper Nuclear Station 05000- 298 2016 -003 -00 | PLANT STATUS Cooper Nuclear Station was in Mode 1, Power Operation, at 89 percent power, approaching the end of Cycle 29 in two-loop operation, at the time the condition was identified. BACKGROUND The safety objective of the Secondary Containment system [EllS:NG] in conjunction with othei:: engineering safeguards and nuclear safety systems is to limit the release to the environs of radipactive material so that off-site doses from a postulated design basis accident will be below the values .'. . permitted. The reactor building isolation and control system serves to trip the reactor building [EllS:NG] supply and exhaust fans [EllS:FAN], isolate the normal ventilation system and provide the starting signals for the Standby Gas Treatment (SGT) [EllS:BH] system in the event of a postulated Loss of Coolant Accident inside the drywall [EllS:NG] or the postulated fuel handling accident in the reactor building. Two normally open dampers [EllS:DMP], in series, are provided both in the supply path and two exhaust paths for the reactor building and the two supply and exhaust paths for Reactor Recirculation Motor Generator (RRMG) set ventilation. Each set of dampers consists of one air actuated damper, supplied by instrument air backed up by an accumulator [EllS:ACC] with an assured one-hour supply capacity, and a motor operated damper. These dampers ensure redundant, diverse isolation capability for the reactor building in the event of a release of radioactive material to the reactor building. These dampers close automatically on a Group 6 (Secondary Containment Isolation) isolation signal. HV-AOV-265 is the RRMG Ventilation Supply Outboard Isolation Valve for RRMG 1 B. This air operated valve (AOV) is normally open during plant operation. In addition to driving the actuator shaft, the air actuator cylinder physically rotates when the valve is opened or closed. This results in a large actuator movement path that includes the actuator shaft, cylinder, valve disc arm, and the airlines that connect to the cylinder. EVENT DESCRIPTION On September 14, 2016, during testing of the Reactor Recirculation Motor Generator Ventilation Air Operated Isolation Valves, the control switch for HV-AOV-265 was taken to close for valve stroke timing. The valve failed to close. HV-AOV-265 was declared inoperable and Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.4.2, Condition A, Required Action A.1, "Isolate the affected penetration flow path by use of at least one closed and de-activated valve within 8 hours," was entered. In addition, Operations commenced preparations for transitioning the plant to single loop operation, including reducing power to approximately 50 percent to support removing the associated RRMG set from service. Operations attempted to close HV-AOV-265 while an Engineer was stationed locally to observe the valve's operation. The Engineer identified that during the attempt to close the valve, the air supply line became pinched between the moving cylinder of the valve actuator and a scaffold that had been erected on June 29, 2016, to support work on a different valve. NRG FORM 366 (06-2016) Page 3 of4 NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BYOMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to LICENSEE EVENT REPORT (LER) industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC (See Page 2 for required number of digits/characters for each 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of block} Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not (See NUREG-1022, R 3 for instruction and guidance for completing this form display a currently valid OMB control number, the NRG may not conduct or sponsor, and a http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Cooper Nuclear Station 05000- 298 2016 -003 -00 NARRATIVE As such, air was restricted from exhausting from the air cylinder, pneumatically locking the piston and preventing the valve from closing. Further investigation revealed that the airline had been crimped and required replacement. After modifying the scaffold to remove the interference with the operation of the valve, the airline for HV A0-265 was replaced and the valve stroke testing was re-performed satisfactorily. HV-A0-265 was declared operable and TS LCO 3.6.4.2 was exited. Upon exiting the LCO, activities to prepare for transition to single loop operation were terminated. BASIS FOR REPORT This condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS because the scaffolding, installed in June 2016, was in a position to block the movement of the valve since that time. SAFETY SIGNIFICANCE The safety significance of this event is low. Secondary Containment AOV, HV-A0-265, could not be fully closed; however, the redundant motor operated valve in the RRMG B ventilation inlet flow path( HV-M0- 264, provided the required safety function for Secondary Containment isolation. This event didmot cause an impact to the safety of the general public, nuclear safety, industrial safety, or radiological safety. CAUSE The root cause of the event was determined to be that the personnel involved in the planning, construction, and inspection of the scaffold built for HV-MOV-264 were not aware of the external movement path of HV-AOV-265 actuator. CORRECTIVE ACTIONS Revise Maintenance Procedure 7.0.7, "Scaffolding Construction and Control," to include specific guidance for the planning, building and inspection of scaffolds in the vicinity of the AOVs listed below: PC-A0-236AV HV-A0-257AV HV-A0-263AV HV-A0-265AV HV-A0-267AV Installed signs in the areas near the AOVs listed below to warn personnel of the external movement of these AOVs: HV-A0-257AV HV-A0-259AV HV-A0-261AV HV-A0-263AV HV-A0-265AV HV-A0-267A V HV-A0-269AV HV-A0-271 AV HV-AO-FCV1045A HV-AO-FCV10458 HV-AO-FCV1046 HV-AO-FCV1047 PC-A0-234AV PC-A0-236AV NRC FORM 366 (06-2016) Page 4 of 4 NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to LICENSEE EVENT REPORT (LER) industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC (See Page 2 for required number of digits/characters for each 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of block) Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not (See NUREG-1022, R 3 for instruction and guidance for completing this form display a currently valid OMB control number, the NRG may not conduct or sponsor, and a http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Cooper Nuclear Station 05000- 298 2016 -003 -00 NARRATIVE PREVIOUS EVENTS There have been no events reported in the last three years related to scaffold construction impacting the ability of components to perform their safety function. NRC FORM 366 (06-2016) | ML16326A261
Peach Bottom Atomic Power Station | Unit 3 | Leak in High Pressure Coolant Injection Drain Pipe Results in a Loss of Safety Function | 11-22-2016 | On 9/26/16, at approximately 1845 hours, investigation of a water leak on a 3/4" diameter drain line for the High Pressure Coolant Injection (HPCI) turbine determined there was a through-wall flaw resulting in a leak of approximately 2 drops per minute. The pipe is classified as ASME Code Class 2 exempt and operates above 200 degrees F. As a result, the HPCI system was declared inoperable. The flaw was the result of a liquid drop impingement erosion process caused by the flow characteristics upstream of the orifice. The pipe section was replaced and the HPCI system was declared operable on 9/28/16 at approximately 2102 hours. There were no actual consequences as a result of the leak. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150.0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Peach Bottom Atomic Power Station Unit 3 05000278 YEAR NUMBER NO. 2016 - 001 0 | Unit Conditions Prior to the Event Unit 3 was operating in Mode 1 at approximately 100% rated thermal power. There were no structures, systems or components out of service that contributed to this event. Description of Event The High Pressure Coolant Injection (HPCI) system (EllS: BJ) is part of the emergency core cooling system that assures that the reactor is adequately cooled in the event of a small break loss of coolant accident. The system permits the reactor to be shut down while maintaining sufficient water inventory until the reactor vessel is depressurized and the low pressure coolant injection system maintains core cooling. The system uses a steam-driven pump with suction from the condensate storage tank or the suppression pool, and injects water into the reactor vessel via one of the two main feedwater lines. The turbine is driven by steam from a main steam line and exhaust steam is discharged to the suppression pool. To remove condensation that forms in the turbine, drain lines are in place that send water to a drain pot. Restricting orifices are located on the 3/4" diameter drain lines to reduce pressure prior to the water entering the drain pot. The drain lines are classified as ASME Code Class 2 exempt and operate above 200 degrees F when the HPCI pump is operating. On 9/26/16, investigation of a water leak on one of the 3/4" diameter drain lines for the HPCI turbine determined there was a through-wall flaw resulting in a leak of approximately 2 drops per minute. Pressure boundary integrity is required for system operability. As a result, the HPCI system was declared inoperable at approximately 1845 hours in accordance with Technical Specification 3.5.1.C. The pipe section was replaced and the HPCI system was declared operable on 9/28/16 at approximately 2102 hours. The elapsed time from the discovery of the failure to when the equipment was returned to service was approximately 50 hours and 17 minutes. Cause and Analysis of the Event The affected section of the pipe was removed. Inspection identified pitting on the interior surface of the pipe, just upstream of the pressure reducing orifice. The flaw was the result of a liquid drop impingement erosion process caused by the flow characteristics upstream of the orifice. A review of maintenance records dating back to the 1980s identified no previous replacements of this pipe; it is likely it was installed as part of original construction. The pump was last operated the previous day (9/25/16) and no leaks were noted. However, the failure mechanism (erosion) requires a significant period of time to develop into a through-wall flaw. HPCI is a single train system. Therefore, this event is being reported in accordance with 1O CFR 50.73(a)(2)(v)(D) as a condition that could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident. This issue was also reported to the NRC in accordance with 10CFR 50. 72(b)(3)(v)(D) on 9/27/16 at 0020 hours by EN# 52264. | ML16327A051
Oyster Creek 05000219 1 OF 4 | Unknown Unit | Technical Specification Violation Due to Main Steam Safety Valve Setpoint Discovered Out of Tolerance , | 11-16-2016 | Oyster Creek Nuclear Generating Station was in Cold Shutdown on 09/29/16 for Refueling Outage 1 R26 when a condition was discovered during routine laboratory as-found testing that a Safety Valve (SV) (EllC:RV) removed on 09/27/16 as part of refueling outage maintenance activities did not meet required setpoint tolerances. There were no structures, systems or components out of service that contributed to this event. In accordance with American Society of Mechanical Engineers (ASME) Operation and Maintenance (O&M) Code requirements, two (2) of the nine (9) SVs installed in the plant were scheduled for removal during the refueling outage (1 R26) and sent for as-found laboratory testing. Based on information received from the laboratory performing SV as-found testing, Site Engineering personnel determined that SV setpoint deficiencies existed with one (1) of the two (2) SVs removed and _sent for testing. Per ASME O&M Code Mandatory Appendix I Section I- 1320, two additional SVs were removed from the plant and sent for as-found testing and both met the required setpoint acceptance criteria. One (1) of the four (4) SVs tested exceeded the setpoint tolerance of +/-3% (+ /-36 psig) as specified in the Technical Specifications {TS), Paragraph 2.3.F. This resulted in a condition prohibited by TS and is considered reportable pursuant to 10 CFR 50. 73(a)(2){i)(B). NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150·0104 EXPIRES: 10/31/2018 (06-2016}} Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 LICENSEE EVENT REPORT {LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http://www. nr e.gov/reading-rm/doc-col lections/nuregs/staff/ s r1 022/r3l) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Oyster Creek, Unit 1 05000-219 YEAR NUMBER NO. 2016 - 004 00 | Unit Condition Prior to Discovery of the Event Oyster Creek Nuclear Generating Station (OCNGS) was in Cold Shutdown on 09/29/16 for Refueling Outage 1 R26 when a condition was discovered during routine laboratory as-found testing that a Safety Valve (SV) removed on 09/27/16 as part refueling outage maintenance activities did not meet required setpoint tolerances. There were no structures, systems or components out of service that contributed to this event. Description of Event In accordance with American Society of Mechanical Engineers (ASME) Operation and Maintenance (O&M) Code requirements, two (2) of the nine (9) SVs installed in the plant were scheduled for removal during the refueling outage (1 R26) and sent for as-found laboratory testing. Based on information received from the laboratory performing SV as-found testing, Site Engineering personnel determined that SV setpoint deficiencies existed with one (1) of the two (2) SVs that were removed and sent for testing. Pursuant to ASME O&M Code Mandatory Appendix I Section 1-1320, two (2) more SVs were removed from the plant and sent for as-found laboratory testing and both met the required setpoint acceptance criteria. One (1) of the four (4) SVs tested exceeded the setpoint tolerance of +/-3% (+/-36 psig) as specified in the Technical Specifications {TS), Paragraph 2.3F. One (1) valve, V-1-164 (Serial number BW05085) was determined to have an as-found setpoint value of-3.3% (-40 psig). The ASME Boiler and Pressure Vessel (B&PV) Code stipulates that relief valves (pressure relief function) have an as tound setpoint tolerance of +/- 3%. This report is being submitted pursuant to 1O CFR 50.73(a)(2)(i)(B) for a condition prohibited by Technical Specifications (TS), since one (1) of the SVs removed and tested exceeded its allowable TS setpoint tolerance of+/- 36 psi(+/- 3%). The setpoint for the one (1) SV was found out-of- tolerance after removal from operation. The safety limit was not exceeded. The applicable transient analysis was bounded by previous analysis results and, therefore, the safety limit would not have been exceeded. Equipment Description There are a total of nine (9) SVs installed to prevent failure of the Reactor Pressure Vessel (RPV) on an over pressurization event (Code-required - refer to ASME B&PV Code). Each valve is designed to limit RPV pressure to 1375 psig (110%) with a Main Steam Isolation Valve closure while operating at 1930 MWt, under the conditions where the: ' • Drywell Recirculation Pumps fail to trip • Turbine Bypass valves fail to open • Isolation Condensers fail to initiate • Electromatic Relief Valves fail to open These conditions assume a reactor SCRAM on High Flux where all nine (9) SVs are required to turn the pressure transient. The ASME B&PV Code allows an as-found +/- 3% of setpoint pressure variation in the lift point of the valves. Four (4) out of nine (9) SVs have a setpoint of 1212 psig, and the remaining five (5) out of nine (9) valves have a setpoint of 1221 psig. Analysis of Event | ML16327A064
PAGE | Unknown Unit | Spent Fuel Storage Design Feature Exceeded | 11-18-2016 | On May 12, 2016, at 16:47 EDT, an assessment of Boron Areal Density Gauge for Evaluating Racks (BADGER) testing results for spent fuel storage racks revealed a single panel, RR35 South with a gap in neutron absorber material that exceeds spent fuel storage design feature assumptions. The assumptions ensure compliance with Technical Specification (TS) Section 4.3.1.1.b to maintain a spent fuel pool K-effective (Keff) of less than or equal to(</=) 0.95. An extent of condition review indicates additional at-risk rack locations that may further challenge compliance with TS 4.3.1.1.b. The cause of the noncompliance with TS 4.3.1.1.b is Boraflex degradation greater than assumed in the criticality safety analysis. Interim actions include declaring the spent fuel pool rack cells adjacent to the panel RR35 South inoperable, installing blade guides into cells adjacent to panel RR35S, and prohibiting fuel movement in Boraflex racks. An additional corrective action was taken to perform a criticality evaluation of the spent fuel pool (SPF). This LER supplement is issued to identify that an additional criticality evaluation has been performed to conservatively identify fuel storage configurations within the Boraflex fuel storage racks that will ensure the Boraflex racks Keff will be able to be maintained </= 0.95. Fuel movement will be required to establish these configurations. NRC FORM 366A (11-2015) p aQe 2 0 f 6 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMS: NO. 3150-0104 EXPIRES: (11-2015) . 1 0/31/2018 ~rl4a.,~,,, . Estimated burden per response to comply with this mandatory collection request: 80 !~. .~ hours. Reported lessons learned are incorporated into the licensing process and fed back ~. ...... ~i LICENSEE EVENT REPORT (LER) to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, CONTINUATION SHEET Washington, DC 20555-0001, or by internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If am eans used to impose an information collection does not display ac urrently valid OMB control number, the NRC may not conduct or '" . .. 1. FACILITYNAME 2. DOCKET 3. LERNUMBER YEAR SEQUENTIAL REVISION NUMBER NUMBER Pilgrim Nuclear Power Station 05000293 2016 003 02 | BACKGROUND: Boraflex degradation is a known industry issue that has warranted monitoring and evaluation to ensure the margin to criticality is maintained in the Spent Fuel Pool (SFP). The Boraflex Monitoring Program is described in Final Safety Analysis Report Appendix S, License Renewal Commitments, as a program that assures degradation of the Boraflex panels in the spent fuel racks does not compromise the criticality analysis in support of the design of the spent fuel storage racks. The program relies on (1) neutron attenuation testing, (2) determination of boron loss through correlation of silica levels in SFP water samples and periodic areal density measurements, and (3) analysis of criticality to assure that the required 5% subcriticality margin is maintained. RACKLIFE is a commercial software program, based on the degradation mechanism of Boraflex, developed to calculate the average Boron loss of a Boraflex panel and to predict the future Boron loss of Boraflex. Boron Areal Density Gauge for Evaluating Racks (BADGER) is a commercial in-situ nondestructive diagnostic tool for measuring the areal density of Boron and the gaps in a neutron absorber as installed in fuel racks. BADGER testing measures the neutron transmission rate through SFP Boraflex panels by placing a neutron source and "- neutron detectors on opposite sides of a panel. Measured neutron transmission is related to Boron areal density and allows for measurement of gaps in the neutron absorber. Overall, RACKLIFE and BADGER approach the loss of Boron areal density from Boraflex from opposite sides. RACKLIFE calculates the percent of Boron that is lost while BADGER measures the areal density of Boron that remains. To quantify the loss of Boron in spent fuel pool racks, the RACKLIFE and BADGER methods are combined. The average number of neutrons that cause new fission events is called the effective neutron multiplication factor, denoted by Kettective (Kett). When Kett is equal to 1, the assembly is called critical, if Kett is less than 1 the assembly is said to be subcritical, and if Kett is greater than 1 the assembly is called supercritical. TS 4.3.1.1.a design criteria for acceptable storage of fuel in the spent fuel storage racks are: 1) Fuel must have lattice-average enrichment of 4.6% or less and 2) The Kintinity which is a conservative credit of maximum reactivity exposures for fuel burnup in the standard core geometry, calculated at the burn up of maximum bundle reactivity, must be 1.32 or less. TS 4.3.1.1.b design requirements for spent fuel pool storage provides for a kett less than or equal to (</=) 0.95. This satisfies the Nuclear Regulatory Commission's (NRC) criteria for fuel storage racks. With Kett</= 0.95 there is an assurance that there can be no sustained fission reaction between fuel assemblies stored in the spent fuel pool, and they therefore remain substantially subcritical. The design of the fuel storage racks assumes that the neutron absorbing material is consistent with gaps size and areal density losses assumed in the criticality safety analysis. Prior to 2016 in-situ examinations of Boraflex material in the PNPS spent fuel racks confirmed expected gap size and areal density loss assumptions. EVENT DESCIPTION: During a BADGER test campaign conducted in the spent fuel pool from March 28, 2016 to April 5, 2016, a 38 inch cumulative gap was found in panel RR35 South that exceeded the maximum analyzed gap size of 10 p aae 3 0 f 6 | ML16333A006
Hope Creek Generating Station 05000354 1 OF4 | Unknown Unit | High Pressure Coolant Injection System Inoperable | 03-00-2016 | On August 6, 2016, at 21 :34, with the Hope Creek reactor operating at 100% power, the High Pressure Coolant Injection (HPCI) system turbine governor valve did not respond as expected during system surveillance testing. The system was declared inoperable and an 8-hour immediate notification was made under 10 CFR 50.72 (B)(3)(v)( d). Subsequent investigation found that HPCI turbine governor was not functioning due to corrosion products in the governor, preventing movement of the pilot valve. Additional research determined that the turbine governor did not respond properly on July 3, 2016 during the collection of an oil sample. Based on this, the HPCI system was inoperable for a period of 39 days from July 3, 2016, until August 11, 2016, when repairs to the governor were completed. The HPCI system Technical Specification has an allowed outage time of 14 days. This report is being submitted under 10 CFR 50.73(a)(2)(i)(B), as a condition which is prohibited by the plant's Technical Specifications, and under 10 CFR 50. 73(a)(2)(v)(D), as an event or condition that could have prevented the fulfillment of a safety function of systems that are needed to mitigate the consequences of an accident. The cause of the event is the accumulation of corrosion products in the HPCI turbine governor due to excessive moisture content in the HPCI system control oil. NRC FORM 366 (02-2014) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 01131/2017 (02-2014) Eslimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are Incorporated into the licensing process and fed back to Industry. Send comments regarding burden eslimate to the FOIA, Privacy and LICENSEE EVENT REPORT (LER) Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to lnfocollects.Resource@nrc.gov, and to CONTINUATION SHEET the Desk Officer, Office of Information and Regulatory Affairs, NEOB-1 0202, (3150-01 04), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 6. LER NUMBER 3. PAGE YEAR SEQUENTIAL REVISION Hope Creek Generating Station 05000354 I NUMBER I NUMBER 2 OF4 2016 • 002 . 001 | PLANT AND SYSTEM IDENTIFICATION General Electric- Boiling Water Reactor (BWR/4) High Pressure Coolant Injection System-EllS Identifier {BJ/65}* *Energy Industry Identification System {EllS} codes and component function identifier codes appear as {SS/CCC} IDENTIFICATION OF OCCURRENCE Event Date: 08/06/2016 Discovery Date: 08/06/2016 CONDITIONS PRIOR TO OCCURRENCE Hope Creek was in Operational Condition 1 at 100 percent rated thermal power (RTP). HPCI System {BJ} surveillance testing was in progress. DESCRIPTION OF OCCURRRENCE On August 6, 2016 at 21 :34, Hope Creek operators were performing a HPCI system valve actuation functional test. During the test, system valves are verified to reposition to their intended position in response to a HPCI manual initiation signal. The HPCI turbine governor valve FV-4879, did not reposition to the open position as expected, and remained in the full closed position. Operators reviewed the event and subsequently declared the HPCI system inoperable. Troubleshooting and investigation determined that the HPCI EG-R (Electronic Governor Remote) was not operating properly. The EG-R is a hydro-electrical device that is mounted on the turbine and receives a low pressure oil supply from the turbine oil system. The EG-R ports oil to the remote servo which moves its output shaft accordingly to move a turbine mounted relay valve to control the flow of steam to the turbine. The EG-R was found to contain corrosion products that prevented proper movement of the EG-R internals. This resulted in the turbine governor valve, FV-4879 remaining in the closed position, and would have prevented HPCI system operation. The HPCI system ensures that the reactor core is not uncovered if there is a small break in the reactor coolant pressure boundary (RCPB) that does not result in rapid depressurization of the reactor vessel. CAUSE OF EVENT The cause of the event is that corrosion products were present in the EG-R. The corrosion products were created due to high moisture content in the turbine control oil. The moisture was most likely introduced into the bearing oil via a path from the turbine shaft seals and into the bearing oil at the shaft bearings. Leak-by of the turbine steam admission valve FDHV-F001, allowed a small, continuous supply of steam to leak into the turbine casing and subsequently, to leak out through the turbine shaft seals. Insulation installed around the turbine casing also contributed by trapping steam in the area around the turbine bearings, increasing the rate of moisture intrusion into the oil. A cause evaluation determined that organizational weaknesses existed in the station process for adverse condition monitoring. The monitoring plan that was developed to prevent and detect moisture intrusion did not adequately establish single point ownership for sampling, or a process to implement the sampling, such as a work order or temporary activity log. In addition, management controls were determined to be insufficient to detect the failure to monitor the adverse condition. Management reviews of data collection were not performed due to overreliance on the monitoring plan to be properly implemented. | ML16335A343
Duane Arnold Energy Center 05000-331 1 OF 4 | Unknown Unit | Unplanned RCIC lnoperability Results in Safety System Functional Failure | 12-06-2016 | On April 28, 2016, at 1055, while operating at 100% power, with no structures, systems, or components inoperable that contributed to this event, during the performance of Surveillance Test Procedure (STP) 3.3.6.1-28, Reactor Core Isolation Cooling (RCIC) System Steam Line Flow- High Channel Functional Test, the RCIC turbine received an unplanned trip signal and subsequent turbine stop valve closure. The cause of the event was a human performance error associated with verifying the correct installation location of the relay block. The turbine trip resulted in the unplanned inoperability of RCIC, therefore, this condition meets the reporting requirements of 10CFR50.73(a)(2)(v)(D). At 1353 on April 28, 2016, the RCIC turbine was reset and RCIC was declared available. The safety significance of this event was low since all Emergency Core Cooling Systems were operable during the time the RCIC turbine was tripped. NRG FORM 366 (02-2014) NRC FORM 36GA U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 01/31/2017 (02-2014) .. ~~1'.AtO(t'"\ Estimated burden per response to comply with this mandatory collection request: 80 hours . Reported lessons learned are incorporated into the licensing process and fed back to industry. s~ II Send comments regarding burden estimate to the FOIA, Privacy and lnfomnation Collections • EII:: Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by ~. ...... ~" LICENSEE EVENT REPORT (LER) internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office cif Management and Budget, CONTINUATION SHEET Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 6. LER NUMBER 3. PAGE I YEAR I SE N Q U U M E B N E T R IA L R N E O V . Duane Arnold Energy Center 05000-331 2 OF 4 2016 002 00 | I. Description of Event: On April 28, 2016, at 0848, while operating at 100% power, with no structures, systems, or components inoperable that contributed to this event, Surveill.ance Test Procedure (STP) 3.3.6.1-28, Reactor Core Isolation Cooling (RCIC) System (System Code BN) Steam Line Flow - High Channel Functional Test was started as part of planned testing. The purpose of STP 3.3.6.1-28 is to demonstrate operability of the Steam Line High Differential Pressure (flow) isolation instruments (PDIS-2441 and PDIS-2442) of the RCIC system. During the performance of the STP, relay blocks are installed to inhibit the RCIC turbine trip associated with the RCIC automatic isolation logic under test. Step 7.3.2, which functional checks PDIS-2442, required the installation of three relay blocks, two associated with the inboard isolation signals and one associated with the turbine trip. During the performance of subsequent steps, the RCIC turbine received an unexpected trip signal and M0-2405, RCIC Trip Throttle Valve closed and Control Room annunciator 1 C04C (A- 5) RCIC M0-2045 Turbine Trip actuated at 1055. Therefore, at 1055 on April 28, 2016, unplanned Limiting Condition for Operability (LCO), LCO 3.5.3 Condition A, RCIC System Inoperable, was entered. Investigations determined that the relay block for the PDIS-2442 turbine trip signal was placed on the contacts for PDIS-2441. At 1353 on April 28, 2016, the RCIC turbine was reset and RCIC was declared available and LCO 3.5.3 was exited. II. Assessment of Safety Consequences: The safety significance of this event was low. During the time that RCIC was unavailable, all of the Emergency Core Cooling Systems (High Pressure Coolant Injection, Core Spray, and Low Pressure Coolant Injection) that would have initiated in response to an accident or transient were operable. All components and systems actuated as designed due to this event. This event resulted in a Safety System Functional Failure and a Maintenance Preventable Functional Failure under the Maintenance Rule. Ill. Cause of Event: An Apparent Cause Evaluation (ACE) was completed for this event. The ACE determined that the direct cause of the RCIC turbine trip was the incorrect installation of relay block associated with inhibiting the RCIC turbine trip associated with the RCIC automatic isolation logic under test. NRG FORM 366A (02-2014) | ML16342C568
Cooper Nuclear Station 05000298 1of4 | Unknown Unit | Closure of Multiple Main Steam Isolation Valves due to High Flow Signal | 11-22-2016 | On September 24, 2016, at 20:40 hours, during reactor cooldown for Refueling Outage 29, Cooper Nuclear Station control room operators closed the inboard Main Steam Isolation Valves (MSIV) to minimize steam flow to control the reactor cooldown rate. Reactor pressure was controlled using the Main Steam Line Drains; and the condensate/feed system was available for reactor water level control. On September 25, 2016, at 01 :03 hours, while equalizing pressure across the MSIVs to below 200 psid, a differential pressure of 190 psid was established. Upon opening MS-AO-BOA, a Group 1 isolation was immediately received due to a Main Steam Line high flow signal. The control room operators subsequently equalized pressure and successfully opened MS-AO-BOA, as well as the remaining MSIVs, at 1B :52 hours. The cause of the event was insufficient procedure guidance exists regarding limitations on opening the MS IVs. To correct this, the applicable procedure has been revised to change the differential pressure limitations for opening MSIVs from 200 psid to BO psid. The safety significance of the event is low and did not pose a threat to the health and safety of the public. NRC FORM 366 (06-2016) Page 2 of4 NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. ............ ~ Reported lessons learned are incorporated into the licensing process and fed back to industry. Send f~<ff~ LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch \~!.) (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to (See Page 2 for required number of digits/characters for each block) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150..0104), Office of Management and Budget, Washington, DC 20503. If a (See NUREG-1022, R 3 for instruction and guidance for completing this form means used to impose an information collection does not display a currently valid OMB control http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Cooper Nuclear Station 05000- 298 2016 -004 -00 | PLANT STATUS Cooper Nuclear Station was in Mode 3, Hot Shutdown, at approximately 330 psig, at the time the condition was identified. BACKGROUND The Main Steam system conducts steam from the reactor vessel, via four steam lines, through the Primary Containment to the Main Steam Turbine. Each steam line has two, normally open, Main Steam Isolation Valves (MSIVs) [EllS:ISV], one inside and one outside the Primary Containment. The MSIVs close automatically upon receipt of certain isolation signals to prevent damage to the fuel cladding by limiting the loss of reactor water during a steam line break outside Primary Containment and also to limit ~-· the release of radioactive materials in case of a major leak from Primary Containment. ,. Main Steam Line (MSL) Flow-High is provided to detect a break of the MSL and to initiate closure of the MS IVs. If the steam were allowed to continue flowing out of the break, the reactor would depressurize and the core could uncover. If the Reactor Pressure Vessel (RPV) water level decreases too far, fuel damage could occur. Therefore, the isolation is initiated on high flow to prevent or minimize core damage. The MSL high flow trip setting was selected high enough to permit the isolation of one MSL for test at rated power without causing an automatic isolation of the rest of the steam lines yet low enough to permit early detection of a steam line break. The MSL flow signals are initiated from 16 differential pressure switches [EllS:PDIS] that are connected to the four MSLs. The differential pressure switches are arranged such that, even though physically separated from each other, all four connected to one MSL would be able to detect the high flow. EVENT DESCRIPTION On September 24, 2016, at 20:40 hours, during reactor cooldown for Refueling Outage 29, Operations closed the inboard MSIVs to minimize steam flow to control the reactor cooldown rate in accordance with the Normal Shutdown procedure. Reactor pressure was controlled using the main steam line drains. The condensate/feed system was available for reactor water level control. On September 25, 2016, at 01 :03 hours, when Operations utilized the Main Steam procedure to equalize pressure across the MSIVs to below 200 psid, a differential pressure (DP) of approximately 190 psid was established. When MS-AO-BOA was opened, a Group 1 Isolation was immediately received. All open MSIVs, as well as the MSL Drain Isolation Valves MS-M0-74 and MS-M0-77, closed. The Group 1 isolation was caused by a MSL high flow signal on MSL 'A' as the valve was opening. This was a valid signal based on a review of the steam flow indication for MSL 'A'. Upon investigation it was discovered that the Differential Pressure Indicating Switches (DPIS) for the MSL 'A' high flow signal have a setpoint of 105.B psid, with a calibration tolerance of+/- 3 psid. The DPIS' measure DP created by flow through the flow element upstream of the MSIV. Therefore, with static DP across the closed MS IVs, at approximately 190 psid prior to opening MS-AO-BOA, it was possible that the DPIS' would exceed their setpoint as the MSIV opened and the DP was transferred to NRC FORM 366 (06-2016) Page 3of4 NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BYOMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) ...,....,..._ Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send \p. , ' LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch ..... ) (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to (See Page 2 for required number of digits/characters for each block) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a (See NUREG-1022, R 3 for instruction and guidance for completing this form means used to impose an information collection does not display a currently valid OMB control http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Cooper Nuclear Station 05000- 298 2016 -004 -00 NARRATIVE the flow element in MSL 'A'. To ensure another Group 1 isolation would not occur, the MSIV DP would have to be below the lowest possible setpoint of the DPIS' (approximately 100 psid). In order to provide margin below the setpoint for the Group 1 isolation, Operations determined that the DP across the MS IVs would be reduced to 75 psid prior to opening the MS IVs. To increase the reactor cooldown rate and lower RPV pressure, Operations began to blow down using Reactor Water Cleanup to Radwaste. Reactor cooldown was also increased by starting Reactor Core Isolation Cooling in pressure control mode. Operations isolated the steam supply to gland steam, High Pressure (HP) turbine cylinder heating, and the Reactor Feed Pump Turbine HP stop valve above the seat drains, bringing the main steam equalizing header pressure up to approximately 118 psig, and the DP across the MSIVs down·to approximately 65 psid. At 18:52 hours, MS-A0-80A was successfully opened and the remaining MSIVs were subsequently opened. BASIS FOR REPORT This condition is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a~(2)(iv)(B) of this section, except when ...... (1) the actuation resulted from and was part of a pre-planned sequence during :,I' ·~· testing or reactor operation; or (2) the actuation was invalid and the system properly removed·from service or with the safety function already completed. SAFETY SIGNIFICANCE The occurrence of the Group 1 isolation signal did not compromise safety systems required to mitigate the consequences of an accident or transient. At fhe time of the event, the reactor vessel was at approximately 330 psig with all control rods previously inserted as part of the shutdown process. All high pressure and low pressure emergency core cooling systems were operable. The isolation signal was a main steam line high flow, however, no steam leak or break was observed. The plant response to the isolation was as expected. The safety significance of the event is low and did not pose a threat to the health and safety of the public. CAUSE The apparent cause was insufficient procedure guidance exists regarding limitations on opening the MS IVs. CORRECTIVE ACTIONS The applicable procedure has been revised to change the DP limitation for opening an MSIV from 200 psid to 80 psid. NRC FORM 366 (06-2016) Page 4of 4 NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-201. . 5 , , ) , . ...... Estimated burden per response to comply with this mandatory collection request: 80 hours. , Reported lessons learned are incorporated into the licensing process and fed back to industry. Send {~"} LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch .;~/,;- (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to .•••••• ,,. (See Page 2 for required number of digits/characters for each block) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a (See NUREG-1022, R 3 for instruction and guidance for completing this form means used to impose an information collection does not display a currently valid OMB control http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Cooper Nuclear Station 05000- 298 2016 -004 -00 NARRATIVE PREVIOUS EVENTS There have been no automatic or manual system actuations in the past three years. NRC FORM 366 (06-2016) | ML16342C572
Brunswick Steam Electric Plant (BSEP) | Unit 1 | Drywell High Range Radiation Monitors Inoperable due to Thermally Induced Current Phenomenon | 00-05-2016 | On October 3, 2016, Units 1 and 2 were in Mode 1 (i.e., Run mode) at 100 percent of rated thermal power. At that time, Engineering personnel were reviewing the plant response to NRC Information Notice 97-45, Supplement 1, on signal cables for the Drywell High Range Radiation Monitors (DWHRRMs). These cables are susceptible to thermally induced current (TIC), which can degrade the accuracy of DWHRRMs. The review resulted in DWHRRMs being declared inoperable on both units. The DWHRRMs were included in Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.3.3.1 beginning in 1984. As a result of the TIC effect on the DWHRRM cables, BSEP Unit 1 and Unit 2 have operated longer than the TS allowed completion times for inoperable DWHRRMs. This event is reportable per 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant TSs. The event resulted from the inherent characteristics of the cables and DWHRRMs. An existing site procedure directs the use of alternate indications for assessment of drywell or fuel cladding conditions, and this procedure will remain in place as a compensatory action. Corrective actions will include replacing the cables on a schedule to be developed after assessment of available options. NRG FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and lnfonmation Collections Branch (T-5 LICENSEE EVENT REPORT {LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of lnfonmation and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an infonmation collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www. n re. gov/readinq-rm/doc-col lections/nu regs/staff/sr1 022/r3/J collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant (BSEP) YEAR NUMBER NO. 05000-325 Unit 1 2016 - 005 000 | Energy Industry Identification System (EllS) codes are identified in the text as [XX]. Background Initial Conditions On October 3, 2016, Unit 1 and Unit 2 were both in Mode 1 (i.e., Run mode) at 100 percent of rated thermal power. No out-of-service equipment contributed to, or affected the course of, this event. Reportability Criteria This event is being reported in accordance with 10 CFR 50. 73(a)(2)(i)(B) because Units 1 and 2 were operated in a condition prohibited by the Technical Specifications (TS). Specifically, both units' Drywell High Range Radiation Monitors (DWHRRMs) [IP] were declared inoperable due to signal cables which can degrade the accuracy of the DWHRRMs. With the DWHRRMs inoperable, a Special Report should have been submitted to the NRC within 14 days per TS 3.3.3.1, Condition F. The requirement to submit a Special Report has been in effect since 1984 following issuance of License Amendments 73 and 99 for Units 1 and 2, respectively. The Special Report was not submitted because the DWHRRMs were not previously recognized as inoperable. Therefore, the plant was operated in a condition prohibited by the TS. In accordance with 1O CFR 50.4(e), this event is being reported by LER only, and a Special Report is not required. Event Description On October 3, 2016, Engineering personnel were re-assessing signal cables for the DWHRRMs. These cables are susceptible to a phenomenon known as thermally induced current (TIC). During transient conditions, TIC can result in connected radiation monitors temporarily not meeting the accuracy requirements of Regulatory Guide (RG) 1.97, Revision 2, "Instrumentation for Light-Water-Cooled Nuclear Power Plants to Assess Plant and Environs Conditions During and Following an Accident." Per RG 1.97, Table 1, note 7, DWHRRMs must be accurate to within a factor of 2. The cables installed in both units at BSEP were previously assumed to be bounded by analysis of Rockbestos cables addressed in Electric Power Research Institute (EPRI) Technical Report 110379, "High Range Radiation Monitor Cable Study: Phase 1." It was assumed that the materials in use at BSEP have essentially the same dielectric properties and thermal response as those tested by EPRI. Based on the reported behavior of those materials, calculations predicted that TIC-induced inaccuracy in the DWHRRMs at BSEP would not result in significant impact. Re-assessment of the previous analysis at BSEP cast doubt on the earlier conclusion. The BSEP cables use an insulation material that was not tested by EPRI, and no rigorous basis supported the assumption that the dielectric properties and thermal response would be the same. Engineering personnel, therefore, determined that the previous conclusion about the acceptability of cables used at BSEP lacked sufficiently rigorous justification. This was reported to Operations personnel via Condition Report 2066681. Both BSEP Unit and Unit 2 DWHRRMs were conservatively declared inoperable. NRG FORM 366A (06-2016) Page _2_ of _4_ | ML16349A616
Monticello Nuclear Generating Plant 05000-263 1 OF 4 | Unknown Unit | Inadequate Appendix R Fire Barrier Impacts Safe Shutdown Capability | 12-19-2016 | On August 4, 2016, while performing a Fire Protection/Appendix R self-assessment, it was discovered that the floor between the Cable Spreading Room (CSR) and the Plant Administration Building (PAB) basement is not an adequate Appendix R fire barrier. Because the CSR and the PAB are located in the same Fire Area (FA), a fire in the PAB could spread to the CSR requiring evacuation of the control room (CR). When the CR is evacuated, alternate shutdown activities are performed at the Alternate Shutdown System (ASDS) Panel. The travel path used to access the ASDS Panel following control room evacuation traverses the same fire area in the PAB. This unanalyzed condition resulted from the determination that because of the inadequate fire barrier, a fire in the PAB would now require use of an alternate shutdown strategy to safely shutdown the reactor. However, the alternate shutdown strategy requires that the operators traverse from the control room through the PAB Fire Area to access the alternate shutdown equipment. This path could be impacted by the PAB fire. In response to this discovery an hourly fire watch was established. NRC FORM 366 (11-2015) Page 1 of 4 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Monticello Nuclear Generating Plant NUMBER NO. 05000-263 2016 - 002 - 01 | UNIT CONDITION PRIOR TO THE EVENT On August 4, 2016, Monticello Nuclear Generating Plant (MNGP) was at 100% power, Mode 1. EVENT DESCRIPTION On August 4, 2016, while performing a Fire Protection/Appendix R self-assessment, it was discovered that the floor between the Cable Spreading Room (CSR) and the Plant Administration Building (PAB) basement is not a credited Appendix R fire barrier. Fire Area (FA) VI encompasses the MNGP CSR (above) and portions of the PAB basement that house the Division I batteries (below the CSR). Specifically it was discovered that the CSR floor was not an adequate fire barrier, because the structural steel supporting the CSR floor did not have a 3-hour fire rating as required by 10 CFR 50, Appendix R, section III.G.2. Since the CSR and the PAB are located in the same fire area without a compliant fire barrier, a fire in the PAB could spread to the CSR. By procedure, a fire in the CSR requires evacuation of the Control Room (CR). The MNGP CR is a separate fire area within the PAB. Upon evacuation of the CR, plant procedures direct the operator to perform shutdown of the reactor using Division II equipment on the Alternate Shutdown System (ASDS) Panel, located in the Emergency Filtration Train (EFT) building. The credited travel path used to access the ASDS Panel following CR evacuation traverses FA VI in the PAB. This is an unanalyzed condition, because of the inadequate fire barrier and its effect on safe shutdown capability. With the inadequate fire barrier, a fire in the PAB would now require use of an alternate shutdown strategy to safely shutdown the reactor. However, the alternate shutdown strategy requires that the operators traverse from the control room through the PAB Fire Area to access the alternate shutdown equipment. This path could be impacted by the PAB fire. In 1982, the Northern States Power (previous licensee for MNGP) (NSP) provided a Safe Shutdown analysis that assumed a modification would be performed to remove Division II equipment from the CSR so that the CSR could be classified as a Division I area along with the rest of FA VI. In addition NSPM requested an exemption from the requirements of 10 CFR 50, Appendix R, Section III.G.2 for structural steel fireproofing, including the structural steel in FA VI. In 1983 the NRC denied the requested exemption for the structural steel in FA VI. After the NRC denial of the exemption, NSP agreed to provide alternate shutdown capability in the CSR in lieu of protecting the structural steel. It has now been determined that neither alternate shutdown capability nor structural steel fireproofing has been implemented in FA VI. EVENT ANALYSIS The condition is reportable to the NRC in accordance with 10 CFR 50.73(a)(2)(ii)(B) for placing the plant in an unanalyzed condition that significantly degrades plant safety. The condition was reported to the NRC on August 4, 2016, in event notification 52154 in accordance with 10 CFR 50.72(b)(3)(ii)(B). Page 2 of 4 | ML16354A653
Fermi 2 05000 341 1 OF 6 | Unknown Unit | Emergency Diesel Generator Inoperable Due to Open Circuit on Loss of Power Instrumentation | 12-20-2016 | At 1644 EDT on April 24, 2016, while operating at 100 percent Reactor Thermal Power, the potential transformer (PT) primary fuses on Bus 64C were found blown, resulting in half of the Loss of Power (LOP) instrumentation relays tripping on Bus 64C. Initially, the LOP instrumentation was incorrectly considered OPERABLE; however, later reviews of the condition determined that the LOP instrumentation was inoperable. Later reviews also concluded that the Division 1 Alternating Current (AC) Source was inoperable from 1644 to 1920 on April 24, 2016, and the Division 1 Emergency Diesel Generator (EDG) 12 was inoperable starting at 1644 on April 24, 2016, until it was restored at 1818 on May 8, 2016, during a Forced Outage following replacement of the blown PT fuses. On six occasions from April 26-30, 2016, Division 2 EDGs 13 and/or 14 were inoperable for planned surveillances. Therefore, this is an event or condition that could have prevented the fulfillment of a safety function to remove residual heat and mitigate the consequences of an accident. Furthermore, failure to enter applicable Limiting Conditions for Operation resulted in a condition prohibited by Technical Specifications. The cause of the event was concluded to be a low energy transient event resulting in the blown PT primary fuses. The incorrect initial operability determination was caused by Operators being unfamiliar with this equipment condition. Operators completed a Department Event Free Day Reset and Event Review and will receive additional training on this condition. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10131/2018 (00-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy andI nformation Collections Branch (T-5 CONTINUATION SHEET F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management andB udget, Washington, DC2 0503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose ani nformation collection does not display a currently valid OMB control number, the http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV ~Fermi 2 0 0 5 5 0 0 0 -3 0- 4 1 2016 NU 0 MB 9 E R N 0 O. --01 009 -- 00 | INITIAL PLANT CONDITIONS Mode-1 Reactor Power - 100 percent There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT At 1644 EDT on April 24, 2016, while operating in Mode 1 at 100 percent Reactor Thermal Power, Operators received alarm 9D8, Transformer [[XFMR]] 64 (SS64) Trouble. An initial investigation revealed that the Potential Transformer (PT) [[XPT]] for Buses [[BU]] 64A and 64C was not providing an output voltage signal to the relaying and instrumentation downstream of the PTs. Half of the loss of voltage (LOV) relays [[27]] and half of the degraded voltage relays (DVRs) for the 4.16 kiloVolt (kV) Emergency Bus 64C undervoltage were tripped while the other half of both of those relays were not tripped. Therefore, the LOP instrumentation trip logic was in a half-tripped state. The LOV relays and DVRs together constitute the Technical Specification (TS) 3.3.8.1 Loss of Power (LOP) instrumentation to detect and respond to a loss of offsite power (LOOP) event. Licensed Operators initially incorrectly considered SS64 OPERABLE based on the proper voltage being maintained on Engineered Safety Feature (ESF) Buses 64B and 64C. Initially, the Division 1 Bus 64C LOP instrumentation was also incorrectly considered OPERABLE by Licensed Operators because the relays failed in their fail safe condition and the logic was capable of performing the safety function. The failure resulted in the LOP instrumentation going from a one out of two, taken twice, logic to a one out of two logic, which would have properly detected and responded to a loss of offsite power or degraded voltage event. At 1920 EDT on April 24, 2016, Operators restored the SS64 output voltage to above 121.3 meter Volts (V) by manual operation of the Load Tap Changer (LTC) [[TTC]] as required by System Operating Procedure 23.320, "Balance of Plant Auxiliary Electrical Distribution System" (Revision 63). Restoration of the voltage to 121.3 meter V ensured that adequate voltage was available to reset the LOV relays and DVRs during a LOCA coincident with a degraded grid. Division 2 offsite power and Combustion Turbine Generator (CTG) [[88]] 11-1 were OPERABLE at all times during the event. Although the equipment was initially determined to be OPERABLE, repairs were still required. Fermi 2 entered Mode 3 at 2301 EDT on May 3, 2016, and subsequently, entered Mode 4 at 1525 EDT on May 4, 2016, for Forced Outage (FO) 16-01 to trouble-shoot and repair the LOP instrumentation. Subsequent analysis of this event by Engineering determined that: A. Starting at 1644 on April 24, 2016, with the LTC automatic function disabled and voltage below 121.3 meter V, per Design Calculation (DC) 6447 Volume I, "Auxiliary Power System Analysis," (Revision C) the DVRs may not have reset upon a Loss of Coolant Accident (LOCA) auto-start of ESF equipment in order to stay connected to the preferred offsite power source. Manual operation of the SS64 LTC by Operations boosted the output voltage of SS64 and ensured adequate voltage to reset the DVRs at 1920 on April 24, 2016. | ML16356A148
Fermi 2 05000 341 1 OF 5 | Unknown Unit | Standby Liquid Control Inoperable due to Sodium Pentaborate Concentration Outside of Technical Specifications | 12-20-2016 | On October 28, 2016, at 1500 EDT, Fermi 2 Operators declared both subsystems of Standby Liquid Control (SLC) inoperable due to the sodium pentaborate concentration in the SLC storage tank being outside of the Technical Specification (TS) requirements. The sodium pentaborate concentration had been measured in response to the receipt of the SLC storage tank high level alarm. The demineralized water isolation valves that could cause a dilution of the tank were verified to be closed. Actions were initiated to add sodium pentaborate to the SLC storage tank to raise the concentration. SLC was declared operable at 1935 EDT following a measurement that verified that sodium pentaborate concentration had been restored to within the TS requirements. The cause of the event was determined to be leak-by of the demineralized water isolation valves that had caused an increase in SLC storage tank level and, therefore, a decrease in sodium pentaborate concentration. The leak-by had been occurring for some time and had gone undetected. The cause of the leak-by not being detected was determined to be inadequate system monitoring. Corrective actions were completed to replace the demineralized water isolation valves and revise the chemistry specification to clearly specify action levels for the tank level and sodium pentaborate concentration and provide margin to the TS limits. Corrective actions were also completed to revise the SLC system monitoring plan to incorporate trending of tank level and boron concentration. The safety significance of this event is very low and the event did not pose a threat to the health and safety of the public or plant personnel. There were no radiological releases associated with this event. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10312018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send g LICEN C S O E N E T I E N V U E A N T T IO N RE P S O H R EE T T ( LER) c F o 5 m 3) m , e U nt . s S . reg N a u r c d l i e n a g r bu R r e d g e u n l a e to st r i y m a C te o m to m i t s h si e on F , OI W A a P, s r h iv in a g c t y o n a , n d D I n C for 2 m 0 a 5 t 5 io 5 n -0 0 C 0 o 1 ll , e ct o io r n s b y B ra e n -m ch a i ( l T t - o 5 C TH Infocollects.Resource@nrc.gov, and to the Desk Officor, Office of Information andR egulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC2 0503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http://www.nrc.gov/readina-rm/doc-collections/nurecs/staff/srl 022/r3/) NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000- NUMBER NO. Fermi 2 341 2016 - 011 - 00 | INITIAL PLANT CONDITIONS Mode-1 Reactor Power - 100 percent There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT At 1051 EDT on October 28, 2016, while operating in MODE 1 at 100% power, the Fermi 2 Main Control Room (MCR) [[NA]] received an alarm for Standby Liquid Control (SLC) [[BR]] tank [[TK]] level. The MCR and local level indications [[LI]] both were above the high SLC storage tank level alarm [[LA]] setpoint. Operators verified SLC storage tank demineralized water isolation valves [[V]] were closed per the Alarm Response Procedure (ARP). The SLC storage tank was then manually measured to confirm level indication at 1214 EDT. The measured level was below the high SLC storage tank level alarm setpoint. A chemistry sample of the SLC storage tank to determine the sodium pentaborate concentration was requested. In order to ensure a representative sample of the SLC storage tank, sparging of the SLC storage tank was begun at 1340 EDT. In accordance with plant procedures, SLC is considered inoperable during the sparging process and, therefore, Technical Specification (TS) Limiting Condition for Operation (LCO) 3.1.7, "Standby Liquid Control (SLC) System," Condition B was entered for two SLC subsystems inoperable. Required Action B.1 to restore one SLC subsystem has a Completion Time of 8 hours. Sparging was completed at 1404 EDT (i.e. 24 minutes after entering LCO 3.1.7 Condition B) and the SLC system was declared OPERABLE. At 1500 EDT, the results of the chemistry sample of the SLC storage tank were obtained and indicated that the sodium pentaborate concentration was 8.3%. Surveillance Requirement (SR) 3.1.7.5 requires the concentration to be within the limits of Figure 3.1.7-1. For the SLC storage tank level at the time of the event (i.e. near the high level alarm setpoint), the sodium pentaborate concentration was required to be in the range from 8.5% to 9.5% (weight percent). As a result, SLC was declared inoperable at 1500 EDT and LCO 3.1.7 Condition B was entered for two SLC subsystems inoperable. A second sample was taken and the results confirmed the previous value of 8.3%. Actions were initiated to add sodium pentaborate to the SLC storage tank to raise the concentration. Subsequent sparging and sampling determined that the sodium pentaborate concentration had been raised to 8.9%. Due to the sodium pentaborate concentration being restored to within the SR 3.1.7.5 requirements, SLC was declared OPERABLE at 1935 EDT (i.e. approximately 4.5 hours after entering LCO 3.1.7 Condition B) and the LCO was exited. The SLC storage tank level was then manually lowered to clear the level alarm per plant procedures. Local level indications and manual measurements confirmed the SLC storage tank level was below the high level alarm setpoint by 2216 EDT. A subsequent review of the event determined that the SLC storage tank level had been slowly increasing over several months due to introduction of water through one or both demineralized water isolation valves that were closed but leaking by. On October 9, a SLC pump and valve operability test was performed, in accordance with SR 3.1.7.7. Following the successful completion of this test, which involved cycling one of the demineralized water isolation valves, the valve leak-by increased as a more substantial increase in SLC storage tank level occurred. This increased leak-by was not detected by Operators until the occurrence of the high level alarm on October 28 as described above. Since the water leaking by the valves was demineralized, dilution of the sodium pentaborate concentration was occurring throughout this time. The frequency of TS SR 3.1.7.5 to determine the sodium pentaborate concentration is monthly. The most recent | ML16356A280
Fermi 2 05000 341 1 OF 5 | Unknown Unit | Unanalyzed Condition for Control Rod Drop Accident at Low Reactor Power | 12-20-2016 | On November 2, 2016, a non-conservatism in the current Fermi 2 design and licensing basis of the control rod drop accident (CRDA) was identified. The current analysis assumes that the fission products released as a result of a CRDA are transported to the condenser and then released from there. An unanalyzed condition was identified where a forced release from the Gland Seal Exhausters (GSEs) could occur which would exceed dose limits in 10 CFR 100.11 and Standard Review Plan 6.4 when operating at low reactor power conditions. The postulated fuel damage and associated release is only credible for low power conditions of less than 10% power. Fermi 2 was at 97% power at the time of discovery and, therefore, the condition did not exist. However, a review of past operating conditions identified five instances in the past three years where Fermi 2 operated at less than 10% power. Based on a subsequent engineering analysis, for each of those five instances, plant conditions and available equipment were such that dose limits would have been met even if a postulated CRDA had occurred during those times; therefore, there was no adverse impact to public health and safety or to plant employees. There were no radiological releases. The cause of the event was that the original design and licensing basis analysis of the CRDA did not evaluate the direct release of steam from the GSEs, and, therefore, the plant was not designed to mitigate the potential consequences associated with that release path. For corrective actions, the plant startup checklist was revised to impose restrictions on future startups based on the engineering analysis. Fermi 2 plans to pursue modifications which would eliminate this potential release path. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY UMB: NO. 3150-0104 EXPIRES: 10/312018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported " LElessons learned are incorporated into the licensing process and fed back to industry. Send EVENT REPORT (LER) aLICENSEE comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 CONTINUATION SHEET F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, andto the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC2 0503. Ifa means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http://www.nrc.gov/readinc-rm/doc-collections/nuregs/staff/srl 022/r3/) NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000- NUMBER NO. Fermi 2 341 2016 - 012 - 00 | INITIAL PLANT CONDITIONS Mode -1 Reactor Power - 97 percent There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT On November 2, 2016, while performing a re-evaluation of the radiological consequences of the control rod drop accident (CRDA) in support of a potential license amendment, DTE Electric Company (DTE) identified a non-conservatism in the current Fermi 2 design and licensing basis of the CRDA. The non-conservatism was identified at approximately 1030 EDT while operating in MODE 1 at 97% power. The current CRDA analysis, which is based on Standard Review Plan (SRP) 15.4.9, postulates that radioactive fission products are released as a result of the control rod drop and the released activity transports directly to the condenser and is released at ground level from the turbine building at the rate of 1% of the condenser volume per day for one day. Doses reported in the current licensing basis analysis demonstrate offsite radiological consequences are well within (less than 25% of) the Title 10 of the Code of Federal Regulations (CFR) Part 100.11 siting criteria. The current licensing basis was approved without specific evaluation of Main Control Room (MCR) [[NA]] personnel dose. Per Updated Final Safety Analysis Report (UFSAR) Section 6.4, the functional design of the habitability systems ensure compliance with 10 CFR 50 Appendix A General Design Criterion (GDC) 19 and that "[u]nder any design-basis conditions, the environment within the main control room is safe, with personnel protected from radiation, fire, toxic gases, and noxious substances." Sufficient radiation shielding and air filtration are provided to ensure that radiation exposures of MCR personnel do not exceed 5 rem whole-body, or its equivalent to any part of the body, for the duration of a design basis accident (DBA). For the DBA Loss of Coolant Accident (LOCA) and the Fuel Handling Accident, the dose to main control room personnel does not exceed 5 rem total effective dose equivalent (TEDE). The Control Room Emergency Filtration (CREF) [[VI]] system is an Engineered Safety Feature (ESF) designed to limit radiation exposure to personnel occupying the MCR to less than 5 rem over the duration of a DBA as required by 10 CFR 50.67 and 10 CFR 50 Appendix A Criterion 19. This function is accomplished by 1) isolating normal unfiltered intakes, 2) directing emergency makeup air through charcoal and High Efficiency Particulate Air (HEPA) filters [[FLT]], 3) re- circulating control room and makeup air through HEPA and charcoal filters, and 4) maintaining the Control Room Envelope (CRE) under a positive pressure with respect to the outside environs to prevent the in-leakage of unfiltered outside air. CRE integrity is necessary to minimize potential unfiltered in-leakage thereby supporting the operation of the Control Center Heating Ventilating and Air Conditioning (CCHVAC) [[Vl]] and CREF systems in their function to protect the health and safety of control room operators post-accident. As described above, the radiological consequences of the CRDA were re-evaluated to support a potential license amendment. The results of the new analysis, which were obtained in accordance with current regulatory guidance that has been updated from the original NUREG 75/087 Section 15.4.9 Fermi 2 licensing basis, predict onsite and offsite radiological consequences that exceed the current applicable regulatory dose limits in 10 CFR 100.11 and SRP 6.4 (GDC 19). The increase in calculated radiological consequences is attributable to the consideration of a forced release via the | ML16356A289
Watts Bar Nuclear Plant | Unit 1 | Failure of Emergency Raw Cooling Water Pump Reverse Rotation Keys Represents Potential Common Cause lnoperability | 01-09-2017 | 12. LICENSEE CONTACT FOR THIS LER LICENSEE CONTACT TELEPHONE NUMBER (lnclude Area Code) Dean Baker, Licensang Engineer 423-452-4589 13. COMPLETE ONE LINE FOR EACH COMPONENT FAILURE DESCRIBED IN THIS REPORT cAUsE I svsre n,r l coueoNENr Lo.ruRER REP T O O R E T P A I B X LE CAUSE SYSTEM I COMPONENT FA M C A TU N R U E - R I I REP T O O R E T P A I B X LE X I ERCW I CLU IFormsprag Y 14. SUPPLEMENTAL REPORT EXPECTED 15. EXPECTED MONTHI DAY I YEAR X vrS (f yes, comptete 15,EXPECTED SUEM/SS/OA/ DATE) tr NO SUB D M A IS T S E ION 03 03 I 2017 ABSTMCT (Limit to 1 400 spaces, ,. e., approximately 1 5 single-spaced typewritten lines) On November 10, 2016, Watts Bar Nuclear Plant personnel identified a failure of the non-reverse clutch key on Emergency Raw Cooling Water (ERCW) motor B-A. While performing a lubrication work order, it was discovered that the clutch key was sheared. Subsequent investigation identified that other clutch key failures had occurred in the recent past. The non-reverse clutch prevents the ERCW pump from rotating in the reverse direction after pump trip, which could cause the motor to develop a higher than normal in-rush current if the motor was subsequently started, such as following an accident. Based on the potential common mode failure of the non-reverse clutch, immediate corrective actions were put in place to ensure that the safety function of the ERCW pumps to start following an accident would not be impaired. The cause of the failure is under investigation NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY GOMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours, Reported lessons learned are incorporated into the licensing process and fed back to industry, Send 'r{*l'"":o^ commenb regarding burden estimate to the FOIA, Privacy and lnformation Collections Branch (T-5 t\ r .,,rrri : lr ',{xC,"! LIGENSEE EVENT REPORT (LER) F ln 5 fo 3 c ), o l U le , c S ts . .R N e u s c o le u a r r c e R @ e n g r u c la .g to o r v y , C an o d m m to i s th si e o n D , e W sk a s O h f i f n ic g e to r, n O , f D iic C e 2 o 0 f 5 ln 5 f 5 o - r 0 m 0 a 0 t 1 io , n o a r n b d y R in e t g e u rn la e to t ry e -m Af a fa il i rs to , CONTINUATION SHEET NE0B-10202, (3150-0104), Ofiice of Management and Budget, Washington, DC 20503. lf a means '¦}lrlr used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection, {. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Watts Bar Nuclear Plant, Unit 05000390 NUMBER NO. 1 - -00 2017 001 | I. PLANT OPERATING CONDITIONS BEFORE THE EVENT Watts Bar Nuclear Plant (WBN) Units 1 and 2 were at 100 percent rated thermal power (RTP) . II. DESCRIPTION OF EVENT A. Event Summary On November 10, 2016, Watts Bar Nuclear Plant personnel identified a failure of the non-reverse clutch key on Emergency Raw Cooling Water (ERCW) system {EllS:Bl} motor B-A. While performing a lubrication work order, it was discovered that the clutch key was sheared. Subsequent investigation identified that other clutch key failures had occurred in the recent past. The non-reverse clutch {EllS:CLU} prevents the ERCW pump {EllS:P} from rotating in the reverse direction after pump trip, which could cause the motor to develop a higher than normal in-rush current if the motor was subsequently started, such as following an accident. Based on the potential common mode failure of the non-reverse clutch, immediate corrective actions were put in place to ensure that the safety function of the ERCW pumps to start following an accident would not be impaired. The cause of the failure is under investigation. This event is being reported to the Nuclear Regulatory Commission (NRC) under 10 CFR 50.73(a)(2)(vii) as a potential common cause inoperability of independent trains of the ERCW system. B. lnoperable Structures, Components, or Systems that Contributed to the Event No inoperable systems beyond the issue with the ERCW non-reverse clutch contributed to this report. C. Dates and Approximate Times of Occurrences l=lata Frrant 1012111985 Engineering Change Notice (ECN) 5940 issued to make clutch key weaker to avoid damage to the non-reverse assembly and motor shaft. 6/09/1999 C-A ERCW motor anti-rotation clutch and torsion arm had sheared bolts and key (CR 14894). 1111612015 H-B ERCW clutch key found sheared (CR 1104777). Key replaced and pump returned to service on 1112012015 WO 116490727) 1112412015 A-A ERCW clutch key found sheared (CR 1108157). 1211712015 Work Order generated to inspect and replace clutch keys on ERCW motors (CR 11 17187). 211012016 A-A ERCW clutch key found sheared (CR 1135397). Key had not been replaced since initial identification on 1112412015. 512012016 A-A ERCW clutch key replaced WO 117442683) 1111012016 B-A ERCW found with a clutch key cracked and broken (CR 1231774). Key replaced on 11122116. ge | ML17009A286
PAGE | Unknown Unit | Emergency Diesel Generator 'A' Past lnoperability | 12-09-2016 | On September 28, 2016, while performing the pre-start checks prior to running the Emergency Diesel Generator (EDG)-A •or the monthly Technical Specification (TS) surveillance, the oil level in the EDG radiator fan right angle gearbox was found ~o be low and additional checks found the gearbox oil pressure relief valve in a loose state which provided a pathway for gear oil to be pumped out of the gear box while the EDG was operating. EDG-A was declared inoperable, the relief valve was repaired, pressure tested and the pressure adjusting threaded union was staked to eliminate any risk from vibration induced motion in the future, the gearbox oil was replaced and the EDG run for a post-maintenance test. A Functional Failure Determination completed on October 11, 2016 determined that the EOG would not have been able to run for its stated mission time of 30 days. This condition existed for a period of 28 days since the last surveillance test on August 31, 2016 which is greater than the TS Allowed Out of Service Time (AOT) of 72 hours. However, the Station Black Out Diesel Generator was available during this time frame. This issue is reportable under 10 CFR 50. 73(a)(2)(i)(B) as an Operation or Condition which was Prohibited by the plant's TSs. On September 15, 2016 EDG-B was made inoperable to perform its monthly operability run. This created a situation where •or a brief period of time both EDGs were inoperable which is a condition that could have prevented the fulfillment of the safety function of a system needed to shut down the reactor and maintain it in a safe condition, remove residual heat, and mitigate the consequences of an accident which is reportable in accordance with 50. 73(a)(2)(v)(A), 50. 73(a)(2)(v)(B), and 50.73(a)(2)(v)(D). EDG-B remained available and could quickly have been restored by manual action to an operable condition if needed during the operability run. rThere was no impact to public health and safety from this condition. NRC FORM 366 (02-2014) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 01/31/2017 (02-2014) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information LICENSEE EVENT REPORT (LER) Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, CbNTINUATION SHEET Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currenlly valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 6. LERNUMBER 3. PAGE I I YEAR SEQUENTIAL REVISION Pilgrim Nuclear Power Station 05000293 NUMBER NUMBER 2 OF4 2016 -008 -00 BACKGROUND rThe safety objective of the emergency diesel generators (EDGs) is to provide a source of on-site AC power adequate for the safe shutdown of the reactor following abnormal operational transients and postulated accidents assuming a complete loss of off-site power, as described in Pilgrim Nuclear Power Station (PNPS) Updated Final Safety Analysis Report (UFSAR). Two EDGs and their associated fuel supply systems provide a single failure proof source of standby AC power. Pilgrim EDGs are 2600 KW ALCO 251-F type diesel generators. These EDGs are designed to automatically start upon receiving a valid signal, and come to operating speed ready to assume load. Each generator is sufficient to power all loads on its emergency bus upon failure of all off-site power. Each generator has the ability to pick up loads in sequence within a specified time period. The two EDGs at PNPS are cooled by a self-contained system consisting of radiators and a fan that is driven through a right angle gearbox. rThe standby AC power source provides two independent diesel generators as the onsite sources of AC power to ~he emergency service portions of the station Auxiliary Power Distribution System. Each onsite source provides ~C power to safely shut down the reactor, maintain the safe shut down condition, and operate all auxiliaries necessary for station safety. Historical review revealed that this fan drive gearbox was replaced on the EOG-A in the May 2000 time frame. At ~hat time, the original gearbox, Cotta Transmission Model Number J1327-2 was replaced with an upgraded Model Number J1327-3. Correspondence with the OEM vendor indicated the inside of the cases were identical with the only major physical change on the outside which was the addition of a relief valve in the oil circuit. Changes to the gearbox inspections were not updated to include any inspections or preventive maintenance for the relief valve. EVENT DESCRIPTION On September 28, 2016, while performing the pre-start checks prior to running the Emergency Diesel Generator (EDG)-A monthly Technical Specification (TS) surveillance, the oil level in the EOG radiator fan right angle gearbox was found low and additional checks found the gearbox oil pressure relief valve was loose. rThe two EDGs at PNPS are each cooled by self-contained systems consisting of radiators and fans that rotate ~hrough a right angle gearbox. At the time of discovery, even though the oil level was low, the EOG would have started on a valid start signal. However, it would have been losing gearbox oil and we conservatively assumed it would have overheated due to failure of the cooling fan from gearbox damage. ~Functional Failure Determination completed on October 11, 2016 conservatively determined that the EOG would not have been able to run for its stated mission time of 30 days. This condition existed for a period of 28 days, which is greater than the TS Allowed Out of Service Time (AOT) of 72 hours. However, the Station Black Out Diesel Generator was available during this time frame. CAUSE OF THE EVENT rThe failure was determined to be low oil level found in the EOG-A radiator fan right angle gearbox due to the external relief valve pressure setting screw and the cap which goes over it being disconnected from the valve body. This allowed a pathway for oil to escape the gearbox when the EOG was running. NRC FORM 366A (02-2014) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION LICENSEE EVENT REPORT (LER) (02-2014) CONTINUATION SHEET 1. FACILITY NAME 2. DOCKET 6. LER Nll\llBER 3. PAGE I I YEAR SEQUENTIAL REVISION Pilgrim Nuclear Power Station 05000293 NUMBER NUMBER 3 OF4 2016 -008 -00 | The radiator fan right angle gearbox oil level is checked prior to every monthly EOG run and the last time it was performed was August 31, 2016 with no problem identified during the pre-start checks. The last maintenance performed on the EOG radiator fan right angle gearbox was part of the routine examination and checks during the 2 year Preventive Maintenance (PM), which was completed on March 7, 2015. The inspection includes draining and changing the oil, performing internal inspection of the drive gears and bearings and performing backlash measurements of the drive and driven gears. However, the two (2) year PM does not perform any maintenance on ihe gearbox oil pressure relief valve. The relief pressure of 15 psig was set at the time of installation in 2000. Changes to the gearbox inspections were not updated to include any inspections or preventive maintenance for the relief valve. The failure is attributed to minimal engagement of the pressure adjusting threaded union for the relief valve setting of 15 psig, and there is some contribution from either engine vibration or possibly human error which makes the cause indeterminate. CORRECTIVE ACTIONS EOG-A was declared inoperable, the relief valve was repaired, pressure tested and the pressure adjusting threaded union was staked to eliminate any risk from vibration induced motion in the future, the gearbox oil was replaced and •he EOG run for a post-maintenance test. PNPS conducted an extent of condition review for EDG-B by performing an inspection to ensure that a common mode failure did not exist. 1 -, The following are additional corrective actions to address this issue which are being processed through the PNPS Corrective Action Program: 1. Update station procedure 8.9.1, "Emergency Diesel Generator and Associated Emergency Bus Surveillance," to identify the plug that is used to check the oil level and visually inspect the reli~f valve to ensure the cap is appropriately aligned before and after each EOG run. 2. Incorporate a vendor manual change to capture the upgraded EDG's Cotta Transmission gear box. The gear box was updated in the 2000 time frame but the drawings/vendor manual was never updated. 3. Establish PM's for both EOG radiator fan right angle gearbox relief valves. SAFETY CONSEQUENCES There were no consequences to the safety of the general public, nuclear safety, industrial safety, and radiological safety due to this event. The safety objective of the EDGs is to provide a source of on-site AC power adequate for the safe shutdown of the reactor following abnormal operational transients and postulated accidents assuming a complete loss of off-site power, as described in PNPS UFSAR. At the time of the event, the preferred AC and the secondary AC power sources were Operable and available to perform their intended safety function. In addition, the Station Blackout AC Power Source was Functional and available as the onsite source of AC power to the emergency service portions of the Auxiliary Power Distribution System. | ML17010A035
Dresden Nuclear Power Station | Unit 2 | Reactor Building Differential Pressure Less than Technical Specification Requirement | 01-09-2017 | On 11/8/16 at 051 O CST, during Under Voltage surveillance testing Bus 33-1 was secured causing Standby Gas Treatment (SBGT) [BH] to start, and the Reactor Building (RB) Ventilation system [VA] automatically isolated. During the evolution RB pressure relative to outside was less than 0.25 inches water column (in WC) vacuum which is required by Technical Specifications (TSs). TS Limiting Condition for Operation (LCO) 3.6.4.1, "Secondary Containment", Condition A was entered. At 0532 CST, the Unit 2 RB Equipment Access Inner door was closed and RB differential pressure was observed to increase above 0.25 in WC vacuum, and Condition A was exited. TS LCO 3.6.4.1 was not applicable to Unit 3 which was in Mode 5 with no recently irradiated fuel moves or any operations with a potential for draining the reactor vessel (OPDRVs) in progress. This event is reportable under 10 CFR 50.73(a)(2)(v)(C), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material." - NRC FORM 366 (06-2016) Page 2 of 3 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150·0104 EXPIRES: 10/31/2011 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and lnlormation Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV Dresden Nuclear Power Station, Unit 2 05000-237 YEAR NUMBER NO. 2016 - 004 - 00 | PLANT AND SYSTEM IDENTIFICATION Dresden Nuclear Power Station (DNPS), Unit 2, is a General Electric Company Boiling Water Reactor with a licensed maximum power level of 2957 megawatts thermal. The Energy Industry Identification System codes used in the text are identified as [XX]. A. Plant Conditions Prior to Event: Unit: 02 Event Date: 11/08/16 Event Time: 0510 CST Reactor Mode: 1 Mode Name: Power Operation Power Level: 100 percent B. Description of Event: On 11/8/16 at 0510 CST, during Under Voltage surveillance testing Bus 33-1 was secured causing Standby Gas Treatment (SBGT) [BH] to start, and the Reactor Building (RB) Ventilation system [VA] automatically isolated. This plant response was expected, but during the evolution RB pressure relative to outside was less than 0.25 inches water column (in WC) vacuum which is required by Technical Specifications (TSs). TS Limiting Condition for Operation (LCO) 3.6.4.1, "Secondary Containment", Condition A was entered. At 0532 CST, the Unit 2 RB Equipment Access Inner door was closed and RB differential pressure was observed to increase above 0.25 in WC vacuum, and Condition A was exited. At the time of the event, the Unit 2 RB Equipment Access Outer door was the boundary for secondary containment. It should be noted that on 11 /7/16 at 2200 CST, during another part of the Under Voltage surveillance testing SBGT was started with RB Ventilation isolated and differential pressure was successfully maintained. TS LCO 3.6.4.1 was not applicable to Unit 3 which was in Mode 5 with no recently irradiated fuel moves or any operations with a potential for draining the reactor vessel (OPDRVs) in progress. This event is reportable under 10 CFR 50.73(a)(2)(v)(C), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material." C. Cause of Event: The Apparent Cause was degraded sealing surface on the Unit 2 RB Equipment Access Outer door coincident with RB Ventilation isolation which resulted in excessive in-leakage. The SBGT system did not have the capacity required to maintain the differential pressure in this condition. A Contributing Cause was a lapse in procedure use and adherence which requires communication of degraded seal conditions. An additional Contributing Cause was the lack of prioritization of repairs due to improper risk perception associated with addressing longstanding issues with the seals. Page _2_ of _3_ Page 3 of 3 | ML17010A281
Clinton Power Station | Unit 1 | Incorrect Calculation Method Used to Demonstrate Control Room Habitability | 01-13-2017 | On November 17, 2016, during the NRC Component Design Basis Inspection {CDBI), Clinton'Power Station {CPS) determined that design calculation C-020 "Reanalysis of Loss of Coolant Accident {LOCA) Using Alternate Source Terms," incorrectly took credit for the dual Main Control Room ventilation (VC) supply inlets being single failure proof (SFP). This assumption allowed the calculation to reduce one of the dose terms by a factor of 4 in accordance with the guidance of Regulatory Guide 1.194, "Atmospheric Relative Concentrations for Control Room Radiological Habitability Assessments at Nuclear Power Plants". However, the inlets to VC at CPS are not SFP. This calculational error, when corrected, resulted in a calculated dose of greater than the 5 rem Total Effective Dose Equivalent (TEDE) allowable dose to occupants of the control room. A cause evaluation identified USAR sections that described the VC system were not clear regarding whether the intake structures were SFP. A standing order was issued for compensatory measures in the event of an emergency until calculations were prepared to demonstrate MCR operator dose limits can be met without compensatory measures. Actions have been initiated to finalize the MCR Operator dose analysis assuming single failure of outside air intake dampers and to revise the USAR to indicate that intake structures are not independently SFP. This event is reportable under 10 CFR 50.73(a)(2)(ii)(B), "Any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety." NRG FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 {06-2016)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send ....'. :p~P,llf;)(I""'"' comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 ~ ~ LICENSEE EVENT REPORT (LEA) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to • lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, \ CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means ")it•*·· used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV Clinton Power Station, Unit 1 05000461 YEAR NUMBER NO. 2016 - 011 - 00 | PLANT AND SYSTEM IDENTIFICATION General Electric-Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX] EVENT IDENTIFICATION Incorrect Calculation Method Used to Demonstrate Control Room Habitability A. Plant Operating Conditions before the Event Unit: 1 Event Date: 11/17/16 Event Time: None Mode: 1 Mode Name: Power Operation Reactor Power: 99 percent B. DESCRIPTION OF EVENT During the NRG Component Design Basis Inspection (GOBI) on November 17, 2016, CPS determined that Calculation, C-020 "Reanalysis of Loss of Coolant Accident (LOCA) Using Alternate Source Terms," incorrectly took credit for the dual Main Control Room ventilation (VG) supply inlets being single failure proof (SFP). The calculation is used to demonstrate control room habitability in the CPS accident analysis. The calculation assumed dual air inlets for the emergency zones as the type of system used for the Main Control Room ventilation system (VG). The dual inlet type system allows for one of the calculated dose concentrations to be reduced by a factor_of 4 in accordance with the guidance of Regulatory Guide 1.194, "Atmospheric Relative Concentrations for Control Room Radiological Habitability Assessments at Nuclear Power Plants." The VG system is SFP, but the individual subsystems at the inlet as designed are not. The calculational error, when corrected, resulted in a calculated dose of greater than the 5 rem Total Effective Dose Equivalent (TEDE) allowable dose to occupants of the control room. The cause investigation team established that the USAR sections which described the VG system were not clear regarding whether the intake structures were SFP. This condition was concluded as the cause of the event. A review of the design calculation established that C-020 was prepared by Sargent & Lundy. The individual responsible for the design calculation preparation considered that both VG intake structures were independently SFP based on his understanding of the USAR sections that described the VG system. This was an unverified assumption by the preparer which resulted in the use of an incorrect methodology when the calculation assumed the outside intakes for VG were SFP. The lack of technical rigor in the preparation of the design calculation was established a condition which contributed to the event described in this report. | ML17018A120
Fermi 2 05000 341 1 OF 4 | Unknown Unit | Turbine Stop Valve Closure and Turbine Control Valve Fast Closure Reactor Protection System Functions Considered Inoperable Due to Open Turbine Bypass Valves | 01-23-2017 | At 1514 EST on January 6, 2016, while operating at 100 percent Reactor Thermal Power (RTP), the East and West Turbine Bypass Valves (TBV) automatically opened as expected for 3 minutes and 32 seconds in response to the number one High Pressure Turbine Stop Valve (TSV) drifting from full open to 25 percent open due to an actuator malfunction. Per Technical Specification (TS) Bases 3.3.1.1, TBVs must remain shut while RTP is at or above 29.5 percent to consider all channels of the TSV closure and Turbine Control Valve (TCV) fast closure Reactor Protection System (RPS) functions operable. Reactor Operators lowered RTP to 91.0 percent and at 1518 EST the TBV automatically closed and the TSV closure and TCV fast closure RPS functions were no longer considered inoperable. TS 3.3.1.1 requires that the TSV closure and TCV fast closure RPS functions be operable at or above 29.5 percent RTP. In this event, during the period of time while TBVs were open, reactor power was maintained above 91 percent and the RPS functions were confirmed to be enabled. The actuator malfunction was caused by faulty connectors within the actuator. The faulty connectors were replaced. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/3112018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 CONTINUATION SHEET F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC2 0503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the htttp_: vW nc gov/ea dina-rm/doc- lcoetns rregs_/_saff/sr1022 .3 1 NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000- NUMBER NO. Fermi 2 341 21 2016 - 0 - 01 | Initial Plant Conditions Mode 1 Reactor Power 100 percent There were no structures, components, or systems that were inoperable at the start of the event that contributed to the event. Description of the Event At 1514 EST on January 6, 2016, while operating at 100 percent Reactor Thermal Power (RTP) the East and West Turbine Bypass Valves (TBV) [[V]] automatically opened as expected for 3 minutes and 32 seconds in response to the number one High Pressure Turbine Stop Valve (TSV) drifting from full open to 25 percent open due to an actuator malfunction. Per Technical Specification (TS) Bases 3.3.1.1, TBVs must remain shut while RTP is at or above 29.5 percent to consider all channels of the TSV closure and Turbine Control Valve (TCV) fast closure Reactor Protection System (RPS) [JD] functions operable. A failure analysis revealed that the valve actuator malfunction and TSV position drift was caused by faulty connectors [[CON]] within the actuator. Reactor Operators lowered RTP to 91.0 percent and at 1518 EST, the TBVs automatically closed and the TSV closure and TCV fast closure RPS functions were no longer considered inoperable. TS 3.3.1.1 requires that the TSV closure and TCV fast closure RPS functions be operable at or above 29.5 percent RTP. An event notification and follow up notification (No. 51755) were made to the NRC based on meeting the reporting criteria of 10 CFR 50.72(b)(3)(v)(A) and (D). This event is reportable under 10 CFR 50.73(a)(2)(v), as an event or condition that could have prevented the fulfillment of the safety function of systems that are needed to: (A) shut down the reactor and maintain it in a safe shutdown condition and (D) mitigate the consequences of an accident. In addition, since this event affected all channels of the TSV closure and TCV fast closure RPS functions, this event is reportable under 10 CFR 50.73(a)(2)(vii), as an event where a single cause or condition caused two independent channels to become inoperable in a single system designed to: (A) shut down the reactor and maintain it in a safe shutdown condition and (D) mitigate the consequences of an accident. There were no radiological releases associated with this event. Significant Safety Consequences and Implications There were no significant safety consequences associated with this event. At no time during this event was there a potential for endangering the public health and safety. | ML17024A304
Cooper Nuclear Station 05000298 1of3 | Unknown Unit | Purchase and Installation of Incorrect Actuator Results in a Condition Prohibited by Technical Specifications | 01-05-2017 | On November 8, 2016 at 11 :27 hours, Cooper Nuclear Station (CNS) declared Reactor Core Isolation Cooling (RCIC) inoperable for surveillance testing and entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.5.3, Condition A. Subsequently at 11 :41 hours, RCIC was declared inoperable due to a water leak from the lube oiler cooler lower flange. During investigation it was determined that valve RCIC-AOV-PCV23, which was replaced during Refueling Outage 29, was full open causing excessive cooling water pressure to the lube oil cooler. This valve regulates cooling water to the lube oil cooler. Initial examination revealed that the actuator was purchased with a closed travel stop instead of the required open travel stop. The work order was revised to fabricate and install an open travel stop. On November 10, 2016, following valve modification, RCIC passed surveillance testing, was declared operable, and TS LCO 3.5.3, Condition A, exited . .T he root cause evaluation determined that the correct air operated valve was not purchased because the material master purchase order text and associated drawing didn't detail the requirement of an open travel stop. I To prevent recurrence, CNS will revise the material master purchase order text to state that the valve includes a travel stop in the open direction to limit valve travel. In addition, the drawing will be modified to show the correct travel stop with a note emphasizing the design function of the travel stop. NRC FORM ~66 !06-2016) Page 2 of 3 NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send (~~\ LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch \~...!..,.:. .) (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to (See Page 2 for required number of digits/characters for each block) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of lnfomnation and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a (See NUREG-1022, R 3 for instruction and guidance for completing this form means used to impose an information collection does not display a currently valid OMB control http:/fwww.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) number, the NRC may not conduct or sponsor, and a person is not required to respond to, the infomnation collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Cooper Nuclear Station 05000- 298 2016 -008 -00 | PLANT STATUS Cooper Nuclear Station (CNS) was in Mode 1, Power Operation, at approximately 10 percent power, at the time of the event. BACKGROUND The Reactor Core Isolation Cooling (RCIC) [EllS:BN] system provides makeup water to the reactor pressure vessel (RPV) [EllS:RPV] following an RPV isolation in order to prevent the release of radioactive materials to the environs as a result of inadequate core cooling. The RCIC system consists of a steam driven turbine-pump unit [EllS:TRB, P], piping, and valves [EllS:V] to provide steam to the turbine, as well as piping and valves to transfer water from the suction sources to the core via the Feedwater [EllS:SJ] system line, where the coolant is distributed within the RPV. The RCIC system pump supply is normally aligned to the Emergency Condensate Storage Tanks. The pump discharge is normally isolated and valve operation is required to align in either RPV injection mode or test return mode. Upon receipt of an initiation signal, the RCIC turbine accelerates to provide a specified pump flow. As the RCIC flow increases, the turbine control valve (EllS:FCV] is automatically adjusted to maintain the required design flow. RCIC is required to be operable during Modes 1, 2 and 3 with reactor steam dome pressure > 150 psig, since RCIC is the primary non-emergency core cooling system water source for core cooling when the RPV is isolated and pressurized. RCIC-AOV-PCV23 is a 1" pressure controlled globe valve located on the RCIC pump discharge line to the RCIC lube oil cooler. This valve has an air operated actuator which regulates the pressure of the cooling water based on the output of its controller, RCIC-PC-23. The valve works as a pressure reducing orifice to maintain the pressure in the lube oil cooling line below 60 psig to prevent over pressurizing the cooling circuit. Upon a loss of air to the valve operator a spring within the actuator will force the valve open. The actuator includes a travel stop, which is designed to prevent over pressurization of the cooling circuit by limiting the distance the valve can open. EVENT DESCRIPTION On November 8, 2016, at 11 :27 hours, CNS Operators declared RCIC inoperable for surveillance testing and entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.5.3, Condition A. Subsequently at 11 :41 hours, Operations declared RCIC inoperable due to a water leak from the lube oiler cooler lower flange. During investigation it was determined that valve RCIC-AOV-PCV23, which was replaced during Refueling Outage 29, was full open causing excessive cooling water pressure to the lube oil cooler. Initial examination revealed that the actuator was supplied with a_ closed travel stop instead of the required open travel stop. This travel stop prevents over-pressurization of the cooling circuit by limiting the opening stroke distance of RCIC-AOV-PCV23. The purchase order for the replacement valve and actuator did not contain a part description stating a travel stop was required. NRG FORM 366 (06-2016) Page 3of3 NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BYOMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to (See Page 2 for required number of digits/characters for each block) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a (See NUREG-1022, R 3 for instruction and guidance for completing this form means used to impose an infonmation collection does not display a currently valid OMB control http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Cooper Nuclear Station 05000- 298 2016 -008 -00 NARRATIVE The work order was revised to fabricate and install an open travel stop. On November 10, 2016, following valve modification, RCIC passed surveillance testing, was declared operable, and TS LCO 3.5.3, Condition A, was exited. BASIS FOR REPORT This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as any operation or condition which was prohibited by Technical Specifications, because RCIC was inoperable during the entry into the Mode of Applicability. SAFETY SIGNIFICANCE There were no actual safety consequences associated with this event. The potential safety consequences of this event were minimal due to the limited duration the condition existed and all Emergency Core Cooling Systems remained operable or available throughout the event. The RGIC system is designed to inject water into the reactor vessel during isolated conditions and is not considered an Emergency Core Cooling System. The total duration of inoperability, including the time prior to discovery of the condition was less than the 14 day Technical Specification Completion Time. During the time period of inoperability, Emergency Core Cooling Systems (High Pressure Coolant Injection, Automatic Depressurization System, Core Spray, and Low Pressure Coolant Injection) were operable or available and would have adequately responded to reactor vessel isolation and design basis events. CAUSE The root cause evaluation determined that the correct air operated valve was not purchased because the material master purchase order text and associated drawing didn't detail the requirement of an open travel stop. CORRECTIVE ACTIONS To prevent recurrence, CNS will revise the material master purchase order text to state that the valve includes a travel stop in the open direction to limit valve travel. In addition, the drawing will be modified to show the correct travel stop with a note emphasizing the design function of the travel stop. PREVIOUS EVENTS There have been no events reported in the past three years related to RCIC being declared inoperable. NRC FORM 366 (06-2016) | ML17025A072
Limerick Generating Station | Unknown Unit | Condition Prohibited by TS due to Parts Quality Issue | 01-27-2017 | Over a period of approximately one month, the 0B Main Control Room (MCR) Heating, Ventilating and Air Conditioning (HVAC) system experienced four failures. Troubleshooting was completed for each of the failures and for three of the failures the cause was determined to be an intermittent dropout or chattering of the Loss of Offsite Power (LOOP) start relay for two fans (0B-V116 MCR Supply and 0B-V121 MCR Return Fans). The fourth failure was due to a contactor in the Motor Control Center (MCC) for the 0B-V116 MCR Supply Fan. On 11/29/16 the second failure occurred on the LOOP start relay for the 0B-V116 MCR Supply fan. The investigation identified a manufacturing defect of the Agastat/Tyco ETR Relays in the lot of relays used for the recent preventative maintenance (PM) relay replacements. The relays were determined to be unreliable since the initial PM replacement on 10/19/16 until 12/5/16, when the quality issue was identified and relays from a different lot were installed. The B train of MCR HVAC was determined to be inoperable due to the relay issue for a period of 47 days, which is greater than the allowable Limiting Condition for Operation (LCO) action window of 7 days (per TS 3.7.2.a.1) for an inoperable Control Room Emergency Fresh Air System (CREFAS) train. Therefore, this was a condition prohibited by Technical Specifications (TS). NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Limerick Generating Station, Units 1 and 2 05000352 & 05000353 YEAR NUMBER NO. 2017 - 001 - 00 | I. Unit Conditions Prior to the Event Limerick Generating Station (LGS) Units 1 and 2 were both operating in Operational Condition (OPCON) 1 at 100 percent power at the time of the event. There were no other structures, systems, or components inoperable at the time of the event that contributed to the event. II. Description of the Event Over a period of approximately one month, the Main Control Room (MCR) Heating, Ventilating and Air Conditioning (HVAC) system experienced four failures. Three of the failures were caused by an intermittent dropout, or chattering of the LOOP start relay for two fans (0B-V116 MCR Supply and 0B-V121 MCR Return Fans). The fourth failure was due to a contactor in the MCC for the 0B-V116 MCR Supply Fan. Each of these events caused an unplanned Limiting Condition for Operation (LCO) entry and inoperability of the Control Room Emergency Fresh Air Supply (CREFAS) system. A timeline of events is as follows: 10/19/16 - KS-078-326B and KS-078-359B relays replaced for Preventative Maintenance (PM). Post Maintenance Testing (PMT) was performed by running the 0B MCR HVAC train. 11/13/2016 - To support chiller swaps the 0A MCR HVAC train was secured and Operations attempted to start the 0B train. This was the first start attempt since the PMT performance on 10/19/16. When the supply fan handswitch was placed in RUN, the fan did not start. Relay replacements were performed for KS-078-026B, which was found failed, and KS-078-326B, which was found chattering. Following replacements, the supply fan was started successfully. When Operations attempted to start the 0B return fan by placing the handswitch in RUN, it did not start. The KS-078-359B relay was found chattering, thereby preventing the return fan from starting. 11/20/16 - After running the 0B train of MCR HVAC for a period of one week, the supply fan tripped. The contactor was observed to be chattering. Breaker maintenance was performed and the contactors were replaced. Additionally, new wiring was installed internal to the breaker cubicle. During troubleshooting, the KS-078-326B and KS-078-026B relays were removed from the field and bench tested satisfactorily. 11/29/16 - To support a MCR chiller swap, the 0A MCR fans were secured and Operations attempted to start the 0B train. When the supply fan handswitch was placed in RUN, the fan did not start. The cause was determined to be a failed KS-078-326B relay. 12/5/16 - The 'B' MCR Return fan tripped and the 'A' MCR return fan auto-started. Troubleshooting efforts identified a chattering KS-078-359B relay in the field. On 11/29/16, the site believed that the relay failure was not an infantile failure and that there may be a common condition that was causing these failures. The relay was sent for testing and evaluation, and on 12/15/16, the station received the analysis which identified a manufacturing issue had caused the relay failures. | ML17027A107
Susquehanna Steam Electric Station | Unit 1 | Secondary Containment Breach due to Simultaneous Opening of Airlock Doors | 10-31-2018 | On November 30, 2016 at approximately 0921, a Talen Security Officer attempted to exit the Unit 1 Air Lock via Security door 585 on elevation 676. A Talen Mechanical Maintenance employee knocked on the Turbine Building door to gain his attention. The Security Officer then stopped from proceeding into the Reactor Building and was allowing the Reactor Building door to close when the mechanic opened the Turbine Building air lock door without verifying a green light. This caused an alarm for a momentary breach of Secondary Containment. The mechanic then closed the door without proceeding into the airlock. This airlock serves as a secondary containment boundary; as such, having both doors open at the same time results in failure to meet Technical Specification 3.6.4.1 as a result of not satisfying Surveillance Requirement 3.6.4.1.3. The condition is being reported in accordance with 1O CFR 50. 73(a)(2)(v)(C). The cause of the event was failure to follow station expectations when entering an airlock and less than adequate · verification practices. Corrective actions included documented coaching of the mechanic. There were no actual consequences to the health and safety of the public as a result of this event. NRG FORM 366A (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail CONTINUATION SHEET to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a (See NUREG-1022, R.3 for instruction and guidance for completing this form means used to impose an information collection does not display a currently valid OMB control http://www.nrc.gov/reading-rm/doc-collections/nureqs/staff/sr1022/r3D number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITYNAME 2. DOCKET NUMBER 3. LER NUMBER I YEAR I SEQUENTIAL REV Susquehanna Steam Electric Station, Unit 1 05000-387 NUMBER NO. 2016 - 025 -00 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, approximately 100 percent Rated Thermal Power Unit 2 - Mode 1, approximately 100 percent Rated Thermal Power There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. EVENT DESCRIPTION On November 30, 2016 at approximately 0921, a Talen Security Officer attempted to exit the Unit 1 Air Lock [EllS: AL] via Security door 585 [EllS: DR] on elevation 676. A Talen Mechanical Maintenance employee knocked on the Turbine Building [EllS: NM] door to gain his attention. The Security Officer then stopped from proceeding into the Reactor Building [EllS: NG] to allow the mechanic to enter the airlock. While the Reactor Building door was closing, the mechanic opened the Turbine Building air lock door without verifying a green light. This caused an alarm [EllS: ALM] for a momentary breach of Secondary Containment [EllS: VA]. The mechanic then closed the door without proceeding into the airlock. This airlock serves as a secondary containment boundary; as such, having both doors open at the same time results in failure to meet Technical Specification 3.6.4.1 as a result of not satisfying Surveillance Requirement 3.6.4.1.3. CAUSE OF THE EVENT The cause of the event was failure to follow station expectations when entering an airlock and less than adequate verification practices. ANALYSIS/ SAFETY SIGNIFICANCE Technical Specification 3.6.4.1 Surveillance Requirement 3.6.4.1.3 requires that one secondary containment access door in each access opening is closed. This event is being reported pursuant to 10 CFR 50.73(a)(2)(v)(C) as having both Secondary Containment airlock doors momentarily open simultaneously results in a condition that could have prevented fulfillment of a safety function to mitigate the consequences of an accident by controlling the release of radioactive material. There was no actual safety consequence as a result of this event. Engineering analysis of this event has determined that secondary containment could have performed its safety function of isolating, as assumed in the accident analysis, and also of re-establishing 0.25 in w.g. vacuum (drawdown) within the assumed accident analysis time (10 minutes). Therefore, the subject event did not cause a loss of safety function. This event will not be counted as a safety system functional failure (SSFF) for the NRG performance indicator based on the Engineering analysis supporting the system's ability to fulfill the safety function. NRG FORM 366A (06-2016) Page 2 of 3 | ML17030A136
Browns Ferry Nuclear Plant | Unit 1 | Main Steam Relief Valves Lift Settings Outside of Technical Specifications Required Setpoints | 01-30-2017 | On November 30, 2016, the Tennessee Valley Authority was presented with as-found testing results indicating that three of the thirteen Main Steam Relief Valves (MSRVs) from Browns Ferry Nuclear, Unit 1, exceeded the +/- 3 percent setpoint required for their operability. Troubleshooting determined that the MSRV discs failed by corrosion bonding to their valve seats. The valve discs were previously platinum coated to prevent this, but the valve seat's rough Stellite surface caused the coating to delaminate. These three MS RVs were found to have been inoperable for an indeterminate period of time between October 29, 2014, and October 1, 2016, and longer than permitted by Technical Specifications. The affected valves remained capable of maintaining reactor pressure within American Society of Mechanical Engineers code limits. Additionally, the valves' ability to open under remote-manual operation, activation through the !Automatic Depressurization System, or MSRV Automatic Actuation Logics was not affected. The valves remained capable of performing their required safety function. Corrective Actions were to replace all Unit 1 MSRV pilot valves, to analyze the pilot valves of the inoperable MSRVs, and to revise procedures to verify the pilot disc finish meets its requirements prior to valve assembly. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Browns Ferry Nuclear Plant, Unit 1 05000259 YEAR NUMBER NO. 2016 - 005 00 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Unit 1, was in Mode 1 at 100 percent power. II. Description of Event A. Event Summary On November 30, 2016, National Technical Systems (NTS) Laboratories provided Tennessee Valley Authority (TVA) with the as-found testing results of the thirteen Main Steam Relief Valves (MSRVs) [RV] which were removed during the Fall 2016 Unit 1 Refueling Outage 11 (U1R11). Three of the Main Steam Line C and D Relief Valves (BFN-1-PCV-001-0030, BFN-1-PCV-001- 0041, and BFN-1-PCV-001-0180) had as-found lift settings which exceeded the+/- 3 percent setpoint required for their operability. Technical Specification (TS) 3.4.3 requires twelve of the thirteen Safety/Relief Valves (S/RVs) to be operable for S/RV system operability. These three MSRVs were found to have been inoperable for an indeterminate period of time between October 29, 2014, and October 1, 2016, and longer than permitted by TS 3.4.3. MSRV operability was restored on November 4, 2016, upon completion of a post-maintenance testing (PMT) following the biennial scheduled replacement of the MSRV pilot valves with refurbished valves which were certified to lift within +/- 1 percent of their setpoints. Throughout this event, the two-stage MSRV pilot valves remained capable of maintaining the reactor pressure below 1375 psig, which is the American Society of Mechanical Engineers (ASME) code limit of 110 percent of the vessel design pressure. The valves remained capable of performing their required safety function. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML17030A311
SEQUENTIAL REV | Unknown Unit | Tornado Missile Vulnerabilities Result in Condition Prohibited by Technical Specifications | 12-07-2016 | On 12/7/16 Units 1 and 2 were in Mode 1 at 100 percent rated thermal power. Engineering personnel determined that the Unit 1 and Unit 2 Service Water Intake Structure (SWIS) intake and exhaust ventilation hoods were not adequately protected from tornado generated missiles. Subsequent evaluations on 1/26/17 resulted in the determination that the emergency diesel generator (EDG) fuel oil storage tank (FOST) vents were also not adequately protected from tornado generated missiles. Operations subsequently declared the affected systems inoperable, implemented Enforcement Guidance Memorandum (EGM) 15·002, "Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance" and the required compensatory measures, and then declared the affected equipment operable but non-conforming. This condition is an original plant design legacy issue. Immediate compensatory measures included actions to take if needed as described in severe weather procedures, and monitoring of system parameters on the MCB in accordance with annunciator response procedures. A risk based evaluation will be performed or plant modifications will be undertaken to establish compliance with the site's tornado missile protection design basis. - ""RC FORM, 3 66A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. ll.SO.OI04 EXPIRES: 10/31/lOIB ll·lOIS) . .. .. " ·' E R s e t p im or a te la d d l e b s w so d n e s n re p a e m r r e a d s p a o re n s in e c 1 o 0 lp c o o ra m ri p td ly In w t i o th t h li e d s riC m 8R an S d in a g iO p I r Y o c c e d s l s e c e t n io d n le r d e q b u a a c s k t : t o 8 0 in d h u o s u tr r y s . . I •• 1 Send commanll reaardng burden estimate to the FOIA. Privacy end lnlormatian Collections Brandl (T·S F~). O.S. Nuclear RegulaiOfY Commission, Wasliilatan, DC 20555-0001. or by \:. •••• i.(J LICENSEE EVENT REPORT (LER) internet Hnlillo Jnlocdlects.Resouaonrc.goy, and to 1111 Desk blficer, Olfice ollnlonnalian and RegulaiOIY Allairs, NEOB-10202, (3150-0104), Ollice ol Mana~! and Budget, CONTINUATION SHEET WaslllniJan, DC 20503. II a maens used to impose en information collection does not displaY a cummdy valid OMB control number, the NRC may nol conducl or sponsor, and a person Is not lli!IUirad to respond to, the lnlormdan colledion. 1. FACIUTY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAl REV YEAR NUMBER NO. Joseph M. Farley Nuclear Plant, Unit 1 05000· 348 2016 - 009 - 00 | PLANT AND SYSTEM IDENTIFICATION Westinghouse • Pressurized Water Reactor A. UNIT STATUS AT TIME OF EVENT Unit 1, Mode 1, 10 0 percent power Unit 2, Mode 1, 100 percent power No plant transients were associated with this event. Thus, no structures, systems, or components (SSC) were inoperable at the start of this event which contributed to this condition. Background NRC documents: Enforcement Guidance Memorandum (EGM) 15-002, "Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance," provides guidance to exercise enforcement discretion when an operating power reactor licensee does not comply with a plant's current site-specific licensing basis for tornado-generated missile protection. Specifically, discretion would apply to the applicable Technical Specification (TS) Limiting Condition(s) for Operation (LCO) that would require a reactor shutdown or mode change in the event a licensee could not meet TS LCO required action(s) within the TS completion time. Interim Staff Guidance DSS-ISG-2016-01, "Clarification of Licensee Actions In Receipt of Enforcement Discretion Per Enforcement Guidance Memorandum EGM 15-002, • provides interim staff guidance to facilitate staff understanding of expectations for consistent oversight associated with implementing enforcement discretion for tornado missile protection noncompliance(s) per EGM 15-002. Appendix A to DSB-ISG-2016-01 provides guidance for acceptable initial and comprehensive compensatory measures for licensee use in implementing the enforcement discretion outlined in EGM 15-002. The licensee should declare (log) the utilization of EGM 15-002, inform the resident inspector, and enter the issue into the corrective action program. For initial compensatory measures, it is expected that the measures listed are already in place at sites that may be affected by severe weather, such as tornados and/or hurricane force winds. The measures should be verified as current and readily deployable within a very short timeframe. B. DESCRIPTION OF EVENT On 1217/16 during the evaluation of protection of Technical Specification (TS) equipment from damage from tornado generated missiles, Farley site engineering identified nonconforming conditions in the plant design such that the specified TS equipment did not meet the current design basis for protection against tornado generated missile impacts. Specifically, the Unit 1 and Unit 2 Service Water (SW) [BI] pumps could be rendered inoperable due to a tornado generated missile strike on the Service Water Intake Structure (SWIS) intake and exhaust ventilation hoods. This vulnerability was not included In the site's tornado missile risk analysis (TORMIS). The SWIS intake and exhaust ventilation hoods, located on the roof of the SWIS, could be crimped as a result of a tornado missile strike, thus reducing air flow and challenging the performance of their heating and cooling safety functions. In addition, if the SWIS ventilation hoods were damaged or removed by a tornado missile strike, rainwater may enter the area below the hoods. The SWIS batteries and breakers Page 2 of4 ~RC FORM 366A U.S. NUCLEAR REGULA TORY COMMISSION APPROVED BY O~IB: NO. 3150~104 EXPIRES: 10/JIIlOIB ll·lOISl ,...~ ......" Esllmated burden per rasponse to comply with this mandatory collec:tion requesl: 80 hours. ! i Repo!led lessons learned are incorporated into tho r:censing process and lad back to 'rdustry. 1 r Send commenls rogarang burden estimate to the FOIA, Privacy and lnfcnnaton Collec:tions ~ .... ?1 Branch (T·S F53), U.S. NUclear Regulatory Commission, Washing:on, DC 20555-0001, or by LICENSEE EVENT REPORT (LER) intemet &-mail to lnfocolfects.RasourceOnn:.gov, and to ltle Desll Officer, Office of Information and Regulatory Allalrs, NEOB-10202, (3t50-0104), Office of Mana(18111ent and Budge1, CONTINUATION SHEET Washington, DC 20503.11 a means used to 'mposa an 'nlonnafon cdlecton does not cfisplay a cunent!y valid OMB control number, the NRC may not conduct or sponsor, and a person Is not required to respond to, the information collection 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR NUMBEft NO. Joseph M. Farley Nuclear Plant, Unit 1 o5ooo- 348 2016 • 009 • 00 NARRATIVE for the 1C and 2C SW pump motors could be rendered inoperable due electrical shorts caused by intrusion of rainwater. Subsequent evaluations on 1/26117 resulted in the determination that the emergency diesel generator (EDG) fuel oil storage tank (FOST) [DC] vents were also not adequately protected from tornado generated missiles. Each EDG FOST is provided with a 1-inch vent pipe that extends above the ground and is exposed to tornado missiles. If these vent pipes were hit by a tornado missile they could become crimped and impede the transfer of fuel oil thereby resulting in failure of the associated EDGs to perform their safety functions. These SSCs were declared inoperable and EGM 15-002 was invoked. To meet the intent of EGM 15-002 to restore the SW Pumps to an operable but degraded I non-conforming (OBDN) status, existing measures were verified as current and readily deployable for both units and were implemented as initial compensatory measures within the allowed time by the applicable LCOs. These measures included actions to take If needed as described in severe weather procedures, and monitoring of system parameters on the MCB in accordance with annunciator response procedures. In addition, new Compensatory Measures were established to inspect, protect, and restore function to the ventilation hoods and affected areas in the SWIS, and similar measures are being established for the FOST vent pipes. C. CAUSE OF EVENT This condition is an original plant design legacy issue. Due to the historical nature of this vulnerability, a specific cause has not been Identified. D. REPORTABILITY ANALYSIS AND SAFETY ASSESSMENT This event is reportable as required by: • 10 CFR 50. 73(a)(2)(i)(B) for a condition that is prohibited by Technical Specifications. • 10 CFR 50.73(a)(2)(v)(D) for a condition that at the time of discovery could have prevented the fulfillment of a safety function of structures or systems needed to mitigate the consequences of an accident. • 10 CFR 50.73(a)(2)(ii)(B) for an event or condition that results in the plant being in an unanalyzed condition that significantly degrades plant safety. As documented in EGM 15-002, tornado missile scenarios that may lead to core damage are very low probability events because safety-related SSCs are typically designed to withstand effects of tornados. For a tornado missile-Induced scenario to occur, a tornado would have to hit the site and result in the generation of missiles that would hit and fail vulnerable, unprotected safety-related equipment, and/or unprotected safety-related subcomponents in a manner that is non-repairable and non-recoverable. In addition, because plants are designed with redundancy and diversity, the tomado missiles would have to affect multiple trains of safety systems and/or means of achieving safe shutdown. The NRC has completed a generic risk analysis of potential tornado missile protection noncompliances to examine the risk significance of these scenarios. This assessment documents a conservative, bounding-type analysis of the risk significance for plant facilities. The generic analysis assumed that core damage would occur if a tornado hit a plant located In the most active tornado region In the country and Page 3 of4 ~RC FORM,. 3 66A U.S. NUCLEAR REGULA TORY COMMISSION APPROVED BY OMB: NO. 3150-4104 EXPIRES: 10/3112018 11-2015) ........... Eslimated burden par rasponse to comply with this mandaloly collection raquest 80 houls. Reported lessons learned 11ft incolpcntid ilto the lil:ensino process and led back to irdlslly. \..~~.f) Send COIII11ents reaarcing burden estimate lo the FO!A, l"rivacy and lnlonnation Collections 81111lCh (T·S F53), O.S. Nucle1r ~allliY Commission, Waslington, DC 20555-0001, or by LICENSEE EVENT REPORT (LER) Internet Hl18ll to tnfocollec:ls.ResourceOnn:.gcw,llliCito the Desk Ollicef, Oftice ol lnfDI!IIItion and RegulaloiV AllaiJS, NEOB-10202. (3150-0104), Office ol Managament and Budget, CONTINUATION SHEET WIISNngton. DC 20503. I a means used to impose an inlonnallon collection does not cisplay a cunently valid OMB controllllll1ber, the NRC may not c:ondlcl or sponsor, and a parson Is nol required to respond lo,lhe infonnatlan collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SE N O U U M E B K E T R IA L R N E O V . Joseph M. Farley Nuclear Plant, Unit 1 05000- 348 2016 - 009 - 00 NARRATIVE that it caused a tornado-generated missile to fail all emergency core cooling equipment at the plant with no ability to recover. Given this conservative assumption, the staff's study established that the core damage frequency (CDF) associated with tornado missile-related noncompliances are well below CDFs requiring immediate regulatory action. In summary, the generic bounding risk analysis performed by the NRC concluded that this issue is of low risk significance. During a postulated design basis tornado, the conditions documented could have resulted In a loss of function for the SW pumps or a loss of the safety function for the EDGs. The SW pumps mitigate the effects of postulated accidents by providing essential plant cooling to safety related systems and components, including those required for emergency core cooling. The EDGs are used to mitigate the effects of a loss of offsite power by providing an emergency AC power source. This condition had no actual safety consequences impacting plant or public safety as Farley did not experience an actual tornado missile event. Compensatory measures were and continue to be in place to mitigate the effects of a tornado missile strike. Also, only three of six exhaust ventilator fans are required to handle the heating load of the pump room. This redundancy reduces the risk of the postulated conditions from occurring during a tornado missile event. Therefore, enforcement discretion until June 10 , 201 B, will not impose significant additional risk to public health and safety. E. CORRECTIVE ACTION A risk based evaluation will be performed or a plant modification will be undertaken to establish compliance with the site's tornado missile protection design basis. F. ADDITIONAL INFORMATION 1) Previous Similar Events: No other similar previous events have been reported. 2) Commitment Information: This report does not create any licensing commitments. Page 4of4 | ML17033B232
Clinton Power Station | Unit 1 | Residual Heat Removal (RHR) "C" Pump Failure During Surveillance Testing as a Result of Breaker Latch Check Switch Adjustment Results in a Condition Prohibited by Technical Specification | 02-01-2017 | On December 5, 2016 at 2011 hours during a surveillance test of the Residual Heat Removal (RHR) "C" pump, a Westinghouse DHP Breaker for the RHR "C" pump failed to close. This occurrence resulted in a failure of RHR "C" pump to start. The pump was declared INOPERABLE and Technical Specification (TS) Limiting Condition of Operation (LCO) 3.5.1, "Emergency Core Cooling System -Operating," Required Action A.1 was entered to restore the pump to OPERABLE status in seven days. Performance records indicate the breaker was installed on March 11, 2016 in the RHR "C" pump cubicle and successfully operated on March 11, June 9, and September 6, 2016, prior to failure. An investigation determined that the breaker latch check switch contacts were not closed and that the latch check switch setting was out of procedural limits. The most likely time that the switch would have become out of adjustment would have been during transport of the breaker to the RHR "C" pump breaker cubicle on March 11, 2016. The apparent cause of the failure was an inadequate verification of the latch check switch setting performed prior to installation of the breaker in the cubicle. Corrective measures have been initiated that include revising plant procedures to record latch check switch adjustment value. The condition described in this report is reportable under 1OCFR50.73(a)(2)(i)(B) as an "operation or condition which was prohibited by the plant's Technical Specifications." NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV Clinton Power Station, Unit 1 05000461 YEAR NUMBER NO. 2016 - 012 - 00 | PLANT AND SYSTEM IDENTIFICATION General Electric-Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX] EVENT IDENTIFICATION Residual Heat Removal (RHR) "C" Pump Failure During Surveillance Testing as a Result of Breaker Latch Check Switch Adjustment Results in a Condition Prohibited by Technical Specifications A. Plant Operating Conditions before the Event Unit: 1 Event Date: 12/05/16 Event Time: 2011 Mode: 1 Mode Name: Power Operation Reactor Power: 99 percent B. DESCRIPTION OF EVENT On December 5, 2016 at 2011 hours, Westinghouse DHP Breaker 1AP09EF for the Residual Heat Removal (RHR) "C" pump failed to close during the operability surveillance. During the test, the pump control switch was held in the start position for approximately 3 seconds with no indication of a pump start. When the control switch was released to the auto position, the pump trip indication illuminated. The RHR "C" pump was declared INOPERABLE and Technical Specification (TS) Limiting Condition of Operation (LCO) 3.5.1, "Emergency Core Cooling System-Operating", Required Action A.1 was entered to restore RHR "C" to OPERABLE status within seven days. During the event investigation, the breaker charging springs were found to be charged and the latch check switch contacts open with the breaker installed in the cubicle. The function of the latch check switch is to indicate when the circuit breaker is "ready to close,'' providing a permissive for the breaker closure. In restoring the RHR "C" pump to OPERABLE status, the latch check switch was measured to be zero inches overtravel. The setting was adjusted to an overtravel value of 3/16 inch past the point that the contacts are closed as specified in plant procedures. Technicians that adjusted the latch check switch during the post event investigation indicated that the contact resistance was acceptable and the switch operated mechanically as expected. The mounting screws were subsequently verified to be tight following the failure. The breaker was placed back in service and post maintenance testing of RHR pump "C" was concluded satisfactorily. The RHR "C" pump was declared OPERABLE on December 6, 2016 at 0822 hours. | ML17037D197
Oyster Creek | Unit 1 | Failure of the #1 Emergency Diesel Generator During Surveillance Testing due to a Cooling Water System Leak | 01-24-2017 | On January 4, 2016, during the biweekly load test surveillance, the Emergency Diesel Generator (EDG) #1 tripped after g6 minutes of operation and an unexpected Main Control Room alarm was received. Locally, at the EOG enclosure, it was discovered that the rubber pipe coupling that connects the coolant surge tank to the right bank cooling water pump inlet tee had ruptured and that the EOG #1 control circuitry processed the trip on low coolant pressure. EOG #1 was declared inoperable and in accordance with Technical Specification (TS) 3.7.C.2 Limiting Condition for Operation (LCO), the unit entered a seven day action period. The EDG #1 was returned to service on January 5, 2016, at 0130 hours, following successful hose replacement and completion of the load test surveillance. The Root Cause investigation determined that an activity to reQlace the rubber QiQe couQling on a 12-year freguency was not established durinrfu;the initial imQlementation of Exelon's Electro-Motive Division Diesel Generator Performance Centered Maintenance (PC ) temQlate. . Ihis event resulted in an ~eration or Condition that was Prohibited by the Plant's Technical Specifications and is therefore being reported under 10C R50.73(a)(2)(i)(B). · · NRG FORM 366 (11-2015) Page 2 of 4 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV Oyster Creek, Unit 1 05000-219 YEAR NUMBER NO. 2016 - 001 - 01 | Description of Event On January 4, 2016, at approximately 0412 hours, the Oyster Creek Nuclear Generating Station (OCNGS) Emergency Diesel Generator (EDG) #1 was started for the normal biweekly load test surveillance in accordance with Procedure 636.4.003 (Diesel Generator 1 Load Test). At 0414 hours, the EDG #1 came up to rated load and at 0440 hours an unexpected alarm (T-4-b EDG 1 DISABLED), was received in the Main Control Room (MCR) when the EDG #1 controls processed a trip on low coolant pressure. MCR Operators noted the EDG #1 output breaker opened, the UNIT START light was not lit, and the UNIT IDLING light was briefly lit, then extinguished. Operators discovered locally at the EDG enclosure that the rubber pipe coupling that connects the coolant surge . tank to the right bank cooling water pump inlet tee had ruptured. The following local alarms were annunciated in the EDG #1 cubicle: ENG TRIP; GEN BKR TRIP, and LOW COOLANT PRESS. These indications were expected based on the "as found" condition of the hose and the mode of engine operation. Following the trip, the EDG #1 was declared inoperable in accordance with the Technical Specification 3.7.C.2 LCO, which placed the plant in a 7-day action and resulted in an unplanned risk change from GREEN to YELLOW. EDG #1 was declared operable at 0130 hours on January 5, 2016, and plant risk was returned to Green, following the replacement of the rubber pipe coupling and successful post maintenance testing. ' Equipment Description OCNGS is equipped with two identical EDG units. The function of the EDGs is to provide AC power to the Class 1 E buses upon a loss of off-site power. The EDGs must be able to provide this power rapidly, within 1O seconds, upon demand. This condition is referred to as a fast start signal. If started with a fast start signal, a high jacket water temperature condition will not trip the EDG. The EDG units are General Motors Corporation, Electromotive Division (EMD) Model EMD 20-645E4, 20-cylinder, 2-cycle, turbo-intercooled diesel engines, which drive their respective EMO A20C AC generators. Each unit is normally operated bi-weekly to demonstrate the ability to carry rated loading upon loss of offsite power to their respective buses. The EOG units are self-contained in enclosures inside the EOG vaults and are provided with air cooled radiators to remove waste heat. Each engine is equipped with two engine-driven cooling water pumps to provide jacket water coolant flow to the power assemblies in each cylinder bank and the turbocharger after coolers. The cooling water, which is demineralized water treated with Nalcool 2000 corrosion inhibitor, is maintained in a closed loop with a surge tank connected to a tee in the suction side of the pumps. The tank is equipped to accommodate the volume of coolant that drains from the radiators in the standby condition and provides adequate coolant level for pump net positive suction head during operation. The rubber pipe coupling which failed on EOG #1 was one of two on that engine, which provided a flexible connection between the tee and the bottom of the tank. To minimize the stress of a fast start, each engine is provided with an immersion heater in the coolant system and auxiliary oil pumps to circulate warm oil. The coolant system is designed for reverse natural circulation flow to provide for oil heating in standby conditions. In standby, the water level in the tank is approximately 14 inches higher thari during operation, where the water is displaced into the piping above the radiator. NRG FORM 366A (11-2015) Page 3 of 4 | ML17038A007
LaSalle County Station | Unit 1 | Reactor Core Isolation Cooling System Inoperable Longer than Allowed by the Technical Specifications due to Low Suction Pressure Trips | 02-08-2017 | On October 18, 2016, the Unit 1 Reactor Core Isolation Cooling (RCIC) system tripped on low suction pressure during a normal system start following completion of scheduled maintenance activities. The system was restored to operable on October 20, 2016. A second event involving a Unit 1 RCIC system trip on low pressure suction pressure occurred on November 17, 2016, during the system's quarterly operability surveillance. The system was restored to operable on November 20, 2016. The component failure analysis completed on December 16, 2016, determined the cause of both Unit 1 RCIC system trips was a failure of the electronic governor-remote (EG-R) hydraulic actuator. The Unit 1 RCIC inoperable period was from the first system trip on October 18, 2016, to when full restoration was completed on November 20, 2016. This time was greater than allowed by Technical Specifications (TS) 3.5.3, "RCIC System," Condition A Completion Time of 14 days. This event is reportable in accordance with 1O CFR 50. 73(a)(2)(i)(B) as a condition prohibited by the plant's TS. The root cause for the low suction pressure trips was i~dequate management of the EG-R preventative maintenance 1 I• (PM) strategy. Corrective actions included replacement of the EG- and a plan to implement an appropriate PM strategy for the RCIC EG-R. The safety consequences were minimal since the RCIC system is not credited in the safety analysis, and the credited High Pressure Core Spray (HPCS) system remained available to provide its safety function. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: BO hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarcing burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Comm'ssion, Washington. DC 20555-0001, or by e-mail to lnlocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nureqs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV LaSalle County Station, Unit 1 05000373 YEAR NUMBER NO. 2017 • 001 00 | PLANT AND SYSTEM IDENTIFICATION LaSalle County Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was Unit 1 Reactor Core Isolation Cooling System (RCIC}. CONDITION PRIOR TO EVENT Unit(s): 1 Event Date: December 16, 2016 Event Time: 0934 CST Reactor Mode(s}: 1 Mode(s) Name: Power Operation Power Level: 100% DESCRIPTION OF EVENT On October 18, 2016, while Unit 1 was in Mode 1 at 100% power, the Unit 1 RCIC system tripped on low suction pressure during a normal start that was being performed in accordance with the RCIC system pump operability valve test procedure, following completion of scheduled maintenance activities. Repairs were performed that restored the system to operability on October 20, 2016. A second event involving a Unit 1 RCIC system trip on low suction pressure occurred on November 17, 2016, revealing a related cause. Previously, the last successful RCIC operability test had been performed on August 27, 2016. Background: The RCIC system is provided to assure adequate core cooling iri the event the reactor is isolated from its primary heat sink in conjunction with a loss of normal feed-water flow to the reactor vessel. The normal water flow path is from the Cycled Condensate Storage Tank through the RCIC pump and into the discharge line. Steam enters the turbine, where most of the energy is removed driving the turbine, and is then exhausted to the Suppression Pool through a check valve and motor operated exhaust isolation valve. The design of the RCIC system has various instrumentation monitoring performance parameters. Various RCIC turbine trip functions are provided, including low pump suction trip to protect against cavitation and lack of cooling that could cause damage to the pump. The RCIC turbine steam admission valve uses a logic in which the turbine speed demand is compared with the actual turbine speed and generates an error signal that is passed to the Electronic Governor Remote (EG-R). The EG·R interprets the signal to hydraulically position the governor valve to control steam admission to the RCIC turbine. Event 1: On October 18, 2016, at 22:23 CST, during start of the Unit 1 RCIC system post-maintenance test (PMT} surveillance following planned maintenance activities, the system tripped on low suction pressure. Troubleshooting identified the potential causes were related to the low-pressure switch out of calibration and the flow controller ribbon cable not seated correctly. Corrective actions included replacement of the pressure switch and the flow controller. Further troubleshooting was not performed due to successful RCIC startup following these initial troubleshooting actions. The RCIC system was declared operable and associated Technical Specifications (TS) timeclocks were exited on October 20, 2016, at 03:00 CST. Event 2: On November 17, 2016, at 11 :00 CST, during start of the Unit 1 RCIC system for its quarterly surveillance, RCIC tripped on low suction pressure following fluctuations in suction pressure. All other parameters, including those in the field, were verified to be normal, and Unit 1 RCIC was placed in a safe configuration and declared inoperable. Troubleshooting determined the cause was degradation of the EG-R. In addition, rust was found on the oil port face, potentially restricting oil flow to the EG-R. The degraded EG-R was replaced with a new EG·R, and the degraded EG-R was sent off-site for component failure analysis. The PMT and a detailed review of historical performance data indicated improved EG-R governor positioning. The RCIC system was declared operable on November 20, 2016, at 19:05 CST. I I | ML17039A744
Nine Mile Point | Unit 1 | l\A::in11::il ~ - 1r ~l"'r::Jm nr It:> tn Hinh Tt trhim Vihr::itinn | 02-08-2017 | On December 10, 2016 at 08:48, Nine Mile Point Unit 1 performed a manual scram of the reactor due to increased vibrations on the main turbine. Following the scram, the High Pressure Coolant Injection (HPCI) System automatically initiated. This event is reportable under 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b )(3)(iv)(A) as any event or condition that resulted in a manual or automatic actuation of any of the systems listed in 10 CFR 50.72(b)(3)(iv)(B). During performance of a load drop to 95% power in support of Turbine Stop Valve Testing, main turbine bearing vibrations rose on several bearings. The Unit 1 Reactor was scrammed and the main turbine was secured when main bearing #1 reached procedural limits. The root cause of the event was a steam leak from a threaded pipe/cap connection that was not seal welded when originally supplied from the manufacturer. The connection !has now been seal welded. A combination of tight tolerance in conjunction with the location of the steam leak resulted in the vibrations when power level was changed. rrhe event described in this LER is documented in the plant's corrective action program. NRG FORM 366A (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. /""-<.'.'\. Reported lessons learned are incorporated into the licensing process and fed back to industry. f~</f. • LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to the FOIA, Privacy and Information Collections \"·~ ...l.. ~ Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail ,; CONTINUATION SHEET to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a (See NUREG-1022, R.3 for instruction and guidance for completing this form means used to impose an information collection does not display a currently valid OMB control htto://www.nrc.gov/readinq-rm/doc-collections/nureqs/staff/sr1022/r3{J number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER I I YEAR SEQUENTIAL REV Nine Mile Point Unit 1 05000220 NUMBER NO. 2017 001 -00 | r. DESCRIPTION OF EVENT A. PRE-EVENT PLANT CONDITIONS: Prior to the event, Nine Mile Point Unit 1 (NMPl) was operating at 100% with Operations performing a load drop to 95% to support turbine stop valve testing and control rod pattern adjustment. B. Event: On December 10, 2016 at 08:48, Nine Mile Point Unit 1 performed a manual scram of the reactor due to increased vibrations on the main turbine. This was performed during a load drop to 95% reactor power to facilitate turbine stop valve testing and rod line adjustments. At 95% reactor power operations noted rising vibrations on the main turbine bearings. The reactor was manually scrammed and the main turbine was secured as the observed vibrations reached procedural limits. Following the scram, as designed, HPCI initiated on low Reactor Pressure Vessel (RPV) water level due to the initial RPV level shrink. HPCI was secured following recovery of RPV water level above the low level scram setpoint of 53 inches. There was no impact on Nine Mile Point Unit 2 (NMP2) from this event. Operations performed the ENS notification (#52425) required by 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) for the manual reactor scram and for the expected HPCI initiation due to the Main Turbine Trip. This notification met the 4 hour and 8 hour reporting requirements. This LER is being submitted pursuant to the requirements of 10 CFR 50.73(a)(2)(iv)(A). C. INOPERABLE STRUCTURES, COMPONENTS, OR SYSTEMS THAT CONTRIBUTED TO THE EVENT: None NRG FORM 366A (06-2016) Page 2 of 6 | ML17044A007
Cooper Nuclear Station 05000298 1of4 | Unknown Unit | Control Room Emergency Filter System Fan Removed from Service Due to Human Error Results in Loss of Safety Function | 02-02-2017 | On December 7, 2016, the Control Room Emergency Filtration System (CREFS) was inadvertently removed from service during the conduct of a scheduled surveillance activity performed by a Control Room Operator. Consequently, Operations declared CREFS inoperable at 22:40 hours. Investigation revealed that the running CREFS supply fan had been turned off in error during the conduct of a surveillance procedure. Upon discovery of this, Operations returned the supply fan to service and declared CREFS operable at 22:4 7 hours. Event Notification 52416 was made to the Nuclear Regulatory Commission Operations Center. The root cause was attributed to human error. To prevent recurrence, applicable operations procedures will be revised to require peer checking during normal operations for all Control Room manipulations directed by these procedures. This is a Safety System Functional Failure. Page 2of4 NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) · Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send I~~ LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and lnfonnation Collections Branch ~ ..... ~ (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 2055S.0001, or by e-mail to (See Page 2 for required number of digits/characters for each block) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of lnfonnation and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a (See NUREG-1022, R 3 for instruction and guidance for completing this form means used to impose an infonnation collection does not display a currently valid OMB control http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) number, the NRC may not conduct or sponsor, and a person is not required to respond to, the infonnation collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Cooper Nuclear Station 05000- 298 2016 -009 -00 | PLANT STATUS Cooper Nuclear Station was in Mode 1, Power Operations, at 100 percent power, at the time of the event. BACKGROUND The Control Room Emergency Filter System (CREFS) [EllS:JH] is designed to provide a radiologically controlled environment to ensure the habitability of the control room for the safety of control room operators under all plant conditions. The CREFS is a standby system. The instrumentation and controls for the CREFS automatically isolate the normal ventilation intake anq initiate action to pressurize the - main control room and filter incoming air to minimize the infiltration of radioactive material into the control room environment. The safety related function of CREFS includes a single high efficiency air filtration system for emergency treatment of outside supply air and a Control Room Envelope boundary that limits the inleakage of unfiltered air. The system consists of a prefilter, a high efficiency particulate air filter [EllS:FLT ], an activated charcoal adsorber [EllS:ADS] section, a supply fan [EllS:FAN], an emergency booster fan, an exhaust booster fan, and the associated ductwork [EllS:DUCT], valves [EllS:V] or dampers [EllS:DMP], doors [EllS:DR], barriers, and instrumentation. Technical Specifications (TS) 3.7.4 requires one supply fan to be Operable to support CREFS Operability. · EVENT DESCRIPTION On December 7, 2016, at 22:20 hours, a Control Room Operator (Operator) was performing the Division 1 Essential Control Building Ventilation functional test (surveillance procedure). The first step in the procedure directs the Operator to remove the non-essential control building Heating Ventilating Air Conditioning (HVAC) system from service per the operating procedure for the HVAC Control Building. This requires the Operator to place the standby control building supply fan to OFF (SF-C-1A-A or SF-C- 1A-B), then place the running control building supply fan to OFF (SF-C-1A-A or SF-C-1A-B). The Operator completed these steps correctly. The next steps are to place the control building recirculation fans RF-C-1A and RF-C-1 B to OFF; respectively. The Operator instead turned off the CREFS supply fan SF-C-1A rather than the control building recirculation fan RF-C-1A. Not aware of the error, the Operator proceeded to the next step to turn off RF-C-1 B. The Operator determined this step was complete when he noted the CREFS supply fan SF-C-1 B was already OFF; although this step directs that RF-C-1 B, control building recirculation fan be placed to OFF. NRC FORM 366 (06-2016) Page 3 of4 NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BYOMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. ,...... ...... ) \_ Reported lessons learned are incorporated into the licensing process and fed back to industry. Send {..~... "J LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to -.. ' (See Page 2 for required number of digits/characters for each block) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a (See NUREG-1022, R 3 for instruction and guidance for completing this form means used to impose an information collection does not display a currently valid OMB control http://www.nrc.gov/reading-rm/doc-rollections/nuregs/staff/sr1022/r3/) number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Cooper Nuclear Station 05000- 298 2016 -009 -00 NARRATIVE During the conduct of surveillance procedure for Division 1 Essential Control Building Ventilation, actions are completed to validate that the non-essential control building ventilation fans will not run while the essential control building ventilation system is running. This is accomplished by attempting to start the control building non-essential ventilation system supply fans and recirculation fans while the essential control building ventilation system is running and verifying that the non-essential fans do not start. The Operator is directed to place the switches for the control building recirculation fans in RUN to check that they do not start. However, during this event, the switches for the recirculation fans were already in RUN, as they were not correctly placed in OFF when the control building non-essential ventilation system was removed from service. The Operator noted these fans were in RUN and that the fans were not running, as displayed by the indicator lights. The Operator proceeded and completed the surveillance procedure and reported to the Control Room Supervisor (CRS) that the surveillance procedure was completed satisfactorily with no issues. Shortly after completion of the surveillance procedure, the CRS noted that the Control Room was becoming warmer and directed the Work Control Operator (WCO) to perform an independent review of the back panel controls that were manipulated during the conduct of the surveillance procedure. The WCO reported to the CRS that both CREFS supply fans were in OFF. The CRS verified the position of the CREFS supply fans and declared CREFS inoperable at 22:40 hours and entered TS Limiting Condition for Operation (LCO) 3.7.4. The CREFS supply fan SF-C-1A was placed in RUN at 22:47 hours, CREFS was declared operable, and the LCO exited. BASIS FOR REPORT This event is reportable in accordance with 10 CFR 50. 73(a)(2)(v)(D) as a condition that could have. prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. Event Notification 52416 was made to the Nuclear Regulatory Commission Operations Center. SAFETY SIGNIFICANCE This is a Safety System Functional Failure. The Safety Significance of this event is low. The CREFS was briefly out of service when the running . supply fan was turned OFF in error during performance of a Surveillance Procedure. CREFS was restored to service when the supply fan was turned on about 20 minutes after it was inadvertently secured. Both CREFS supply fans were available throughout the event. This event did not cause an impact to the safety of the general public, nuclear safety, industrial safety or radiological safety. NRC FORM 366 (06-2016) Page 4 of 4 NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BYOMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) ,.... Estimated burden per response to comply with this mandatory collection request: 80 hours. ...... )\_ Reported lessons learned are incorporated into the licensing process and fed back to industry. Send {~ J LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch ~..... (See Page 2 for required number of digits/characters for each block) (T-5 F53}, U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory (See NUREG-1022, R 3 for instruction and guidance for completing this form Affairs, NEOB-10202, (315~104}, Office of Management and Budgel, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Cooper Nuclear Station 05000- 298 2016 -009 -00 NARRATIVE CAUSE The root cause was attributed to human error. CORRECTIVE ACTIONS To prevent recurrence, applicable operations procedures will be revised to require peer checking during normal operations for all Control Room manipulations directed by these procedures. PREVIOUS EVENTS LER 2016-006-00 - On October 23, 2016, a high vibration on CREFS supply fan 'A' resulted in inoperability ar:id a loss of safety function. LER 2011-007-00 - On November 22, 2011, a drywell vacuum breaker was inadvertently opened when a rolling podium being used by a Control Room Operator made contact with the Master Control Switch for the Torus to Drywell Vacuum Breakers, resulting in a loss of safety function. A previous similar event involving the inadvertent contact of a switch in the Control Room occurred on August 27, 2011. A Gaitronics handset was dropped and contacted the "A" side Automatic Depressurization System (ADS) inhibit switch. This contact was sufficient to move the switch from the AUTO position to the INHIBIT position. The CRS was immediately informed and direction was given to place the switch back to AUTO. The "B" side of the ADS remained operable thus maintaining safety function of the ADS. NRC FORM 366 (06-2016) | ML17047A461
Oconee Nuclear Station | Unit 1 | Containment High Range Radiation Monitors Inoperable Due to Potential Thermally Induced Current Effects | 12-16-2016 | On October 25, 2016, the Containment High Range Radiation Monitorl> (CHRRMs) for each unit were declared inoperable as they could not meet the accuracy requirements of Regulatory Guide (RG) 1.97 for Type E post-accident monitoring (PAM) instrumentation. Oconee Nuclear Station (ONS) Engineering determined that a High Energy Line Break (HELB) in the East Penetration Room of each Unit could cause a false high reading on the CHRRMs RIA-57 and RIA-58 for that Unit. The false high reading would be due to the potential for Thermally Induced Currents (TIC) to affect the accuracy of the radiation monitor readings as discussed in NRC Information Notice 97-45, Supplement 1. ~ This condition existed for as long as the CHRRMs were installed with none of the actions required in Technical Specification (TS) 3.3.8 taken. Therefore the Completion Times of TS 3.3.8 were exceeded and the condition is reportable under 10 CFR 50.73(a)(2)(i)(B) as plant operation prohibited by Technical Specifications. ONS will review Fleet and Industry Operating Experience when determining the best path forward for restoring operability of the CH RR Ms. NRC FORM 366 (06-2016) NRC FORM 366A (06-2016) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES 10/31/2018 LICENSEE EVENT REPORT (LER) (See form 366 above for burden estimate) CONTINUATION SHEET 1. FACILITY NAME 2. DOCKET 6. LER NUMBER I I YEAR SEQUENTIAL REV Oconee Nuclear Station, Unit 1 05000269 , NUMBER NO. 2016 - 002 - 00 | BACKGROUND On February 17, 1998, the NRC issued Information Notice (IN) 97-45, Supplement 1, to alert licensees of . the potential of erratic indications from high-range radiation monitors as a result of a problem with the associated coaxial cables. The IN describes that these erratic indications could mislead operators assessing radiation levels in the containment building during accident scenarios. The erratic indications result from positive and negative current flow when detector cables are exposed to transient temperature conditions, such as those postulated during a loss-of-coolant accident or a main steamline break. This phenomenon is known as thermally induced current (TIC), and could result in false high radiation readings. At ONS, the aforementioned TIC issue is only a concern for a HELB in the East Penetration Room. It is worth noting that it is beyond the ONS design and licensing basis to postulate a HELB outside of containment that would result in an actual high containment radiation condition. · The physical configuration and arrangement of the CHRRMs [RIT] detectors are such that the detectors are located in modified electrical penetrations in the containment wall with the cables located in the East and West Penetration Rooms external to containment. As such, none of the detector cables are exposed to temperature transients resulting from events that occur within containment. Since these cables are not exposed to the temperature transients that could occur inside containment, there are no TIC concerns that coulq cause inaccurate CHRRMs indications during an event inside containment. The existing accuracy calculation for the CHRRMs determined that the CHRRMs meet the RG 1.97 accuracy requirements for Post-Accident Monitoring (PAM) instrumentation for events inside containment. Thus, RIA-57 and RIA-58 are fully able to meet their designated safety functions as defined by TS 3.3.8 and the UFSAR for events inside containment, including a Loss of Coolant Accident (LOCA). However, on October 25, 2016, it was determined that the CHRRMs were inoperable as they could not " meet the accuracy requirements of RG 1.97 for Type E PAM instrumentation during a HELB event in the East Penetration Room (outside containment). This condition has existed for as long as the CHRRMs were installed with none of the actions required in TS 3.3.8 taken. Therefore the Completion Times of TS 3.3.8 were exceeded and the condition is reportable under 10 CFR 50.73(a)(2)(i)(B) as plant operation prohibited by Technical Specifications. At the time this conditiori was identified, Oconee Units 1, 2, and 3 were all operating in Mode 1 at approximately 100% power. There were no structures, systems or components out of service at the time of this event that contributed to this event. No change in plant mode or reactor power occurred on any unit as a result of the conditions described within this report. I EVENT DESCRIPTION ONS Engineering determined that a HELB event in the East Penetration Room of each Unit could cause a false high reading on the CHRRMs for that Unit. The false high reading would be due to the potential TIC effects ~n the accuracy of the radiation monitor readings as discussed in IN 97-45, Supplement 1. On October 25, 2016, CHRRMs RIA-57 and RIA-58 were declared inoperable on all three ONS Units due to the aforementioned TIC effects. The TIC effect could cause the CHRRMs to experience spurious indication spikes. The indication spikes would likely result in exceeding the RG 1.97 accuracy requirements for these post-accident monitors during the temperature transient. This deficiency does not Page 2 of 4 | ML17048A520
Browns Ferry Nuclear Plant | Unit 2 | High Pressure Coolant Injection Safety System Functional Failure due to a Blown Fuse and a Failed Relay | 02-21-2017 | On June 17, 2016, while performing a High Pressure Coolant Injection (HPCI) Time Delay Relay Calibration surveillance, an abnormal indication of no voltage to the Time Delay Relay coil was received. The electricians backed out of the procedure and informed Operations. Later that day, upon performing procedure step 7.3[17], fuse BFN-2-FU2-073-0039B cleared and a HPCI Logic Power Failure alarm was received. The loss of logic power rendered Unit 2 HPCI system inoperable. The most likely cause of the blown fuse was an equipment ground induced by the TM200 timer used in the calibration procedure for timing pick-up of the time delay relays. While the HPCI Time Delay Relay calibration was being performed, there was already a known ground on Battery Board 2. The corrective action is to revise the calibration procedures to reconfigure the setup of the test equipment to reduce the probability and consequences of a ground induced by the test equipment. During troubleshooting of the blown fuse, relay 2-RL Y-073-23A-K43 was replaced. It was later identified during bench testing that this relay was faulty as the result of normal breakdown of the coil insulation over time. This breakdown was attributed to end-of-life failure. The immediate corrective action to address the relay failure was replacement of the relay. To address the end of life failure of this relay, a preventative maintenance (PM) task was created to replace this relay every 16 years. NRC FORM 366A (11-2015) Page 2of10 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send G._.t.•" 11•0..,("> comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 ~ g ° .., . ' .:: - :> .. - ., ~ . < . ~ : . . . , . . 01 i' : LICENSEE EVENT REPORT (LER) F ln 5 fo 3) c , o l U le . c S t . s . N R u e c s l o e u a r r c e R @ eg n u rc la .g to o r v y , C an o d m m to is th si e o n D , e W sk a O sh f i f n ic g e t r o , n O , f D fic C e 2 o 0 f 5 In 55 fo - r 0 m 00 a 1 tio , n o r a n b d y R in e t g e u rn la e t t o r e y - m Af a fa il irs to , l CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Browns Ferry Nuclear Plant, Unit 2 05000260 YEAR NUMBER NO. 2016 - 001 01 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Unit 2, was in Mode 1 at 100 percent power. II. Description of Events A. Event: On June 17, 2016, while performing High Pressure Coolant Injection (HPCI) [BJ] Time Delay Relay Calibration surveillance 2-SR-3.3.6.1.6(3), Electrical Maintenance personnel received an abnormal indication of no voltage to the coil [CL] of 2-RL Y-073-23A-K43 at step 7. 3(17] of the procedure. The electricians backed out of the procedure, informed Operations, and initiated Condition Report (CR) 1183105. Later that day, a different crew performed the remaining sections of 2-SR-3.3.6.1.6(3) successfully, then returned to section 7.3. Upon performing the procedure step 7.3[17], fuse [FU] BFN-2-FU2-073-0039B cleared and 2-XA-55-3F window 3, HPCI Logic Power Failure, alarmed in the Control Room. The fuse was replaced and the procedure was continued. This loss of logic power rendered Unit 2 HPCI inoperable. Basic troubleshooting was performed on the circuit to determine what, if any, component had failed, and no component failure was identified; however, relay [RL Y] 2-RL Y-073-23A-K43 was replaced, along with its base, 3500 ohm dropping resistor, and zener diode. On June 20, 2016 at 0455 Central Daylight Time (CDT), 2-SR-3.3.6.1.6(3) was completed satisfactorily, and Unit 2 HPCI was declared operable. The old relay and the TM200 timer were bench tested on June 29, 2016, and the relay did not function properly. The 3500 ohm dropping resistor and zener diode tested acceptably, and the relay coil resistance was normal, but the relay did not pull in the contacts. The TM200 timer operated properly during the testing. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event: There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML17052A038
Browns Ferry Nuclear Plant | Unit 1 | Signal Timer for 4kV Shutdown Board C Inoperable for Longer Than Allowed by Technical Specifications due to Detached Restraining Strap | 02-21-2017 | On December 21, 2016, at 1228 Central Standard Time (CST), during a performance of the 4KV Shutdown Board (SDBD) C Undervoltage and Time Delay Relay Calibration and Functional Test, personnel discovered a detached restraining strap on a 4kV SDBD C Degraded Voltage Relay Timer. At 1835 CST, Operations personnel declared the relay inoperable. The timer retaining strap was replaced, and the relay was declared operable on December 22, 2016, at 1251 CST. A Past Operability Evaluation determined that the timer was inoperable from October 5, 2016, until December 22, 2016, exceeding the Technical Specification allowed outage time. The most likely cause of this event was human error. Rounding of the screw attaching the retaining strap to the backplane of the electrical cabinet in which the timer was housed allowed the retaining strap to become detached. This deficiency was not corrected despite testing and Quality Control verification. Corrective Actions include replacing the retaining strap using a longer screw, identifying relays previously installed under similar plant modifications, and ensuring that work packages for future installation of relays with seismic retaining straps contain steps to obtain adequate screw engagement during strap installation. NRC FORM 366A (06-2016) Page 1 of 6 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Browns Ferry Nuclear Plant, Unit 1 05000-259 YEAR NUMBER NO. 2017 - 001 - 00 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Unit 1, was operating in Mode 1 at approximately 100 percent rated thermal power, and BFN, Unit 2, was operating in Mode 1 at approximately 99 percent power. II. Description of Event A. Event Summary: On December 21, 2016, at 1228 Central Standard Time (CST), during a performance of surveillance requirement (SR) O-SR-3.3.8.1.2(C), 4KV Shutdown Board [ECBD](SDBD) C Undervoltage and Time Delay Relay Calibration and Functional Test, Protective Relay Group personnel discovered a detached restraining strap on the 4kV SDBD C Degraded Voltage Relay [RLY][27][2] timer [TMR] BFN-0-02-211-0002C. At 1835 CST, Operations personnel declared 4kV SDBD C Degraded Voltage Relay timer inoperable and entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.3.8.1.A, with required actions to immediately verify by administrative means that the other two degraded voltage relay channels [CHA] and associated timers on the affected SD BDs are operable; and to place the degraded voltage relay channel in trip within fifteen days. The timer retaining strap was replaced, and the SDBD was declared operable on December 22, 2016, at 1251 CST. A Past Operability Evaluation (POE) determined that the relay was inoperable from October 5, 2016, until December 22, 2016, exceeding the TS allowed outage time. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event: There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. C. Dates and approximate times of occurrences: October 5, 2016 4kV SDBD C Degraded Voltage Relay installed under Work Order 118393397 December 21, 2016, Protective Relay Group discovered a detached restraining strap on the at 1228 CST 4kV SDBD C Degraded Voltage Relay timer. December 21, 2016, Operations personnel declared 4kV SDBD C Degraded Voltage Relay at 1835 CST inoperable and entered TS LCO 3.3.8.1.A. December 22, 2016, Operations personnel declared 4kV SDBD C Degraded Voltage Relay at 1251 CST operable and exited TS LCO 3.3.8.1.A. | ML17052A501
Cooper Nuclear Station 05000298 1of4 | Unknown Unit | Inadequate Compensatory Measures Results in a Condition Prohibited by Technical Specifications | 02-15-2017 | From July 11, 2016, to July 15, 2016, the Torus area and Reactor Building floor drain valve control switches were placed in the OPEN position, per alarm card FP-1/C-4, due to fire detector FP-TD-19-2 being impaired. Subsequently, it was determined that by placing the floor drain valve control switches to OPEN, the automatic flood protection function that is credited in Cooper Nuclear Station's internal flooding analysis, was defeated. During the time the detector was impaired, there were no credited compensatory actions taken to ensure Division 1 Core Spray (CS) and Division 1 Residual Heat Removal (RHR) systems were protected from postulated flooding caused by a high-energy line break. As such, it was determined that both Division 1 CS and Division 1 RHR were inoperable for a period greater than allowed by Technical Specifications. The cause was determined to be that when the flooding requirements in the Reactor Building changed, a review of alarm cards did not identify alarm card FP-1/C-4 as needing updated. Alarrri card FP-1/C-4 was revised to remove taking radwaste valves out of AUTO for each quad. In addition, the applicable procedure has been revised to ensure actions taken will ensure operability is maintained for environmentally qualified components in each of the Reactor Building quads; and a review of fire panel alarm cards will be performed for similar occurrences where monitoring is the only action taken. NRC FORM 366 (06-2016) Page 2of4 NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BYOMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-201,.5,,) . ..... Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send !~\ LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and lnfonmation Collections Branch '.~....I (See Page 2 for required number of digits/characters for each block) (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of lnfonmation and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a (See NUREG-1022, R 3 for instruction and guidance for completing this form means used to impose an infonmation collection does not display a currently valid OMB control http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) number, the NRC may not conduct or sponsor, and a person is not required to respond to, the infonmation collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Cooper Nuclear Station 05000- 298 2016 -010 -00 | PLANT STATUS Cooper Nuclear Station was in Mode 1, Power Operations, at 100 percent power, at the time of the event. BACKGROUND The Emergency Core Cooling System (ECCS) is designed, in conjunction with the primary and secondary containment, to limit the release of radioactive materials to the environment following a loss of coolant accident (LOCA). The ECCS uses two independent methods (flooding and spraying) to ·cool the core. during a LOCA. The ECCS network consists of the High Pressure Cooling Injection (HPCI) System [EllS:BJ], the Core Spray (CS) System [EllS:BM], the Low Pressure Coolant Injection (LPCl):mode of the Residual Heat Removal (RHR) System [EllS:BO], and the Automatic Depressurization System (ADS). The suppression pool provides the required source of water for the ECCS. The emergency condensate storage tanks (ECSTs) are capable of providing a source of water for the HPCI system. ECCS components located in the four Reactor Building [EllS:NG] quads are subject to flooding from line breaks such as the steam tunnel feedwater line break. The Technical Specifications (TS) related equipment contained in these quads are: Division 1 CS and Reactor Core Isolation Cooling [EllS:BN] in . ' -•.t t- the Northeast quad; Division 1 RHR in the Northwest quad; Division 2 CS in the Southeast quad, and Division 2 RHR and HPCI in the Southwest quad. Division 2 CS is assumed and evaluated as.lost during the 18-inch feedwater flooding event, .:· The Reactor Building floor drain and Torus drain valves [EllS:V] are designed to close on respective sump hi-hi level conditions to divert water to the Torus area. The Reactor Building floor drain and the Torus drain valve closure are barriers credited in the internal flooding analysis. FP-TD-19-2 causes the following valves to fail closed: RW-AOV-A0767, Torus Drain to Sump A RW-AOV-A0770, Reactor Building Drains to Sump A RW-AOV-A0768, Torus Drain to Sump B RW-AOV-A0771, Reactor Building Drains to Sump B RW-AOV-A0773, Reactor Building Drains to Sump C RW-AOV-A0772, Reactor Building Drains to Sump D EVENT DESCRIPTION On July 11, 2016, at 1430 hours, while performing fire detection systems examination per surveillance procedure, it was identified that detector FP-TD-19-2 would not reset, thus initiating alarm FP-1/C-4, Reactor Building Southeast Quad Zone 19. Per the alarm card, if no fire is detected, and the detectors cannot be reset, the Operator is to place the floor drain valve control switches to OPEN and periodically NRC FORM 366 (06-2016) Page 3 of 4 NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BYOMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) ,..... ...... Estimated burden per response to comply with this mandatory collection request: 80 hours. )\_ Reported lessons learned are incorporated into the licensing process and fed back to industry. Send f ~ ~ LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch i.~....) (See Page 2 for required number of digits/characters for each block) (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a (See NUREG-1022, R 3 for instruction and guidance for completing this fonm means used to impose an information collection does not display a currently valid OMB control http://www.nrc.gov/reading-nm/doc-collections/nuregs/staff/sr1022/r3/) number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Cooper Nuclear Station 05000- 298 2016 -010 -00 NARRATIVE monitor sump levels. As such, Operations placed the Torus area and Reactor Building floor drain valve control switches in the OPEN position and commenced hourly checks of the Reactor Building floor drain sump levels for unusual changes. Detector FP-TD-19-2 was replaced, post work testing completed satisfactory, and the detector was declared unimpaired on July 15, 2016, at 14:32 hours. Additionally, the control switches for the applicable valves were placed to AUTO. It was subsequently determined that by placing the drain valve control switches to OPEN, the automatic flood protection function that is credited in CNS' internal flooding analysis, was defeated. During the time the detector was impaired, there were no compensatory actions taken to ensure Division 1 ·•, CS and Division 1 RHR systems were protected from postulated flooding caused by a high::energy line , break. As such, it was determined that both Division 1 CS and Division 1 RHR were inoperable for a ·,:i. period greater than allowed by TS 3.5.1, Condition H. · BASIS FOR REPORT This event is reportable in accordance with 10 CFR 50. 73(a)(2)(i)(B) as any operation or condition which . .. was prohibited by the plant's Technical Specifications, and also in accordance with 10~CFR 50. 73(a)(2)(ix)(A) as any event or condition that as a result of a single cause could have prever:ited the fulfillment of a safety function for two or more trains or channels that are needed to remove residual heat. SAFETY SIGNIFICANCE The safety significance of this event is low. The Division 1 CS and Division 1 RHR Systems were inoperable for approximately 4 days. In the case of postulated flooding caused by a main feedwater break, Division 2 RHR system and the ADS were available to mitigate the event. This event did not cause an impact to the safety of the general public, nuclear safety, industrial safety, or radiological safety. CAUSE The apparent cause was determined to be that when the flooding requirements in the Reactor Building changed, a review of alarm cards did not identify alarm card FP-1/C-4 as needing updated. NRC FORM 366 (06-2016) Page 4 of 4 NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BYOMB: NO. 3150-0104 EXPIRES: 10/31/2018 (11-2015) Estimated burden per response to comply with this mandatory collection request: 80 hours. . . Reported lessons learned are incorporated into the licensing process and fed bock to industJy. Send !¥~ LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch '-: .... .:.r (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 2055!>-0001, or by e-mail to (See Page 2 for required number of digits/characters for each block) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a (See NUREG-1022, R 3 for instruction and guidance for completing this form means used to impose an information collection does not display a currently valid OMB control http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Cooper Nuclear Station 05000- 298 2016 -010 -00 NARRATIVE CORRECTIVE ACTIONS Alarm card FP-1/C-4 was revised to remove taking radwaste valves out of AUTO for each quad. In addition, the applicable procedure has been revised to ensure actions taken will ensure operability is maintained for environmentally qualified components in each of the Reactor Building quads; and a review of fire panel alarm cards will be performed for similar occurrences where monitoring is the only action taken. PREVIOUS EVENTS There have been no recent reportable events related to inadequate internal flooding protection', compensatory measures. NRC FORM 366 (06-2016) | ML17054C825
Perry Nuclear Power Plant 05000 440 1 OF 4 | Unknown Unit | : | 02-24-2017 | On December 28, 2016, at 2119 hours (EST), standby liquid control (SLC) subsystem A was declared inoperable in accordance with the surveillance instruction for performance of a routine surveillance test. At 2229 hours, control room operators received an out-of-service alarm for SLC discharge valve B. With both subsystems inoperable, the SLC system was in a condition that required reporting under 10 CFR 50.72(b)(3)(v)(A) and 10 CFR 50.72(b}(3)(v)(D). At 2335 hours, the surveillance was completed and subsystem A was declared operable. The cause for subsystem B inoperability was an indicated loss of continuity to one of the two firing circuits in the discharge valve due to a loose connection between a pin and jack on the connector. This was not a safety system functional failure since continuity was interrupted to only one of the two redundant firing circuits for discharge valve B and if an initiation signal was sent to the valve, it would have operated as designed and supported chemical injection to the vessel. The risk of this event is considered small in accordance with the regulatory guidance. The power supply cable was replaced and post maintenance testing was completed satisfactorily. The preventative maintenance task will be revised to include a step to inspect connection pins and jacks when changing the firing assembly. Additionally, the cable on the discharge valve for SLC subsystem A will be replaced and sent to FirstEnergy BETA Laboratory for analysis when the valve is replaced during the next refueling outage. The analysis will be used to determine if a new preventative maintenance task is necessary for periodic replacement of these cables. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/3112018 (11-2015) ....... .,.., Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments . LICENSEE EVENT REPORT (LER) l~.\ regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 ; ~ " '· . r ,, - ,.. J CONTINUATION SHEET F ln 5 fo 3 c ), o lle U c .S ts . .R N es u o c u le r a ce r @ R n e r g c u .g la o t v o , r y a nd C o to m t m he is s D io e n sk , O W ff a ic s e h r, in O gt f o fi n ce , o D f C In fo 2 r 0 m 5 a 5 t 5 io -0 n 0 a 0 n 1 d , R o e r g u b la y tor e y - m A a ff i a l irs to , ·••*"' NEOB-10202, (3150-0t04), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currenUy valid OMB control number, the http://www.n r e.g ov/readi ng-rm/d oc-collections/n ur egs/staff/sr1 022/r3/ NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Perry Nuclear Power Plant 05000 - 440 NUMBER NO. 2016 004 00 | Energy Industry Identification System (EllS) codes are identified in the text as [XX]. INTRODUCTION On December 28, 2016, at 2229 hours (EST), both standby liquid control (SLC) [BR] subsystems were declared inoperable due to performance of a surveillance test on subsystem A and the indicated loss of continuity to a firing circuit on the discharge valve for subsystem 8. With both subsystems having been declared inoperable, this was determined to be a reportable event under 10 CFR 50.72(b)(3)(v)(A) and 10 CFR 50.72(b)(3)(v)(D) for an event or condition that that could have prevented the fulfillment of the safety function of structures or systems that are needed to shut down the reactor and maintain it in a safe shutdown condition and mitigate the consequences of an accident. As such, an event notification was made to the NRC Operations Center and recorded under Event Number 52468. This event is being reported in accordance with 10 CFR 50. 73(a)(2)(v)(A) and 10 CFR 50. 73(a)(2)(v)(D), which requires reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to shut down the reactor and maintain it in a safe shutdown condition and mitigate the consequences of an accident. This was not a safety system functional failure since discharge valve B would have operated as designed and supported chemical injection to the vessel. DESCRIPTION OF EVENT On December 28, 2016, at 2119 hours, with the plant in mode 1 at 98 percent power, SLC subsystem A was declared inoperable for performance of a routine surveillance test. Technical Specification (TS) Limiting Condition for Operation (LCO) 3.1. 7, Action A was entered, which required restoring the single subsystem to operable status within 7 days. On December 28, 2016, at 2229 hours, the control room received an out-of-service alarm for SLC subsystem B directly after pump A was started in accordance with the surveillance instruction. Control room operators verified this alarm to be due to an indicated loss of continuity to discharge valve B, as read on a control room indicator. At 2229 hours, SLC subsystem B was declared inoperable and TS LCO 3.1.7, Action B was entered, which required restoring one SLC subsystem to operable status within 8 hours. With both subsystems declared inoperable, the SLC system was in a condition that rendered it unable to fulfill its safety function. On December 28, 2016, at 2257 hours, pump A was stopped in accordance with the surveillance instruction and at 2302 hours, the SLC B out-of-service alarm reset. Following performance of the surveillance test at 2335 hours, SLC subsystem A was declared operable and TS LCO 3.1. 7, Action B was exited. Troubleshooting determined that the cause for SLC subsystem B inoperability was an indicated loss of continuity to one of the two firing circuits in the discharge valve. On December 29, 2016, at 1708 hours, SLC subsystem B was declared operable and TS LCO 3.1.7, Action A was exited after repairs were completed. CAUSE OF EVENT Continuity was interrupted by a high resistance in a connector to one of the two firing circuits for discharge valve B. This brought in the alarm as expected for this condition and also reduced the available firing circuits | ML17055C355
Comanche Peak Nuclear Power Plant 05000 445 1 OF 6 | Unknown Unit | Unanalyzed Condition Involving Potential Moderate Energy Line Break | 02-22-2017 | On September 13, 2016, and September 14, 2016, during plant walk downs by Engineering and the NRC Senior Resident inspector, pressurized fire protection piping in the Service Water Intake Structure was found to not be shielded against a Moderate Energy Line Break (MELB), resulting in inoperability of one train of Service Water for both units. I During extent of condition walk downs conducted on October 6, 2016, October 10, 2016, November 17, 2016, December 5, 2016, and December 22, 2016, additional piping in the Unit 1 and Unit 2 Safeguards and Auxiliary Buildings was found to not be shielded against a MELB, resulting in inoperability of one train of various .safety related equipment for both units. The most likely cause of this event was the methodology used to conduct the initial MELB walk downs was flawed a,id allowed some MELB threats to be missed. Corrective actions include shielding the affected piping, performing a 100 percent walk down of rooms containing MELB piping identified for shielding, and revising the systems interaction program maintenance procedure. I All times in this report are approximate and Central Time unless noted otherwise. ~· NRC FORM 366 (06-2016) NRC F , O ,. R - M . . 3 , 6 6A ·U.S. NUCLEAR REGULATORY COMMISslON APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/3112018 (06-20161 Eslinallld burden per response to comply v.ilh lhb mandatory colJedlon request 80 houtS. Repa1ed iessOnS learned are inalrporaled into lhe licensing process and fed back to lndusby. Send \¥) LICENSEE EVENT REPORT (LER) convnents regarding burden estimale to lhe FOIA, Privaey and lnfonnalian Collections Branch (T-5 ..... CONTINUATION SHEET. F53), u.s: Nuclear Regulatory Commission. Washinglon, DC 2055&-0001, or by IHTlai to lnfocolleds.R~, and to Ile Desk Otlicer, Oftice ol lnlormallon and Ragulatory Affail1, NE00-10202, {3150-0104), Offtce ol Management end Budge~ Washington, DC 20503. U a means {See NUREG-1022, R.3 for ins!n.lction and guidance for completing this form used to impose an infonnation coll8cllon does not display a cummlly valil OMB coll1JOI number. lhe httjrlfwww.nrc.®vlreading-rmldoc-co!JectloostnuregsJstatfisrl022/QD NRC may not conduct or sponsor, and a person is not required lo respond to, Iha lnlonnation coleclion- 1. FACILITY NAME . 2. DOCKET NUMBER 3. LER NUMBER r-Y:E:A-R1 SEQUENTIAL REV 05000-1 Comanche Peak Nuclear Power Plant · 445 I NUMBER 1-NO0. ~-I 002 | I. DESCRIPTION OF THE REPORTABLE EVENT A. REPORTABLE EVENT CLASSIFICATION: 10CFR50.73(a)(2)(i)(B), ~Any operation or condition which was prohibited by the plant's Technical Specifications," 10CFR50.73(a)(2Xii)(B), "The nudear power plant being in an unanalyzed condition," 10CFR50.73(a)(2)(v), "Any event or condition that could have prevented the fulfillment of a safety function," 10CFR50.73(a)(2)(vll), "Any event where a single cause or condition caused at least one independent train or channel to become inoperable in multiple systems or two independent trains oi'channels to become inoperable in a single system," and 10CFR50.73(a)(2)(ix)(A), "Any event or condition that as a result of a single cause could have prevented the fulfillment of a safety function for two or more trains or channels in different systems.~ I B. PLANT CONDITION PRIOR TO EVENT: On September 13, 2016, September 14, 2016, Oct9ber 6, 2016, October 10, 2016, November 17, 2016, December 5, 2016, and December 22, 2016, CPNPP Units 1and2 were in Mode 1 operating at 100% power. C. STATUS OF STRUCTURES, SYSTEMS, OR COMPONENTS THAT WERE INOPERABLE AT THE START OF THE EVENT AND THAT CONTRIBUTED TO THE EVENT There were no inoperable structures, systems, or components at the start of the event that contributed to the event. D~ NARRATIVE SUMMARY. OF THE EVENT, INCLUDING DATES AND APPROXIMATE TIMES: At 1730 on September 13, 2016, during a plant walk down with the NRC Senior Resident inspector, a vertical section of I pressurized fire protection pipe [EllS:(KP)(PSP)] In the Service Water Intake Structure (SWIS) was found to not be shielded against a Moderate Energy Line Break (MELB). In the event of a MELB crack along any portion of the unshielded portion of pipe, the MELB had a potential Impact to the function of any one of the 4 Service Water (SW) pumps, but only one train would have been affected during the event. This Is due to physical configuration/separation relative to the source line and target pumps and/or associated Motor Control Centers (MCCs) that support pump operation. ·Upon discovery of this condition, SW Train B and Emergency Diesel Generator (EDG) Train B on each Unit was declared Inoperable .per Technical Specifications (TS). NRC Event Report 52239 reported this as an unanalyzed condition per 10CFR50;72(b)(3)(ii)(B). At the time of discovery, all four Service Water trains were operable, therefore, this condition was not reportable as a loss of safety function per 10CFR50.72(b)(3)(v). At 2233 on September 13, 2016, the affected fire protection pipe was isolated and SW Train Band EOG Train Bon each Unit were declared operable. On September 14, 2016, the NRC Senior Resident Inspector identified an additional section of fire protection piping that was not adequately shielded for a MELB. On September 16, 2016, the required MELB shielding was installed on affected fire protection piping in the SWIS. Since the SW trains have been periodically declared inoperable at various times in the last three years for surveillance testing or maintenance, given the MELB condition, two SW trains could have been Inoperable and this is reportable per 10CFR50.73(a)(2)(i)(B), 10CFR50.73(a)(2)(ii)(B), 1OCFR50.73(a)(2)(v), 1O CFR50.73(a)(2)(vl1), and 1OCFR50.73(a)(2)(ix)(A). At 1410 on October 6, 2016, during extent of condition walk downs, a section of eyewash station pipe [EllS:(KC)(PSP)] in the Unit 2 Safeguai"ds (SG) Building was identified that was not adequately shielded for a MELB. In the event of a MELB crack along any portion of this unshielded pipe, the MELB had the potential to Impact Unit 2 Train B 480V MCC 2EB2-1. | ML17062A302
Watts Bar Nuclear Plant | Unit 1 | lnadequate Operability Determination Leads to a Condition Prohibited by the Technical Specifications | 03-03-2017 | 12. LICENSEE CONTACT FOR THIS LER LICENSEE CONTACT TELEPHONE NUMBER (lnclude Area Code) Dean Baker, Licensing Engineer 423-452-4589 13. COMPLETE ONE LINE FOR EACH COMPONENT FAILURE DESCRIBED IN THIS REPORT cAUSE I svsren,r IcorueoNENrlr^t+U[- l*t?3T#" CAUSE SYSTEM I COIIIIPONENT FA M C A TU N R U E - R I I REP T O O R E T P A I B X LE BIgIIFCVITPGIY 14. SUPPLEMENTAL REPORT EXPECTED 15. EXPECTED MONTHI Ony I yenn x E vf S (tf yes, comptete 15.EX PECTED SUBMISS/O/V DATE) NO SUBMISSION DATE ABSTMCT (Limittol400spaces,i.e.,approximatelylssingte-spacedtypewrittentines) On January 4,2017 at 1010 Eastern Standard Time (EST), Watts Bar Nuclear Plant Operations personnel declared Essential Raw Cooling Water (ERCW) strainer flush valve 2-FCV-67-9B inoperable due to having a through-wall leak. The valve was replaced and the ERCW strainer was returned to service on January 5,201T at O0SZ ESt. This event is reportable because the valve had had a through-wall leak since January 31,2016 and had not been declared inoperable. With a through-wall leak, a flaw evaluation is required to be performed to demonstrate the through-wall leak was stable. The failure to perform an adequate operability evaluation allowed the valve to remain in service for a period of time longer than allowed by Technical Specification (TS) 3.7.8, Essential Raw Cooling Water, Limiting Condition for Operation (LCO) Condition A. This represents a condition prohibited by the TS. Subsequent anJtysis of the valve demonstrated that it remained structurally sound with the leak, and would not have impacted tne operibility of the ERCW system. The cause of the failure to perform an adequate operability evaluation has been determined to be human performance errors on the part of both operations and engineering personnel. Additional training of operations and engineering personnel is planned as corrective action to address the potential for recurrence of this issue. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO.3150-0104 EXPIRES: 10tiit201} (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry, Send commenB regarding burden estimate to the FOIA, Privacy and lnformation Collections Branch (T-5 LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to lnfocollecb.Resource@nrc.gov, and to the Desk 0fficer, ffice of lnbrmation and Regulatory Afiairs, CONTINUATION SHEET NE0B-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503, lf a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection, 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Watts Bar Nuclear Plant, Unit 05000390 YEAR NUMBER NO. 1 - -00 2017 003 | I. PLANT OPERATING CONDITIONS BEFORE THE EVENT Watts Bar Nuclear Plant (WBN) Units 1 and were at 100 percent rated thermal power (RTP) il. DESCRIPTION OF EVENT A. Event Summary On January 4,2017 at 1010 Eastern Standard Time (EST), Wafts Bar Nuclear Plant Operations personnel declared Essential Raw Cooling Water (ERCW) (EllS:Bl) strainer flush valve 2-FCV-67- 98 {EllS:FCV} inoperable due to having a through-wall leak. The valve was replaced and the ERCW was returned to service on January 5,2017 at 0952 EST. This event is reportable because the valve had had a through-wall leak since January 31,2016 and had not been declared inoperable. A flaw evaluation is required in this situation to demonstrate the through-wall leak was stable and would not become worse. The failure to perform an adequate operability evaluation allowed the valve to remain in service for a period of time longer than allowed by Technical Specification (TS) 3.7.8, Essential Raw Cooling Water, Limiting Condition for Operation (LCO), Condition A. This event is being reported to the Nuclear Regulatory Commission (NRC) under 10 CFR 50.73(aX2)(i)(B) as a condition prohibited by Technicat Specifications. lnoperable Structures, Components, or Systems that Contributed to the Event No additional inoperable systems or components beyond the one identified valve contributed to this report. C. Dates and Approximate Times of Occurrences Date Time Event 1t31t2016 Condition Report (CR) 1131468 documents a through-wall leak in the body of 2-FCV-67-98. 1t04t2017 1010 Technical Requirement 3 .4.5 Piping System Structural lntegrity determined not met tor 2-FCV-67-98. ERCW TS LCo 3 .T.a Condition A entered. 1t05t2017 0930 Work Order 117564121 completed to replace valve 2-FCV-67-98. 1t05t2017 0952 ERCW TS LCO 3.7.8 Condition A exited. D. Manufacturer and Model Number of Components that Failed During the Event The leaking valve was a four inch 150 pound class carbon steel ball valve provided by Energy Products Group with a rated operating pressure of 200 psig. ge2 of e 5 | ML17065A019
Fermi 2 05000 341 1 OF 4 | Unknown Unit | Loss of Reactor Protection System Scram Function During Main Steam Isolation Valve and Turbine Stop Valve Channel Functional Tests due to Use of a Test Box | 03-06-2017 | On January 6, 2017 an Operations Shift Engineer determined that use of the Reactor Protection System (RPS) test box described in station procedures would result in the loss of two RPS reactor scram functions. Technical Specification (TS) 3.3.1.1 requires that RPS instrumentation for Table 3.3.1.1-1 Function 5 for Main Steam Isolation Valves (MSIVs) and Table 3.3.1.1-1 Function 9 for Turbine Stop Valves (TSV) remain OPERABLE. Operations procedures were revised to incorporate the use of the test box in August of 2016. Between September 22 and 23, 2016 the MSIV and TSV procedures were each performed one time using the test box. The failure to recognize the impact of the procedure revisions is considered a human performance error by engineering and operations personnel. The procedures were corrected in January 2017 to remove the use of the RPS test box. Subsequently, on January 7 and 9, 2017, respectively, the procedures for the TSVs and the MSIVs were performed successfully. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 10/3112018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 CONTINUATION SHEET F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CS Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the tt r r do collections/nuregsstaff/Fsr1022/r3 NRC may not conduct or sponsor, and a person is not required to respond to, the information collection, 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000- NUMBER NO. Fermi2 341 207-L00 - 0 | INITIAL PLANT CONDITIONS Mode - 1 Reactor Power - 100 percent There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT On January 6, 2017 an Operations Shift Engineer (i.e. a Licensed Operator) determined that use of the Reactor Protection System (RPS) [JC] test box [IIS] in procedures 24.137.0.1 "Main Steam Line Isolation Channel Functional Test" and 24.110.05, "Turbine Control and Stop Valve Functional Test" would result in the loss of RPS reactor scram functions. Technical Specification (TS) 3.3.1.1 requires that RPS instrumentation for Table 3.3.1.1-1 Function 5 "Main Steam Isolation Valve - Closure" for Main Steam Isolation Valves (MSIVs) [ISV] and Table 3.3.1.1-1 Function 9 "Turbine Stop Valve - Closure" for Turbine Stop Valves (TSV) [ISV] remain OPERABLE. Both Operations procedures were revised to incorporate the use of a test box in August of 2016. Implementation of the test box was intended to reduce unnecessary RPS actuations by eliminating the half scram created during previous test procedure performances. Between September 22 and 23, 2016, the MSIV and TSV procedures were each performed one time using the test box. The performance of the MSIV and TSV procedures using the test box caused the loss of the RPS trip functions by bypassing more than the TS minimum allowed inputs per trip channel to maintain trip function operability. The unintended loss of RPS trip functions during these tests resulted in a NRC reportable condition under 10CFR50.73(a) (2)(v) as "any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: 10CFR50.73(a)(2)(v)(A) shutdown the reactor and maintain it in a safe shutdown condition," and 10CFR50.73(a)(2)(v)(D) "Mitigate the consequences of an accident." The error in the procedures was self-identified by the Operations Shift Engineer during a procedure review on January 6, 2017. The procedures were corrected reinstating the previous method of testing such that the test box was no longer used. Subsequently, on January 7 and 9, 2017, respectively, the procedures for the TSVs and the MSIVs were performed successfully. SIGNIFICANT SAFETY CONSEQUENCES AND IMPLICATIONS The test box was designed to reduce unnecessary RPS actuations. The test box consists of a 3-ohm resistor in parallel with a 5 VAC lamp terminated with banana jacks. The RPS test box is a low resistance path in parallel with the trip logic relay contacts. The RPS initiates a reactor scram when at least one MSIV in 3 of 4 Main Steam Lines (MSLs) close (Function 5) or when 3 of 4 TSVs close (Function 9). The automatic MSIV and TSV closure reactor scrams preserve the integrity of the fuel cladding and the Reactor Coolant System (RCS) in anticipation of the transients caused by closure of these valves. | ML17065A226
Clinton Power Station | Unit 1 | Failure to Complete Technical Specification Required Actions within the Completion Time Resulted in a Condition Prohibited by Technical Specifications | 03-06-2017 | On October 14, 2016, Clinton Power Station (CPS) determined subsequent to the 3rd Quarter NRC Exit Meeting that a condition prohibited by Technical Specification (TS) 3.7.6, "Main Turbine Bypass System," had occurred associated with a failure to complete a TS Required Action within the associated Completion Time. Specifically, testing of Main Steam Turbine Bypass Valve (TBV) Numbers 4, 5, and 6 was not performed within the required test interval and the TBVs were appropriately declared inoperable as required by TS Surveillance Requirement .(SR) 3.d.1. Thermal Limit penalties were applied as required by Limiting Condition tor Operation (LCO) 3.7.6. A Surveillance Frequency Change was processed in accordance with TS Program 5.5.16, "Surveillance Frequency Control Program," in June 2016 to change the Frequency tor SR 3.7.6.1 from 31 days to 12 months. TBVs 5 and 6 were subsequently declared OPERABLE and the thermal limit penalties removed without performing the required SR 3.7.6.1, contrary to TS SR 3.0.1 Bases. The apparent cause of this event was determined to be that no specific requirement exists in either plant procedures or industry guidance which prohibits declaring a component or system OPERABLE based solely on an extension of the required surveillance test interval. Corrective actions include testing the valves with an alternate method and completing administrative procedure changes. This event is reportable under 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarcing burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 LICENSEE EVENT REPORT (LEA) F53), U.S. Nuclear Reg~atory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washing1on, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV Clinton Power Station, Unit 1 05000461 YEAR NUMBER NO. 2016 - 010 - 01 | PLANT AND SYSTEM IDENTIFICATION General Electric-Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX] EVENT IDENTIFICATION Failure to Complete Technical Specification Required Actions within the Completion Time Resulted in a Condition Prohibited by Technical Specifications· A. Plant Operating Conditions before the Event Unit: 1 Event Date: 10/14/16 Event Time: 0830 Mode: 1 Mode Name: P?wer Operation Reactor Power: 99 percent B. DESCRIPTION OF EVENT · On October 14, 2016, Clinton Power Station (CPS) det~rmined subsequent to the 3rd Quarter I NRC Exit Meeting that a condition prohibited by Technical Specification {TS) 3.7.6, "Main Turbine ·Bypass System,'' had occurred associated with a failure to complete a TS Required Action within the associated Completion Time. Specifically, on June 6, 2016, the TS Limiting Condition for Operations (LCO) Surveillance Requirement (SR) 3.0.2 grace period of 1.25 times the normal required Frequency (31 days) for completing testing of the Main Steam Bypass Valves per SR 3.7.6.1 was exceeded for the Main Turbine Bypass System. Turbine Bypass Valves (TBV) 4, 5, and 6 were not tested within the required Frequency and the valves were declared inoperable as required by TS SR 3.0.1.Thermal Limit penalties were applied as required by LCO 3. 7.6. On July 7, 2016, a Surveillance Frequency Ch?nge was processed in accordance with TS Program 5.5.16, "Surveillance Frequency Control Program," for TS SR 3.7.6.1 to change the required Frequency from 31 days to 12 months. The last performance credit date of the TBV test was April 28, 2016. This new revision changed the due date for testing the TBVs to April 28, 2017. With TBV testing performed within the new required interval, the valves were declared OPERABLE and the Thermal Limit penalties removed without performing the required SR 3.7.6.1. It was subsequently determined, however, that in accordance with TS SR 3.0.1 Bases, the Surveillance had to be met and performed in accordance with SR 3.0.2 prior to returning equipment to OPERABLE status. The failure to perform the TS SR within the test interval without applying the Actions of TS 3.7.6 . was a condition prohibited by TS. | ML17067A413
Susquehanna Steam Electric Station | Unit 1 | Secondary Containment Breach Due to Simultaneous Opening of Airlock Doors | 00-08-2017 | On January 17, 2017 at approximately 11:45, three employees with a group of visitors were exiting the Unit 1 Reactor Building Airlock on Elevation 676'. While processing through the card reader, an individual in the group opened the Turbine Building airlock door prior to the Reactor Building airlock door being completely closed. This resulted in not meeting Technical Specification 3.6.4.1 Surveillance Requirement 3.6.4.1.3, which requires that one secondary containment access door in each access opening is closed. The cause of this event was determined to be less than adequate use of Human Performance Tools, including Self-Checking/ Stop, Think, Act and Review (STAR). This condition requires reporting in accordance with 10 CFR 50.73(a)(2)(v)(C) as having both Secondary Containment airlock doors momentarily open simultaneously results in a condition that could have prevented fulfillment of a safety function. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366A (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail CONTINUATION SHEET to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a (See NUREG-10 22, R.3 for instruction and guidance for completing this form means used to impose an information collection does not display a currently valid OMB control http:l/vvww.nrc.gov/readinq-rm/doc-collections/nuregs/staff/sr1 022/r3/) number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER I YEAR I SEQUENTIAL REV Susquehanna Steam Electric Station 05000387 NUMBER NO. Unit 1 2017 -001 -00 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, approximately 100 percent Rated Thermal Power Unit 2 - Mode 1, approximately 100 percent Rated Thermal Power There were no systems, structures or components that were inoperable at the start of the event and contributed to the event. EVENT DESCRIPTION On January 17, 2017 at approximately 11:45, three employees with a group of visitors were exiting the Unit 1 Reactor Building [EllS Component Identifier: AL] Airlock [EllS Component Identifier: DR] on Elevation 676'. While processing through the card reader, an individual in the group opened the Turbine Building [EllS Component Identifier: NM] airlock door prior to the Reactor Building airlock door being completely closed. Upon hearing the alarm, security, who was present to help process visitors through the card reader, notified Security Control and the Shift Manager. All personnel then provided statements with respect to the event. CAUSE OF EVENT The cause of the event was determined to be less than adequate use of Human Performance Tools including Self-Check (STAR). ANALYSIS/SAFETY SIGNIFICANCE Technical Specification 3.6.4.1 Surveillance Requirement 3.6.4.1.3 requires that one secondary containment access door in each access opening is closed. This event is being reported pursuant to 10 CFR 50.73(a)(2)(v)(C) as having both Secondary Containment airlock doors momentarily open simultaneously results in a condition that could have prevented fulfillment of a safety function to mitigate the consequences of an accident by controlling the release of radioactive material. There was no actual safety consequence as a result of this event. Engineering analysis of this event has determined that secondary containment could have performed its safety function of isolating, as assumed in the accident analysis, and also of re-establishing 0.25 in w.g. vacuum (drawdown) within the assumed accident analysis time (1 0 minutes). Therefore, the subject event did not cause a loss of safety function. This event will not be counted as a safety system functional failure (SSFF) for the NRC performance indicator based on the Engineering analysis supporting the system's ability to fulfill the safety function. CORRECTIVE ACTIONS Key corrective actions include the following: 1. Coaching was provided to the individuals involved with respect to the use of airlock doors (Complete). | ML17067A475
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Vent Line Socket Weld Failure | 03-13-2017 | Refueling Outage 22 commenced on January 14, 2017 at James A. FitzPatrick Nuclear Power Plant (JAF). With the plant in Mode 2 at 0613, the initial Drywell inspection identified a through wall leak on the ¾ inch vent line off of the bonnet of the motor operated gate valve on the suction side of Reactor Water Recirculation Pump ‘A’. This condition was determined to constitute Reactor Coolant Pressure Boundary (RCPB) leakage, which is prohibited by Technical Specification (TS) Limiting Condition for Operation (LCO) 3.4.4. The average reactor coolant temperature decreased to less than 212 degrees F and the plant was in Mode 4 at 1530 of the same day, which is within the applicable TS LCO 3.4.4 required completion time. The condition of a through wall leak on the RCPB is reportable pursuant to 10 CFR 50.73(a)(2)(ii), as a condition of the nuclear plant, including its principle safety barriers, being seriously degraded. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 – 333 NUMBER N0. 2017 – 001 – 00 | Background The Reactor Water Recirculation (RWR) System [EIIS identifier: AD] is designed to provide forced coolant flow through the core to remove heat from the fuel. The forced coolant flow removes more heat from the fuel than would be possible with just natural circulation. The forced flow, therefore, allows operation at significantly higher power than would otherwise be possible. The recirculation system also controls reactivity over a wide span of reactor power by varying the recirculation flow rate to control the void content of the moderator. The Reactor Water Recirculation System consists of two recirculation pump loops external to the reactor vessel. These loops provide the piping path for the driving flow of water to the reactor vessel jet pumps. Each external loop contains one variable speed motor driven recirculation pump, driven by a motor generator (MG) set to control pump speed, and associated piping, jet pumps, valves, and instrumentation. Motor operated gate valves on the suction and discharge sides of each recirculation pump serve as isolation valves for the pumps. A ¾” stainless steel line coming from the bonnet section of each valve provides a vent line for the valves. The recirculation loops are part of the Reactor Coolant Pressure Boundary (RCPB) and are located inside the drywell structure. The Reactor Coolant System (RCS) includes systems and components that contain or transport the coolant to or from the reactor core. The pressure containing components of the RCS and the portions of connecting systems out to and including the isolation valves define the RCPB. The joints of the RCPB components are primarily welded or bolted. During plant life, the joint and valve interfaces can produce varying amounts of reactor coolant leakage, through either normal operational wear or mechanical deterioration. Limits on RCS operational leakage are specified in Technical Specification (TS) Limiting Condition for Operation (LCO) 3.4.4, and are required to ensure appropriate action is taken before the integrity of the RCPB is impaired. TS LCO 3.4.4 is applicable in Modes 1, 2, and 3, and allows for no RCPB leakage. JAF is required to be in Mode 4 within thirty-six (36) hours if RCPB leakage exists. Event Description Drywell inspections are conducted at the discretion of the Operations Manager during shutdown to identify sources of Drywell leakage. During the initial Refueling Outage 22 (R22) Drywell inspection, personnel observed a three to four foot steam plume emanating from the vent line coming from the bonnet section of the motor operated gate valve on the suction side of RWR Pump ‘A’ (02-2MOV-43A). The steam plume was observed on the vertical run of 02-2-3/4”-WH-1504-35A where the line leaves the insulation. Investigation revealed that the leak originated from a weld on the downstream side of a 45 degree elbow which is the first fitting on the line coming from the bonnet of 02-2MOV-43A. Further analysis by the Welding Engineer determined that the crack originated at the toe of the socket weld on the 45 degree elbow, and then propagated out away from the point of origin and into the pipe wall. The RCPB leakage was discovered during the initial drywell inspection with the plant in Mode 2 at 0613 on January 14, 2017. The average reactor coolant temperature decreased to less than 212 degrees F and the plant was in Mode 4 at 1530 of the same day, which is within the applicable TS LCO 3.4.4 required completion time. Page 2 of 5 | ML17072A041
Hope Creek Generating Station 05000354 1 OF3 | Unknown Unit | Reactor Protection S stem Actuation While the Reactor Was Shutdown | 01-03-2017 | On November 5, 2016, at 0404, a Reactor Protection System (RPS) actuation occurred due to a valid scram discharge volume high water level signal. This actuation was the result of a Redundant Reactivity Control System (RRCS) Alternate Rod Insertion (ARI) signal that was inadvertently generated during testing. The reactor was in cold shutdown at the time of the RPS actuation, with all control rods inserted. The Reactor Coolant System (RCS) pressure was 830 psig to support excess flow check valve testing, and shutdown cooling was removed from service. When the RRCS/ARI actuated, the B reactor recirculation pump tripped as expected, and the scram air header depressurized as expected. The depressurization of the scram air header is a design feature of the ARI. The ARI signal established the control rod drive (CRD) system scram flow path. This resulted in a high water level in the scram discharge volume (SDV), an expected response. High water level in the scram discharge volume is an actuation signal for the RPS. This is a condition reportable under 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in a manual or automatic actuation of a listed system. The cause of the RRCS/ARI actuation is inadequate procedural guidance which resulted in a personnel error associated with partial procedure performance. NRC FORM 366A (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. ENSEE EVENT REPORT (LER) Reported lessons learned are incorporated into the licensing process and fed back to industry. LIC Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail CONTINUATION SHEET to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a (See NUREG-1 022, R.3 for instruction and guidance for completing this form means used to impose an information collection does not display a currently valid OMB control http://www.nrc.gov/reading-rm/doc-collections/nureqs/staff/sr1 022/r3/) number, the NRC may not conduct or sponsor, and a person is not required to respond to, the Information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER I Hope Creek Generating Station 05000-354 YEAR I SE N Q U U M E B N E T R IA L R N E O V . 2016 -005 -01 | PLANT AND SYSTEM IDENTIFICATION General Electric- Boiling Water Reactor (BWR/4) Reactor Protection System - EllS Identifier {JC}* Redundant Reactivity Control System - EllS Identifier {JC }* Reactor Recirculation System - EllS Identifier {AD}* Control Rod Drive System - EllS Identifier {AA}* Reactor Water Cleanup System - EllS Identifier {CE}* *Energy Industry Identification System {EllS} codes and component function identifier codes appear as {SS/CCC} IDENTIFICATION OF OCCURRENCE Event Date: November 5, 2016 Discovery Date: November 5, 2016 CONDITIONS PRIOR TO OCCURRENCE Hope Creek was in Operational Condition (OPCON) 4, Cold Shutdown, at 0 percent rated thermal power. No other structures, systems or components that could have contributed to the event were inoperable at the time of the event. The reactor pressure vessel (RPV) in-service pressure test had been completed and reactor vessel pressure had been reduced from 1005 psig to 830 psig. Pressure was being held at 830 psig while excess flow check valve testing was being performed. Shutdown cooling was out of service to support the RPV pressure test, and the B reactor recirculation {AD} pump was in service to provide forced circulation. DESCRIPTION OF OCCURRENCE On November 5, 2016 at 0404 a RRCS I ARI {JC} signal was generated while excess flow check valve testing was in progress. The RRCS/ARI signal was generated due to trip signals on reactor pressure vessel dome pressure high channel "B" (expected for testing) and RPV water level low channel "A" (unexpected for testing condition). The unexpected signal was generated during the performance of isolating transmitters during preps for excess flow check valve (EFCV) testing. This signal would have been reset in accordance with procedures if followed. There were two procedures being executed in parallel by technicians to perform the excess flow check valve testing. The test procedure is written to test all EFCV's, with the EFCV's being separated into 21 groups based on channel and instrument rack relationships. Only one of the EFCV groups, group J, was to be tested. A second procedure is used to align and isolate the instrument racks for testing. Since only one group was to be tested, the evolution required partial procedure performance and coordination of both procedures to accomplish the test. In marking up the procedures for partial performance, the steps to isolate transmitters that were not to be tested were marked Not Applicable (N/A). In the process of marking up the procedure, the steps to reset any RRCS trips was also inappropriately marked N/A. As a result, the trip of the "A" channel low RPV water level was not reset prior to performing the test of the "B" channel high RPV pressure. Upon RRCS initiation, the B reactor recirculation pump tripped as expected. The ARI system depressurized the scram air header, establishing the CRD {AA} system scram flow path, and the SDV filled with water that was being discharged from the control rod drive mechanisms, as expected. When the water level reached the SDV high level set-point, an RPS {JC} actuation occurred. All rods were already inserted. Operators reset the RRCS and RPS signals and then lowered RPV pressure in accordance with procedures, and placed shutdown cooling in service. All systems operated as expected following the trip of RPS. | ML17072A135
LaSalle County Station | Unit 1 | Secondary Containment Inoperable Due to Interlock Doors Open | 03-17-2017 | On January 18, 2017, LaSalle County Station, Unit 1 was in Mode 1 at 100 percent power, and Unit 2 was in Mode 1 at 100 percent power with movement of irradiated fuel {MIF) in progress. At 2056 hours CST, both air-lock doors of the Unit 2 reactor building 710- foot elevation three-way air-lock opened simultaneously for approximately five seconds during personnel ingress. Both doors were immediately secured in the interlock, and MIF activities were immediately suspended. While both interlock doors were open, Technical Specifications {TS) Surveillance Requirement {SR) 3.6.4.1.2 to verify one secondary containment access door in each access opening is closed was not met. Secondary containment was declared inoperable for the period of time that both interlock doors were open. TS 3.6.4.1 Required Action {RA) A.1 to restore secondary containment to OPERABLE status within four hours was entered and exited. TS 3.6.4.1 RA C.1 to immediately suspend MIF in secondary containment was entered and exited. The most probable cause of the interlock failure was the intermittent failure of the relays on the door controller circuit card based on previous history with these circuit boards. Previous events and prior causal investigations have indicated degradations in the relays for these circuit cards, and the corrective actions to replace interlock door circuit cards was ongoing at the time this event occurred. The controller circuit card was replaced, which restored the interlock functionality on January 19, 2017. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/3112018 (06-2016)) Estimated burden per response to comply with this mandatory collection request 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.ResourceOnrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budge~ Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information htto://www.nrc.gov/reading-rm/doc-collectlons/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV LaSalle County Station, Unit 1 05000373 YEAR NUMBER NO. 2017 - 002 00 | PLANT AND SYSTEM IDENTIFICATION LaSalle County Station Unit 1 and Unit 2 are each a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The secondary containment is the reactor building, common to both reactor units, which contains the reactor auxiliary and serving equipment for the two reactors. The secondary containment access doors, or air-locks, provide a means for personnel and equipment to enter or exit the reactor building without breaching secondary containment integrity. CONDITION PRIOR TO EVENT Unit(s): 1 I 2 Event Date: January 18, 2017 Event Time: 2056 CST Reactor Mode(s): 1 I 1 Mode(s) Name: Power Operation/Power Operation Power Level: 100 percent/100 percent DESCRIPTION OF EVENT On January 18, 2017, LaSalle County Station, Unit 1 was in Mode 1 at 100 percent power, and Unit 2 was in Mode 1 at 100 percent power with movement of irradiated fuel (MIF) in progress. At 2056 hours CST, both air-lock doors of the Unit 2 reactor building to the diesel generator corridor (doors 507 and 402) were opened simultaneously for approximately five seconds during personnel ingress. The employee immediately secured both doors in the interlock and notified the Main Control Room (MCA). Shift Operations personnel subsequently blocked access until repairs could be made, and MIF activities were immediately suspended. While both interlock doors were open, Technical Specifications (TS) Surveillance Requirement (SR) 3.6.4.1.2 to verify one secondary containment access door closed was not met. Secondary containment was declared inoperable for the period of time that both interlock doors were open. Reactor building differential pressure, as observed in the MCA, remained less than -0.25 inches vacuum water gauge at all times. TS 3.6.4.1 Required Action (RA) A.1 to restore secondary containment to OPERABLE status within four hours was entered and exited. TS 3.6.4.1 RA C.1 to immediately suspend MIF in secondary containment was entered and exited. CAUSE OF EVENT The cause of the interlock failure was the intermittent failure of a circuit board which is designed to prevent more than one door to be open at a time. Similar previous interlocked door circuit board failures have been identified, through formal failure analysis, to have been caused by degraded relays integral to the circuit board. A causal investigation for an event in 2015 first identified interlock circuit cards as a cause, with a causal investigation for an event in 2016 identifying that relays on the circuit card as the specific cause of the circuit cards. Corrective actions from the 2016 investigation had been ongoing to upgrade interlock door circuit cards with ones that had improved relays. The interlock that failed was scheduled to have its circuit card replaced the week following this event as a corrective action from the previous interlock failure event in 2016. REPORTABILITY AND SAFETY ANALYSIS This event is reportable in accordance with 1 O CFR 50. 73(a)(2)(v)(C) and 1O CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material or mitigate the consequences of an accident. These doors are ground elevation personnel air-lock between the common diesel generators' corridor to the Unit 2 reactor building. The secondary containment access doors, or air-locks, provide a means for personnel and equipment to enter or exit the reactor building without breaching secondary containment integrity. This is necessary so that the negative pressure can be maintained. | ML17076A183
Fermi 2 05000 341 1 OF 6 | Unknown Unit | High Water Level Indications at Low Reactor Pressures Causes Some Functions of High Pressure Coolant Injection System and Reactor Core Isolation Cooling System to be Inoperable | 03-16-2017 | On January 19, 2017, a condition was identified that impacted the operability of certain functions associated with the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems under low reactor pressure conditions. HPCI and RCIC both have automatic and manual actuation functions to inject water into the reactor vessel. HPCI and RCIC also both have an automatic function (i.e. Level 8 trip signal) to prevent injection to the reactor vessel so that water does not reach the steam lines. This Level 8 trip signal comes from instrumentation that is calibrated to be most accurate at normal operating conditions. Under low reactor pressure conditions (i.e. below 600 psig), the high drywell pressure automatic actuation of HPCI and the manual initiation of both HPCI and RCIC are prevented by a Level 8 trip signal such that the affected HPCI and RCIC functions should be considered inoperable per Technical Specifications (TS). This can cause HPCI to also be considered inoperable, which could prevent the fulfillment of a safety function since HPCI is a single train system. Fermi 2 was at a pressure above 600 psig at the time of discovery and, therefore, the condition did not exist. However, a review of past operating conditions identified twelve instances in the past three years where the condition did exist. Based on an engineering analysis, the affected HPCI and RCIC functions are not required to perform a safety function at low reactor pressures; therefore, there was no adverse impact to public health and safety or to plant employees. There were no radiological releases. The cause of the event was an inconsistency between the Fermi 2 TS and the original design and licensing basis of the HPCI and RCIC systems. For corrective actions, Fermi 2 has submitted a license amendment request to clarify the TS. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/3112018 (06-2016) Estimated burden perre spontos ceo mply with this mandatory collection request 80 hours. Reported lessons learneadr ei ncorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) commernetsg ardibnurgde n estimate to the FOIA, Privacy and InformaCtioollenc tions Branch (T-5 I C N TO SHEET F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of ManagemaenndBt udgeWt,a shingDtCo n2,0 503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to imposaeni n formation collection does not display a currently valid OMB control number, the http://www nrc ov/reading-rm/doc-collections/nuregs/staff/srl022/r3/) NRC may not conduct or sponsor, anda persoisn not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. 05000- Ferml 2 341 2017 - 002 - 00 | INITIAL PLANT CONDITIONS Mode - 1 Reactor Power - 100 percent There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT On January 19, 2017, while performing a review of Fermi 2 design and licensing basis information in support of a potential license amendment, DTE Electric Company (DTE) identified a condition impacting the operability of certain functions associated with the High Pressure Coolant Injection (HPCI) [[BJ]] and Reactor Core Isolation Cooling (RCIC) [[BN]] systems under certain plant conditions. This condition was entered into the Fermi 2 Corrective Action Program at approximately 1545 EST on January 19, 2017. The condition had previously been entered into the Fermi 2 Corrective Action Program in August 2016 as a result of a similar condition identified at another plant. However, the impact on operability of HPCI and RCIC system functions was not confirmed until January 19, 2017; hence this is considered the time of discovery. The HPCI system provides coolant to the reactor vessel following a small break loss of coolant accident (LOCA) until reactor pressure is below the pressure at which the low pressure coolant injection systems maintain core cooling. The RCIC system is designed to ensure that sufficient reactor water inventory is maintained in the reactor vessel to permit adequate core cooling in the event of a loss of normal feedwater flow. HPCI and RCIC system controls automatically start the systems from the receipt of a reactor vessel water level low-low signal (Level 2). In addition, the HPCI system is designed to automatically start on high primary containment (drywell) pressure. The HPCI and RCIC systems can also be initiated manually. In all actuation modes, the systems are prevented from operating above high reactor vessel water level (Level 8) using trip logic that originates from wide range reactor vessel level instrumentation. The HPCI and RCIC system controls function to provide design makeup water flow to the reactor vessel until the amount of water delivered to the reactor vessel is adequate (i.e. Level 8), at which time the HPCI and RCIC systems automatically shut down. The HPCI and RCIC systems are designed to automatically cycle between the low-low (i.e. Level 2) and high (i.e. Level 8) reactor vessel water levels. Low reactor vessel water level is monitored by level sensors that sense the difference between the pressure of the water column in a constant reference leg (which is independent of reactor water level and density) and the pressure of the water column in the variable leg which varies linearly with the reactor vessel water level but is also dependent on the reactor water density. Each level sensor provides input to a trip unit and associated logic to provide an automatic HPCI and RCIC actuation signal. The reactor vessel low-low water level setting for HPCI and RCIC system actuation (Level 2) is selected high enough above the active fuel to start the HPCI and RCIC systems in time to maintain level above the top of the active fuel. The same wide range reactor vessel water level sensors that provide the HPCI and RCIC low-low water level actuation signals also provide the HPCI and RCIC high reactor vessel water level trip signals. Sensors are used with associated logic to automatically shut down the HPCI and RCIC systems. High water level in the reactor vessel indicates that the HPCI and RCIC systems have performed satisfactorily in providing makeup water to the reactor vessel and core cooling requirements are satisfied. The reactor vessel high water level setting that shuts down HPCI and RCIC (Level 8) is near the top of the steam separators and is sufficient to prevent gross moisture carry over to the HPCI and RCIC turbines. | ML17076A431
Columbia Generating Station 05000 397 1 OF 3 | Unknown Unit | Contactor Coil Failure Results in Tripping ofHPCS Diesel Mixed Air Fan | 03-20-2017 | On January 25, 2017 at 1836 PST, smoke was detected in the High Pressure Core Spray (HPCS) System diesel room with no indication of a fire. Immediate recovery actions by Operations personnel included opening the disconnect for the affected motor starter, at which point the smoke dissipated. Investigation of the condition found the motor starter for the Diesel Mixed Air Fan had failed. Prior to the start of the event, the HPCS system had been declared inoperable in accordance with plant Technical Specifications for planned maintenance. The apparent cause of the motor starter failure was overheating of the contactor coil due to elevated system voltages. Corrective actions for this event include replacement of the contactor coil, increased frequency of preventative maintenance, and procedure revision. There were no other event-related equipment malfunctions. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and lnfonnation Collections Branch (T-5 CONTINUATION SHEET F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resoun:e@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budge~ Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to Impose an information collection does not display a currently valid OMB control number, the blmJJwww.nrc,goy!reading-rm/doc-colleclions/nuregs/staff/sr1022Jr3l) NRC may not conduct or sponsor, and a person is not required to respond to, the information conection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 05000-1 DYE AR SEQUENTIAL REV NUMBER NO. Columbia Generating Station 397 u-1 ° 1-0 I 01 | Plant Conditions At the time of the event, the plant was operating in Mode 1 at 100% power. There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. Event Description On January 25, 2017 at 1836 PST, with the High Pressure Core Spray (HPCS) System [BG] declared inoperable in accordance with plant Technical Specifications for planned maintenance, the Diesel Mixed Air (DMA) Fan [FAN] was in normal operation with the fan running continuously, supplying air to the HPCS diesel room. The control room received a loss of power alarm for the fan's motor starter [MSTR], which was then followed by notification of smoke in the HPCS diesel room. The Operator at the motor control center [MCC] for the motor starter opened the disconnect and the smoke dissipated. Inspection of the motor starter found that the contactor coil [CNTR] had overheated. This event is reportable as an event that could have prevented fulfillment of safety functions needed to mitigate the consequences of an accident per 10 CFR 50.73(a)(2)(v)(D), should the HPCS diesel have received a start signal during a design basis event. This condition was reported under 10 CFR 50.72(b)(3)(v)(D) via Event Notification #52510 for an event or condition that, at the time of discovery, could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident; however, the Event Notification was retracted on February 3, 2017, based on the determination that the HPCS System had been declared inoperable prior to the smoke incident in accordance with plant Technical Specifications. Immediate Corrective Actions Operations personnel opened the disconnect for the affected motor starter, at which point the smoke dissipated. Assessment of Safety Consequences There were no actual safety consequences associated with this event, as there was no loss of safety function. There was no change in plant status or operating condition, and there was no risk to the public at any time due to this event. At the time of the event, work on the HPCS Service Water System was being performed in accordance with 10 CFR 50.65(a)(4) for managing risk. In emergency conditions, the HPCS System is used to provide core cooling and, during a loss of coolant accident, maintains reactor inventory. The DMA fan maintains suitable temperatures within the HPCS diesel generator room to ensure equipment operability temperature limits are not exceeded during an emergency. Had the HPCS System been in service and credited for accident mitigation, this event could have challenged the ability of the HPCS System to perform its safety function. Cause of Event The investigation into the apparent cause of the unexpected fan failure determined that the contactor coil for the fan's motor starter had overheated. The cause evaluation determined that the premature coil failure was likely caused by two contributing factors: increased coil operating currents and heating caused by elevated system voltages, and increased heating of the coil assembly caused by high magnet assembly temperatures due to loose shading coils. NRC FORM 368A (06-2018) Page 2 of 3 | ML17079A545
Brunswick Steam Electric Plant (BSEP) | Unit 1 | Speed and Frequency Oscillations Result in Inoperable Emergency Diesel Generator | 02-02-2017 | On February 7, 2016, at 1312 Eastern Standard Time (EST), Unit 1 was in Mode 1 (i.e., Run) at 88 percent of rated power in end-of-cycle coastdown. At that time, an event occurred which resulted in a loss of offsite power (LOOP) on Unit 1. Emergency diesel generators EDG-1 and EDG-2 started and tied to their respective Unit 1 emergency buses. During diesel operation, EDG-1 exhibited oscillations in engine speed and bus frequency. These oscillations had no adverse effect on equipment supplied by the bus, and all supplied loads continued to perform their safety functions without interruption and without need for operator intervention. However, due to the speed and frequency oscillations, EDG-1 was deemed after the fact to have been inoperable. Following extensive testing and evaluation, the cause of the oscillations has not been determined. The governor system for EDG-1 was replaced on March 6, 2016, as part of a planned upgrade to EDG-1. Since that time, the oscillations have not recurred. Based on the fact that the governor replacement eliminated the oscillations, it’s concluded that the oscillations resulted from a deficiency in the governor system. Since the cause of the inoperability has been eliminated, no further corrective actions are planned. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 CONTINUATION SHEET F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant (BSEP) 05000-325 YEAR NUMBER NO. Unit 1 2017 - 001 - 000 | Energy Industry Identification System (EllS) codes are identified in the text as [XX]. Background Inspection Report 2016-004, dated February 9, 2017 (ADAMS accession number ML17041A010), includes a Severity Level IV non-cited violation for failure to submit a Licensee Event Report (LER) due to inoperability of Emergency Diesel Generator 1 (EDG-1). This LER fulfills the requirement of 10 CFR 50.73(a)(1) pertaining to that violation. On February 7, 2016, during a loss of offsite power (LOOP) event, oscillations of the EDG-1 fuel rack were observed. During the event, maximum bus frequency oscillations of +/- 0.4 Hz were observed. According to recorded electronic data, at the highest loading during the event, the load was oscillating by approximately +/-300 kW. Loads supplied by EDG-1 continued to perform their safety functions without interruption and without need for operator intervention. However, it was determined after the fact that the observed speed and frequency oscillations rendered EDG-1 inoperable, due to the uncertainty of the effect of the oscillations on EDG-1 at full load. Duration of EDG 1 Inoperability Based on data gathered by electronic monitoring, the oscillations commenced at approximately 1404 Eastern Standard Time (EST) on February 7, 2016. Prior to this time, there was no indication of frequency, speed, or power oscillations on EDG-1. Without firm evidence to the contrary, this is assumed to be the start time for EDG-1 inoperability. On March 2, 2016, at 1458 EST, EDG-1 was removed from service for governor replacement. Work associated with this modification corrected the condition causing the oscillations. EDG-1 was declared operable following the governor replacement and associated testing on March 9, 2016, at 0151 EST. Based on the above, EDG-1 was inoperable from February 7, 2016, at 1404 EST until March 9, 2016, at 0151 EST (i.e., approximately 30 days, 11 hours, 47 minutes). Concurrent Inoperability of EDG-2, EDG-3, and EDG-4 EDG-2 February 19 from 2025 EST to 2053 EST (i.e., 28 minutes) for barring. February 19 from 2104 EST to February 20 at 0014 EST (i.e., 3 hours, 10 minutes) for surveillance testing. | ML17081A236
Quad Cities Nuclear Power Station | Unit 1 | Secondary Containment Interlock Doors Opened Simultaneously | 03-22-2017 | On January 24, 2017, at 10:00 hours, Operations was notified that both doors in the secondary containment interlock on the 595 foot elevation between the Reactor Building (RB) and the Unit 2 Reactor Feed Pump room (located inside the Turbine Building (TB)) were opened simultaneously for approximately 3 seconds. The failure of this interlock caused a loss of secondary containment per Technical Specification (TS) 3.6.4.1, Condition A. The doors were immediately reclosed, and the secondary containment boundary was immediately reestablished. Operators verified the RB (secondary containment) differential pressure was maintained operable at greater than 0.10 inches of water vacuum. Secondary containment remained available and functional during the event since the secondary containment interlock was immediately restored by closing the doors and since the RB differential pressure was maintained during the event. The RB is a common volume to both Units 1 and 2, and an interlock failure can impact the secondary containment for both units. The cause of the interlock failure was due to a dirty contact that caused the interlock relay to stick. This allowed the second door to open before the first door was secured. Corrective actions included inspecting and cleaning of the interlock relay contacts. Steps will be added to the Preventative Maintenance Work Orders to perform a visual inspection and cleaning of interlock relays. The safety significance of this event was minimal. Given the impact on the secondary containment, this report is submitted (for Units 1 and 2) in accordance with the requirements of 10 CFR 50.73 (a)(2)(v)(C), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Quad Cities Nuclear Power Station Unit 1 05000254 YEAR NUMBER NO. 2017 - 001 - 00 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Both doors in the secondary containment interlock between the Reactor Building and the Unit 2 Reactor Feed Pump room were opened simultaneously and caused a momentary loss of secondary containment. A. CONDITION PRIOR TO EVENT Unit: 1 / 2 Event Date: January 24, 2017 Event Time: 10:00 hours Reactor Mode: 1 / 1 Mode Name: Power Operation / Power Operation Power Level: 98% / 100% B. DESCRIPTION OF EVENT On January 24, 2017 at 10:00 hours, the Operations Department was notified that both doors [DR] in the secondary containment [NG] interlock [IEL] on the 595 foot elevation between the Reactor Building (RB) [NG] and the Unit 2 Reactor Feed Pump (RFP) [SK] room (located inside the Turbine Building (TB)) [NM] were opened simultaneously for approximately 3 seconds. The failure of this interlock caused a loss of secondary containment per Technical Specification (TS) 3.6.4.1, Condition A. The doors were immediately reclosed, and the secondary containment boundary was immediately reestablished. Operators verified the RB (secondary containment) differential pressure was maintained operable at greater than 0.10 inches of water vacuum. The Operations Field Supervisor was then dispatched to the interlock to investigate the condition. It was determined that the condition that led to both doors being open simultaneously could be recreated. At no time during the initial investigation were the doors opened at the same time. The doors were then taken out of service to allow repairs. Secondary containment remained available and functional during the event since the secondary containment interlock was immediately restored by closing the doors and since the RB differential pressure was maintained during the event. A review of the Station Event Recorder (SER) verified that RB low differential pressure alarms were not received during this event. The RB is a common volume to both Units 1 and 2, and an interlock failure can impact the secondary containment for both units. On January 24, 2017, at 14:00 hours, ENS #52508 was made to the NRC under 10 CFR 50.72(b)(3)(v)(C), to report this event as an event or condition that could have prevented the fulfillment of a safety function. At the time of the event, another individual had traversed through the RB door when a contractor started transitioning through the TB door. As they opened the TB-side door the RB-side door was noticed open and in the process of closing. At no time during the event were the open door indicating lights illuminated. The door was fully closed in three seconds. It was found that the sticking relay made up the logic falsely signaling to the system that the opposite door was closed. | ML17081A289
LaSalle County Station | Unit 2 | Manual Reactor Scram due to Turbine-Generator Run-Back Caused by Stem-Disc Separation in Stator Water Cooling Heat Exchanger Inlet Valve | 03-24-2017 | On January 23, 2017, operators initiated a manual scram of the LaSalle County Station Unit 2 reactor as a result of observing a generator run-back due to a generator stator winding cooling (GC) system malfunction. Initial troubleshooting identified the most likely cause was plugging in the 'A' GC heat exchanger, based on inspection of the GC system flow-path components. The GC system was realigned to the 'B' heat exchanger until inspections could be performed in the upcoming refueling outage, and the unit was re-started on January 24, 2017. Further inspections of the GC components were performed while the unit was shut down for a planned refueling outage. These inspections determined the cause of the GC system failure was stem-disc separation in the 'A' GC heat exchanger inlet valve. The valve was repaired during the refueling outage. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in manual or automatic actuation of the Reactor Protection System (RPS). There were no safety consequences associated with the event since there was no loss of safety function, and the RPS functioned as designed. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 UCENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information colleclion does not display a currenUy valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the informalion http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV LaSalle County Station, Unit 2 05000374 YEAR NUMBER NO. 2017 - 001 00 | PLANT AND SYSTEM IDENTIFICATION LaSalle County Station Unit 2 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the generator stator winding cooling (GC) system, which supports main generator reliability by removing heat from the generator field rectifiers and generator terminal bushings. The GC system supplies cooling water from one of two pumps in combination with one of two heat exchangers. CONDITION PRIOR TO EVENT Unit(s): 2 Event Date: January 23, 2017 Event Time: 0806 CST Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 99 percent DESCRIPTION OF EVENT On January 23, 2017, LaSalle County Station Unit 2 was in Mode 1 at 99 percent, while in coast-down for a scheduled refueling outage. At 0806 hours CST, operators inserted a manual scram, in accordance with station procedures, in response to a GC system malfunction and generator load run-back. The unit was placed in a stable condition with all control rods fully inserted. Reactor pressure was maintained with the turbine bypass valves, and reactor water level was controlled using the main feedwater system. At the time of the event, stator water cooling was being provided by the 'B' GC pump aligned to the 'A' GC heat exchanger. The event was preceded by unexpected alarms with the GC and electro-hydraulic control (EHC) systems. Field operators reported that local alarms were observed for stator inlet flow, stator inlet pressure, and stator outlet temperature. CAUSE OF EVENT Initial investigation found the 'B' GC pump had been running with a higher than normal discharge pressure as indicated on a local gauge between the pump and the discharge check valve. Further investigation found evidence that limited cooling water flow to the generator existed, suggesting that blockage or a stem-to-disc separation of an upstream valve had occurred. Thermography, visual inspection, borescope inspection, and testing of all valves in the normal flow-path from the 'B' GC pump and the 'A' heat exchanger to the pressure control valve indicated that the most likely cause was plugging in the 'A' heat exchanger. Additional inspections of the GC system were performed during the scheduled refueling outage in order to ascertain a more definitive cause. These inspections determined the cause of the GC system failure was stem-disc separation in the 'A' GC heat exchanger inlet valve 2GC-Y08. The preliminary results from the root cause investigation indicate the likely cause of the stem-disc separation was due to maintenance activities from a valve disassembly performed in 2003 for a suspected leak-by. If the investigation reveals insights or cause different than described in this LER, a supplement will be provided. REPORTABILITY AND SAFETY ANALYSIS This event is reportable in accordance with 10 CFR 50. 73(a)(2)(iv)(A) as an event or condition that resulted in a manual or automatic actuation of the Reactor Protection System (RPS). There was no safety consequences associated with the event since all equipment functioned as designed to shut down the reactor and operational and safety limits were maintained within margin to place the unit into safe shutdown condition. The main generator provides electrical power from the motive force supplied by the main turbine. The main generator consists of a rotor, bearings, stator, collector rings, brushes, and high-voltage bushings. One of the support systems for the main generator is the GC system. Since the turbine and generator are used together, the main turbine is designed with several trip signals, including a loss of GC. | ML17083A122
I I | Unknown Unit | Hiah Pressure Core Sorav (HPCS) Jockev Pumo Trio 5.EVENTDATE 6.LERNUMBER 7.REPORTDATE 8.OTHERFACILITIESINVOLVED SEQUENTIAL REV FACILITYNAME DOCKETNUMBER MONTH DAY YEAR YEAR MONTH DAY YEAR N/A 05000N/A NUMBER NO. FACILITYNAME DOCKETNUMBER 1 27 2017 2017 001 00 3 28 2017 N/A 05000 N/A 9.OPERATINGMODE 11.THISREPORTISSUBMITTEDPURSUANTTOTHEREQUIREMENTSOF10CFR§:(Checkallthatapply) D 20.2201(b) D 20.2203(a)(3)(i) D 50.73(a)(2)(ii)(A) D 50.73(a)(2)(viii)(A) 2 D 20.2201(d) D 20.2203(a)(3)(ii) D 50.73(a)(2)(ii)(B) D 50.73(a)(2)(viii)(B) D 20.2203(a)(1) D 20.2203(a)(4) D 50.73(a)(2)(iii) D 50.73(a)(2)(ix)(A) D 20.2203(a)(2)(i) D 50.36(e)(1)(i)(A) D 50.73(a)(2)(iv)(A) D 50.73(a)(2)(x) 10.POWERLEVEL D 20.2203(a)(2)(ii) D 50.36(e)(1)(ii)(A) D 50.73(a)(2)(v)(A) D 73.71(a)(4) D 20.2203(a)(2)(iii) D 50.36(e)(2) D 50.73(a)(2)(v)(B) D 73.71(a)(5) Raising power in D 20.2203(a)(2)(iv) D 50.46(a)(3)(ii) D 50.73(a)(2)(v)(C) D 73.77(a)(1) the source range to D 20.2203(a)(2)(v) D 50.73(a)(2)(i)(A) ~ 50.73(a)(2)(v)(D) D 73.77(a)(2)(i) returnto power D 20.2203(a)(2)(vi) D 50.73(a)(2)(i)(B) D 50.73(a)(2)(vii) D 73.77(a)(2)(ii) operations D 50.73(a)(2)(i)(C) D OTHER SpecifyinAbstractbeloworinNRCForm366A 12.LICENSEECONTACTFOR THIS LER LICENSEECONTACT r~LEPHONE NUMBER(IncludeAreaCode) James Nadeau1Manager, Regulatory Assurance (601)-437-2103 13.COMPLETEONEUNEFOREACHCOMPONENTFAILUREDESCRIBEDINTHISREPORT MANU- REPORTABLE MANU- REPORTABLE CAUSE SYSTEM COMPONENT CAUSE SYSTEM COMPONENT FACTURER TOEPIX FACTURER TOEPIX N/A N/A N/A N/A N/A N/A N/A N/A N/A N/A 14.SUPPLEMENTALREPORTEXPECTED 15. EXPECTED MONTH DAY YEAR D YES (Ifyes,complete 15.EXPECTEDSUBMISSIONDATE) ~ NO SUBMISSION N/A N/A N/A DATE ABSTRACT(Limitto1400spaces,i.e.,approximately15single-spacedtypewrittenlines) At 1808 hours on 1/27/17, Grand Gulf Nuclear Station entered into LCO 3.5.1.Bwhen the High Pressure Core Spray (HPCS) Jockey Pump (Component Function Identifier- P)failed and the HPCS System was declared inoperable. The Reactor Core Isolation Cooling (RCIC) System was verified operable and investigation into the cause was initiated. Under those plant conditions the Plant Technical Specifications action to restore the HPCS System to operable status allows a 14day completion time. Noother safety systemswere inoperable at the time of this event. The decision was made to disassemble the HPCS Jockey Pump and rebuild the pump using parts from thewarehouse which was completed on 1/29/17. The pump was tested to demonstrate functionality of the pump on 1/29/17 and the system was returned to service. NRCFORM366A(06-2016) NRCFORM366A U.S.NUCLEARREGULATORYCOMMISSION APPROVED BYOMB: NO.3150-0104 EXPIRES: 10/31/2018 (06-2016) I Estimated burden per response to comply with this mandatory collection request: 80hours. Reported lessons learned areincorporated intothelicensing process and fed back toindustry. LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to theFOIA, Privacy and Information Collections Branch (T-5 F53); U.S. NuclearRegulatoryCommission,Washington, DC20555-0001,orbye-mail CONTINUATION SHEET toInfocollects.Resource@nrc.gov, and totheDesk Officer, Office ofInformation and Regulatory Affairs, NEOB-10202, (3150-0104), Office ofManagementandBudget, Washington, DC 20503. Ifa (SeeNUREG-1022,R.3forinstructionandguidanceforcompletingthisform means used toimpose aninformation collection does notdisplay acurrently valid OMB control http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3(J number, theNRC may notconduct orsponsor, and aperson isnotrequired torespond 10,the informationcollection. 1. FACILITY NAME 2. DOCKETNUMBER 3.LERNUMBER I I YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 05000-416 NUMBER NO. 2017 001 00 NARRATIVE PLANT CONDITIONS PRIOR TO THE EVENT Atthe time ofthe event, Grand Gulf Nuclear Station (GGNS) Unit 1was in Mode 2 and raising power inthe source range to returnto power operations. No other safety systems were inoperable at the time ofthis event. DESCRIPTION At 1808 hours on 1/27/17, the Main Control Room received "HPCS PMP SUCT PRESS ABNORMAL" (1 H13-P601-16A 04) annunciatordue to a High Pressure Core Spray (HPCS) JockeyPump trip. The Control Room dispatched an operator and electrician to HPCS jockeypump breaker52-170105 and dispatched an operator locally to the HPCSjockey pump. The operator reported the HPCS breakerto be inthe ON position with no abnormalities noted. The local operator reported the HPCS Jockey Pump not running but noother abnormalities were identified. At 1817 hours "HPCS JKY PMP DISCH PRESS LO" annunciatoralarmed and "HPCS PMP SUCT PRESS ABNORMAL" annunciatorcleared. HPCS pump suction pressure indicated 23.75 psig on Main Control Room Panel 1H13-P625. Average suction pressure overthe lastfive years is21.3 psig. The LCOAction Statement entered was LCO 3.5.1.B, ECCS Operating- for HPCS System inoperable. Initialinvestigation ofthe feeder breaker (52-170105) revealed that the overloads atthe breaker were tripped. The motor amperage was measured at 53 amps during a 13second run inwhich the pump did not rotate. The thermals tripped again.The decision was made to disassemblethe HPCS Jockey Pump and rebuild the pump using parts from the warehouse which was performed on 1/29/17. During disassemblyofthe pump, the following conditions were identified: • Badthrust bearing • Agroove inthe bearing housing The pump was tested to demonstratefunctionality ofthe pump on 1/29/17 and the system was returned to service. REPORTABILITY Event Notification No. 52516 was made tothe U.S. Nuclear Regulatory Commission (NRC) Operations Center. This LER isbeing submitted pursuant to Title 10Code of Federal Regulations 10CFR 50.73(a)(2)(v)(D) for any event or condition that could have prevented the fulfillment ofthe safety function of structures or systems that are needed to mitigate the consequences of anaccident. Telephonic notification was made to the NRC Operations Center via the Emergency Notification System on 1/27/17, at 2305 hours, pursuant to 10CFR 50.72(b)(3)(v)(D) for any event orcondition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences ofan accident. CAUSE DirectCause: The HPCS JockeyPump failed on 1/27/17 due to the thrust bearing being degraded causing the pumpto seize. Apparent Cause: Itwas identified that the HPCS Jockev Pump (Gould 3196) does not have atime-based replacement NRCFORM366A (06-2016) Page 2 of 4 NRCFORM366A U.S.NUCLEARREGULATORYCOMMISSION APPROVED BYOMB: NO.3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. l~¥"""'''''''~\ Reported lessons learned areincorporated into thelicensing process and fedback toindustry. LICENSEE EVENT REPORT (LER) . • \. .... < ? l .i ~ Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (l-5 F53), U.S. NuclearRegulatoryCommission,Washington, DC20555-0001,orbye-mail CONTINUATION SHEET toInfocoliects.Resource@nrc.gov, and totheDesk Officer, Office ofInformation and Regulatory Affairs, NEOB-10202,(3150-0104), Office ofManagement and Budget, Washington, DC 20503. Ifa (SeeNUREG-1022,R.3forinstructionandguidanceforcompletingthisform means used toimpose aninformation collection does notdisplay acurrently valid OMB control http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr10221r30 number, theNRC may notconduct orsponsor, and aperson isnotrequired torespond to, the informationcollection. 1. FACILITY NAME 2. DOCKETNUMBER 3.LERNUMBER I I YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 05000-416 NUMBER NO. 2017 001 00 maintenance task. GGNS implements apredictive monitoring maintenance strategy in lieuoftime-based replacement preventive maintenancetasks. The failure ofthe thrust bearing would have shown up inthe axial vibration trends ofthe pump. Current preventive maintenance was notsufficient to prevent failure of the jockeypump. Aconservative time based replacement PMtask to replace the pump will reduce the likelihood of anotherfailure ofthe pump. Contributing Cause: The HPCS operating instructions does notcontain enough guidance to maintain the HPCS System available when the jockeypump issecured. The inadequate guidance does notcause the jockeypump tofail, but increases the consequences (non-functional time) ofthe event. The HPCS System can be made operable by keeping the HPCS Pump discharge line full by either the HPCS JockeyPump or by running the HPCS Pump. During this failure, the procedural guidance did notallow for the HPCS Pump to be runto keep the HPCS System operable. EXTENT OF CONDITION The condition may exist inthe following equipment, procedures, processes, and/or organizations: • Residual Heat Removal (RHR) JockeyPumps A, B,and C • Low Pressure Core Spray (LPCS) Jockey Pump • Noprocedures are affected • Noprocesses are affected • Noorganizations are affected EXTENT OF CAUSE The cause may exist inthe following equipment, procedures, processes, and/or organizations: • RHRJockeyPumps A, B,and C • LPCS JockeyPump • Noprocedures are affected • Noprocesses are affected • Noorganizations are affected CORRECTIVE ACTIONS The HPCSJockey Pump was rebuilt and apartial HPCS Quarterly Functional Surveillance was performed to demonstrate functionality ofthe pump. This partial surveillance was completed satisfactorilyon 1/29/17 andthe pump was returned to service. To prevent this failure from occurring inthe future, the following actions have been taken: • Initiated preventive maintenancetask to perform thermography and oil analysis ofthe HPCS Jockey Pump bearings. • Initiated preventive maintenancetasks to perform thermographyand oil analysis of allthree RHRJockeyPump bearings. • Initiated preventive maintenance task to perform thermography and oil analysis ofthe LPCS JockeyPump bearings. Page 3 of 4 NRCFORM366A(06-2016) NRCFORM 366A U.S.NUCLEARREGULATORYCOMMISSION APPROVED BYOMB: NO.3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned areincorporated intothelicensing process and fedback toindustry. LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch(T-5 F53), U.S. NuclearRegulatoryCommission, Washington, DC20555-0001, orbye-mail CONTINUATION SHEET toInfocoliects.Resource@nrc.gov, and totheDesk Officer, Office ofInformation and Regulatory Affairs, NEOB-10202,(3150-0104), Office ofManagement and Budget, Washington, DC 20503. Ifa (SeeNUREG-1022,R.3forinstructionandguidanceforcompletingthisform means used toimpose aninformation collection does notdisplay a currently valid OMB control http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D number, theNRC may notconduct orsponsor, and aperson isnotrequired torespond to,the informationcollection. 1. FACILITY NAME 2. DOCKETNUMBER 3.LERNUMBER I I YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 05000-416 NUMBER NO. 2017 001 00 • Initiated preventive maintenance task to replace the HPCS Jockey Pump on a conservativetime-based frequency. • Initiated preventive maintenance task to replace all three RHR JockeyPumps on a conservativetime-based frequency. • Initiated preventive maintenance task to replace the LPCS JockeyPump on a conservative time-based frequency. SAFETY SIGNIFICANCE The event posed nothreat to the health and safety of the general public or to nuclearsafetyas safety-systems performed as designed. No Technical Specification safetylimits were violated. Industrial safetywas not challenged, and there was no potential or actual radiological release during the event. PREVIOUS SIMILAR EVENTS There are no known previous similar events at Grand Gulf Nuclear Station. Page 4 of 4 NRCFORM366A(06-2016) | 03-28-2017 | At 1808 hours on 1/27/17, Grand Gulf Nuclear Station entered into LCO 3.5.1.Bwhen the High Pressure Core Spray (HPCS) Jockey Pump (Component Function Identifier- P)failed and the HPCS System was declared inoperable. The Reactor Core Isolation Cooling (RCIC) System was verified operable and investigation into the cause was initiated. Under those plant conditions the Plant Technical Specifications action to restore the HPCS System to operable status allows a 14day completion time. Noother safety systemswere inoperable at the time of this event. The decision was made to disassemble the HPCS Jockey Pump and rebuild the pump using parts from thewarehouse which was completed on 1/29/17. The pump was tested to demonstrate functionality of the pump on 1/29/17 and the system was returned to service. NRCFORM366A(06-2016) NRCFORM366A U.S.NUCLEARREGULATORYCOMMISSION APPROVED BYOMB: NO.3150-0104 EXPIRES: 10/31/2018 (06-2016) I Estimated burden per response to comply with this mandatory collection request: 80hours. Reported lessons learned areincorporated intothelicensing process and fed back toindustry. LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to theFOIA, Privacy and Information Collections Branch (T-5 F53); U.S. NuclearRegulatoryCommission,Washington, DC20555-0001,orbye-mail CONTINUATION SHEET toInfocollects.Resource@nrc.gov, and totheDesk Officer, Office ofInformation and Regulatory Affairs, NEOB-10202, (3150-0104), Office ofManagementandBudget, Washington, DC 20503. Ifa (SeeNUREG-1022,R.3forinstructionandguidanceforcompletingthisform means used toimpose aninformation collection does notdisplay acurrently valid OMB control http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3(J number, theNRC may notconduct orsponsor, and aperson isnotrequired torespond 10,the informationcollection. 1. FACILITY NAME 2. DOCKETNUMBER 3.LERNUMBER I I YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 05000-416 NUMBER NO. 2017 001 00 | PLANT CONDITIONS PRIOR TO THE EVENT Atthe time ofthe event, Grand Gulf Nuclear Station (GGNS) Unit 1was in Mode 2 and raising power inthe source range to returnto power operations. No other safety systems were inoperable at the time ofthis event. DESCRIPTION At 1808 hours on 1/27/17, the Main Control Room received "HPCS PMP SUCT PRESS ABNORMAL" (1 H13-P601-16A 04) annunciatordue to a High Pressure Core Spray (HPCS) JockeyPump trip. The Control Room dispatched an operator and electrician to HPCS jockeypump breaker52-170105 and dispatched an operator locally to the HPCSjockey pump. The operator reported the HPCS breakerto be inthe ON position with no abnormalities noted. The local operator reported the HPCS Jockey Pump not running but noother abnormalities were identified. At 1817 hours "HPCS JKY PMP DISCH PRESS LO" annunciatoralarmed and "HPCS PMP SUCT PRESS ABNORMAL" annunciatorcleared. HPCS pump suction pressure indicated 23.75 psig on Main Control Room Panel 1H13-P625. Average suction pressure overthe lastfive years is21.3 psig. The LCOAction Statement entered was LCO 3.5.1.B, ECCS Operating- for HPCS System inoperable. Initialinvestigation ofthe feeder breaker (52-170105) revealed that the overloads atthe breaker were tripped. The motor amperage was measured at 53 amps during a 13second run inwhich the pump did not rotate. The thermals tripped again.The decision was made to disassemblethe HPCS Jockey Pump and rebuild the pump using parts from the warehouse which was performed on 1/29/17. During disassemblyofthe pump, the following conditions were identified: • Badthrust bearing • Agroove inthe bearing housing The pump was tested to demonstratefunctionality ofthe pump on 1/29/17 and the system was returned to service. REPORTABILITY Event Notification No. 52516 was made tothe U.S. Nuclear Regulatory Commission (NRC) Operations Center. This LER isbeing submitted pursuant to Title 10Code of Federal Regulations 10CFR 50.73(a)(2)(v)(D) for any event or condition that could have prevented the fulfillment ofthe safety function of structures or systems that are needed to mitigate the consequences of anaccident. Telephonic notification was made to the NRC Operations Center via the Emergency Notification System on 1/27/17, at 2305 hours, pursuant to 10CFR 50.72(b)(3)(v)(D) for any event orcondition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences ofan accident. CAUSE DirectCause: The HPCS JockeyPump failed on 1/27/17 due to the thrust bearing being degraded causing the pumpto seize. Apparent Cause: Itwas identified that the HPCS Jockev Pump (Gould 3196) does not have atime-based replacement NRCFORM366A (06-2016) Page 2 of 4 NRCFORM366A U.S.NUCLEARREGULATORYCOMMISSION APPROVED BYOMB: NO.3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. l~¥"""'''''''~\ Reported lessons learned areincorporated into thelicensing process and fedback toindustry. LICENSEE EVENT REPORT (LER) . • \. .... < ? l .i ~ Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (l-5 F53), U.S. NuclearRegulatoryCommission,Washington, DC20555-0001,orbye-mail CONTINUATION SHEET toInfocoliects.Resource@nrc.gov, and totheDesk Officer, Office ofInformation and Regulatory Affairs, NEOB-10202,(3150-0104), Office ofManagement and Budget, Washington, DC 20503. Ifa (SeeNUREG-1022,R.3forinstructionandguidanceforcompletingthisform means used toimpose aninformation collection does notdisplay acurrently valid OMB control http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr10221r30 number, theNRC may notconduct orsponsor, and aperson isnotrequired torespond to, the informationcollection. 1. FACILITY NAME 2. DOCKETNUMBER 3.LERNUMBER I I YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 05000-416 NUMBER NO. 2017 001 00 maintenance task. GGNS implements apredictive monitoring maintenance strategy in lieuoftime-based replacement preventive maintenancetasks. The failure ofthe thrust bearing would have shown up inthe axial vibration trends ofthe pump. Current preventive maintenance was notsufficient to prevent failure of the jockeypump. Aconservative time based replacement PMtask to replace the pump will reduce the likelihood of anotherfailure ofthe pump. Contributing Cause: The HPCS operating instructions does notcontain enough guidance to maintain the HPCS System available when the jockeypump issecured. The inadequate guidance does notcause the jockeypump tofail, but increases the consequences (non-functional time) ofthe event. The HPCS System can be made operable by keeping the HPCS Pump discharge line full by either the HPCS JockeyPump or by running the HPCS Pump. During this failure, the procedural guidance did notallow for the HPCS Pump to be runto keep the HPCS System operable. EXTENT OF CONDITION The condition may exist inthe following equipment, procedures, processes, and/or organizations: • Residual Heat Removal (RHR) JockeyPumps A, B,and C • Low Pressure Core Spray (LPCS) Jockey Pump • Noprocedures are affected • Noprocesses are affected • Noorganizations are affected EXTENT OF CAUSE The cause may exist inthe following equipment, procedures, processes, and/or organizations: • RHRJockeyPumps A, B,and C • LPCS JockeyPump • Noprocedures are affected • Noprocesses are affected • Noorganizations are affected CORRECTIVE ACTIONS The HPCSJockey Pump was rebuilt and apartial HPCS Quarterly Functional Surveillance was performed to demonstrate functionality ofthe pump. This partial surveillance was completed satisfactorilyon 1/29/17 andthe pump was returned to service. To prevent this failure from occurring inthe future, the following actions have been taken: • Initiated preventive maintenancetask to perform thermography and oil analysis ofthe HPCS Jockey Pump bearings. • Initiated preventive maintenancetasks to perform thermographyand oil analysis of allthree RHRJockeyPump bearings. • Initiated preventive maintenance task to perform thermography and oil analysis ofthe LPCS JockeyPump bearings. Page 3 of 4 NRCFORM366A(06-2016) NRCFORM 366A U.S.NUCLEARREGULATORYCOMMISSION APPROVED BYOMB: NO.3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned areincorporated intothelicensing process and fedback toindustry. LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch(T-5 F53), U.S. NuclearRegulatoryCommission, Washington, DC20555-0001, orbye-mail CONTINUATION SHEET toInfocoliects.Resource@nrc.gov, and totheDesk Officer, Office ofInformation and Regulatory Affairs, NEOB-10202,(3150-0104), Office ofManagement and Budget, Washington, DC 20503. Ifa (SeeNUREG-1022,R.3forinstructionandguidanceforcompletingthisform means used toimpose aninformation collection does notdisplay a currently valid OMB control http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D number, theNRC may notconduct orsponsor, and aperson isnotrequired torespond to,the informationcollection. 1. FACILITY NAME 2. DOCKETNUMBER 3.LERNUMBER I I YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 05000-416 NUMBER NO. 2017 001 00 • Initiated preventive maintenance task to replace the HPCS Jockey Pump on a conservativetime-based frequency. • Initiated preventive maintenance task to replace all three RHR JockeyPumps on a conservativetime-based frequency. • Initiated preventive maintenance task to replace the LPCS JockeyPump on a conservative time-based frequency. SAFETY SIGNIFICANCE The event posed nothreat to the health and safety of the general public or to nuclearsafetyas safety-systems performed as designed. No Technical Specification safetylimits were violated. Industrial safetywas not challenged, and there was no potential or actual radiological release during the event. PREVIOUS SIMILAR EVENTS There are no known previous similar events at Grand Gulf Nuclear Station. Page 4 of 4 NRCFORM366A(06-2016) | ML17087A135
Duane Arnold Energy Center 05000-331 1 OF 5 | Unknown Unit | Condition Prohibited by Technical Specification - Containment Vent and Purge Valve Leakage | 03-27-2017 | On January 25, 2017, at 1800 CST, while operating at 100% power, during planned surveillance testing, Drywell Vent Inboard Isolation Valve, CV4302 (System Code JM}, was found to exceed its Leakage Integrity Test limits and was declared inoperable. The initial observed conditions indicated that CV4302 was the likely source of leakage and was the focus of repair efforts. After completion of repairs to CV4302, post maintenance testing showed that the Drywell Vent Line Outboard Isolation valve, CV4303, was exceeding its valve leakage limits, and therefore, was declared inoperable at 0300 CST on January 26, 2017. This resulted in a containment penetration flow path not within purge valve leakage limits and was reported in accordance with 10 CFR 50. 72(b)(3)(v)(C) (reference EN#52511 ). Repairs were completed on CV4303 and both primary containment valves were declared operable at 1007 CST on January 26, 2017. The cause of this event was determined to be inadequate work instructions and maintenance procedures. This event was of low safety significance and had no impact on public health or safety. This event is reportable pursuant to 1OCFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) ~"'A~C... Estimated burden per response to comply with this mandatory collection request: 80 hours. f~ :. g . Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and lnfonnalion Collections \ ..... .J Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by LICENSEE EVENT REPORT (LER) internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of lnfonnation and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, CONTINUATION SHEET Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the infonnation collection. 1. FACILITY NAME 2. DOCKET · 6. LER NUMBER 3. PAGE I YEAR I SEQUENTIAL REV NUMBER NO. Duane Arnold Energy Center 05000-331 2 OF 5 2017 001 00 | I. Description of Event: CV4302/CV4303 Background The Fisher series 9200 butterfly valve used for the Primary Containment Purge and Vent System, including valves CV4302, Drywell Vent Line Inboard Isolation valve, and CV4303, Drywell Vent Line Outboard Isolation valve, employs a heavy-duty butterfly valve body designed for stringent shutoff requirements. In the particular model valve used for Containment Purge and Vent, a rubber T-ring seat is contained in the valve body, and an external sealing pressure forces the T-ring against the disc periphery only when the disc is closed. There is no contact between the disc and T-ring when the disc is opening or closing. T-ring (or T-seal) pressurization is accomplished automatically through the use of a plunger-actuated Numatics valve which allows air pressure to the T-seal chamber when activated by an external lever. This lever is attached to the valve shaft opposite the actuator end, and is secured with a key and setscrew such that the lever is in line with the disc. Fine adjustment of the Numatics valve plunger depression is afforded by a capscrew threaded into the lever and held in place with a locking nut. Event During Refueling Outage (RFO) 25, planned maintenance was performed on CV4302 and CV4303. The following narrative discusses the work performed on CV4302, which is also indicative of work performed on CV4303. RFO 25 began on October 3, 2016. On October 6, 2016, as-found Local Leak Rate Tests (LLRTs) were performed on CV4302 and CV4303 with satisfactorily results. On October 9, Preventative Maintenance (PM) 40389727, CV4302: Replace T-seal, 0-Rings, and Numatics Valve, commenced. From October 10 to October 17, the valve rebuild activities were completed. On October 19, a new Numatics valve was installed. As part of this task, the Numatics valve is set up in accordance with maintenance procedure VALVE-F130-01, Repair of 9200 Series T-ring Butterfly Valves, Appendix 3. Post Maintenance Testing (PMT) was completed satisfactorily on October 20, 2016. As-left Leakage Integrity Testing was completed with satisfactory results on October 25. During startup from RFO 25, CV4302 and CV4303 were cycled as part of primary containment inerting. The cycling of the valves started a 92 day Technical Specification (TS} Action Statement, to perform Surveillance Requirements (SRs) for Leakage Integrity Testing (TS SR 3.6.1.3.4). NRC FORM 366 (06-2016) | ML17089A381
LaSalle County Station | Unit 2 | High Pressure Core Spray System Declared Inoperable due to Cooling Water Strainer Backwash Valve Stem-Disc Separation | 03-30-2017 | On January 30, 2017, during routine surveillance testing of the Unit 2 Division 3 Diesel Generator Cooling Water (DGCW) system, the cooling water strainer backwash valve·w as unable to open. The Division 3 DGCW system was declared inoperable. Upon investigation, operators determined the cause of the valve malfunction was due to stem-disc separation. Division 3 DGCW is a support system for the Division 3 Emergency Diesel Generator and the High Pressure Core Spray (HPCS) system. The required actions of Technical Specifications (TS) 3.7.2 and 3.5.1 were entered on January 30, 2017 when the DGCW and HPCS system, respectively, were determined to be inoperable. TS 3.7.2 Required Action (RA) A.1 requires the supported system to be immediately declared inoperable. TS 3.5.1 RA B.2 requires restoration of the HPCS system to operable within 14 days. TS 3.8.1 · was not applicable since a note provides that Division 3 AC electrical power sources are not required to be operable when HPCS is inoperable. The valve was replaced, and the HPCS system was returned to operable on February 2, 2017. This condition could have prevented the HPCS system, a single train safety system, from performing its design function. This event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of the safety function of structures or system that are needed to mitigate the consequences of an accident. There were minimal safety consequences associated with the event since the other emergency safety systems remained operable, and the Division 3 DGCW system remained functional as it retained the ability to provide the required flow through the system. The apparent cause of the stem-disc separation was erosion due to the carbon-steel valve internals in a raw water system environment. NRC FORM 366 (06·2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/201 B (06-2016)) Estimated burden per response to comply with this mandatory collection request: BO hours. Reported lessons learned are incorporated into the licensing process and led back to industry. Send comments regarcing burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office al Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office al Management and Budget, Washington, DC 20503. II a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r30 collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV LaSalle County Station, Unit 2 05000374 YEAR NUMBER NO. 2017 - 002 00 | PLANT AND SYSTEM IDENTIFICATION LaSalle County Station Unit 2 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the Division 3 Diesel Generator Cooling Water (DGCW) system, which is a support system for the High Pressure Core Spray (HPCS) system and associated Division 3 Emergency Diesel Generator. CONDITION PRIOR TO EVENT Unit(s): 2 Event Date: January 30, 2017 Event Time: 1908 CST Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 98 percent DESCRIPTION OF EVENT On January 30, 2017, during monthly operability surveillance testing of the Unit 2 Division 3 DGCW system, the cooling water strainer backwash valve 2E22-F319 was unable to open when the strainer control switch was selected and during subsequent manual operation of the valve. The valve was eventually able to be closed; however, no flow was detected during the manual backwash operation_ The Division 3 DGCW system was declared inoperable. Upon investigation, operators determined the cause of the valve malfunction was due to stem-disc separation. The Division 3 DGCW system is a support system for the HPCS system and the associated Division 3 Emergency Diesel Generator. The required actions ofTechnical Specifications (TS) 3.7.2 were entered on January 30, 2017 at 1908 CST when the 28 DGCW system was declared inoperable. Required Action (RA) A.1 was immediately completed to declare the supported HPCS system inoperable. TS 3.5.1 RA B.1 to administratively verify the Reactor Core Isolation Cooling (RCIC) system operability was completed immediately, and RA B.2 was entered to restore HPCS to operable status within 14 days. TS 3.8.1 was not applicable since a note provides that Division 3 AC electrical power sources are not required to be operable when HPCS is inoperable. An Emergency Notification System (ENS) report 52519 was made on January 30, 2017 in accordance with 10 CFR 50.72(b)(3)(v)(D), for an event or condition that could have prevented fulfillment of the safety function of structures or system that are needed to mitigated the consequences of an accident. CAUSE OF EVENT The Division 3 DGCW strainer backwash valve 2E22-F319 was unable to open due to stem-disc separation within the valve body. The apparent cause of the stem-disc separation was erosion due to the carbon-steel valve internals in a raw water system environment. The use of carbon steel valves and components in raw water systems led to the valve component's accelerated corrosion and pitting. Contributing causes include extension of preventative maintenance (PM) to replace the valve beyond the life of valve 2E22- F319, and T-gap measurement used to determine valve health requires optimization. The use of carbon steel valves in raw water systems was first evaluated in 1996 as an operational vulnerability at LaSalle Station. The valve failed prior to its scheduled replacement in November 2017. REPORTABILITY AND SAFETY ANALYSIS This event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of the safety function of structures or system that are needed to mitigate the consequences of an accident. This condition could have prevented the HPCS system, a single train safety system, from performing its design function, to provide cooling to the required equipment, which rendered the cooling water system inoperable in accordance with TS 3.7.2, Diesel Generator Cooling Water (DGCW) System. | ML17089A657
Edwin I. Hatch Nuclear Plant | Unit 1 | High Pressure Coolant Injection System Declared Inoperable Due to Degraded Inverter | 04-07-2017 | On February 8, 2017, at 1151 EST with Unit 1 at approximately 100 percent rated thermal power, the High Pressure Coolant Injection (HPCI) suction and discharge pressure indicators were noted to be downscale during a main control room panel walk down. Upon further investigation, it was discovered that the output voltage of the DC to AC inverter was degraded. The HPCI DC to AC inverter supplies power to the HPCI flow controller and power supply. HPCI was therefore declared inoperable due to the degraded voltage condition. The inoperable as found condition of the HPCI pressure indicators was due to degraded output voltage from the DC to AC HPCI inverter. The degraded inverter was removed and replaced and HPCI was returned to operable status. As part of an extent of condition review, the internals of the degraded inverter were inspected to determine what caused premature failure of the inverter. Based on the findings of this inspection, the preventative maintenance frequency for inverter replacement and calibration will be adjusted as necessary. NRC FORM 366A (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016,). ,. ......... Estimated burden per response to comply with this mandatory collection request: 80 hours Reported lessons learned are incorporated into the licensing process and fed back to industry ; 1 ~ l -"i· LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to the FOIA, Privacy and Information Collections ~ ..... ~' CONTINUATION SHEET Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-ma1l to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a (See NUREG-1 022, R.3 for instruction and guidance for completing this form means used to impose an information collection does not display a currently valid OMB control http://www.n rc.gov/reading-rm/doc-collections/nureas/staff/sr1 022/r3D number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER I I YEAR SEQUENTIAL REV Edwin I. Hatch Nuclear Plant Unit 1 05000-321 NUMBER NO 2017 -002 -00 | Event Description On February 8, 2017, at 1151 EST with Unit 1 at approximately 100 percent rated thermal power, the High Pressure Coolant Injection (HPCI) suction and discharge pressure indicators were noted to be downscale during a main control room panel walk down. Upon further investigation, it was discovered that the output voltage of the DC to AC inverter (EllS Code INVT) was degraded. This inverter provides power to multiple HPCI control room indications as well as to the HPCI flow controller and power supply. HPCI was therefore declared inoperable. Failed Components Information: Master Parts List Number: 1 E41 K603 Manufacturer: Abacus Controls Inc. Model Number: 452-4-120M9 Type: Inverter Event Cause Analysis The cause of the event is due to degradation of the output voltage of the DC to AC inverter. The HPCI DC to AC inverter supplies power to the HPCI flow controller and power supply. The flow controller maintains constant flow over the pressure range of HPCI system operation and automatically starts if HPCI system initiation is required. The power supply provides DC control power to the HPCI Turbine Speed Control logic. Without the flow controller and the power supply, the HPCI Turbine would not be able to run if called upon, causing HPCI to be declared inoperable. Safety Assessment This event is reportable per 10 CFR 50.73(a)(2)(v)(D) due to an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. The HPCI system is a single train system designed to permit the unit to be shut down while maintaining sufficient reactor pressure vessel (RPV) water inventory. The system continues to operate until the RPV is below the pressure at which either operation of the Low Pressure Coolant Injection (LPCI) mode of the Residual Heat Removal or the Core Spray (CS) system will maintain core cooling. The HPCI system consists of a steam turbine that drives a constant flow pump, system piping, valves, controls, and instrumentation. Upon receipt of an initiation signal, the HPCI turbine stop valve and turbine control valve open simultaneously. The HPCI turbine then accelerates to a specified speed to provide necessary pump flow. Upon a "small" or "intermediate" break resulting in a loss of coolant accident (LOCA), HPCI provides sufficient inventory to prevent the core from being uncovered. It performs a dual function by providing j makeup water to the reactor pressure vessel (RPV) as well as supplementing the break in depressurizing the RPV. If HPCI is unavailable, the Automatic Depressurization System (ADS) is credited to depressurize | ML17097A333
Susquehanna Steam Electric Station | Unit 1 | Secondary Containment Breach due to Simultaneous Opening of Airlock Doors | 01-02-2017 | On February 17, 2017, three technicians were walking through the 818' Airlock doors. The lead (first) technician observed the green light, swiped their badge and entered into the airlock. The two additional technicians then swiped their badges and walked into the airlock. The lead technician observed the first door closing and turned to open the second airlock door. As the first technician opened the second door the Airlock Door alarm sounded briefly as the first door was not completely closed and latched. This caused an alarm for a momentary breach of Secondary Containment. When they heard the alarm, both workers shut the doors. This airlock serves as a secondary containment boundary; as such, having both doors open at the same time results in failure to meet Technical Specification 3.6.4.1 as a result of not satisfying Surveillance Requirement 3.6.4.1.3. The condition is being reported in accordance with 10 CFR 50. 73(a)(2)(v)(C). The cause of the event was less than adequate situational awareness. Corrective actions included documented coaching of the worker. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366A (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. l'··;:;·<.\ Reported lessons teamed are incorporated into the licensing process and fed back to industry. LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to the FOIA, Privacy and Information Collections \~!!i Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail CONTINUATION SHEET to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a (See NUREG-1022, R.3 for instruction and guidance for completing this form means used to impose an information collection does not display a currently valid OMB control http://www.nrc.gov/readinq-rm/doc-collections/nureos/staff/sr1022/r3/) number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER I I YEAR SEQUENTIAL REV Susquehanna Steam Electric Station, Unit 1 05000-387 NUMBER NO. 2017 -002 -00 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, approximately 097 percent Rated Thermal Power Unit 2 - Mode 1, approximately 092 percent Rated Thermal Power There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. Unit 2 was in coast down prior to the refueling outage. EVENT DESCRIPTION On February 17, 2017 at approximately 1040, three maintenance workers entered the Refuel Floor Air Lock [EllS: AL]. The first worker entered the airlock followed by the second and third workers and began to open the second door [EllS: DR] before the third individual closed the first door. This caused an alarm [EllS: ALM] for a momentary breach of Secondary Containment [EllS: VA]. When they heard the alarm, both workers shut the doors. This airlock serves as a secondary containment boundary; as such, having both doors open at the same time results in failure to meet Technical Specification 3.6.4.1 as a result of not satisfying Surveillance Requirement 3.6.4.1.3. CAUSE OF THE EVENT The cause of the event was less than adequate situational awareness. ANALYSIS/ SAFETY SIGNIFICANCE Technical Specification 3.6.4.1 Surveillance Requirement 3.6.4.1.3 requires that one secondary containment access door in each access opening is closed. This event is being reported pursuant to 10 CFR 50.73(a)(2)(v)(C) as having both Secondary Containment airlock doors momentarily open simultaneously resulting in a condition that could have prevented fulfillment of a safety function to mitigate the consequences of an accident by controlling the release of radioactive material. There was no actual safety consequence as a result of this event. Engineering analysis of this event has determined that secondary containment could have performed its safety function of isolating, as assumed in the accident analysis, and also of re-establishing 0.25 in w.g. vacuum (drawdown) within the assumed accident analysis time ( 10 minutes). This event will not be counted as a safety system functional failure (SSFF) for the NRC performance indicator. CORRECTIVE ACTIONS Corrective actions completed included coaching of the individual who opened the second airlock door. | ML17102B408
Edwin I. Hatch Nuclear Plant | Unit 1 | Inoperable Secondary Containment Due to Incorrect Penetration Flange Installation | 10-31-2018 | On February 17, 2017 at 1414 EST, with Un~ 1 at 100 percent rated thermal power and Unit 2 at 0 percent rated thermal power due to a scheduled refueling outage, it was identified during an operations walkdown that a temporary blind flange was installed incorrectly, rendering secondary containment inoperable. In support of the Unit 2 Hardened Containment Vent System Wetwell Project, a temporary blind flange was to be installed downstream of the Standby Gas Treatment (SBGT) inlet isolation valve to prevent a breach of secondary containment. It was subsequently identified that upon removal of the SBGT isolation valve, the blind flange was installed on the wrong side of the piping. At 1503 EST on February 17, 2017, the blind flange was moved to the correct side of the piping and secondary containment was declared operable. The cause of the event is due to having a lack of oversight, a lack of intrusiveness, and an inadequate challenge of the work instructions provided to the supplemental workers performing the work. Workers assumed that the work instructions meant for the blind flange to be installed downstream of primary containment rather than downstream of the SBGT inlet isolation valve. The work order planning procedure will be updated to require Southern Nuclear Operating Company (SNC) verification and signature for the installation of flanges and similar equipment. NRC FORM 366 (06-2016) NRC F,O.R M 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) ...... Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and led back to industry. ~~~ LICENSEE EVENT REPORT (LEA) Send comments regarding burden estimate to the FOIA, Privacy and Information Collections \~..l..'. j Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail CONTINUATION SHEET to lnlocollects.Resource@nkgov, and to the Desk Officer, Office ol Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office ol Management and Budget, Washington, DC 20503. II a (See NUREG-1 022, R.3 for instruction and guidance for completing this form means used to impose an information collection does not display a currently valid OMB control http://www.nrc.gov/reading-rrn/doc-collections/nureas/staff/sr1 022/r31) number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER I I YEAR SEQUENTIAL REV Edwin I. Hatch Nuclear Plant Unit 1 05000-321 NUMBER NO. 2017 -003 -00 | Event Description On February 17, 2017 at 1414 EST, with Unit 1 at 100 percent rated thermal power and Unit 2 at 0 percent rated thermal power due to a scheduled refueling outage, it was identified during an operations walkdown that a temporary blind flange was installed incorrectly, rendering secondary containment inoperable. The temporary blind flange was installed on February 8, 2017 at 0920 EST in support of the Unit 2 Hardened Containment Vent System (HCVS) Wetwell Project. As part of the project, the Unit 2 Standby Gas Treatment (SBGT) inlet isolation valve which separates the primary containment purge and inerting system from the SBGT system was removed from the line for local leak rate testing. During the period of time the isolation valve was to be removed, a temporary blind flange was to be installed on the downstream side of the opening to prevent a breach of secondary containment. After finding the temporary blind flange on the upstream side of the opening, it was revealed that upon removal of the SBGT isolation valve, the blind flange was installed on the wrong side of the opening. This opened a pathway outside of containment when containment modes changed on February 8, 2017 at 10 35 EST when the Unit 2 reactor building was opened to the environment due to a scheduled refueling outage, resulting in a breach of secondary containment. The as-found configuration rendered secondary containment inoperable for Unit 1. Actions were made to immediately suspend fuel movement and restore secondary containment by putting the flange on the correct side of the opening. At 1503 EST on February 17, 2017, the blind flange was moved to the correct side of the flange and secondary containment was declared operable. Event Cause Analysis The cause of the event is due to having a lack of oversight, a lack of intrusiveness, and an inadequate challenge of the work instructions provided to the supplemental workers performing the work. The supplemental maintenance workers had an incorrect mindset and assumed that the blind flange was to be installed on the primary containment side of the containment piping to provide protection for the reactor. Therefore, the work instructions to install the blind flange on the "downstream" side of the opening were not followed. Workers assumed that the work instructions meant for the blind flange to be installed downstream of primary containment rather than downstream of the SBGT inlet isolation valve. The associated work order package did not contain annotated drawings showing the exact installation location of the blind flange. Workers consequently proceeded with the installation of the blind flange on the incorrect side of the opening without having their assumptions verified. Safetv Assessment This event is reportable per 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications and also per 10 CFR 50.73(a)(2)(v)(C) as a condition that at the time of discovery, could have prevented the fulfillment of the safety function of a system needed to control the release of radioactive material. The secondary containment system contains the primary containment system and other nuclear systems, and limits the ground-level release of airborne radioactive material. It provides a means for a controlled elevated release of the building atmosphere such that offsite doses from a fuel-handling or loss-of-coolant accident (LOCA) will be below the guideline values stated in 10 CFR 50.67. It is designed to provide secondary containment when the primary containment is closed and in service, and to provide primary containment when the primary containment is open, e.g., during a refueling outage. Secondary containment is isolated on the same signals that actuate the Standby Gas Treatment (SBGT) system. Activation of the SBGT Page 2 of 3 | ML17103A233
Susquehanna Steam Electric Station | Unit 2 | Secondary Containment Breach Due to Simultaneous Opening of Airlock Doors | 10-31-2018 | On March 2, 2017, at approximately 0930, two employees were transporting a cart of scaffold materials from Reactor Building Elevation 818' to Elevation 779'. While maneuvering the cart through an airlock on Elevation 779', personnel failed to ensure that the Reactor Building-side airlock door was fully closed prior to opening the Turbine Building-side airlock door. This resulted in not meeting Technical Specification 3.6.4.1 Surveillance Requirement 3.6.4.1.3, which requires that one secondary containment access door in each access opening is closed. The cause of this event was determined to be less than adequate use of Human Performance Tools, specifically Verification Practices. This condition requires reporting in accordance with 10 CFR 50. 73(a)(2)(v)(C) as having both Secondary Containment airlock doors momentarily open simultaneously results in a condition that could have prevented fulfillment of a safety function. There were no actual consequences to the health and safetyof the public as a result of this event. NRC FORM 366A (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016} Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555·0001, or by e-mail CONTINUATION SHEET to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a (See NUREG-1022, R.3 for instruction and guidance for completing this form means used to impose an information collection does not display a currenlly valid OMB control http://lf-.IWN.n rc.gov/readi nq-rm/doc-collections/nuregs/staff/sr1 022/r3/) number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITYNAME 2. DOCKET NUMBER 3. LER NUMBER I I SEQUENTIAL REV YEAR Susquehanna Steam Electric Station 05000388 NUMBER NO. Unit2 2017 -003 -00 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, approximately 100 percent Rated Thermal Power Unit 2- Mode 1, approximately 89 percent Rated Thermal Power There were no systems, structures or components that were inoperable at the start of the event and contributed to the event. EVENT DESCRIPTION On March 2, 2017, at approximately 0930, two contract employees were transporting a cart of scaffold materials from Reactor Building [EllS Component Identifier: NG] Elevation 818' to Elevation 779'. While maneuvering the cart through an airlock [EllS Component Identifier: AL] on Elevation 779', personnel failed to ensure that the Reactor Building-side airlock door [EllS Component Identifier: DR] was fully closed prior to opening the Turbine Building-side [EllS Component Identifier: NM] airlock door. This resulted in not meeting Technical Specification 3.6.4.1 Surveillance Requirement 3.6.4.1.3, which requires that one secondary containment access door in each access opening is closed. CAUSE OF EVENT The cause of this event was determined to be less than adequate use of Human Performance Tools, specifically Verification Practices. ANALYSIS/SAFETY SIGNIFICANCE Technical Specification 3.6.4.1 Surveillance Requirement 3.6.4.1.3 requires that one secondary containment access door in each access opening is closed. This event is being reported pursuant to 10 CFR 50.73(a)(2)(v)(C) as having both Secondary Containment airlock doors momentarily open simultaneously results in a condition that could have prevented fulfillment of a safety function to mitigate the consequences of an accident by controlling the release of radioactive material. There was no actual safety consequence as a result of this event. Engineering analysis of this event has determined that secondary containment could have performed its safety function of isolating, as assumed in the accident analysis, and also of re-establishing 0.25 in w.g. vacuum (drawdown) within the assumed accident analysis time (10 minutes). Therefore, this event will not be counted as a safety system functional failure (SSFF) for the NRC performance indicator. CORRECTIVE ACTIONS Key corrective actions include the following: 1. Review Secondary Containment door verification practices communication with all employees of this contractor (Complete). | ML17103A320
LaSalle County Station | Unit 1 | Automatic Reactor Scram due to Main Generator Trip on Differential Current During Back-Feed Operations | 04-14-2017 | On February 13, 2017, LaSalle County Station Unit 1 was in Mode 1 at 100 percent power and Unit 2 shut down for a planned refueling outage. At 2309 CST, a reactor scram signal was received on Unit 1 due to turbine control valves fast closure while the station was aligning back-feed operation to the Unit 2 main power transformer (MPT). The Unit 1 turbine trip was due to the main generator trip on differential current. The plant was placed in a stable condition with reactor pressure maintained by the turbine bypass valves and reactor water level controlled using feedwater. Unit 2 was unaffected by the event. The root cause of the Unit 1 trip on differential current was a marginal generator differential relay design that was prone to responding to faults outside its zone of protection. Both units' 345 kV ring buses were connected together through the cross-tie bus, which allowed the Unit 1 generator to supply some of the electrical current that resulted in its differential circuit to create an unbalanced current that actuated the differential relay. This event is reportable in accordance with 1O CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in manual or automatic actuation of the reactor protection system (RPS), including reactor scram. There were no safety consequences associated with the event since RPS and other emergency safety systems functioned as designed. NRC FORM 366 (04·2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) . Estimated burden per response to comply with this mandatory collection request: 80 hoors. Reported lessons teamed are inc01pOraled into the licensing process and fed back lo industry. Send comments regarcing burden estimate to the lnfonnation Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LEA) Regulatory Commission, Washington, DC 20555-0001, or by e-mail lo fnfocollecls.Resource@nrc.gov, and to the Desk Officer, Office of lnfonnation and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an infonnation collection does not cisplay a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is nol required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r31) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR LaSalle County Station, Unit 1 0500073 NUMBER NO. 2017 - 003 00 | PLANT AND SYSTEM IDENTIFICATION LaSalle County Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system is the 345 kV switchyard. The switchyard consists of a ring-bus arrangement for each unit and a cross-tie bus that interconnects the units' ring buses. Each unit has a main power transformer (MPT), system auxiliary transformer (SAT), and a unit auxiliary transformer (UAT). Each of the two main generators is connected to two half-size main transformers and a UAT through isolated phase electrical bus ducts. The main power transformers step up the voltage, where power is delivered to the switchyard. The main generator and associated isolated phase bus duct is protected from electrical faults by several relaying features that will trip the generator to protect it from damage. CONDITION PRIOR TO EVENT Unit(s): 1 Event Date: February 13, 2017 Event Time: 2309 CST Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 100 percent DESCRIPTION OF EVENT On February 13, 2017, LaSalle County Station Unit 1 was in Mode 1 at 100 percent power, while Unit 2 was in a planned refueling outage. Unit 2 switchyard switching activities were in progress necessary to establish electrical back-feed power supply to the Unit 2 MPT. Switching activities included closing a main generator output breaker on Unit 2. At 2309 hours CST, the Unit 1'main generator received a trip on the 'B' phase differential current relay and subsequent main generator lock-out, which resulted in a Unit 1 automatic main turbine trip and subsequent Unit 1 automatic reactor scram due to fast closure of the turbine stop valves. In response to the event, one of the safety relief valves actuated in the relief mode upon the turbine trip and subsequently reset with tailpipe temperature returning to normal. The plant was in a stable condition with reactor pressure maintained by the turbine bypass valves. Reactor water level was controlled with feedwater, and all control rods fully inserted for the scram. CAUSE OF EVENT The root cause of the. Unit 1 trip on differential current was a marginal generator differential relay design prone to responding to faults outside its zone of protection. Since both units' 345 kV ring buses are connected together through a cross-tie bus, this allowed the Unit 1 generator, which is the closest and strongest source, to supply some of the current and resulted in its differential circuit creating an unbalanced current that actuated the differential relay. Contributing to this event was the current switchyard alignment methodology used for MPT back-feed operations. The current methodology challenges the margin of electro-mechanical differential current protective relays. An additional contributing cause was the use of larger transformers in place of the existing MPT, which changed the nature of the in-rush transient and introduced different current transformers into the differential relay scheme. There has been operating experience regarding similar consequences related to similar differential relay scheme designs and related to transformer in-rush transients. Although some of this experience was recognized by the station and the corporate organization, the opportunity to change the back-feed switching scheme to mitigate the in-rush transient was missed. | ML17104A085
Browns Ferry Nuclear Plant | Unit 2 | High Pressure Coolant Injection Safety System Functional Failure Due to a Blown Fuse | 04-14-2017 | On February 16, 2017, the spurious failure of a fuse protecting a High Pressure Coolant Injection (HPCI) system !flow controller rendered the HPCI system inoperable. Operators replaced both the line and neutral fuses, and restored HPCI availability. Following a period of monitoring the current flow through the fuse and HPCI system operation tests, Operations declared the Unit 2 HPCI system to be Operable on February 17, 2017. Since HPCI is a single-train safety system, any period of unplanned inoperability constitutes a safety-system !functional failure affecting accident mitigation, and is reportable. However, in the event of an emergency, the Reactor Core Isolation Cooling (RCIC) system remained operable, and all other Emergency Core Cooling Systems and the Automatic Depressurization System were available throughout this event to facilitate core cooling. Failure analysis indicates that the fuse failed when its internal resistor lead and its tension/retraction spring became uncoupled at their soldered junction, as a result of age-induced solder creep. Corrective Actions include he prompt replacement of the failed fuses, determining the population of fuses on the HPCI system and RCIC system that should be replaced on a one-time basis, and to initiate work orders to replace these fuses. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http ://www. n re.g ov /reading-rm/doc-col lectio ns/nu regs/staff/sr1 022/r3[J NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Browns Ferry Nuclear Plant, Unit 2 05000-260 NUMBER NO. 2017 - 001 - 00 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Unit 2, was in Mode 1 at approximately 76 percent power. II. Description of Event A. Event Summary On February 16, 2017, at 1052 Central Standard Time (CST), while the BFN Unit 2 High Pressure Coolant Injection (HPCI) system [BJ] was in standby readiness, Operations received the HPCI 120VAC POWER FAILURE alarm on Panel 2-9-3F. The crew responded per the Alarm Response Procedure and identified that fuse [FU] 2-FU2-073-0033C in the Auxiliary Instrument Room had cleared. This fuse protected the HPCI system flow controller (2-FIC-77-33), power supplies to the governor controls, and power supplies to various pressure transmitters from overcurrent events. Since the HPCI system is a single-train safety system, any period of unplanned inoperability constitutes a safety-system functional failure affecting accident mitigation, and is a reportable event. Operators replaced both the line and neutral fuses, and HPCI system availability was restored on February 16, 2017 at 1145 CST. Following a period of monitoring the current flow through the fuse and HPCI system operation tests, Operations declared the Unit 2 HPCI system Operable on February 17, 2017 at 1730 CST. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components whose inoperability contributed to this event. | ML17104A238
LaSalle County Station | Unit 1 | Secondary Containment lnorerable Due to Interlock Doors Open | 04-17-2017 | On February 16, 2017, Unit 1 was in Mode 2 for startup at five percent power, and Unit 2 was defueled for a planned refueling outage with movement of irradiated fuel (MIF) in progress. At 0835 CST, both air-lock doors of the Unit 1 reactor building to the chemistry corridor were opened simultaneously for approximately five seconds during personnel ingress. The employee immediately secured both doors in the interlock and notified the Main Control Room. While both interlock doors were open, Technical Specifications (TS) Surveillance Requirement (SR) 3.6.4.1.2 to verify one secondary containment access door in each access opening is closed was not met. Secondary containment was declared inoperable for the period of time that both interlock doors were open. TS 3.6.4.1 Required Action (RA) A.1 to restore secondary containment to operable status within four hours was entered and exited. TS 3.6.4.1 RA C.1 to immediately suspend MIF in secondary containment was entered and exited. This event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(C) and 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material or mitigate the consequences of an accident. The most probable cause of the interlock failure was the intermittent failure of a circuit board which is designed to prevent more than one door to be open at a time. Previous events and prior causal investigations have indicated degradations in the relays for these circuit cards, and the corrective actions to replace interlock door circuit cards was ongoing at the time this event occurred. The door interlock was satisfactorily tested by maintenance technicians, and the door interlock was returned to service on February 18, 2017. NRC FORM 366 (04·2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: BO hours. Reported lessons learned are incoiporated Into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR LaSalle County Station, Unit 1 05000373 NUMBER NO. 2017 - 004 00 | PLANT AND SYSTEM IDENTIFICATION LaSalle County Station Unit 1 and Unit 2 are each a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The secondary containment is the reactor building, common to both reactor units, which contains the reactor auxiliary and serving equipment for the two reactors. The secondary containment access doors, or air-locks, provide a means for personnel and equipment to enter or exit the reactor building without breaching secondary containment integrity. CONDITION PRIOR TO EVENT Unit(s): 1 / 2 Event Date: February 16, 2017 Event Time: 0835 CST Reactor Mode(s): 2 / 5 Mode(s) Name: Startup/Refueling Power Level: 5 percent/O percent DESCRIPTION OF EVENT On February 16, 2017, Unit 1 was in Mode 2 for plant startup at 5 percent power, and Unit 2 was defueled for a planned refueling outage with movement of irradiated fuel (MIF) in progress. At 0835 CST, both air-lock doors of the Unit 1 reactor building to the chemistry corridor (doors 225 and 226) were opened simultaneously for approximately five seconds during personnel ingress. The employee immediately secured both doors in the interlock and notified the Main Control Room (MCA). Shift Operations personnel subsequently blocked access until repairs could be made, and MIF activities were immediately suspended. While both interlock doors were open, Technical Specifications (TS) Surveillance Requirement (SR) 3.6.4.1.2 to verify one secondary containment access door closed was not met. Secondary containment was declared inoperable for the period of time that both interlock doors were open. Reactor building differential pressure, as observed in the MCA, remained less than -0.25 inches vacuum water gauge at all times. TS 3.6.4.1 Required Action (RA) A.1 to restore secondary containment to OPERABLE status within four hours was entered and exited. TS 3.6.4.1 RA C.1 to immediately suspend MIF in secondary containment was entered and exited. CAUSE OF EVENT The most probable cause of the interlock failure was the intermittent failure of a circuit board which is designed to prevent more than one door to be open at a time. Similar previous interlocked door circuit board failures have been identified, through formal failure analysis, to have been caused by degraded relays integral to the circuit board. This interlock had used an upgraded style of circuit board that had been installed less than a week earlier on February 10, 2017. The door was satisfactorily tested by Mechanical Maintenance, but the failure could not be reproduced. A causal investigation for an event in 2016 identified relays on the circuit cards as the specific cause of the failures. Corrective actions from the 2016 investigation had been ongoing to upgrade interlock door circuit cards with ones that had improved relays. REPORTABILITY AND SAFETY ANALYSIS This event is reportable in accordance with 1O CFR 50.73(a)(2)(v)(C) and 1O CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material or mitigate the consequences of an accident. These doors are ground elevation personnel air-lock between the common diesel generators' corridor to the Unit 2 reactor building. The secondary containment access doors, or air-locks, provide a means for personnel and equipment to enter or exit the reactor building without breaching secondary containment integrity. This is necessary so that the negative pressure can be maintained. The safety significance of this event was minimal, since the reactor building to outside differential pressure remained negative throughout the period that the secondary containment was inoperable. The secondary containment was inoperable for approximately five seconds, which was significantly less than the four-hour Completion Time to restore secondary containment to operable status allowed by TS 3.6.4.1 Required Action A.1. NAC FOAM 366A (04-2017) Page _2_ of _4_ | ML17107A089
LaSalle County Station | Unit 1 | Manual Reactor Scram Resulting From Feedwater Regulating Valve Failure Causing High Reactor Water Level | 04-18-2017 | On February 17, 2017, at 2353 CST, during Unit 1 power ascension from a previous forced shutdown, operators inserted a manual scram as a result of a high reactor water level condition caused by a rapid change in feedwater flow. The high reactor water level trip occurred due to a failure of the feedwater regulating valve (FRV) 1F W005 positioner arm, which caused the regulating valve to be driven to the full open position. This resulted in a rapid increase of reactor water level that required operators to perform a manual reactor scram. The plant was placed in a stable condition, with no complications in achieving shutdown. This event is reportable in accordance with 1O CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in manual or automatic actuation of the reactor protection system (RPS). The safety significance of this condition was minimal, as plant equipment responded as expected for the event. The feedback drive arm and new positioner were installed on the Unit 1 FRV, which allowed the unit to restart following repairs. The FRV positioner feedback assembly had been installed in 2002, during a modification to upgrade of the air-operated valve assembly. This design has proven not to be robust enough for the FRV application. NRC FORM 366 {04·2017) NRG FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory ccllection request: BO hours. Reported lessons learned are incorporated into the licensir.g process and fed back to industry. Send comments regarding burden es:imate to the ln!ormaticn Services Branch (T-2 F43}, U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfoconects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management anc Budget, Washington, DC 20503. If a means used to impose an information collection does not Cisplay a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR LaSalle County Station, Unit 1 05000373 NUMBER NO. 2017 - 005 00 | PLANT AND SYSTEM IDENTIFICATION LaSalle County Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The Feedwater (FW) system provides a source of processed water to the reactor pressure vessel (RPV) to maintain the desired water level during normal plant operating conditions. The affected component was the Feedwater Regulating Valve (FRV), which is used to control the flow of FW to the RPV for water level control when the motor-driven reactor feed pump is used. CONDITION PRIOR TO EVENT Unit(s): 1 Event Date: February 17, 2017 Event Time: 2353 CST Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 30 percent DESCRIPTION OF EVENT On February 17, 2017, Unit 1 was in the process of power ascension at approximately 30 percent power from a previous forced shutdown. At 23:53 CST, the Main Control Room received a FW control RPV high level alarm. Operators quickly diagnosed an abrupt change in reactor water level and that level was rapidly increasing. The operators entered the abnormal procedures in parallel with setting manual scram criteria of greater than 50 inches reactor water level and not in control, as directed by station procedures. The manual scram was initiated as level was approaching the turbine trip set point of 55.5 inches in order to terminate the transient. The scram was not complicated, and all equipment performed as designed. The plant was placed in a stable condition, with reactor pressure maintained by the turbine bypass valves. Reactor water level was controlled with FW through the low-flow regulating valve. All control rods fully inserted, and decay heat was removed via steam to the main condenser using bypass valves. CAUSE OF EVENT The high reactor water level trip occurred due to a failure of the FW regulating valve (FRV) positioner arm, which caused the regulating valve to be driven to the full open position and resulted in a rapid increase in RPV level. Field observations at FRV 1 FW005 revealed that the valve positioner feedback drive arm had broken cleanly into two pieces at the junction between the arm and shaft. The feedback drive arm extension was also found to be severely bent. The FRV positioner feedback assembly was a standard vendor design when installed as part of the hydraulics for the upgrade of the air-operated valve (AOV) performed in 2002. This design of the valve position feedback assembly has proven not to be robust enough for the FRV application. Contributing to this event were FRV cycling during operations caused by the inherent dead-band of the valve positioner and the · positioner feedback assembly. REPORTABILITY AND SAFETY ANALYSIS The event was reportable to the NRC in accordance with 10 CFR 50.72(b)(2)(iv)(B) for any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical. An Emergency Notification System (ENS) report number 52564 was made on February 18, 2017. This event is also reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in manual or automatic actuation of the reactor protection system (RPS). The safety significance of this condition was minimal, as plant equipment responded as expected for the event; therefore, there were no impacts to plant safety o.r design margins. | ML17108A430
Beaver Valley Power Station | Unknown Unit | Inadequate Tornado Missile Protection Identified Due to Non-Conforming Design Conditions | 04-18-2017 | In order to address the concerns outlined in NRC Regulatory Issue Summary (RJS) 2015-06 "TORNADO MISSILE PROTECTION", an evaluation of tornado missile vulnerabilities and their potential impact on Technical Specification (TS) plant equipment was conducted. This evaluation concluded that the following Structures, Systems, and Components (SSCs) are potentially vulnerable to tornado generated missiles: The steam discharge flow paths to atmosphere of the Beaver Valley Power Station Unit 1 (BV-1) and Unit 2 (BV-2) Main Steam Safety Valves (MSSVs) (reference TS 3.7.1) are potentially vulnerable to tornado generated missiles. The steam discharge flow paths to atmosphere of the BV-1 and BV-2 Atmospheric Dump Valves (ADVs) (reference TS 3.7.4) are potentially vulnerable to tornado generated missiles. On February 23, 2017, the BV-1 and BV-2 TS required MSSVs and ADVs were declared inoperable and Enforcement Guidance Memorandum (EGM) 15-002Rev1 "Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance," was applied. Compensatory measures were implemented within the time allowed by the applicable Limiting Condition(s) for Operation and the associated systems were then declared Operable but nonconforming. The apparent cause of this issue was a lack of clarity during the original design and licensing of the plants that led to inadequate understanding of the tornado missile protection regulatory requirements. In addition, as part of the evaluation of tornado missile vulnerabilities, two BV-2 tornado missile barrier doors were found to be open. Specifically, Auxiliary Building door (A-35-5A) was found open and Fuel Building door (F-66-3), was found to be partially open. These doors were then closed and latched. Actions will be taken to establish compliance for the MSSVs and ADVs either by plant modification or by employing a methodology for addressing tornado missile noncompliance for the MSSVs and the ADVs. These conditions (as applicable) were reported to the NRC on February 23, 2017 in Event Notification (EN) number 52571 under 10 CFR 50.72(b)(3)(ii)(B) and 10 CFR 50.72(b)(3)(v)(A). NRC FORM 366 (11-2015) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear CONTINUATION SHEET Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER DYEA R SEQUENTIAL REV Beaver Valley Power Station Unit Number 1 05000-1 334 NUMBER 1-NO0. ~-I I 001 | NARRATIVE Energy Industry Identification System (EllS) codes identified in the in the text as [XX]. CONDITIONS PRIOR TO OCCURENCE Beaver Valley Power Station Unit 1 (BV-1) and Unit 2 (BV-2) were in Mode 1 at 100% Power There were no Structures, Systems, or Components (SSCs) that were inoperable at the start of the event that contributed to the event. DESCRIPTION OF EVENT In order to address the concerns outlined in NRC Regulatory Information Summary (RIS) 2015-06 "TORNADO MISSILE PROTECTION", an evaluation of tornado missile vulnerabilities and their potential impact on Technical Specification (TS) plant equipment was conducted. This evaluation concluded that the following Structures, Systems, and Components (SSCs) are potentially vulnerable to tornado generated missiles: The steam discharge flow paths to atmosphere for the Beaver Valley Power Station Unit 1 (BV-1) and Unit 2 (BV-2) Main Steam [SB] Safety Valves [SV] (MSSVs) (reference TS 3.7.1) are potentially vulnerable to tornado generated missiles. A tornado could generate missiles capable of striking the steam exhaust piping of the MSSVs potentially crimping the piping resulting in reduced steam flow exhaust capacity. In the worst case, (based on multiple missile strikes), all fifteen MSSVs at each Unit (five per steam line) [SB] could be rendered inoperable. On February 23, 2017, the BV-1 and BV-2 TS required MSSVs were declared inoperable and Enforcement Guidance Memorandum (EGM) 15-002 Rev 1 "Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance," was applied. Compensatory measures were· implemented within the time allowed by the applicable Limiting Condition(s) for Operation and the MSSVs were then declared Operable but nonconforming. The BV-2 MSSVs exhaust piping is less vulnerable to horizontal missile strikes than the BV-1 MSSVs exhaust piping due to the four sided concrete structure around the steam exhaust piping. The steam discharge flow paths to atmosphere of the BV-1 and BV-2 Atmospheric Dump Valves (ADVs) [RV] (Reference TS 3.7.4) are potentially vulnerable to tornado generated missiles. A tornado could generate missiles capable of striking the steam exhaust piping of the ADVs potentially crimping the piping resulting in reduced steam flow capacity. In the worst case, (based on multiple missile strikes), all TS required ADVs at each Unit could be rendered inoperable. On February 23, 2017, the BV-1 and BV-2 TS required ADVs were declared inoperable and EGM 15-002 Rev 1 was applied. Compensatory measures were implemented within the time allowed by the applicable Limiting Condition for Operation and the associated ADVs were then declared Operable but nonconforming. The BV-2 ADVs exhaust piping is less vulnerable to horizontal tornado missiles strikes than the BV-1 ADVs exhaust piping due to the four sided concrete structure around the steam exhaust piping. | ML17110A191
Browns Ferry Nuclear Plant | Unit 2 | Inoperable Primary Containment Isolation Valve Resulting in Condition Prohibited by Technical Specifications | 04-24-2017 | On February 23, 2017, radiography results for the Browns Ferry Nuclear Plant (BFN), Unit 2, Reactor Core Isolation Cooling (RCIC) system stop check valve, 2-HCV-071-0014 (71-14 valve), showed the valve to be in the fully open position. In this position, the valve was incapable of performing its design function as a Primary Containment Isolation Valve (PCIV). In order to isolate the affected primary containment penetration flowpath, the RCIC Steam Line Outboard Isolation Valve was closed and deactivated to secure flow through the adjacent PCIV check valve in the exhaust line in accordance with plant Technical Specifications (TS) Limiting Conditions for Operation (LCO) for Primary Containment Isolation. It is assumed in the Past Operability Evaluation (POE) that the 71-14 valve had been inoperable from April 2015 to February 2017, in violation of TS LCO 3.6.1.3. During this time period, another check valve (upstream of the 71-14 valve) remained capable of isolating the affected penetration. The 71-14 valve was repaired during the BFN, Unit 2, Cycle 19 Refueling Outage which began on February 25, 2017. The cause of this condition was determined to be inadequate minimum allowable internal clearances for the 71-14 valve. The 71-14 valve internals were machined to minimum allowable material as an interim action to mitigate risks. The corrective action to prevent recurrence is to replace the 71-14 valve with a new valve design that is not susceptible to the same internal binding potential. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Browns Ferry Nuclear Plant, Unit 2 05000-260 NUMBER NO. 2017 002 00 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Unit 2, was in Mode 1 at approximately 74 percent rated thermal power. II. Description of Event A. Event Summary: On February 23, 2017, at approximately 2239 Central Standard Time (CST), radiography results for BFN, Unit 2, Reactor Core Isolation Cooling (RCIC) [BN] system stop check valve [ISV], 2-HCV-071-0014 (71-14 valve), was discovered to be in the fully open position, thereby not meeting the acceptance criteria of Surveillance Instruction 2-Sl-3.2.3, Testing ASME OM Code and Augmented IST Check Valves (Internal Inspection). This valve is the RCIC turbine exhaust stop check valve and is one of two Primary Containment Isolation Valves (PCIVs) connecting the RCIC exhaust directly to primary containment. The acceptance criteria is for the valve to be fully closed to satisfy the containment isolation function. A Past Operability Evaluation (POE) determined that the 71-14 valve was inoperable from April 3, 2015, at 2356 Central Daylight Time (CDT), until Unit 2 was placed in Mode 4 on February 25, 2017, at 0506 CST. BFN, Unit 2, Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.6.1.3 requires each PCIV, except reactor building-to-suppression chamber vacuum breakers, to be Operable in Modes 1, 2, and 3, and when associated instrumentation is required to be Operable per LCO 3.3.6.1, “Primary Containment Isolation Instrumentation”. In response to this event, on February 23, 2017, at 2250 CST, Operations personnel entered TS 3.6.1.3 Required Action A.1 which required the RCIC system to be isolated within 4 hours to prevent flow through the RCIC Turbine Exhaust check valve, 2-CKV-071-0580 (71-580 valve). Based on the results from the POE, the 71-14 valve was inoperable longer than allowed by the TS. On February 24, 2017, at 0018 CST, Operations personnel isolated the RCIC system in accordance with plant TS by closing the RCIC Steam Line Outboard Isolation Valve 2-FCV-071-0003 (71-3 valve). On February 25, 2017, the scheduled Unit 2 refueling outage commenced. On March 24, 2017 at 1641 CDT, BFN completed repairs to the 71-14 valve and restored the RCIC penetration flowpath. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event The 71-14 valve was unable to perform its function as a PCIV because it was stuck in the open position. | ML17114A252
Clinton Power Station | Unit 1 | Failure of the 138 kV Offsite Power Source Results in a Loss of Secondary Containment Vacuum | 10-31-2016 | On February 24, 2017 at approximately 2239 hours (CDT), the Main Control Room (MGR) received numerous annunciators which indicated a loss of the 138 kV off-site supply to the Emergency Reserve Auxiliary Transformer (ERAT). The MGR entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1, AC Sources- Operating, Required Actions A.1 and A.2. The Division 1 Fuel Building ventilation (VF) system isolation dampers closed due to the voltage transient causing a trip of the VF supply and exhaust fans and Secondary Containment (SC) vacuum to rise to slightly greater than 0 inches water gauge (WG), exceeding the TS requirement of greater than 0.25 inches vacuum WG. The MCA entered Emergency Operating Procedure (EOP)-8, Secondary Containment Control, and TS LCO 3.6.4.1, Secondary Containment, Required Action A.1. SC vacuum was restored within TS requirements at approximately 2242 hours by starting the Standby Gas Treatment (VG) system. The Transmission System Operator confirmed that the loss of the 138 kV line was due to a line fault external to the Station. The 138 kV line was successfully re-energized at 0053 hours on February 25, 2017 and the ERAT off-site source was restored and declared OPERABLE at 0300 hours. This event is reportable per 1O CFR50.73(a)(2)(v)(C). NRC FORM 366 (11·2015) NRC FOAM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 01/31/2017 (02-2014) ............. Estimated burden per response to comply l\ith this mandatory collection request: BO hours . l \ Reported lessons learned are .incorporated into the licenslng process and fed back to industry. ~,' ) ) Send comments regarding burden estimate to the FOIA, Pnvacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by ~~. .... ."/ LICENSEE EVENT REPORT (LER) internet e-mail to lnlocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Aftairs, NEOB-10202, (3150-0104), Office of Management and Budget, CONTINUATION SHEET Washington, DC 20503. II a means used to impose an information collection does not display a currenHy valid OMB control number, the NRC may not conduct or sponsor, and a person is not required lo respond to, the information collection. 1. FACILITY NAME 2. DOCKET 6. LEA NUMBER I 3. PAGE I YEAR SE N Q U U M E B N E T R IA L R N E O V . Clinton Power Station, Unit 1 05000461 2 OF 5 2017 001 00 | PLANT AND SYSTEM IDENTIFICATION General Electric-Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX] EVENT IDENTIFICATION Failure of the 138 kV Offsite Power Source Results in a Loss of Secondary Containment Vacuum A. Plant Operating Conditions before the Event Unit: 1 Event Date: 02/24/17 Event Time: 2239 Mode: 1 Mode Name: Power Operation Reactor Power: 99 percent B. DESCRIPTION OF EVENT On February 24, 2017, at approximately 2239 hours CDT the Emergency Reserve Auxiliary Transformer (ERAT) and the associated Static VAR Compensator (SVC) tripped due to a loss of the 138 kV line owned and maintained by Ameren Illinois. The Main Control Room (MGR) entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1, AC Sources-Operating, Required Actions A.1 and A.2. The Clinton area was experiencing very strong winds at the time of the 138 kV power loss and the ERAT trip. As a result of the voltage transient caused by automatic transfer to the Reserve Auxiliary Transformer (RAT), the Division 1 Fuel Building Ventilation (VF) system isolation dampers closed causing a trip of the VF supply and exhaust fans. The effect of this condition was that Secondary Containment (SC) vacuum rose to slightly greater than O inches water gauge (WG) and exceeded the TS limit of -0.25 inch WG. Operations personnel entered Emergency Operating Procedure (EOP) -8, Secondary Containment Control, and TS LCO 3.6.4.1, Secondary Containment, Required Action A.1. As a result of the loss of power and subsequent bus transfer, the following additional system actuations occurred: Division 1 MGR Ventilation Chiller tripped Division 1 Diesel Generator room Exhaust Fan 1V D02CA tripped, Division 1 Shutdown Service Water Pump auto started, Fission Product Monitoring (FPM) skid isolation valves shut, Division 1 Hydrogen Monitoring system isolations valves shut, Containment Service Air system Outboard Isolation 1S A029 shut Nuclear Systems Protection System Inverter Trouble alarms annunciation (due to loss of syncronization). | ML17114A470
Susquehanna Steam Electric Station | Unit 2 | Secondary Containment Breach Due to Simultaneous Opening of Airlock Doors | 03-02-2017 | On March 2, 2017 at approximately 10:30, three employees were entering the Unit 2 Airlock on elevation 676' from the Reactor Building door. After entering the airlock, one employee opened the second airlock door prior to the first door being closed, resulting in an alarm. This resulted in not meeting Technical Specification 3.6.4.1 Surveillance Requirement 3.6.4.1.3, which requires that one secondary containment access door in each access opening is closed. The cause of this event was determined to be less than adequate Situational Awareness. This condition requires reporting in accordance with 10 CFR 50.73(a)(2)(v)(C) as having both Secondary Containment airlock doors momentarily open simultaneously results in a condition that could have prevented fulfillment of a safety function. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366A (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET /nfocollects.Resource@nrc.gov, and to lhe Desk 0/licer, 0/lice of Information and Regulatory Affairs, NEOB-10202, (3150·0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http://WNW.n rc.gov/readi ng-rm/doc-collections/nuregs/staff/sr1 022/r3/) NRC may not conduct or sponsor, and a person is not required to respond to, the in/ormation collection. 1. FACILITYNAME 2. DOCKET NUMBER 3. LER NUMBER I I YEAR SEQUENTIAL REV Susquehanna Steam Electric Station Unit 2 05000-388 NUMBER NO. 2017 -004 -00 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, approximately 100 percent Rated Thermal Power Unit 2 - Mode 1, approximately 88 percent Rated Thermal Power EVENT DESCRIPTION On March 2, 2017 at approximately 10:30, three employees were entering the Unit 2 Airlock [EllS Component Identifier: AL] on elevation 676' from the Reactor Building [EllS System Identifier: NG] door. The first employee observed the green light, swiped their badge and entered into the airlock. The two additional employees also swiped their badges and traversed into the airlock. As the first employee opened the second door within the airlock, the airlock door alarm sounded briefly as the first door was not completely closed and latched. Upon hearing the alarm, the employees promptly reported the incident to oversight and Operations. All personnel then provided statements with respect to the event. CAUSE OF EVENT The cause of the event was determined to be less than adequate use of Situational Awareness. ANALYSIS/SAFETY SIGNIFICANCE Technical Specification 3.6.4.1 Surveillance Requirement 3.6.4.1.3 requires that one secondary containment access door in each access opening is closed. This event is being reported pursuant to 10 CFR 50.73(a)(2)(v)(C) as having both Secondary Containment airlock doors momentarily open simultaneously results in a condition that could have prevented fulfillment of a safety function to mitigate the consequences of an accident by controlling the release of radioactive material. There was no actual safety consequence as a result of this event. Engineering analysis of this event has determined that secondary containment could have performed its safety function of isolating, as assumed in the accident analysis, and also of re-establishing 0.25 in w.g. vacuum (drawdown) within the assumed accident analysis time (1 0 minutes). Therefore, the subject event did not cause a loss of safety function. This event will not be counted as a safety system functional failure (SSFF) for the NRC performance indicator based on the Engineering analysis supporting the system's ability to fulfill the safety function. CORRECTIVE ACTIONS Key corrective actions include the following: 1. Coaching was provided to the individuals involved with respect to the use of airlock doors (Complete). | ML17115A328
Sequoyah Nuclear Plant | Unit 1 | Breached Door Renders Both Trains of the Auxiliary Building Gas Treatment System Inoperable | 03-31-2020 | On March 3, 2017, at 2232 eastern standard time (EST), Door A212 was improperly breached to facilitate a continuous fire watch. On March 7, 2017, at 0830 EST, a senior reactor operator discovered Door A212 blocked open during a walk down of the Auxiliary Building. The open door created a breach of the auxiliary building secondary containment enclosure (ABSCE) boundary. The identified breach exceeded the allowed ABSCE breach margin. As a result, both units entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.12, Condition B for two trains of the Auxiliary Building Gas Treatment System (ABGTS) inoperable due to an inoperable ABSCE boundary in Mode 1, 2, 3, or 4. At 0949 EST, on March 7, the door was closed and both units exited LCO 3.7.12, Condition B. Both trains of ABGTS were inoperable longer than allowed by TS. There were no actual safety consequences as a result of this event. An evaluation determined the cause to be a less than adequate single barrier breaching standard exists at Sequoyah Nuclear Plant. A contributing cause was an inconsistent approach to entry into the barrier breaching process. Corrective actions include revising the breaching procedure to address all possible breaches and include a matrix for doors and their associated impacts, and addressing potential knowledge deficiencies. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Sequoyah Nuclear Plant Unit 1 05000-327 NUMBER NO. 2017 - 001 - 00 | I. Plant Operating Conditions Before the Event At the time of the event, Sequoyah Nuclear Plant (SQN) Unit 1 and Unit 2 were in Mode 1 at 100 percent rated thermal power. II. Description of Event A. Event Summary: As a result of fire protection [EIIS: KF] piping inspections, the fire protection for the Fuel Handling Exhaust Fan (FHEF) [EIIS: FAN] Filter [EIIS: FLT] Enclosure was authorized to be isolated under a clearance. The isolation required a continuous fire watch to inspect the inside of the FHEF Filter Enclosure. With the FHEF in service, excessive differential pressure across Auxiliary Building [EIIS: NF] Door [EIIS: DR] A212 hindered opening the door for the inspection. Therefore, a fire protection impairment permit was generated to breach Door A212; however, the door was not evaluated as a breach of the auxiliary building secondary containment enclosure (ABSCE) boundary. On March 3, 2017, at 2232 eastern standard time (EST), Door A212 was breached to facilitate the continuous fire watch. On March 7, 2017, at 0830 EST, a senior reactor operator (SRO) discovered Door A212 blocked open during a walk down of the Auxiliary Building. The open door created a breach of the ABSCE boundary. The identified breach exceeded the allowed ABSCE breach margin. As a result, both units entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.12, Condition B for two trains of the Auxiliary Building Gas Treatment System (ABGTS) [EIIS: VF] inoperable due to an inoperable ABSCE boundary in Mode 1, 2, 3, or 4. At 0949 EST, on March 7, the door was closed and both units exited LCO 3.7.12, Condition B. An 8-hour non-emergency event notification (EN 52597) was made to the NRC in accordance with 10 CFR 50.72(b)(3)(v) as an event or condition that could have prevented fulfillment of a safety function of structures or systems that are needed to: (C) control the release of radioactive material and (D) mitigate the consequences of an accident. This LER documents the reportable event under 10 CFR 50.73(a)(2)(v)(C) and 10 CFR 50.73(a)(2)(v)(D). Additionally, it was determined that both trains of ABGTS were inoperable from March 3, 2017, at 2232 to March 7, 2017, at 0949. LCO 3.7.12, Condition B requires restoration of the ABSCE boundary within 24 hours. Upon failure to meet the Required Action and associated Completion Time of Condition B, LCO 3.7.12, Condition C requires the unit to be in Mode 3 within 6 hours. Because both trains of ABGTS were inoperable for approximately 83.3 hours and remained in Mode 1, this is a condition prohibited by TS and is therefore being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant’s TS. | ML17117A495
Browns Ferry Nuclear Plant | Unit 1 | Unauthorized Firearm Introduced into the Protected Area | 04-27-2017 | On March 2, 2017, an unauthorized firearm was introduced into the protected area (PA) after passing through the search process undetected. This led to the declaration of a Notification of an Unusual Event for a security condition that does not involve a hostile action. This event is reportable due to the actual introduction of a contraband firearm into the PA Immediate actions include the following: The individual who introduced the firearm was removed from the PA, their badge was disabled, their access was revoked, and their personal vehicle searched for additional contraband. A post-event fitness for duty test was attempted but the individual declined after numerous failed attempts to provide a sample. The Nuclear Security Officers (NSOs) on-duty when the individual entered the PA were disqualified. The Search Lane where the individual entered was closed for Maintenance to inspect its x-ray machine, which was found to be working as designed. Two NSOs are now assigned to each lane's search monitor to view the items being processed through the x-ray machine, and any unidentifiable items are physically searched. A fleet-wide policy of random physical searches of personnel and packages has been implemented. Additionally, over 800 lockers, cubicles, and other areas, were searched for contraband. No other contraband or unauthorized items were found The cause was determined to be that the training provided to NSOs drove the identification of contraband instead of driving the NSO to conduct a physical search when they cannot positively identify all materials using the x-ray image. The corrective action to prevent recurrence is to revise task practical evaluation training and the Personnel Access Control procedure to include acceptance criteria for performing successful material searches. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMS control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Browns Ferry Nuclear Plant, Unit 1 05000-259 2017 - 002 - 00 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Units 1 and 3, were in Mode 1 at 100 percent power. Unit 2 was in Mode 5 to support a refueling outage. II. Description of Event A. Event Summary On March 2, 2017, at 1215 Central Standard Time (CST), a firearm was found and confiscated in the protected area (PA). This resulted in an unauthorized firearm in the PA, which led to the declaration of a Notification of an Unusual Event (NOUE) based on Emergency Action Level (EAL) 6.7-U, a security condition that does not involve a hostile action. Required actions for the NOUE were taken in accordance with the stations emergency plan implementing procedures. An unauthorized weapon in the PA is contrary to the requirements of 10 CFR 73.55, the BFN Security plan, and procedure SSl-7.6, Personnel Access Control. The actual introduction of contraband into the PA constitutes a reportable safeguards event, in accordance with NSDP-1, Safeguards Event Reporting Guidelines, and 10 CFR 73.71 (a)(4). The contract employee who introduced the firearm was removed from the PA, their badge was disabled, their access was revoked, and their personal vehicle searched for additional contraband. A post-event fitness for duty (FFD) test was attempted but the individual declined after numerous failed attempts to provide a sample. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components whose inoperability contributed to this event. C. Dates and approximate times of occurrences Dates & Approximate Times Occurrence March 2, 2017, An individual processed through the electronic search at 0913 CST equipment and gained access to the PA while unintentionally in possession of a firearm. While processing through, the individual placed their backpack and coat into an x-ray machine bucket. The Nuclear Security Officer (NSO) on duty did not positively identify all items prior to granting PA access, which led to the unauthorized firearm inside the PA. NRG FORM 366A (04-2017) Page 2 of 6 | ML17118A010
Quad Cities Nuclear Power Station | Unit 1 | Secondary Containment Differential Pressure Momentarily Lost Due to Air Line Failure (RWCU Hx Rm) | 05-01-2017 | On January 12, 2016, at 13:40 hours, The Main Control Room received alarms indicating a low differential pressure in the reactor building. The alarms occurred during an entry to the Unit 2 Reactor Water Cleanup (RWCU) Heat Exchanger (HX) room. A negative reactor building pressure was restored within one minute (alarm cleared at 13:41 hours) by immediately securing a reactor building supply fan. Since both Units 1 and 2 share a common reactor building (RB), the loss of differential pressure (RB pressure went positive) for approximately one (1) minute impacted both Units 1 and 2 secondary containments. The cause was a sheared air line inside the Unit 1 RB ventilation exhaust plenum which depressurized the air header supplying operating air to all three Unit 1 reactor building exhaust fan isolation dampers and causing the dampers to fail open, including the one on the standby fan. Corrective actions included replacing the sheared air line, and the addition of a preventive maintenance task for replacement of equivalent air lines on all RB supply and exhaust fan dampers. The safety significance of this event was minimal. Given the impact on the secondary containment, this report is submitted (for Units 1 and 2) in accordance with the requirements of 1 OCFR 50.73(a)(2)(v)(C), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. NRG FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: BO hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, ·"· CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means .***"' used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/readinq-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Quad Cities Nuclear Power Station YEAR 05000254 NUMBER NO. Unit 1 2016 - 001 01 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Momentary Loss of Secondary Containment Differential Pressure due to a manufacturing defect in the tubing fitting of an air line in the Unit 1 Reactor Building Exhaust fan plenum. A. CONDITION PRIOR TO EVENT Unit: 1 I 2 Event Date: January 12, 2016 Event Time: 13:40 hours Reactor Mode: 1 I 1 Mode Name: Power Operation I Power Operation Power Level: 100% I 100% B. DESCRIPTION OF EVENT On January 12, 2016, at 13:40 hours, unexpected Main Control Room Reactor Building (RB) Low differential pressure (DP) alarms were received due to loss of negative DP in the RB. At approximately the same time, technicians had notified the control room that they would be entering and exiting the Unit 2 RWCU HX Room to perform a scaffolding walkdown. Reactor building DP was observed rising to O inches water column (WC) and peaked at +0.2 inch WC. Technical Specification (TS} 3.6.4.1 Condition A, and QGA 300, Secondary Containment Control were entered tor both Units Secondary Containment being inoperable. The 1B RB ventilation supply fan was immediately secured and at 13:41 hours negative reactor building DP was restored. TS 3.6.4.1 Condition A and QGA 300 were then exited. At 13:43 hours, the 1 B RB ventilation supply tan was restarted and negative building DP was maintained within TS limits. On January 12, 2016, at 18:08 hours, ENS #51650 was made to the NRC under 10 CFR 50.72 (b)(3)(v)(C), to report this event as an event or condition that could have prevented the fulfillment of a safety function of structures or systems that are needed to control the release of radioactive material. An investigation of this event was performed which determined that a sheared air line to the 1C RB exhaust tan isolation damper depressurized a common air header to all three Unit 1 RB exhaust fan isolation dampers, causing them to tail open. This air line was internal to the exhaust ductwork, therefore it could not be identified through normal Operator rounds. With a normal fan lineup of two supply and two exhaust fans operating per unit, the isolation damper tor the standby Unit 1 exhaust fan remained open. This created a recirculation path which was compensated by the RB DP control dampers throttling nearly full open. This significantly degraded the margin available tor the system to respond to changes in building DP. When an entry was made into the Unit 2 RWCU HX room, the area DP control system responded as expected by throttling closed all area DP control dampers which decreased total building exhaust flow. With reduced margin available in the building DP control, this caused a positive pressure condition in the RB. | ML17121A150
Quad Cities Nuclear Power Station | Unit 1 | Secondary Containment Differential Pressure Momentarily Lost Due to Air Line Failure (RWCU Pump Rm) | 05-01-2017 | On January 15, 2016, at 20:38 hours, The Main Control Room received alarms indicating a low differential pressure in the reactor building. The alarms occurred during an entry to the Unit 2 Reactor Water Cleanup (RWCU) pump room. A negative reactor building pressure was restored within two minutes (approximately 20:40 hours) without operator action. Since both Units 1 and 2 share a common reactor building (RB), the loss of differential pressure impacted both Units 1 and 2 secondary containments. The cause was a sheared air line inside the Unit 1 RB ventilation exhaust plenum which depressurized the air header supplying operating air to all three Unit 1 RB exhaust fan isolation dampers and causing the dampers to fail open, including the one on the standby fan. Corrective actions included replacing the sheared air line, and the addition of a preventive maintenance task for replacement of equivalent air lines on all RB supply and exhaust fan dampers. The safety significance of this event was minimal. Given the impact on the secondary containment, this report is submitted (for Units 1 and 2) in accordance with the requirements of 1O CFR 50.73(a)(2)(v)(C), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03131/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1 D22, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http://www. n re. gov /reading-rm/doc-collections/nu regs/staff ls r1 022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV Quad Cities Nuclear Power Station YEAR 05000254 NUMBER NO. Unit 1 2016 - 002 01 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Momentary Loss of Secondary Containment Differential Pressure due to a manufacturing defect in the tubing fitting of an air line in the Unit 1 Reactor Building Exhaust fan plenum. A. CONDITION PRIOR TO EVENT Unit: 1 I 2 Event Date: January 15, 2016 Event Time: 20:38 hours Reactor Mode: 1 I 1 Mode Name: Power Operation I Power Operation Power Level: 100% I 100% B. DESCRIPTION OF EVENT On January 15, 2016, at 20:38 hours, unexpected Main Control Room Reactor Building (RB) Low differential pressure (DP) alarms were received due to loss of negative DP in the RB. At approximately the same time, Operations had entered the Unit 2 RWCU Pump room. Reactor building DP was observed rising to 0 inches water column (WC) and peaked at +0.2 inch WC. Technical Specification (TS) 3.6.4.1 Condition A, and QGA 300, Secondary Containment Control were entered for both Units Secondary Containment being inoperable. With no operator action, a negative reactor building DP was restored at approximately 20:40 hours. TS 3.6.4.1 Condition A and QGA 300 were exited at 20:42 hours. On January 16, 2016, at 01:42 hours, ENS #51659 was made to the NRC under 10 CFR 50.72 (b)(3)(v)(C), to report this event as an event or condition that could have prevented the fulfillment of a safety function of structures or systems that are needed to control the release of radioactive material. An investigation of this event was performed which determined that a sheared air line to the 1C RB exhaust fan isolation damper depressurized a common air header to all three Unit 1 RB exhaust fan isolation dampers, causing them to fail open. This air line was internal to the exhaust ductwork, therefore it could not be identified through normal Operator rounds. With a normal fan lineup of two supply and two exhaust fans operating per unit, the isolation damper for the standby Unit 1 exhaust fan remained open. This created a recirculation path which was compensated by the RB DP control dampers throttling nearly full open. This significantly degraded the margin available for the system to respond to changes in building DP. When an entry was made into the Unit 2 RWCU Pump room, the area DP control system responded as expected by throttling closed all area DP control dampers which decreased total building exhaust flow. With reduced margin available in the building DP control, this caused a positive pressure condition in the RB. | ML17121A152
Brunswick Steam Electric Plant (BSEP) | Unit 1 | Control Room Air Conditioning Units Inoperable due to Corroded Supports | 05-03-2017 | On December 13, 2016, Units 1 and 2 were in Mode 1 (i.e., Run mode) at 98 percent and 97 percent of rated thermal power, respectively. At that time, shift personnel were notified that structural supports for the 2D Control Room air conditioning system condenser were corroded. An operability assessment found the affected air conditioning system inoperable due to the effect on its seismic qualification. Technical Specifications (TS) 3.7.4, Condition A, was entered. On January 30, 2017, the 1D air conditioning system was found with similar conditions. The duration of the condition and the fact that more than one air conditioning system was inoperable simultaneously resulted in the plant operating in a condition prohibited by the TS and in a loss of the safety function. This event resulted from a lack, in some cases, of station personnel being cognizant of risks related to resolving complex, long-standing issues that continue to degrade over time. All affected support steel was replaced by February 2, 2017. The remaining air conditioner was inspected and found acceptable. Administrative actions will be taken to identify high consequence plant issues and periodically reassess priorities. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 CONTINUATION SHEET F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant (BSEP) 05000-325 YEAR NUMBER NO. Unit 1 2016 - 006 - 001 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. Background Initial Conditions On December 13, 2016, at 16:27 Eastern Standard Time (EST), Unit 1 was in Mode 1 at approximately 98 percent of rated thermal power. Unit 2 was in Mode 1 at approximately 97 percent of rated thermal power. Other than the components specifically named in this report, no out-of-service equipment contributed to, or affected the course of, this event. Reportability Criteria This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) because Units 1 and 2 were operated in a condition which is prohibited by the Technical Specifications (TS). Specifically, air conditioning units 1D and 2D for the Main Control Room [NA] were inoperable on account of seismically- qualified structural supports being degraded due to corrosion. The duration of the inoperability could not be conclusively determined. Therefore, the air conditioners are conservatively concluded to have been inoperable for longer than the 30 days allowed by TS 3.7.4, Condition A (i.e., one Control Room Air Conditioning subsystem inoperable) and the 72 hours allowed by TS 3.7.4, Condition B (i.e., two Control Room Air Conditioning subsystems inoperable). Since these times were exceeded, the plant was in a condition prohibited by the TS. The condition applies to both units because the air conditioning system serves the shared Control Room. The event is also reportable per 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. With two air conditioning units inoperable, the safety function of maintaining Control Room habitability could not be assured. The condition applies to both units because the air conditioning system serves the shared Control Room. Event Description On December 13, 2016, a periodic inspection was being performed on the Control Building [NA] air conditioner compressors and condensing coils of air conditioner 2D. During the inspection, seismically qualified support members were found to be degraded due to corrosion. This condition was reported to shift personnel in the Main Control Room, and further assessment was initiated. On December 14, 2016, it was determined that the air conditioning unit supported by the corroded members could not be reasonably assured of meeting its seismic qualifications. Therefore, air conditioner 2D was declared inoperable and TS 3.7.4, Condition A was entered. The affected support members for air conditioning unit 2D were replaced under Work Order 20132955 on December 22, 2016, and the TS condition was exited. | ML17123A296
Hope Creek Generating Station 05000354 1 OF 4 | Unknown Unit | Mode Chanae Without B Channel Reactor Level Instrumentation Or: erable | 00-04-2017 | On November 9, 2016, at 0420 with the Hope Creek reactor in Operational Condition 2, Startup, the B channel reactor level instrumentation was found to be inoperable. The inoperable instrumentation was discovered as reactor level was being lowered into the normal band in preparation for plant startup. Hope Creek had made a mode change from Operational Condition 4, Cold Shutdown, to Operation Condition 2, Startup, on November 9, 2016, at 0317, approximately 1 hour prior to discovering the inoperable instrumentation. The B Channel reactor level instrumentation is required to be operable in order to enter Oper.ational Condition 2 to support the B division of the Reactor Protection System (RPS), the Emergency Core Cooling Systems (ECCS), and the Primary Containment Isolation System (PCIS). The cause was determined to be an improperly filled reference leg for the B channel reactor level instrumentation. This report is being made under 10 CFR 50.73(a)(2)(i)(B), as a condition which was prohibited by the plant's Technical Specifications. NRC FORM 366A (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150·0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail CONTINUATION SHEET to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a (See NUREG-1 022, R.3 for instruction and guidance for completing this form means used to impose an Information collection does not display a currently valid OMB control http://www. nrc.gov/readi ng-rm/doc-collections/nuregs/staff/sr1 022/r3/) number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER I YEAR I SEQUENTIAL REV Hope Creek Generating Station 05000-354 NUMBER NO. 2016 -006 -01 | PLANT AND SYSTEM IDENTIFICATION General Electric- Boiling Water Reactor (BWR/4) Reactor Protection System- EllS Identifier {JC/LI}* ESF Actuation System- EllS Identifier {JE/LI}* Containment Isolation Control System- EllS Identifier {JM/ Ll}* *Energy Industry Identification System {EllS} codes and component function identifier codes appear as {SS/CCC} IDENTIFICATION OF OCCURRENCE Event Date: November 9, 2016 Discovery Date: November 9, 2016 CONDITIONS PRIOR TO OCCURRENCE When the inoperable instrumentation was discovered, Hope Creek was in Operational Condition (OPCON) 2, Startup, with the reactor sub-critical, and a reactor startup in progress. No other structures, systems or components that could have contributed to the event were inoperable at the time of the event. DESCRIPTION OF OCCURRENCE I During the twentieth refueling outage (H1 R20) at Hope Creek, a section of the reference leg for one instrument on the B channel reactor vessel level instrumentation was replaced and rerouted using the design change process. The reference leg is normally maintained at a constant height of water by a condensing pot connected to the reactor vessel steam space. Initially, the reference leg needs to be backfilled with water to remove small pockets of air or voids which may be present. On November 9, 2016, the reference leg had not been backfilled following the re-routing of the reference leg tubing, resulting in an incorrect level indication on all B channel level instruments. Following replacement of the reference leg, the design change package (DCP) did not provide instructions for back filling the reference leg. Instead, the DCP relied on the maintenance department to backfill the reference leg while I returning the affected instruments to service. The assigned maintenance supervisor was not cognizant of the DCP scope, and determined that the step to backfill the reference leg was not required. A second maintenance supervisor, who was aware of the work scope, did not question the decision to sign-off the backfill as not required. The B channel instruments were returned to service by maintenance without completing the backfill evolution. As a result, the reference leg for the B channel was not completely filled with water, and level on this channel indicated higher than actual level. The top of the indicating band for Technical Specification required reactor vessel instrumentation is +60 inches, and water level was being maintained in a band of 60 to 65 inches inches prior to making the mode change. Under this condition, all four channels of Technical Specification required vessel level indication indicated off-scale high, above 60 inches. Vessel level was being monitored using non-Technical Specification required level instrumentation which has a wider indicating range. Under this condition, the incorrect indication on the B channel instrumentation was not observable to the plant operators. Following the mode change, when vessel level was being lowered into the normal band of 30-39 Inches, the A, C and D channels of vessel level instrumentation all tracked together into the indicating range, while the B channel remained off scale high. At approximately 0420, control room operators recognized the condition, declared the B channel inoperable and directed maintenance personnel to investigate. At 0528 a prompt investigation was initiated by the Shift Manager. | ML17124A407
Oyster Creek | Unit 1 | Automatic SCRAM due to APRM High Flux during Turbine Valve Testing | 05-03-2017 | On 11/20/2016 at approximately 0342 EST, an automatic reactor SCRAM occurred at 92% power due to Average Power Range Monitor (APRM) high flux. Oscillations of the turbine control valves and bypass valves were experienced during planned testing of the Turbine Master Trip Solenoid Valve at 95% power. Power was reduced from 95% to 92% by the Main Control Room Operators in an effort to stop the observed oscillations. The control valves did not respond properly'during the power reduction, leading to an unexpected rise in reactor pressure and the subsequ~nt scram on high flux. There were no safety consequences impacting the plant or public safety as a result of this event. All control rods fully inserted and the plant response was as expected. This event is being reported pursuant to 10CFR50.73(a)(2)(iv)(A) due to an actuation of the Reactor Protection System (RPS). NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017}} Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process . and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collectidh does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/@ collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR NUMBER NO. Oyster Creek, Unit 1 05000219 2017 - 001 - 01 | Plant Conditions Prior To Event Event Date: November 20, 2016 Event Time: 0342 EST Unit 1 Mode: Power Operation Power Level: 92% Description of Event On 11/20/2016, the Main Control Room (MCR) Operators were conducting quarterly Main Turbine surveillance testing. At 0326 EST, the MCR Operators commenced testing the Turbine Master Trip Solenoid Valve (MTS-3) at 95% reactor power in accordance with plant procedures. After actuating the Turbine Master Trip Solenoid Valve, the MCR Operators observed fluctuations in control valve and bypass valve position indication. The Control Room Operators also identified a transfer between the EPR and MPR and fluctuations in reactor pressure. Field Operators were dispatched to the turbine front standard to inspect for any abnormalities. The Field Operators reported vibration and high frequency oscillations of the control linkages contained in the front standard. In response to the field report, the MCR Operators commenced a controlled power reduction in an effort to arrest the oscillations. At approximately 0342 EST, an automatic reactor SCRAM occurred at 92% power due to Average Power Range Monitor (APRM) high flux. The turbine control valves failed to properly control reactor pressure during the power reduction due to a malfunction of the Mechanical Hydraulic Control (MHC) System. After the plant scram, the. vibration and oscillations at the front standard ceased, and the bypass valves responded to regulate reactor pressure. An inspection of the front standard and the turbine control valve hydraulic enclosure was performed following the plant shutdown. The inspection identified that the hydraulic feedback linkage for the number 2 turbine control valve had come disconnected and the fastener for the hydraulic feedback linkage on the number 4 control valve was loose due to the vibration that was experienced. The feedback linkage degradation resulted in the unexpected change in control valve position during the power reduction and the subsequent reactor scram. Cause of Event The root cause investigation determined that the performance of the Turbine Master Trip Solenoid Valve operability test with the plant at power challenged the stability of the MHC system due to unrecognized design vulnerability in the configuration of the hydraulic tubing. The hydraulic tubing for the Turbine Master Trip Solenoid Valve is routed to the bypass valve loading piston. The design function of the bypass valve loading piston is to dampen vibration on the control linkages contained in the front standard. During the Turbine Master Trip Solenoid Valve Operability Test, a pressure pulse is placed on the bypass pilot valve loading piston that can lead to an oscillation of the MHC system. The design vulnerability was unrecognized because the OEM drawings did not identify the function or location of the loading piston with respect to the location of the Master Trip Solenoid hydraulic supply. I The root cause investigation also determined that degradation of the bypass valve loading piston contributed to the oscillation of the MHC System. Analysis of Event | ML17129A602
Turkey Point | Unit 3 | Loss of 3A 4kV Vital Bus Results in Reactor Trip, Safety System Actuations and Loss of Safety Injection Function | 05-16-2017 | On March 18, 2017 at approximately 1107 hours, the Turkey Point Unit 3 reactor tripped from 100% power as a result of an electrical fault on the 3A 4kV vital bus. The Auxiliary Feed Water System actuated as expected, and the 3A Emergency Diesel Generator started but did not load, as designed, due to the lockout of the 3A 4kV bus. The 3A 4kV bus remained de-energized and the reactor was stabilized in Mode 3. Both Unit 4 High Head Safety Injection (HHSI) pumps were out of service for maintenance. The 3A HHSI pump was unable to be powered from the 3A 4kV bus resulting in a loss of the Safety Injection safety function for approximately 2.5 hours on both Units 3 and 4. The safety function is achieved by operation of two of the four pumps which are shared by both units. The loss of the 3A 4kV bus was caused by an electrical fault created by a conductive foreign material that had entered the current-limiting reactor cubicle that bridged an air gap between an uninsulated bus bar and the cubicle wall. The foreign material was a carbon fiber mesh used to reinforce a Thermo-Lag installation taking place in the 3A 4kV switchgear room. Corrective actions include: 1) The Thermo-Lag installation procedure will be revised to incorporate additional precautions for handling Thermo-Lag materials, and 2) the Engineering product risk and consequence assessment process will be revised to ensure a review is conducted of Safety Data Sheets for material being considered in the design. This event had no effect on the health and safety of the public. NRC FORM 366 (02-2014) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 01/31/2017 (02-2014) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by LICENSEE EVENT REPORT (LER) internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, CONTINUATION SHEET Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 6. LER NUMER 3. PAGE SEQUENTIAL REV YEAR NUMBER NO. Turkey Point Unit 3 05000250 2 of 4 2017 001 00 | DESCRIPTION OF THE EVENT On March 18, 2017 at approximately 1107 hours, the Turkey Point Unit 3 reactor [AC, RDT] tripped from 100% power as a result of an electrical fault on the 3A 4kV vital bus [EB, BU]. The three reactor coolant pumps (RCP) [AB, P] tripped. The 3B RCP was later restarted for forced recirculation. The reactor was stabilized in Mode 3. The 3A 4kV bus remained de-energized. Unit 4 remained operating at 100% power. The loss of the 3A 4kV bus required a plant shutdown to Mode 5 (cold shutdown) in accordance with Technical Specification 3.8.3.1, Action ‘a’. The completion of the shutdown is reportable in accordance with 10 CFR 50.73(a)(2)(i)(A). The electrical fault resulted in smoke in the 3A 4kV switchgear room which prompted the declaration of an alert (Event Notification 52621) that ended at 1420 hours. Auxiliary Feed Water (AFW) [BA] actuated as expected on low level in Steam Generator A [SB, SG] and was secured at approximately 1135 hours. The 3A Emergency Diesel Generator (EDG) [EK, DG] started but did not load, as designed, due to the lockout resulting from the 3A 4kV bus fault. The 3A EDG was stopped at approximately 1332 hours. The actuations of the Reactor Protection System [JC], AFW and the 3A EDG are reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). The Unit 4 4A and 4B High Head Safety Injection (HHSI) pumps [BQ, P] were out of service for maintenance. A loss of safety function affecting both Units 3 and 4 occurred upon the loss of the 3A 4kV bus because the 3A HHSI pump could not be powered. This caused three of the four HHSI pumps to be inoperable. The four HHSI pumps are shared by both Units 3 and 4. The safety function is achieved by two of the four HHSI pumps. Both Unit 4 HHSI pumps were restored to operable status at 1336 hours on 3/18/17. The loss of safety function is reportable in accordance with 10 CFR 50.73(a)(2)(v)(D). The Unit 3 shutdown required by the TS and the equipment actuations were reported in accordance with 10 CFR 50.72 in Event Notification 52623. CAUSE OF THE EVENT The direct cause of the reactor trip was loss of the 3A 4kV bus. The direct cause of the fault in the 3A 4kV bus is attributed to the introduction of foreign material (FM) into the Current-Limiting Reactor (CLR) cubicle. Root Cause: The Thermo-Lag installation procedure does not address control of FM nor provide guidance on precautions that should be taken to control airborne debris fibers generated during installation of Thermo- Lag. Contributing Causes: 1. Workers performing Thermo-Lag installation did not recognize that airborne FM could enter closed switchgear cabinets and cause an adverse affect. Personnel and the FM exclusion program focus more on | ML17136A372
Cooper Nuclear Station 05000298 1of4 | Unknown Unit | Valve Test Failures Result in Condition Prohibited by Technical Specifications and a Loss of Safety Function | 04-27-2017 | In February and March 2017, three Main Steam Safety Relief Valve (SRV) body assemblies (main body and pilot assembly) and the remaining five SRV pilot assemblies were tested at National Technical Systems Laboratories (formerly Wyle Laboratories). These SRVs had been removed from Cooper Nuclear Station during Refueling Outage 29 in the Fall of 2016. One SRV pilot assembly failed the as-found lift pressure testing; another SRV pilot assembly was conservatively considered a failure due to lack of as-found lift pressure test data since it was inadvertently disassembled prior to performing the as-found lift pressure test. There were two causes for the failures. One of the SRV pilot assemblies failed due to corrosion bonding; the other SRV pilot assembly failed due to a lack of a barrier to prevent inadvertent disassembly of the SRV pilot prior to testing. Although the Technical Specifications limits related to the set point lift pressures of the SRV pilot valve assemblies were exceeaed, an analysis indicates that the design basis pressures to ensure safety of the reactor vessel and its pressure related appurtenances were not challenged. Public safety was not at risk. Safety to plant personnel and plant equipment was not at risk. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BYOMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a (See NUREG-1022, R 3 for instruction and guidance for completing this form means used to impose an information collection does not display a currently valid OMB control http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Cooper Nuclear Station 05000- 298 2017 -002 -00 | PLANT STATUS Cooper Nuclear Station (CNS) was in Mode 1, Power Operations, 100 percent power, at the time of discovery i.e., February 28, 2017. BACKGROUND The pressure relief system includes three American Society of Mechanical Engineers code safety valves (SV) [EllS:SB] and eight safety relief valves (SRV) [EllS:RV], all of which are located on the main steam lines [EllS:SB] within the drywell [EllS:NH], between the reactor vessel [EllS:RPV] and the first main steam isolation valve [EllS:ISV]. The SVs provide protection against over pressurization of the nuclear system and discharge directly into the interior space of the drywell. The SRVs discharge to the suppression pool and provide three main functions: overpressure relief operation to limit the pressure rise and prevent safety valve opening, overpressure safety operation to prevent nuclear system over pressurization, and depressurization operation (opened automatically or manually) as part of the emergency core cooling system [EllS:BJ, BM, BO]. Technical Specifications (TS) Limiting Condition for Operation 3.4.3 requires the safety function of seven SRVs and three SVs to be operable. The nominal set pressure and tolerances for these valves are established in CNS TS Surveillance Requirement (SR) 3.4.3.1. The SRVs installed at CNS are Target Rock Model 7567F, two-stage, pilot-actuated valves with pilot assemblies comprised of Stellite 21 pilot discs and Stellite 6B pilot body seats. The pilot assemblies had been in continuous service since the Fall of 2014. In 2015, five of eight SRV pilot valve assemblies removed in the Fall of 2014 failed to lift within the TS lift setpoint requirements. The cause of these failures was determined to be corrosion bonding. Corrective actions included submitting a TS change to the Nuclear Regulatory Commission requesting setpoint changes as noted in EE 10-053, "Margin Evaluation for SRVs Out-of-Service," and reducing the number of operable SRVs from seven to five. This action has not been completed. EVENT DESCRIPTION Three Main Steam SRV body assemblies (main body and pilot assembly) and the remaining five SRV pilot assemblies, removed during Refueling Outage (RE) 29 in the Fall of 2016, were tested at National Technical Systems Laboratories (NTS; formerly Wyle Laboratories). One SRV pilot assembly failed the as-found lift pressure testing; another SRV pilot assembly was conservatively considered a failure due to lack of as-found lift pressure test data since it was disassembled prior to performing the as-found lift pressure test. The pressure setpoint for SRV pilot assembly serial number 377 is 1090 psig. The TS SR 3.4.3.1 as tound limit of acceptance is 1090 +/- 3%. The first actual lift pressure of this SRV pilot assembly was recorded as 1127 psig. Second and third lifts were performed with the results being 1113 psig and 1106 psig respectively. | ML17139D350
Limerick Generating Station | Unit 1 | Condition Prohibited by TS Due to Inoperable RPIS | 05-22-2017 | A power supply in the Rod Position Indication System (RPIS) failed causing a Main Control Room (MGR) alarm and loss of several control rod position indications. Using the Four Rod Display, the control room operators determined the affected control rods and found approximately half of the control rods had no indication. Although the Four Rod Display did not show control rod position for these rods, the staff concluded that the Full Core Display indication satisfied control rod position indication requirements for a majority of the control rods that were either full-in or full-out. It was later determined that the Full Core Display indicates the last known position in memory which is not replaced until new data is received. In this case, no data would have been received for the control rods due to the power supply failure. The failure to identify loss of control rod position indication for the control rods caused a failure to meet the plant's Technical Specifications (TS) and is reportable under 1O CFR 50.73(a)(2)(i)(B). This condition existed for approximately 19.5 hours prior to the power supply replacement, which was greater than the TS required actions to determine rod position within 1 hour or be in hot shutdown within the following 12 hours. NRG FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03131/2020 (04·2017)) Estimated burden per response to comply with this mandatory collection request 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555·0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office ol Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150·0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-colfections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR Limerick Generating Station, Unit 1 05000352 NUMBER NO. 2017 - 003 - 00 | I. Unit Conditions Prior to the Event Limerick Generating Station (LGS) Unit 1 was operating in Operational Condition (OPCON) 1 at 100 percent power at the time of the event. There were no other structures, systems, or components inoperable at the time of the event that contributed to the event. 11. Description of the Event On 3/16/17 at 1724, the Unit 1 Main Control Room (MCR) received a Rod Position Indication System (RPIS) Inoperable alarm and identified that multiple control rod position indications were inoperable due to a failed power supply. The crew entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.1.3.7 Action a.1 which directs, "with one or more control rod position indicators inoperable, within 1 hour, determine the position of the control rod by using an alternate method." Of the 83 control rods with no indication on the four rod display, 81 control rods indicated the expected position of full-in or full-out on the full core display. A method of alternate control rod position determination was initiated for the remaining two control rods that were mid-position and thus had no indication. On 3/16/17 at 1819, to satisfy the TS LCO Action, the crew determined control rod position of the two control rods by using the RPIS test box. Therefore, the TS LCO 3.1.3.7 Action was documented as being satisfied. On 3/17/17 at 1251, the power supply was replaced and RPIS position indication was restored to operable. LCO 3.1.3.7 action was exited for all control rods. On 3/22/17, it was identified that the power supply failure rendered the full core display incapable of updating in response to a position change for the affected control rods. Subsequently, it was determined to not be a valid means that could be used to verify control rod position indication. The condition existed for approximately 19.5 hours prior to the power supply replacement, which is greater than the TS required actions to determine rod position within 1 hour or be in hot shutdown within the following 12 hours. Therefore, the failure to identify loss of control rod position indication and thus take the required TS actions is a condition prohibited by TS and is reportable under 1 O CFR 50. 73(a)(2)(i)(B). Ill. Analysis of the Event On 3/16/17, Limerick Unit 1 MCR received an alarm for "RPIS INOPERATIVE" due to a power supply failure. Review of indicators by the control room staff found that several indicators were impacted and did not show control rod position for some of the control rods. The operating crew discussed the observed indications and impacts of the power supply failure. Since the majority of the impacted control rods were either full-in or full-out, it was concluded that the red or green indicator on the Full Core Display satisfied the RPIS rod position TS action for those control rods. This left two control rods without position indication. Rod position was obtained using an alternate method, which met the TS required action. NRG FORM 366A (04·2017) Page _2_ of _4_ | ML17142A145
i | Unknown Unit | Inadvertent Isolation of the High Pressure Coolant Injection System 5. EVENTDATE 6. LER NUMBER 7. REPORTDATE 8. OTHER FACILITIES INVOLVED MONTH DAY YEAR YEAR SE N Q U U M EN BE T R IAL RE N V O MONTH DAY YEAR FACILITYNAME DOCKETNUMBER N/A N/A FACILITYNAME DOCKETNUMBER 4 4 2017 2017 - 003 - 00 6 5 2017 N/A N/A 9. OPERATINGMODE 11.THIS REPORT15SUBMITTED PURSUANTTOTHEREQUIREMENTS OF 10 CFR§: (Checkallthatapply) 20.2201(b) 20.2203(a)(3)(i) 50.73(a)(2)(ii)(A) 50.73(a)(2)(v8i)(A) 20.2201(d) 20.2203(a)(3)(H) 50.73(a)(2)(H)(B) 50.73(a)(2)(v8i)(B) 20.2203(a)(1) 20.2203(a)(4) 50.73(a)(2)Øii) 50.73(a)(2)(ix)(A) 20.2203(a)(2)(i) 50.36(c)(1)C)(A) 50.73(a)(2)(iv)(A) 50.73(a)(2)(x) 10. POWERLEVEL 20.2203(a)(2)(U) 50.36(c)(1)(ii)(A) 50.73(a)(2)(v)(A) 73.71(a)(4) U 20.2203(a)(2)(Ui) 50.36(c)(2) 50.73(a)(2)(v)(B) Jj 73.71(a)(5) 20.2203(a)(2)v) 50.46(a)(3)Øi) 50.73(a)(2)(v)(C) 73.77(a)(1) 100 20.2203(a)(2)(v) 50.73(a)(2)(i)(A) 50.73(a)(2)(v)(D) 73.77(a)(2)(i) U 20.2203(a)(2)(vi) 50.73(a)(2)(i)(B) 50.73(a)(2)(vii) 73.77(a)(2)(0) 50.73(a)(2)Ø)(C) OTHER SpecifyinAbstractbeloworin NRCForm366A 12.LICENSEECONTACTFORThIS LER LICENSEECONTACT TELEPHONENUMBER(IncludeAreaCode) Mr. William Drews, RegulatoryAssurance Manager 315-349-6562 13. COMPLETEONELINEFOREACH COMPONENTFAILURE DESCRIBED INTHIS REPORT CAUSE SYSTEM COMPONENT FA M C A TU NU R - ER REP T O O R E T P A IX BLE CAUSE SYSTEM COMPONENT I FA M C A T N U U R - ER REP T O O R E T P A IX BLE A BJ N 14. SUPPLEMENTALREPORTEXPECTED 15. EXPECTED MONTH DAY YEAR EJ SUBMISSION YES (Ifyes, complete 15. EXPECTED SUBMISSIONDATE) NO DATE ABSTRACT (Limitto 1400spaces,i.e.,approximately15single-spacedtypewnftenlines) On April 4, 2017 at 0735, with the James A. FitzPatrick Nuclear Power Plant operating in Mode 1 at 100 percent power the High Pressure Coolant Injection System (HPCI) was inadvertently isolated during the performance of l&C testing. Technicians were in the process of performing instrument surveillance tests for low pressure emergency core cooling systems when a trip signal was applied to the incorrect instrument. This caused a HPCI System isolation signal on High Area Temperature, resulting in the closure ofthe HPCI steam isolation valves. The surveillance testing was aborted and the HPCI system was restored. HPCI is a single-train system; therefore, the inadvertent isolation is being reported as an event or condition that could have prevented fulfillment ofthe safety function ofa system needed to mitigate the consequences ofan accident per 10 CFR 50.73(a)(2)(v)(D). NRCFORM366(06-2016) NRC FORM 366A U.S. NUCLEARREGULATORYCOMMISSION APPROVED BY0MB: NO. 3150-0104 EXPIRES: 0313112020 (06-2016) .,&‘“ ‘“c, LICENSEE EVENT REPORT (LER) E le s s h s m on a s ted lea b r u n r e d d en ar p e er in r c e o s r p p o or n a s t e ed to in c t o o m th p e ly li w ce th nsi th n i g n p m r a o n c d es a s tor a y nd co f l e l d ect b io ac n k re to qu in e d s u t: st 8 ry 0 . ho S u e r n s d . co R m ep m o e rt n e t d s y’ CONTINUPTION SHEET regardingburdenestimatetothe FOIA, PrivacyandIntormation Collections Branch (T-5 F53), U.S. ‘% ‘ ç /j l N n u fo c c le o a ll r ects. R R e e g s u o l u a r to c r e y @nrc C .g o o m v m , i a s n s d ion to , the W D a e s s h k in O gt f o fi n c , er,O D ff C iceof 20 In 5 f 5 o 5 r - m 0 a 0 t 0 io 1 n , an o d r R by egulato e r - y m A ai f l fairs to , % NEOB-10202, (3150-0104), OfficeofManagementand Budget,Washington, DC 20503. Ifa means * usedtoimposeaninformationcollectiondoesnotdisplayacurrentlyvalid0MB controlnumber,the (See NUREG-1022, R.3for instruction and guidanceforcompletingthis form NRCmaynotconductorsponsor.andapersonisnotrequiredtorespondto, theinformahoncollechon. http:I/wwvv.nrc.gov/reading-rm/doc-collections/nuregs/staff/srl022/r3/) 1. FACILITY NAME 2. DOCKETNUMBER 3. LERNUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 333 NUMBER NO. — 2017 —003 —00 NARRATIVE Background The High Pressure Coolant Injection (HPCI) System [EllS Identifier: BJJ is part ofthe Emergency Core Cooling System (ECCS); HPCI provides and maintains an adequate coolant inventory inside the Reactor Pressure Vessel [RPVJ to prevent damage to the reactor core under postulated accident scenarios. The system is comprised of various components which include a turbine, pumps, valves, piping, and instrumentation. The HPCI System may be initiated by automatic or manual means; although, manual initiation requires manipulation of individual pump and valve control switches. Automatic initiation occurs for conditions of Reactor Vessel Water Level ‘Low Low” or Drywell Pressure “High.” Automatic isolation occurs upon receipt — — ofthe following signals: high steam flow, high temperature in the HPCI equipment area, low steam supply pressure, high turbine exhaust pressure, and high suppression pool area temperature. HPCI area temperatures are provided to detect a leak from the associated system steam piping. The isolation occurs when a leak has occurred and is diverse to the high flow instrumentation. Ifthe leak is allowed to continue without isolation, offsite dose limits may be reached. The HPCI area isolation function is not assumed in any UFSAR transient or accident analysis since bounding analyses are performed for large breaks such as recirculation or main steam line breaks. Area Temperature-High signals are initiated from resistance temperature detectors (RTD5) that are appropriately located to protect the system that is being monitored. Two instruments monitor each area for a total of 16 channels for HPCI. All channels for each HPCI Area Temperature High Function are available and are required to be operable to ensure that no single instrument - failure can preclude the isolation function. The Allowable Values are set high enough above normal operating levels to avoid spurious operation but low enough to provide timely detection of a steam leak. Event Description On April 4, 2017, I&C technicians were performing ISP-i75B1, Reactor and Containment Cooling Instrument Functional Test I Calibration, when the HPCI System was inadvertently isolated. ISP-i75B1, Step 9.4.5 directs the connection of a DC voltage source on 02-3MTU-252B (Reactor Pressure Interlock CSP/RHR/RHR SDC Master Trip Unit). While performing the Core Spray test, the technician at the trip unit mistakenly connected the energized voltage source to the adjacent trip unit, 23MTU-217B (HPCI Area Temp Hi Master Trip Unit), afterthe lead had become disconnected. Flagging was used at the start ofthe test but when the lead became disconnected it removed the installed flagging. The worker identified the incorrect component and installed the test lead into the HPCI trip unit. The error was immediately identified by the unexpected receipt of annunciators. The test was stopped, the technician at the 09-96 panel was removed from the field and a plan was developed and executed to abort the test and restore conditions to normal for HPCI. The following is a timeline of pertinent events on April 4, 2017: 0730— Commencement of ISP-i75B1, Reactor and Containment Cooling Instrument Functional Test/Calibration 0735 HPCI inoperable due to inadvertent isolation; Reactor Core Isolation Cooling (RCIC) [BN] verified — operable and protected per procedure 1038 Isolation verification and recovery complete; Hi-Hi Temperature Isolation restored to normal — 1132 Completed NRC Notification ENS 52664, and informed resident — 1238 HPCI restored to operable status — NRCFORM366A(O6-2016) Page 2 of4 NRC FORM 366A U.S. NUCLEARREGULATORYCOMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 0313112020 (06-2016) “r., LICENSEE EVENT REPORT (LER) E le s s t s i o m n a s te l d ea b r u n r e d d en ar p e er in r c e o s r p p o or n a s t e ed to in c t o o m th p e ly li w c i e t n h si t n h g is p m r a o n c d e a ss tor a y nd co f l e l d ect b i a o c n k re to qu in e d st u : st 8 ry 0 . ho S u e r n s d . co R m ep m o e r n te t d s y . regardingburdenestimatetothe FOIA, PrivacyandInformation Cotections Branch (1-5 F53),U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to u .,, ’ lnfocollects.Reoourcenrc.gov,andtotheDeskOfficer,OfficeofInformation and RegulatoryAffairs, ‘ NEOB-10202, (3150-0104),OfficeofManagementand Budget,Washington, DC 20503 If a means usedtoimposeaninformationcollectiondoesnotdisplayacurrentlynalid0MB controlnumber,the (See NUREG-1022, R.3forinstruction and guidanceforcompletingthisform NRCmaynotconductorsponsor.andapersonisnotrequiredtorespondto, theinformatoncotechon, http:l/iwiw.nrc.gov/reading-rm/doc-collections/nuregs/staff/srl022/r3/) 1. FACILITYNAME 2. DOCKETNUMBER 3. LERNUMBER YEAR SEQUENTIAL REV James A. FitzPatriCk Nuclear Power Plant 05000 333 NUMBER NO. — 2017 —003 —00 Cause The active error and event were the result ofthe l&C technician mistakenly connecting the energized voltage source to an adjacent trip unit, 23MTU-217B (HPCI Area Temp Hi Master Trip Unit). The error was immediately identified by the unexpected receipt of control room annunciatots which indicated the HPCI system had isolated. The Senior l&C technician in the Control Room subsequently questioned the l&C technician at Panel 09-96 in the Relay Room as to what action had just been performed, and directed all work to be stopped immediately. The apparent cause was identified as failure to implement the requited human performance tools. The l&C technician failed to stop and reverify the correct component priorto re-landing the test lead and proceeding with the task after conditions had changed. Similar Events Browns Ferry Nuclear Plant, Unit 3: LER 2016-006-00, High Pressure Coolant Injection System Found to be Inoperable During Testing Limerick Generating Station, Unit 2: LER 2015-005-00, Condition that Could Have Prevented Fulfillment of the High Pressure Coolant Injection (HPCI) System Safety Function Corrective Actions Completed Actions • All work immediately stopped; RCIC verified operable, and protected per procedure • HPCI operability restored per OP-i5, High Pressure Coolant Injection • NRC notified via ENS 52664 • I&C technician qualifications removed • Increased observations, peer checks, and validation of l&C activities Safety Significance Nuclear Safety Actual Consequences There were no actual nuclear safety consequences during this period as a result ofthis event. Potential Consequences This event resulted in the inoperability of the single train HPCI system for approximately five (5) hours. The HPCI System is provided to ensure that the reactor is adequately cooled to limit fuel clad temperature in the event of a small break in the Reactor Coolant System piping with a loss-of-coolant which does not result in rapid depressurization ofthe reactor vessel. The HPCI System permits the plant to be shut down while maintaining sufficient reactor vessel water inventory until the reactor vessel pressure is below the pressure at which either the Low Pressure Coolant Injection (LPCI) [BOJ or Core Spray [BMJ System can maintain core cooling. Several alternate methods were available to Operations personnel in the event of an emergency to provide core cooling, and mitigation of the consequences of an accident. In the event of HPCI inoperability during a design basis accident, adequate core cooling is ensured by the operability of the other ECCS injection/spray subsystems in conjunction with the Automatic Depressurization System (ADS). The JAF Operations Log was reviewed to determine if the ADS orthe low pressure ECCS were inoperable during the period ofthe HPCI NRCFORM366A(06-2016) Page 3 of4 NRC FORM 366A U.S. NUCLEARREGULATORYCOMMISSION APPROVEDBY 0MB: NO. 3150-0104 EXPIRES: 0313112020 (06-2016) .,&‘ ,, “‘•., LICENSEE EVENT REPORT (LER) E le s s t s i o m n a s te l d ea b r u n r e d d en ar p e er in r c e o s r p p o or n a s t e ed to in c t o o m th pl e y li w c i e t n h si t n h g is p m r a o n c d e a ss tor a y nd co f l e l d ect b io ac n k re to qu in e d st u : st 8 ry 0 . ho S u e r n s d . co R m ep m o e r n te t d s ‘W’ regardingburdenestimatetothe FOIA, PrivacyandInformation Collections Branch (T-5 F53), U.S. .. ,, Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to % - ...‘ N ln E f O oc B o -1 lle 0 c 2 t 0 s 2 .R , e (3 s 1 o 5 u 0 rc -0 e 1 n 0 r 4 c ) .g , o O v f , fi a c n e d of to M th a e na D g e e s m k e O nt ffi a c n e d r, B O u ff d ic g e et o , f W In a f s o h rm in a g t t i o o n n , an D d C 2 R 0 e 5 g 0 u 3 l , at I o f ry a A m f e fa a i n rs s , usedtoimposeaninformationcollectiondoesnotdisplayacurrentlyvalid0MB controlnumber,the (See NUREG-1022. R.3forinstruction and guidanceforcompleting this form NRCmaynotconductorsponsor.andapersonisnotrequiredtorespondto, theinformahoncollechon. http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/srl022/r31) 1. FACILITY NAME 2. DOCKET NUMBER 3. LERNUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 333 NUMBER NO. — 2017 —003 —00 system inoperability. The ADS, Core Spray and LPCI were confirmed to oe operable during the period of HPCI inoperabiIity. In addition, the approximate five (5) hours of HPCI inoperability is well belowthe TS LCD 3.5.1 .C completion time offourteen (14) days. Based on the above, during the period that the HPCI system was inoperable, sufficient systems were available to provide the required safety functions to protect the health and safety ofthe public. Therefore, no significant reduction in the health and safety ofthe public or plant personnel is associated with this event. Radiological Safety There was no radiological safety impact associated with this event. Industrial Safety There was no industrial safety impact associated with this event. References • Issue Report No. 03993791, Connection ofTest Equipment to Incorrect Component • JAF Technical Specifications NRCFORM366A(06-20161 Page 4 of4 | 06-05-2017 | On April 4, 2017 at 0735, with the James A. FitzPatrick Nuclear Power Plant operating in Mode 1 at 100 percent power the High Pressure Coolant Injection System (HPCI) was inadvertently isolated during the performance of l&C testing. Technicians were in the process of performing instrument surveillance tests for low pressure emergency core cooling systems when a trip signal was applied to the incorrect instrument. This caused a HPCI System isolation signal on High Area Temperature, resulting in the closure ofthe HPCI steam isolation valves. The surveillance testing was aborted and the HPCI system was restored. HPCI is a single-train system; therefore, the inadvertent isolation is being reported as an event or condition that could have prevented fulfillment ofthe safety function ofa system needed to mitigate the consequences ofan accident per 10 CFR 50.73(a)(2)(v)(D). NRCFORM366(06-2016) NRC FORM 366A U.S. NUCLEARREGULATORYCOMMISSION APPROVED BY0MB: NO. 3150-0104 EXPIRES: 0313112020 (06-2016) .,&‘“ ‘“c, LICENSEE EVENT REPORT (LER) E le s s h s m on a s ted lea b r u n r e d d en ar p e er in r c e o s r p p o or n a s t e ed to in c t o o m th p e ly li w ce th nsi th n i g n p m r a o n c d es a s tor a y nd co f l e l d ect b io ac n k re to qu in e d s u t: st 8 ry 0 . ho S u e r n s d . co R m ep m o e rt n e t d s y’ CONTINUPTION SHEET regardingburdenestimatetothe FOIA, PrivacyandIntormation Collections Branch (T-5 F53), U.S. ‘% ‘ ç /j l N n u fo c c le o a ll r ects. R R e e g s u o l u a r to c r e y @nrc C .g o o m v m , i a s n s d ion to , the W D a e s s h k in O gt f o fi n c , er,O D ff C iceof 20 In 5 f 5 o 5 r - m 0 a 0 t 0 io 1 n , an o d r R by egulato e r - y m A ai f l fairs to , % NEOB-10202, (3150-0104), OfficeofManagementand Budget,Washington, DC 20503. Ifa means * usedtoimposeaninformationcollectiondoesnotdisplayacurrentlyvalid0MB controlnumber,the (See NUREG-1022, R.3for instruction and guidanceforcompletingthis form NRCmaynotconductorsponsor.andapersonisnotrequiredtorespondto, theinformahoncollechon. http:I/wwvv.nrc.gov/reading-rm/doc-collections/nuregs/staff/srl022/r3/) 1. FACILITY NAME 2. DOCKETNUMBER 3. LERNUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 333 NUMBER NO. — 2017 —003 —00 | Background The High Pressure Coolant Injection (HPCI) System [EllS Identifier: BJJ is part ofthe Emergency Core Cooling System (ECCS); HPCI provides and maintains an adequate coolant inventory inside the Reactor Pressure Vessel [RPVJ to prevent damage to the reactor core under postulated accident scenarios. The system is comprised of various components which include a turbine, pumps, valves, piping, and instrumentation. The HPCI System may be initiated by automatic or manual means; although, manual initiation requires manipulation of individual pump and valve control switches. Automatic initiation occurs for conditions of Reactor Vessel Water Level ‘Low Low” or Drywell Pressure “High.” Automatic isolation occurs upon receipt — — ofthe following signals: high steam flow, high temperature in the HPCI equipment area, low steam supply pressure, high turbine exhaust pressure, and high suppression pool area temperature. HPCI area temperatures are provided to detect a leak from the associated system steam piping. The isolation occurs when a leak has occurred and is diverse to the high flow instrumentation. Ifthe leak is allowed to continue without isolation, offsite dose limits may be reached. The HPCI area isolation function is not assumed in any UFSAR transient or accident analysis since bounding analyses are performed for large breaks such as recirculation or main steam line breaks. Area Temperature-High signals are initiated from resistance temperature detectors (RTD5) that are appropriately located to protect the system that is being monitored. Two instruments monitor each area for a total of 16 channels for HPCI. All channels for each HPCI Area Temperature High Function are available and are required to be operable to ensure that no single instrument - failure can preclude the isolation function. The Allowable Values are set high enough above normal operating levels to avoid spurious operation but low enough to provide timely detection of a steam leak. Event Description On April 4, 2017, I&C technicians were performing ISP-i75B1, Reactor and Containment Cooling Instrument Functional Test I Calibration, when the HPCI System was inadvertently isolated. ISP-i75B1, Step 9.4.5 directs the connection of a DC voltage source on 02-3MTU-252B (Reactor Pressure Interlock CSP/RHR/RHR SDC Master Trip Unit). While performing the Core Spray test, the technician at the trip unit mistakenly connected the energized voltage source to the adjacent trip unit, 23MTU-217B (HPCI Area Temp Hi Master Trip Unit), afterthe lead had become disconnected. Flagging was used at the start ofthe test but when the lead became disconnected it removed the installed flagging. The worker identified the incorrect component and installed the test lead into the HPCI trip unit. The error was immediately identified by the unexpected receipt of annunciators. The test was stopped, the technician at the 09-96 panel was removed from the field and a plan was developed and executed to abort the test and restore conditions to normal for HPCI. The following is a timeline of pertinent events on April 4, 2017: 0730— Commencement of ISP-i75B1, Reactor and Containment Cooling Instrument Functional Test/Calibration 0735 HPCI inoperable due to inadvertent isolation; Reactor Core Isolation Cooling (RCIC) [BN] verified — operable and protected per procedure 1038 Isolation verification and recovery complete; Hi-Hi Temperature Isolation restored to normal — 1132 Completed NRC Notification ENS 52664, and informed resident — 1238 HPCI restored to operable status — NRCFORM366A(O6-2016) Page 2 of4 | ML17156A293
i | Unknown Unit | Isolation of HPCI | 05-25-2017 | On March 27, 2017, at 1825 [EDT], with the reactor at 100 percent core thermal power and steady state conditions, plant personnel caused a High Pressure Coolant Injection (HPCI) System isolation. Pilgrim Nuclear Power Station was performing planned testing on the Reactor Core Isolation Cooling (RCIC) when the HPCI System isolated. Accordingly, the HPCI System was declared inoperable. IThe Technical Specifications Limiting Conditi9n for Operation~Action Statement 3.5.C.2 was entered and planned troubleshooting into the cause of the HPCI isolation was started. This event is reportable under 10 CFR 50. 73(a)(2)(v)(D), any event or condi.tion that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. There was no impact to public health and safety from this condition. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) ... .,., Estimated burden per response to comply wilh lhis mandatory collection request: 80 hours. Reported ~,,,,. lessons learned are incorporated into the licensing process and fed back to industry. Send ; R %i. LICENSEE EVENT REPORT (LER) comments regarding burden estimale to the Information Services Branch (T-2 F43), U.S. Nuclear ..... \; "/ Regulatory Commission, Washington, DC 20555-0001, or by e-mail . lo CONTINUATION SHEET lnfocollecls.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information col/eclion does not display a currently valid OMS conlro/ number, the htto://www.nrc.gov/reading-rm/doc-collections/nureos/staff/sr1022/r3D NRC may not conduct or sponsor, and a person is not required to respond to, lhe information col/eclion. 1. FACILITY NAME 2. DOCKET NUMBER 3. LERNUMBER YEAR SEQUENTIAL REV Pilgrim Nuclear Power Station 05000- 293 NUMBER NO. 2017 -002 -00 | BACKGROUND The High Pressure Coolant Injection (HPCI) System is provided to ensure that the reactor core is adequately cooled to limit fuel clad temperature in the event of a small break in the nuclear system and loss of coolant which does not result in rapid depressurization of the reactor vessel. The HPCI System permits the reactor to be shut down while maintaining sufficient reactor vessel water inventory until the reactor vessel is depressurized. HPCI continues to operate until reactor vessel pressure is below the pressure at which Low Pressure Coolant Injection or Core Spray systems would maintain core cooling. EVENT DESCRIPTION On March 27, 2017, at 1825 [EDT], with the reactor at 100 percent core thermal power and steady state conditions, the HPCI System was declared inoperable and Technical Specifications (TS) Limiting Condition for Operation (LCO) Action Statement (AS) 3.5.C.2 was entered. Pilgrim Nuclear Power Station (PNPS) personnel were performing planned testing of the Reactor Core Isolation Cooling (RCIC) System per TS Table 4.2.B. During the test, it has been determined that plant personnel heated the wrong temperature switch causing the HPCI system to isolate. CAUSE OF THE EVENT The Direct Cause of the event was the application of heat to a HPCI temperature switch. The system responded as designed and the HPCI primary containment isolation valves closed making HPCI unavailable. The Root Cause of this event is two Nuclear Controls Technicians decided to deviate from procedure requirements while p~rforming procedure 8.M.2-2.6.3 Attachment 1, RCIC Steam Line High Temperature Instrument Functional Test. CORRECTIVE ACTIONS The corrective action to preclude repetition documents that both individuals' qualifications have been removed and their site access restricted. Specific disciplinary actions have been taken with the individuals involved pursuant to the requirements of 10 CFR 73.56(c). . NRG FORM 366A (04-2017) Page 2 of 3 I --- | ML17163A179
Brunswick Steam Electric Plant (BSEP) | Unit 2 | Plant Mode Change with Primary Containment Inoperable | 06-09-2017 | On April 13, 2017, Unit 2 was in Mode 4 preparing to exit a refueling outage. The primary containment was being vented to ensure habitability of the Drywell. The valve alignment for Drywell ventilation makes the primary containment inoperable due to the Drywell and Suppression Chamber airspaces being in communication with each other. At 23:47 Eastern Daylight Time (EDT), the reactor mode was changed from Mode 4 to Mode 2 with ventilation still in progress. In Mode 2, the Primary Containment is required to be operable. Therefore, the plant entered a condition prohibited by the Technical Specifications, and the event is reportable per 10 CFR 50.73(a)(2)(i)(B). It is also reportable per 10 CFR 50.73(a)(2)(v)(D) because the primary containment safety function was lost. The condition was discovered 28 minutes later on April 14, 2017, at 00:15 EDT and was corrected by closing the ventilation flowpaths at 00:30 EDT on April 14, 2017. This event resulted from Control Room personnel not initiating a tracking document while in Mode 4 with the primary containment inoperable. When preparing to change the plant mode from Mode 4 to Mode 2, the primary containment ventilation status was overlooked. Corrective actions for this event included closing the containment ventilation paths and remediating the Shift Manager and Control Room Supervisor. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) E le s s t s im on a s te d le b a u rn rd e e d n a p r e e r r in e c s o p r o p n o s r e a t t e o d c o in m to p ly t h w e i th li c th e i n s s m ing a nd p a ro to c r e y s s c ol a le n c d t io f n e d r eq b u a e c s k t : t 8 o 0 i h n o d u u r s s tr . y R . e p S or e te n d d LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear CONTINUATION SHEET Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant (BSEP) YEAR 05000324 NUMBER NO. Unit 2 2017 - 002 - 000 | Energy Industry Identification System (EllS) codes are identified in the text as [XX]. Background Initial Conditions On April 13, 2017, at approximately 23:47 Eastern Daylight Time (EDT), Unit 2 was in Mode 4 (i.e. Cold Shutdown) in preparation for exiting a refueling outage. At that time, the ventilation valves for both the Drywell and Suppression Chamber were open to ensure the atmosphere in the containment was breathable for personnel performing maintenance in the Drywell. Reportability Criteria This event is reportable per 10 CFR 50.73(a)(2)(i)(B) because the plant entered a condition which is prohibited by the plant’s Technical Specifications (TS). Specifically, TS 3.6.1.1 requires the primary containment to be operable in Modes 1, 2, and 3. With the drywell and suppression chamber atmospheres communicating, the containment is inoperable. Additionally, TS Limiting Condition for Operation (LCO) 3.0.4 requires all LCOs to be met for the plant condition to be entered, prior to entry. Primary containment operability is required in Mode 2 (i.e., Startup). Therefore, at 23:47 EDT on April 13, 2017, when the plant changed modes from Mode 4 to Mode 2 without meeting the LCO for primary containment, this failed to meet TS LCO 3.0.4. This event is reportable per 10 CFR 50.73(a)(2)(v)(D) because the plant experienced a loss of the safety function of a system designed to mitigate the consequences of an accident. Since the containment was rendered inoperable by having the Drywell and Suppression Chamber airspaces in communication with each other, the safety function was lost. This event is also reportable per 10 CFR 50.72(b)(3)(v)(D) via an 8-hour telephone report. The telephone report was completed as Event Number 52679 at 07:37 EDT on April 14, 2017. Event Description On April 13, 2017, Unit 2 was in Mode 4 preparing to exit a refueling outage. At 20:48 EDT, Control Room personnel began ventilating the primary containment in preparation for a personnel entry into the Drywell to perform minor maintenance. The ventilation procedure requires valves be opened from the Suppression Chamber atmosphere and the Drywell atmosphere into a shared ventilation line. With both atmospheres communicating, the Primary Containment is not operable. However, Primary Containment is not required to be operable with the unit in Mode 4. When the maintenance was completed in the Drywell, Control Room personnel resumed preparations for starting up the reactor. At 23:47 EDT, the reactor mode was changed from Mode 4 to Mode 2. In Mode 2, | ML17163A361
Brunswick Steam Electric Plant (BSEP) | Unit 1 | Foreign Material in Switch Results in Unplanned Automatic Start of Emergency Diesel Generators | 06-12-2017 | On April 17, 2017, at 0004 Eastern Daylight Time, Unit 1 was in Mode 1 at approximately 100 percent of rated power, and Unit 2 was in Mode 1 at approximately 22 percent of rated power and was starting up from a refueling outage. Operators manually tripped the Unit 2 main turbine to halt increasing bearing vibration. The power circuit breakers (PCBs) for the Unit 2 main generator did not open as expected on the turbine trip, but subsequently opened when main generator reverse power relays actuated. This resulted in the automatic start of all four emergency diesel generators (EDGs). The EDGs did not tie to emergency busses because offsite power was still available. This event resulted from a component which failed due to foreign material intrusion. A limit switch associated with a main turbine stop valve failed to change states when the turbine was tripped. The limit switch configuration, together with other logic, satisfied the conditions to start the EDGs. The limit switch failure resulted from foreign material in the switch. The failed limit switch was replaced. Planned corrective actions include inspecting similar switches on both units, and sealing the wire entrances of the switch bodies to improve foreign material exclusion. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) E le s s t s im on a s te d le b a u rn rd e e d n a p r e e r r in e c s o p r o p n o s r e a t t e o d c o in m to p ly t h w e i th li c th e i n s s m ing a nd p a ro to c r e y s s c ol a le n c d t io f n e d r eq b u a e c s k t : t 8 o 0 i h n o d u u r s s tr . y R . e p S or e te n d d LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear CONTINUATION SHEET Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant (BSEP) YEAR 05000325 NUMBER NO. Unit 1 2017 - 002 - 000 | Energy Industry Identification System (EllS) codes are identified in the text as [XX]. Background Initial Conditions On April 17, 2017, at 00:04 Eastern Daylight Time (EDT), Unit 1 was in Mode 1 at approximately 100 percent of rated power, and Unit 2 was in Mode 1 at approximately 22 percent of rated power. Unit 2 was restarting following a refueling outage. Personnel were engaged in actions to resolve high bearing vibration on the main turbine [TA]. Reportability Criteria This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) because the plant experienced a valid start of its four emergency diesel generators (EDGs) [EK]. This event is also reportable per 10 CFR 50.72(b)(3)(iv)(A) via an 8-hour telephone report. The telephone report was completed as Event Number 52683 at 07:40 EDT on April 17, 2017. Event Description On April 17, 2017, at 00:04 EDT, the Unit 2 main turbine experienced high bearing vibration. Control Room personnel tripped the main turbine at a prearranged vibration level. The power circuit breakers (PCBs) [FK] for the main generator [EL] did not immediately open on the turbine trip as expected. Subsequently, a main generator lockout occurred on reverse power. The generator lockout sends a start signal to the plant’s four EDGs. These started as expected but did not tie to their emergency electrical buses because there was no loss of offsite power. The EDGs were then manually shut down. Event Cause This event occurred when a contact in a switch associated with a main turbine stop valve did not close correctly in response to a turbine trip. When the switch was disassembled, a small piece of foreign material was found inside, which was a fragment of a plastic tie-wrap. This interfered with proper contact function. The switch was installed with the wire entrance facing upward which allowed foreign material to fall into the switch body. The apparent cause of the event was that vendor guidance does not require any special foreign material consideration for installation of this switch with its wire entrance facing upward. Safety Assessment The site’s Electrical Power Distribution System sources consist of the offsite power sources (i.e., preferred and alternate power sources), and the onsite standby power sources, EDGs 1, 2, 3, and 4. The AC electrical power system provides independence and redundancy to ensure an available source of power to | ML17163A366
Monticello Nuclear Generating Plant 05000 -263 1 OF 3 | Unknown Unit | Reactor Scram and Group II Isolation Due to 11 Reactor Feed Pump (RFP) Removal from Service with 12 RFP Isolated | 06-13-2017 | On April 15, 2017 at 0436 hours, the 11 Reactor Feedwater Pump (RFP) was removed from service and the discharge valve closed. With the discharge valve closed and 12 RFP previously isolated no flow path was lined-up for the Condensate pumps to supply water to the vessel. Reactor water level lowered resulting in valid Reactor Protection System (RPS) actuation and Primary Containment Group II Isolation signals. The 11 RFP discharge valve was reopened to reestablish a flowpath to restore level. The RPS and Group II isolation logic was reset when cleared. Two apparent causes were identified: 1) Failure to identify and address the unusual Feedwater System configuration prior to execution of the 11 RFP shutdown. 2) Guidance for shutdown of the RFP did not take into account the state of the other train when shutting down a RFP. The corrective actions were: 1) Revise plant startup and shutdown procedures to ensure abnormal equipment lineups are addressed to avoid unexpected interactions. 2) Revise the Feedwater System operation procedure to maintain a flow path when the opposite train Reactor Feed Pump is isolated NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) LICENSEE EVENT REPORT (LER) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send CONTINUATION SHEET comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Monticello Nuclear Generating Plant NUMBER NO. 05000-263 2017 - 001 - 0 | EVENT DESCRIPTION On April 10, 2017, at approximately 1140 hours, prior to the 2017 Refueling Outage (RFO), the 12 Reactor Feedwater Pump (RFP) [EIIS: P] was removed from service and isolated for maintenance. On April 15, 2017, at 0142 hours, a manual reactor scram was inserted to shutdown the plant for the 2017 RFO. On April 15, 2017 at 0436 hours, with the unit in Mode 3, the 11 RFP in the Feedwater System [SJ] was removed from service in accordance with plant shutdown procedures and the 11 RFP discharge valve (FW-68-1) [ISV] was closed. With the 11 RFP discharge valve closed and the 12 RFP previously isolated, there was no make-up flow path lined-up for the Condensate pumps to supply water to the reactor vessel [RPV]. Reactor water level lowered, and at approximately 0441 hours, resulted in a valid Reactor Protection System (RPS) [JD] actuation (scram) signal and a valid Primary Containment Group II Isolation [JM] signal when level decreased below +9 inches as indicated on the Safeguards level instrumentation. The 11 RFP discharge valve was reopened to reestablish a flowpath from the Condensate pumps restoring reactor water level. The RPS and Group II isolation logic was reset at 0452 and 0500 hours, respectively, as stated in the station log. An eight hour event notification was made pursuant to 10 CFR 50.72(b)(3)(iv)(A). All systems functioned as required. EVENT ANALYSIS This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), “Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph 10 CFR 50.73(a)(2)(iv)(B).” Specifically, the RPS and the Primary Containment Isolation System (PCIS) actuations. This event is not classified as a safety system functional failure. CAUSE Two apparent causes were identified: 1. Operators failed to identify and address the unusual Condensate and Feedwater System configuration prior to execution of the 11 RFP shutdown. 2. The guidance for shutdown of the RFP in the Condensate and Reactor Feedwater System operation procedure did not take into account the state of the other train when shutting down a RFP. Page 2 of 3 | ML17164A171
Columbia Generating Station 05000 397 1 OF 3 | Unknown Unit | Automatic Scram Due to Off-site Load Reject | 06-08-2017 | On December 18, 2016 at l l :24 hours, an automatic scram occmTed due to a fault on an off-site transmission network. A reactor scram was automatically initiated by the plant response to the transient. All rods fully inserted, Main Steam Isolation Valves [SB,V] automatically closed due to loss of power to both Reactor Protection System [JC] busses. All safety systems operated as designed. Two Safety Relief Valves [SB,V] were initially cycled automatically, then several manually to maintain Reactor Pressure Vessel [AC] pressure. Reactor water level was maintained with Reactor Core Isolation Cooling [BN], Control Rod Drive [AA] flow, and High Pressure Core Spray [BG]. The entity responsible for the off-site transmission network, Bonneville Power Administration (BPA ), performed a cause evaluation for the loss of off-site power. The cause evaluation stated the event was caused by three sequential 500-kV breaker failures. BPA took immediate corrective actions to restore the off-site transmission network. The root cause evaluation addressing the plant response was performed by plant personnel. NRG FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMS: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA. Privacy and Information Collections Branch (T-5 CONTINUATION SHEET F53), U.S. Nuclear Regulatory Commission, Washington. DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov. and to the Desk Officer. Office of Information and Regulatory Affairs, NEOB-10202. (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number. the http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER CYEARl SEQUENTIAL REV 05000-1 I NUMBER 1-NO0. Columbia Generating Station 397 ~-I 004 | Plant Conditions The plant was operating at 100% power prior to the event. There were no safety related systems out of service prior to the event. Event Description On December 18, 2016 at 11 :24 hours, an automatic scram occurred due to a fault on an off-site transmission network. A reactor scram was automatically initiated by the plant response to the transient. All rods fully inserted and Main Steam Isolation Valves [SB,V] automatically closed due to loss of power to both Reactor Protection System (RPS) [JC] busses that occurred during the transient following the scram. All safety systems operated as designed. A full safety system isolation occurred due to the loss of RPS, which isolated Reactor Closed Cooling [CC] flow from containment. This caused Primary Containment (PC) temperature and pressure to increase causing high PC pressure actuations to occur. Two Safety Relief Valves [SB,V] were initially cycled automatically, then several manually to maintain Reactor Pressure Vessel (RPV) [AC] pressure. Reactor water level was restored with Reactor Core Isolation Cooling (RCIC) [BN], Control Rod Drive [AA] flow, and High Pressure Core Spray (HPCS) [BG]. After the initial successful start and injection of RCIC, a plant operator failed to establish the proper line up for re-initiation. This resulted in a trip of RCIC and using HPCS to maintain RPV level. Per plant procedures after the scram an operator tripped the main turbine (MT) [TAJ, but failed to trip the main generator (MG) [TB]. This allowed voltage to degrade until power was automatically transferred to the backup power sources. The PC was vented through a Standby Gas Treatment Filter [BH] per plant procedures to lower PC pressure. Cause Bonneville Power Administration (BPA) (operator of the off-site transmission network) performed an evaluation of the off site transmission network failure. The evaluation found that three breakers failed, each with different causes. The first breaker failed to operate properly due to air and water contamination in the hydraulic fluid combined with low ambient temperature, and a defective motor contactor. Corrective actions were performing a hydraulic service and replacing the motor contactor. The second breaker failure was due to condensed water vapor in the pneumatic control valve freezing during cold-weather conditions. The corrective action taken was installing heaters. The third breaker failure was due to condensed water vapor in the pneumatic control valve freezing during cold-weather conditions and a failure in a trip circuit. Corrective actions taken were installing heaters and replacing the damage in the trip circuit. Station personnel performed a root cause evaluation on the station's response to the reactor scram, including failure to trip both the MT and MG, and human performance issues operating RCIC. The plant responded to the transient as designed. The human performance issues are being addressed in Operations by updating procedures, training, and oversight. NRG FORM 366A (06-2016) Page 2 of 3 | ML17164A443
Monticello Nuclear Generating Plant 05000-263 1 OF 4 | Unknown Unit | Main Steam Isolation Valve Closure Time Outside of Technical Specification Requirements | 06-13-2017 | On April 15, 2017 at approximately 10:56 am, with the plant at 0% power in Mode 4 (Shutdown), while performing a plant shutdown procedure the "D" outboard Main Steam Isolation Valve (MSIV), A0-2- 860 was functionally tested. The Monticello Nuclear Generating Plant (MNGP) Technical Specifications (TS) Surveillance Requirement (SR) 3.6.1.3.6 requires that the isolation time of each MSIV is~ 3 seconds and_::: 9.9 seconds. During the functional test the "D" Outboard MSIV closing ime was measured at approximately 40.7 seconds. The valve was declared inoperable and subsequently repaired. The failure was attributed to the air pack pilot valves. This component failure is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS 3.6.1.3 "Primary Containment Isolation Valves," since A0-2-860 may have been inoperable for greater than the TS 3.6.1.3, Required Action A.1, Completion Time of 8 hours to isolate a main steam line, and the Completion Time forTS 3.6.1.3, Required Action F, to be in Mode 3 in 12 hours and Mode 4 in 36 hours when the completion time of A.1 is not met. There were minimal safety consequences associated with the condition since the primary containment isolation function was maintained. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT (LER) lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Monticello Nuclear Generating Plant NUMBER NO. 05000-263 2017 002 - 00 | EVENT DESCRIPTION On April15, 2017 at approximately 10:56 AM, with the plant at 0% power in Mode 4 (Shutdown), while performing a plant shutdown procedure the "D" outboard Main Steam [SB] Isolation Valve (MSIV) [ISV] A0-2-86D was functionally tested. The Monticello Nuclear Generating Plant (MNGP) Technical Specifications (TS) Surveillance Requirement (SR) 3.6.1.3.6 requires that the isolation time of each MSIV is:::, 3 seconds and,:: 9.9 seconds. During the functional test the "D" Outboard MSIV closing time was measured at approximately 40.7 seconds. The valve was declared inoperable and repaired during the refueling outage. During the test A0-2-86D was given a close signal via the control room hand switch [HS]. The valve delayed to start of closing by approximately 35 seconds and then proceeded to close normally in about 5 seconds. On site troubleshooting activities commenced and determined that the Hiller Co. air pack pilot valves (Model No. C1 001 OA- called V1 and V3) were the cause of the closure delay. The V1 pilot valve was found to be stuck in a closed position. The air pack was sent to the vendor to perform more inspection, testing and repair. The vendor discovered scoring on the piston rod and mounting plate of the booster assembly on the V1 pilot valve. This is evidence of binding and misalignment that caused the valve to not shuttle when called upon. The V3 pilot valve was shown through data analysis to have delayed movement during the event. The air pack was repaired by the vendor replacing the solenoid cluster and the pilot valves, and the boosters were rebuilt. The air pack was returned to MNGP, reinstalled and A0-2-86D completed satisfactory testing on 5/5/2017. A previous similar failure occurred on November 23, 2015 when A0-2-86D closed in 130 seconds after delaying start of closure. The troubleshooting of that failure indicated the plunger sticking or binding of an in-series solenoid valve was the cause of the failure to close in the required TS limits. Upon further review, this MSIV closure time failure is now attributed to the A0-2-86D air pack pilot valves failing to function as designed. EVENT ANALYSIS The event was determined to be reportable in accordance with 10 CFR 50.73 (a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications." Specifically, this component failure is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition Page 2 of 4 | ML17165A346
Edwin I. Hatch Nuclear Plant | Unit 1 | Automatic Scram Due to Intermediate Range Monitors Spiking Upscale | 06-16-2017 | On April 20, 2017 at 0302 EDT with Unit 1 at approximately 1 percent rated thermal power due to a reactor startup from a planned maintenance outage, an automatic reactor scram was received due to the "A" and "8" Intermediate Range Monitors (IRMs) spiking upscale simultaneously. The instrument's set points for high-high neutron flux were reached, giving false trip signals to both channels of the reactor protection system (RPS) trip logic. Upon the automatic reactor scram signal, all control rods fully inserted appropriately. No primary containment isolation system (PCIS) actuations occurred and none were expected to occur based upon plant conditions following the reactor scram. The cause of the event is due to the integrity of the IRMs signal cable connectors being in a degraded condition. Degradation was found on "A" IRM at the detector connector, while the "8" IRM had connection issues between the penetration and the jumper connector. These IRM cable integrity issues allowed a signal path to exist between the cables' shielding and center conductors, causing the IRMs to spike upscale. The "A" and "8" IRM jumper cables and the associated connections were replaced and all Unit 1 IRM cables and associated trip logics were tested satisfactorily. NRC FORM 366A (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMS: NO. 3150-0104 EXPIRES: 10/31/2018 (06·2016) ,..... ..... Estimated burden per response to comply with this mandatory collection request: 80 hours. ~ Reported lessons learned are incorporated into the licensing process and fed back to industry. LICENSEE EVENT REPORT (LER) ~~~ Send comments regarding burden estimate to the FOIA, Privacy and Information Collections \~/ CONTINUATION SHEET Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc gov, and to the Desk Offtcer, Office of Information and Regulatory Affairs, NEOB-10202, (3150.0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control htto:ltwww.nrc.gov/readinq-rm/doc-col!ectionstnuregslstaff/sr1022/f3(} number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER I I YEAR SEQUENTIAL REV Edwin I. Hatch Nuclear Plant Unit 1 05000-321 NUMBER NO 2017 -005 -00 | Event Description On April 20, 2017 at 0302 EDT with Unit 1 at approximately 1 percent rated thermal power due to a reactor startup from a planned maintenance outage, an automatic reactor scram was received due to the "A" and "B" Intermediate Range Monitors (IRMs) spiking upscale simultaneously. The instrument's set points for high-high neutron flux were reached, giving false trip signals to both channels of the reactor protection system (RPS) trip logic. Upon the automatic reactor scram signal, all control rods fully inserted appropriately. No primary containment isolation system (PCIS) actuations occurred and none were expected to occur based upon plant conditions following the reactor scram. Event Cause Analysis The cause of the event is due to the integrity of the IRMs signal cable connectors being in a degraded condition. Degradation was found on "A" IRM at the detector connector, while the "B" IRM had connection issues between the penetration and the jumper connector. These IRM cable integrity issues allowed a signal path to exist between the cables' shielding and center conductors. The noise signal was magnified when the signal was transmitted to the instrumentation's amplifier, causing both the "A" and "B" IRMs to spike upscale and trip. Safety Assessment This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in the automatic actuation of the reactor protection system (RPS). The IRMs monitor neutron flux from the upper portion of the source range monitor (SRM) range to the lower portion of the power range neutron monitoring (PRNM) range. The IRM system has eight IRM channels, each of which includes one detector that can be physically positioned in the core by remote control. The detectors are inserted into the core for a reactor startup and are withdrawn after the reactor mode selector switch is turned to RUN. The IRM system is capable of generating a trip signal that can be used to prevent fuel damage resulting from anticipated operational occurrences (AOOs) that occur while operating in the intermediate power range. The independence and redundancy incorporated in the design of the IRMS are consistent with the safety design basis of the RPS. The IRM system is divided into two groups of IRM channels arranged in the core. IRM channels "A", "C", "E", and "G" are associated with trip system A of the RPS and IRM channels "8", "D", "F", and "H" are associated with trip system B. While the reactor mode switch is in REFUEL or STARTUP, an IRM upscale or inoperative trip signal actuates a neutron monitoring system trip of the RPS. All control rods fully inserted and the plant responded as expected. Therefore, this event is considered to have very low safety significance. Corrective Actions As part of corrective actions, the "A" and "B" IRM jumper cables were replaced and all Unit 1 IRM cables | ML17167A032
Edwin I. Hatch Nuclear Plant | Unit 1 | Manual Scram Initiated Due to Inoperable Intermediate Range Monitors | 06-19-2017 | On April 20, 2017 at 2345 EST with Unit 1 in Mode 4 at 0 percent rated thermal power, the Unit 1 Reactor Mode Switch was taken from the REFUEL to the SHUTDOWN position per Technical Specification (TS} Limiting Condition for Operation (LCO} 3.1 0.4, Required Action A.2.2, due to having no operable intermediate range monitors (IRMs} in one quadrant of the reactor vessel because of maintenance activities. All control rods had been previously inserted, therefore no control rod motion occurred when the mode switch was positioned to SHUTDOWN. The cause of this event was due to flawed technical decision making surrounding maintenance activities related to inoperable I RMs. An inadequate review of TS LCO 3.1 0.4, in part due to the emergent nature of the maintenance activities to restore IRMs to operable status, resulted in Operations' incorrect determination that one of the requirements of TS LCO 3.1 0.4, "Single Control Rod Withdrawal-Cold Shutdown" was not met. The Unit 1 Reactor Mode Switch was therefore placed to the SHUTDOWN position per TS 3.1 0.4, Condition A.2.2. Corrective actions included ensuring TS Bases 3.1 0.4 language is not ambiguous, issuing an order that requires the shift manager to approve the removal of TS equipment from service for maintenance, and inclusion of this event in licensed operator continuing training. NRC FORM 366A (06-2016) NRC F , O . R M 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) ..... Estimated burden per response to comply with this mandatory collection request 80 hours. ~ Reported lessons learned are incorporated into the licensing process and fed back to industry. f~'i LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to the FOIA, Privacy and Information Collections \.~I CONTINUATION SHEET Branch (T·5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc gov, and to the Desk OlfiCer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-01 04), Office of Management and Budget, Washington, DC 20503.1f a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control http:ltwww.nrc.gov/reading-rm/doc-wllectionstnureas/stafflsr1022/r31) number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER I I YEAR SEQUENTIAL REV Edwin I. Hatch Nuclear Plant Unit 1 05000-321 NUMBER NO 2017 -006 -00 | Event Description On April 20, 2017 at 2345 EST with Unit 1 in Mode 4 at 0 percent rated thermal power, the Unit 1 Reactor Mode Switch was taken from the REFUEL to the SHUTDOWN position per Technical Specification (TS) Limiting Condition for Operation (LCO) 3.1 0.4, Required Action A.2.2, due to having no operable intermediate range monitors (IRMs) in one quadrant of the reactor vessel because of maintenance activities. All control rods had been previously inserted, therefore no control rod motion occurred when the mode switch was positioned to SHUTDOWN. Event Cause Analysis The cause of this event was due to flawed technical decision making surrounding maintenance activities related to inoperable IRMs. An inadequate review of TS LCO 3.1 0.4, in part due to the emergent nature of the maintenance activities to restore IRMs to operable status, resulted in Operations' incorrect determination that one of the requirements of TS LCO 3.1 0.4, "Single Control Rod Withdrawal - Cold Shutdown" was not met. The requirements of TS LCO 3.1 0.4 dictate that the MODE 5 requirements of TS LCO 3.3.1.1 for operable IRMs be met. In MODE 5, with a control rod withdrawn in a cell containing fuel, TS LCO 3.3.1.1 requires that there be an operable IRM in each quadrant. In this case, since all rods were already inserted, LCO 3.3.1.1 MODE 5 requirements for IRMs were not applicable, thus the LCO 3.1 0.4 requirements for IRMs were met. However, due to the incorrect determination that this requirement of TS LCO 3.1 0.4 was not met, the Unit 1 Reactor Mode Switch was placed to the SHUTDOWN position per TS 3.1 0.4, Condition A.2.2. Safety Assessment This event is reportable per 10 CFR 50. 73(a)(2)(iv)(A) as an event that resulted in the automatic actuation of the reactor protection system (RPS). The IRMs monitor neutron flux from the upper portion of the source range monitor (SRM) range to the lower portion of the power range neutron monitoring (PRNM) range. The IRM system consists of eight IRM channels and detectors that are inserted into the core for a reactor startup and are withdrawn after the reactor mode selector switch is positioned to RUN. The IRM system is divided into two groups of IRM channels arranged in the core. IRM channels "A", "C", "E", and "G" are associated with trip system A of the RPS and IRM channels "B", "D", "F", and "H" are associated with trip system B. There are two IRM channels in each quadrant of the core. The IRM system is capable of generating a trip signal that can be used to prevent fuel damage resulting from abnormal operating transients that occur while operating in the intermediate power range. There was no change in reactivity and no movement of the control rods occurred since all rods were inserted prior to this event. Therefore, this event is considered to have low safety significance. | ML17170A072
arkansas nuclear one | Unknown Unit | Automatic Start of an Emergency Diesel Generator Due to the Loss of Offsite Power due to Severe Weather | 06-26-2017 | On April 26, 2017, Arkansas Nuclear One, Unit 1 (ANO-1), was operating normally at 100% rated thermal power. The 500kV transmission line to the substation at Pleasant Hill, Arkansas was out of service for planned maintenance. The area around the plant was experiencing severe weather from thunderstorms and tornado warnings had been issued from the National Weather Service for the four county area. At approximately 1002 CST switchyard breakers for 500kV lines opened on fault current. High winds had damaged the transmission towers approximately 16 miles away from ANO and caused phase to ground faults. This resulted in a loss of all offsite power lines to the 500kV bus. The autotransformer also locked out as designed when the 500kV transmission lines faulted. The Reactor Operator initiated a manual reactor trip about 8 seconds after the 500kV lines tripped and prior to the reactor protection system initiating an automatic trip. During this time both emergency diesel generators (EDGs) [EK] started as expected. EDG #2 re-energized one Engineered Safeguards bus. EDG #1 ran unloaded until shutdown. The plant was stabilized in Mode 3 with Emergency Feedwater (EFW) pumps supplying the steam generators, maintaining the water level at the natural circulation setpoint. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear CONTINUATION SHEET Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Arkansas Nuclear One, Unit 1 05000-313 NUMBER NO. 2017 001 00 | A. PLANT STATUS Arkansas Nuclear One, Unit 1 (ANO-1) was operating at 100% rated thermal power. The 500kV transmission line to the substation at Pleasant Hill, Arkansas was out of service for planned maintenance. The area around the plant was experiencing severe weather from thunderstorms and tornado warnings had been issued from the National Weather Service for the four county area. There were no other structures, systems, or components (SSCs) that were inoperable at the time that contributed in the event. B. BACKGROUND Switchyard and High Voltage Electrical System Description The switchyard 500kV bus is a ring bus design, which allows transmission of 500kV power through three transmission lines to substations in Mabelvale, Ft. Smith, and Pleasant Hill, Arkansas. A fourth line supplies power to the bus tie autotransformer. The autotransformer interconnects the 500kV and 161kV busses. It has two tertiary windings to provide 22kV power from the 500kV or 161kV buses to offsite power transformer Startup #1 (SU1), which supplies power to ANO-1, and to offsite power transformer Startup #3 (SU3), which supplies power to ANO, Unit 2 (ANO-2). The 161kV bus is also a ring bus design, and includes two transmission lines to substations at Russellville East and Pleasant Hill, Arkansas, and a distribution line to the London, Arkansas, substation. It also supplies power to the SU2 which can supply power to both ANO-1 and ANO-2. During normal operation of ANO-1, station equipment is supplied from the main generator through the Unit Auxiliary Transformer (UAT). During startup and shutdown conditions, the switchyard is used as a means of supplying station equipment from the utility grid through one of the startup transformers. Following a turbine generator trip, station loads are designed to fast transfer to one of the startup transformers without the loss of power to plant loads. There are four 4160-volt buses. The main buses, A1 and A2 [EA], provide power to non-Engineering Safeguards (ES) motors and supply transformers that feed 480-volt non-ES load centers. The 4160-volt ESF buses, A3 and A4 [EB], are also powered through A1 and A2, and supply equipment essential for the safe shutdown of the plant. Two 6.9kV buses, H1 and H2 [EA], supply the reactor coolant pumps. On an ANO-1 trip, power is automatically fast transferred from the UAT to either SU1 or SU2, whichever is selected as the preferred power source. If the selected transformer is not available, the buses will transfer to the non-preferred startup transformer. If all normal and backup offsite power sources are lost, ES buses A3 and A4 are energized from their respective emergency diesel generator (EDG) [EK]. SU1, which only supplies ANO-1, can support buses A1, A2, H1, and H2 simultaneously. Since SU2 is shared by both units, it must be protected from overload. Procedures administratively limit automatic transfer of loads to SU2 only to ANO-1 buses A1 and A3, and ANO-2 buses 2A1 and 2A3. This is assured by normally maintaining the supply breakers from SU2 to ANO-1 buses A2, H1, and H2, and ANO-2 buses 2A2, 2H1, and 2H2 in pull-to-lock. In this condition, the associated supply breakers from SU2 to these buses will not close automatically after a loss of power from another power source. Another source of power to ESF bus A3 / A4 cross-tie is the alternate AC diesel generator (AACDG). The AACDG is an independent, non-safety related power source intended to be used in the event of a station blackout (SBO). The AACDG is started using a touch screen in the ANO-2 Control Room or the AACDG building. NRC FORM 366B (04-2017) Page 2 of 5 | ML17177A314
Oyster Creek | Unit 1 | Control Rod Drive Cooling Water System Isolation Scram Time Testing Was Not Performed | 06-23-2017 | On 03/16/2016, it was identified that isolating or reducing cooling water to the Hydraulic Control Units (HCUs) for three control rods should have been considered a modification since it had the potential to impact the scram times of the control rods. Even though scram time penalties were applied for the three control rods where the cooling water flow was either isolated or reduced, the control rods should have been scram time tested, as directed by the Generic Electric (GE) Service Information Letter (SIL) 173, Supplement 1, Revision 1. By not completing scram time testing for the control rods whose cooling water was isolated or reduced, the station was in violation of the requirements of Technical Specifications Section 3.2, since the issue was not identified previously and the affected control rods were not declared inoperable and isolated. This event resulted in an Operation or Condition that was Prohibited by the Plant's Technical Specifications (TS) and is therefore being reported under 1O CFR50.73(a)(2)(i)(B). NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 {04-2017)) Estimated burden per response to comply with this mandatory collection request 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send f <>""'""'",. comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear ·~~ LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, \ CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means "JI ......... used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/~r1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR Oyster Creek, Unit 1 05000219 NUMBER NO. 2016 - 002 - 01 | Description of Event On 03/16/2016, the NRC identified that scram time testing had not been performed following the isolation of cooling water flow to control rods 18-47 and 42-27, and the reduction in cooling water flow to control rod 30-03 as a result of a failed isolation valve to fully open. The valves were isolated as a compensatory action to mitigate leakage from the Control Rod Drive Mechanism (CROM) seals that was being quantified as unidentified leakage within the drywell. The isolated, or reduced, cooling water results in a hot CROM condition that is expected to impact scram times as documented in Generic Electric (GE) Service Information Letter (SIL) 173, Supplement 1, Revision 1, "Control Rod Drive High Operating Temperature." Technical Specification (TS) Section 4.2.C.2. states that: "For specifically affected individual control rods following maintenance on or modification to the control rod or control rod drive system which could affect the scram insertion time of those specific control rods in accordance with either "a" or ''b" as follows: a. 1 Specifically affected individual control rods shall be scram time tested with the reactor depressurized and the scram insertion time from the fully withdrawn position to 90% insertion shall not exceed 2.2 seconds, and a.2 Specifically affected individual control rods shall be scram time tested at greater than 800 psig reactor coolant pressure prior to exceeding 40% power. b. Specifically affected individual control rods shall be scram time tested at greater than 800 psig reactor coolant pressure." The isolation of cooling water flow to a control rod, while it does not affect the operability or functionality, does reduce the flow to the CROM and can impact the scram time. Accordingly, scram time testing should have been performed per the TS due to a system modification that could impact the scram time. Since the testing was not performed, TS. 4.0.1 was also applicable as a surveillance requirement that was not met. In accordance with this TS section, if the surveillance requirements are not satisfied, this would require entry into the appropriate LCO as described under TS Section 3.2.B.4, which would have required the control rods be declared·inoperable, fully inserted, and isolated. Additionally, TS Sections 3.2.A.2 and 3.2.A.3 are also applicable and would require a determination that adequate shutdown margin would be maintained within six hours of declaring the rods inoperable. Since this was not accomplished, this resulted in an Operation or Condition that was prohibited by the plant's TS. Equipment Description The control rod and drive mechanism provides control of reactor power, including the ability to provide a sufficiently rapid insertion of control rods (scram) so that no fuel damage results from any abnormal operating transient and limits fuel damage under accident conditions. The 137 control rods for the Oyster Creek reactor are located uniformly throughout the core. The control rods are operated by CRDMs. The hydraulic control units (HCUs) for the control rods supply and control the pressure and flow requirements to the Control Rod Drives (CRDs). The HCUs provide hvdraulic power to be able to position control rods | ML17187A134
Hope Creek Generating Station 05000354 1 OF3 | Unknown Unit | s~l;L ~::~rv CcmtainmAnt Door Not Latched in Closed Position | 05-08-2017 | On May 10, 2017, a Hope Creek secondary containment door was observed to be unlatched in the closed position. The door was being held closed by the negative pressure within the reactor building (secondary containment). The door was determined to have been opened for equipment passage on, May 8, 2017, at 1323. It was concluded that the door was most likely unlatched for passage at that time and notre-latched following the passage. A review of Hope Creek design basis accident (DBA) conditions determined that the secondary containment pressure would become slightly positive for a short period of time, under certain DBA events. Based on the area of the door, and the expected pressure rise within secondary containment, the door could not be assured to remain closed. Hope Creek Technical Specifications require that secondary containment integrity be maintained while in Operational Condition 1. Secondary Containment Integrity is defined as having all doors in the closed position except for normal passage. Since the closed door position could not be assured under all postulated accident conditions, the event is being reported under 10 CFR 50.73 (a)(2)(i)(B) as a condition prohibited by Technical Specifications, and under 10 CFR 50.73 (a)(2)(v)(C) as a condition that could have prevented the ~ulfillment of a safety function needed to control the release of radioactive material. NRC FORM 366A (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06·-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. LICENSEE EVENT REPORT (LER) Reported lessons teamed are Incorporated Into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail CONTINUATION SHEET to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a (See NUREG-1 022, R.3 for instruction and guidance for completing this form means used to impose an Information collection does not display a currently valid OMB control http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1 022/r3/) number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Hope Creek Generating Station 05000-354 YEAR I SE N Q U U M E B N E T R IA L I R N E O V . 2017 -001 -00 | PLANT AND SYSTEM IDENTIFICATION General Electric- Boiling Water Reactor (BWR/4) Reactor Building - EllS Identifier {NG} IDENTIFICATION OF OCCURRENCE Event Date: May 8, 2017 Discovery Date: May 10, 2017 CONDITIONS PRIOR TO OCCURRENCE Hope Creek was in Operational Condition 1 at 1 00 percent rated thermal power (RTP). DESCRIPTION OF OCCURRENCE During a walk down of the Reactor Building at Hope Creek on May 10, 2017, at approximately 10:00, door 4302 was found to be closed but the hand wheel not rotated to engage the latches. The door was being held in the closed position by the negative pressure in the Reactor Building. This condition was reported immediately to the control room, and the door handle was repositioned to engage the latches. The door position is indicated in the control room, and the door was verified to indicate closed at the time it was found to be not latched. -----1-Goor-4302-is-a-seeonelary-eontainment-bounelary-eleer-;-and-is--a-sin~le-eleer--arr-an~ement-:-Her:>e-Greek-"FeeMnieai---­ Specifications require that for single door arrangements, the door remain closed except for routine entry and exit. Technical Specifications require that the Secondary Containment Integrity be re-established within 4 hours, or the reactor be in Hot Shutdown within the following 12 hours. A review of the door alarm history for·door 4302 indicates that the door was last opened on May 8, 2017 at 1323. The door opening indication lasted approximately one minute, which corresponds to a routine entry or exit, as permitted by the Technical Specifications. There was no indication of the door being left open for an extended period of time and there were no door openings indicated after this transit until the time that the door was re-latched in the closed position on May 10, 2017. During the transit on May 8, 2017, the Reactor Building differential pressure lowered to approximately 0.16 inches of vacuum water gauge and quickly recovered to its normal control point of approximately 0.48 inches of vacuum water gauge, also indicating that the door remained closed following the transit. Based on the review of door alarm history, the door was not latched for a period exceeding the Technical Specification allowable time period of 4 hours, and therefore this represents a condition prohibited by Technical Specifications. CAUSE OF EVENT The cause is a failure to properly use human performance tools such as self-check or a peer check to ensure the proper configuration of the door is maintained. Proper use of human performance tools when closing the door and engaging the latches would have identified that the latches on the door were not made up. SAFETY CONSEQUENCES AND IMPLICATIONS There were no adverse safety consequences as a result of this event. The Secondary Containment is designed to minimize any ground level release of radioactive material which may result from an accident. In the as found condition, the secondary containment door was in the closed position, supporting the function of the secondary containment. However, in reviewing the postulated design basis accidents, the door could not be assured to remain closed under all accident conditions during the time when it was unlatched. Based on this, the secondary containment is considered to | ML17188A314
Quad Cities Nuclear Power Station | Unit 2 | High Pressure Coolant Injection Minimum Flow Valve Failed to Open | 07-13-2017 | On May 15, 2017, at 19:18 hours, station Operations personnel were performing a High Pressure Coolant Injection (HPCI) Pump Operability Test which ensures the HPCI Minimum Flow Valve opens as pump flow decreases. When the HPCI Turbine was tripped, the Minimum Flow Valve did not open as expected when system flow was reduced to the low flow setpoint. Operators took steps to open the valve manually, but upon release of the control switch, the valve returned to the closed position. The valve was then left in the closed position. The HPCI system was declared inoperable and Technical Specification 3.5.1 Condition G was entered. The cause of the Minimum Flow Valve failing to open was attributed to the HPCI Pump Discharge Flow Indicating Switch, specifically, intermittent failure of the high side micro switch caused by residual material from the manufacturing process. The Flow Indicating Switch, which had been installed for three months, was replaced and the HPCI Pump Operability Test was successfully re-performed. The failed switch was then sent to Exelon's Power Labs for failure analysis. The safety significance of this event was minimal. Given the impact on the HPCI system, this report is submitted for Unit 2 in accordance with the requirements of 10 CFR 50. 73(a)(2)(v)(D), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. The HPCI system is a single train system and the loss of HPCI could impact the plant's ability to mitigate the consequences of an accident. NRG FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nureqs/staff/sr1022/r31) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV Quad Cities Nuclear Power Station Unit 2 05000265 YEAR NUMBER NO. 2017 - 001 - 00 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX]. EVENT IDENTIFICATION The High Pressure Coolant Injection (HPCI) [BJ] Minimum Flow Valve failed to open during HPCI Pump operability testing. A. CONDITION PRIOR TO EVENT Unit: 2 Event Date: May 15, 2017 Event Time: 19:18 hours Reactor Mode: 1 Mode Name: Power Operation Power Level: 100% B. DESCRIPTION OF EVENT On May 15, 2017 at 19:18 Central, station Operations personnel were performing Procedure QCOS 2300-05, "HPCI Pump Operability Test," which ensures the Motor Operated (MO) 2-2301-14, "HPCI Minimum Flow Valve," opens as pump flow decreases. During the test, the valve unexpectedly failed to open. Operators took steps to open the valve manually, but upon release of the control switch, the valve immediately returned to the closed position. Operators left the valve in the closed position. The Unit 2 HPCI system remained available but was declared inoperable. Troubleshooting determined that the failure was due to a failure of the commercially dedicated HPCI Flow Indicating Switch (FIS) 2-2354. FIS 2-2354 had been recently replaced on February 2, 2017, under a corrective work order utilizing a commercially dedicated switch. The FIS was bench tested and post maintenance tested satisfactorily on February 2, 2017. The switch was again calibrated under a preventative maintenance work order during the next quarterly system work window on May 15, 2017, in accordance with a 92-day preventative maintenance frequency. All results were satisfactory. The switch then failed during the subsequent quarterly system run on the same day. In the follow-up failure analysis Power Labs reported that the switch had an intermittent failure of the high side micro switch due to residual material remaining from the manufacturing process. On May 15, 2017, at 23:27 Central, ENS #52758 was made to the NRC under 1O CFR 50.72(b)(3)(v)(D), to report this event as an event or condition that could have prevented the fulfillment of a safety function. Given the impact on the HPCI system, this report is submitted for Unit 2 in accordance with the requirements of 1O CFR 50.73(a)(2)(v)(D), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. NRG FORM 366A (06-2016) Page _2_ of _4_ | ML17194A817
LaSalle County Station | Unit 1 | Low Pressure Core Spray Inoperable due to Minimum Flow Valve Failure in Closed Position | 07-14-2017 | On May 17, 2017 at 0908 CDT, during Unit 1 full-power operations, operators received an unexpected alarm for the Low Pressure Core Spray (LPCS) pump injection high flow and automatic closure of the LPCS minimum flow valve (1 E21 ·F011 ). Inspections indicated the flow switch that actively controls the LPCS minimum flow valve had a faulty diaphragm which allowed for water intrusion into the device. There were no impacts on plant operations. The required actions of Technical Specifications 3.5.1, "ECCS - Operating" and TS 3.3.5.1, "Emergency Core Cooling System (ECCS) Instrumentation" were entered. The switch was replaced and LPCS system tested, which allowed full restoration of the system on May 17, 2017 at 18:45 CDT. This condition could have prevented the LPCS system from performing its design function. This condition is reportable in accordance with 10 CFR 50. 73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. There was minimal safety consequences associated with the condition since other emergency safety systems remained operable. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150·0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to ndustry. Send comments regarding burden estimate to the lnlormalion Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail lo lnfocollecls.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an inlormation collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is nal required to respond lo, the inlormation http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR LaSalle County Station, Unit 1 05000373 NUMBER NO. 2017 - 006 00 | PLANT AND SYSTEM IDENTIFICATION LaSalle County Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The Low Pressure Core Spray (LPCS) system is part of the Division 1 Emergency Core Cooling System (ECCS). LPCS provides low-pressure coolant into the reactor core under accident conditions. The LPCS minimum flow switch 1 E21·N004 monitors pump discharge flow. This flow switch initiates opening of LPCS minimum flow valve 1 E21-F011, if flow drops below the set point (1325 gpm) and initiates closing of 1 E21-F011, if flow rises above its reset point (1774 gpm). CONDITION PRIOR TO EVENT Unit(s): 1 Event Date: May 17, 2017 Event Time: 0908 CDT Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 100 percent DESCRIPTION OF EVENT At 0908 CDT on May 17, 2017, the Unit 1 Main Control Room received an unexpected alarm on panel 1H13-P601-C508 for the LPCS pump injection high flow and automatic closure of the LPCS minimum flow valve 1 E21-F011. The automatic closure of the LPCS minimum flow valve occurred as appropriate for this alarm condition_ An operator was dispatched, who verified that there were no abnormal conditions in the LPCS pump room and that there were no abnormal indications at the 1 E21-N004 flow switch, which is the device that initiates this alarm and subsequent actions. LPCS was declared inoperable and the appropriate Technical Specification (TS) required actions were entered in accordance with TS 3.5.1, "ECCS - Operating" and TS 3.3.5.1, "Emergency Core Cooling System (ECCS) Instrumentation." There were no related work activities in progress at the time the condition was identified. The applicable TS required action (RA) entries were TS 3.5.1 RA A.1, restore LPCS to operable in 7 days; TS 3.3.5.1 RA A.1 to enter condition referenced in Table 3.3.5.1-1 for the LPCS pump discharge flow-low (bypass) channel; TS 3.3.5.1 RA D.1 to declare supported features inoperable when its redundant feature ECCS initiation capability is inoperable; and, TS 3.3.5.1 RA D.4 to restore the channel to operable in 7 days. Instrument maintenance technicians inspected the LPCS minimum flow switch and found water intrusion in the switch electrical housing. This switch was removed and sent offsite for failure analysis. The failed switch was replaced and calibrated. Unit 1 LPCS was declared operable on May 17, 2017 at 18:45 CDT. CAUSE OF EVENT Water intrusion into the switch electrical housing for the LPCS minimum flow switch 1 E21-N004 resulted in a ground fault causing the actuation of relay 1 E21-K006 and subsequent LPCS minimum flow valve closure. The flow switch was replaced with a like for like replacement, and the switch was sent to Power Labs for failure analysis. The cause was determined to be process water leakage past an internal "U-cup" seal around the shaft from the sensing element into the electrical switch housing. This failure has previously occurred with a similar model of flow switch used in another system's application. The causal investigation concluded the design of this component was not optimal for its function. This was the first failure of this type noted with model 141 N6-WX7-M9 that is utilized for residual heat removal (RHR) and LPCS minimum flow applications. A previous design change to improve the reliability of static 0-ring (SOR) differential pressure switches and associated failure analysis did not evaluate all SOR switches using the deficient U-cup design. | ML17195A356
Sequoyah Nuclear Plant | Unit 1 | Automatic Actuation of Emergency Diesel Generators Due to Loss of Power to 6.9kV Shutdown Board | 07-14-2017 | On May 23, 2017, at 2330 eastern daylight time (EDT), while transferring the 2A-A 6.9 kilovolt (kV) Shutdown Board (SDBD) from its alternate power source to its normal power source, in support of outage testing for Unit 2, a loss of power to the 2A-A 6.9kV SDBD resulted in the automatic actuation of all four emergency diesel generators. The power was restored to the SDBD on May 24, at 0027 EDT. At the time of the event, Unit 1 was in Mode 1 at 100 percent power and Unit 2 was in Mode 5 for a refueling outage. There were no actual safety consequences as a result of this event. The cause of the event was indeterminate. The direct cause of the event was an upstream unit board overcurrent relay actuation associated with the A phase. The corrective action was to obtain acceptable test results from all equipment in the zone of protection. This included all the cables, current transformers, relays and breakers that were in contact with the associated relay. There was no evidence of equipment degradation. Transient monitoring will be performed for 6.9kV SDBD normal and alternate feeder breakers. Data will be captured for each initial transfer. Any identified anomalies will be addressed via the corrective action program. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Sequoyah Nuclear Plant Unit 1 05000-327 NUMBER NO. 2017 - 002 - 00 | I. Plant Operating Conditions Before the Event At the time of the event, Sequoyah Nuclear Plant (SQN) Unit 1 was in Mode 1 at 100 percent rated thermal power. Unit 2 was in Mode 5 for a refueling outage. II. Description of Event A. Event Summary: On May 23, 2017, at 2330 eastern daylight time (EDT), while transferring the 2A-A 6.9 kilovolt (kV) Shutdown Board (SDBD) [EIIS: EA, ECBD] from its alternate power source to its normal power source, in support of outage testing for Unit 2, a loss of power to the 2A-A 6.9kV SDBD resulted in the automatic actuation of all four emergency diesel generators (EDGs) [EIIS: EK, DG]. During transfer of the 2A-A 6.9kV SDBD, the hand switch [EIIS: HS] for the normal feeder breaker [EIIS: BKR] on the SDBD was maintained in the “CLOSE” position while the alternate feeder breaker hand switch was placed in “TRIP.” As expected, the alternate feeder breaker opened and the normal feeder breaker closed. However, the upstream supply breaker to the normal feeder breaker immediately tripped due to an overcurrent relay [EIIS: RLY] actuation on the A phase. As a result, the 2A-A 6.9kV SDBD de-energized, initiating a blackout signal that started all four EDGs. During load shedding of the SDBD to prepare for the automatic re-energization from the EDG, the normal feeder breaker to the 2A A 6.9kV SDBD remained closed, as designed. With the normal feeder breaker hand switch in the “CLOSE” position, the associated relay coil [EIIS: CL] remained sealed in. Because the normal feeder breaker remained closed, the 2A-A EDG emergency feeder breaker could not close as it must be the only source supplying the SDBD when running in the emergency mode. As a result, the 2A A 6.9kV SDBD remained de-energized following the event. This prevented the cooling water supply valve for the 2A-A EDG from opening due to the loss of motive power. Per procedure, the lack of cooling water caused operators to emergency stop the 2A-A EDG. Main control room (MCR) operators entered the appropriate response procedures and re- established power to required loads. Power was restored to the SDBD on May 24, at 0027 EDT. An 8-hour non-emergency event notification (EN 52769) was made to the NRC in accordance with 10 CFR 50.72(b)(3)(iv)(A) as any event or condition that resulted in manual or automatic actuation of emergency ac electrical power systems, including EDGs. This LER documents the reportable event under 10 CFR 50.73(a)(2)(iv)(A). | ML17195A419
River Bend Station | Unit 1 | : | 07-13-2017 | On May 15, 2017, an engineering investigation determined that a modification installed in 2014 on two of the four safety-related main control building chillers had a design error. The nature of that error was such that the performance of a regularly scheduled preventative maintenance (PM) task to draw an oil sample from'the chiller gearbox inadvertently caused the chiller to be incapable of responding to an automatic start signal. A review of the. history of the PM found that, on three occasions since the modification was installed, the task was performed on the operable chiller that was in the standby condition. The inadvertent inoperability of the standby division of the main control building chillers causes the loss of safety function of the supported electrical distribution systems in the building. The control building chilled water system provides cooling to the equipment rooms housing the battery chargers and inverters for the safety-related onsite electrical distribution systems. The loss of cooling to the various equipmeht rooms in the control building requires that the supported equipment in those areas be declared inoperable. The Technical Sp~cifications for the I Division 3 DC distribution system requires that the high pressure core spray (HPCS) system be immediately declare.d inoperable. This condition potentially causes the HPCS system to be incapable of performing its safety function, and is, thus, reportable in accordance with 10 CFR 50.73(a)(2)(v)(D). The error in the subject modification is considered a legacy issue since its design was completed and approved in July 2012. The PM task will be revised to preclude its performance on chillers in the standby configuration. At no time during the three performances of the PM on the operable standby chiller was there an actual demand for its automatic start. This condition was, thus, of minimal significance with respect to the health and safety of the public. I NRC FORM 366 {04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APP,ROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported ' LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process .and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If. a means (See NU REG· 1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. ILER NUMBER YEAR : SEQUENTIAL REV River Bend Station - Unit 1 05000-458 NUMBER NO. 2017 006 00 | REPORTED CONDITION On May 15, 2017, an engineering investigation determined that a modification installed in 2014 on two of the four safety-related main control building chillers (**CHU**) had a design error. The nature of that error was such that the performance of a regularly scheduled preventative maintenance (PM) task to draw an oil sample from the chiller gearbox inadvertently caused the chiller to be incapable of responding to an automatic start signal. A review of the history of the PM found that, on three occasions since the modification was installed, the task was performed on the operable chiller that was in the standby condition. The inadvertent inoperability of the standby division of the main control building chillers causes the loss of safety function of the supported electrical distribution systems in the building. The control building chilled water system [VI] provides cooling to the equipment rooms housing the battery chargers and inverters for the safety-related onsite electrical distribution systems. The loss of cooling to the various equipment rooms in the control building requires that the supported equipment in those areas be declared inoperable. The Technical Specifications for the Division 3 DC distribution system requires that the high pressure core spray (HPCS) system be immediately declared inop~able. This condition potentially causes the HPCS system to be incapable of performing its safety function, and is, thus, reportable in accordance with 10 CFR 50.73(a)(2)(v)(D). INVESTIGATION The subject modification was installed on the Division 1 "C" chiller in August 2014, and on the Division 2 "D" chiller in April 2014. (Each division has a redundant chiller that has yet to be modified.) The purpose of the modification was to upgrade the chiller controls to a digital system. An error occurred in the development of the modification design that involved the controls for the motor-driven chiller oil pump. The switch for the oil pump is on the main control room panel, and is normally in the "AUTOMATIC" position. The work instructions in the PM require that the control switch be placed in the "RUN" position to start the pump. The effect of the design error is that the automatic start feature of the chiller is disabled when the switch is in the "RUN" position. The review of the PM history found that the "C" chiller was sampled on February 2nd and August 3rd in 2015. The "D" chiller was sampled on March 21, 2017. In each case, the subject chiller was operable and configured for an automatic start should the operating chiller in the opposite division unexpec,tedly trip. The execution of the PM step to place the oil pump control switch in "RUN" rendered the chiller inoperable. IMMEDIATE CORRECTIVE ACTIONS When this condition was discovered, the oil pump control switches on the "C" and "D" chillers were "CAUTION" tagged to prohibit taking the switch to the "RUN" positio~ if the chiller is in the standby configuration. CORRECTIVE ACTIONS TO PREVENT RECURRENCE The error in the subject modification is considered a legacy issue since its design was completed and approved in July 2012. Since that time, a comprehensive root cause analysis on the issue of quality in engineering products was conducted in 2015, which resulted in numerous programmatic changes. Therefore, no new causal analysis was | ML17200C938
Fermi 2 | Unknown Unit | Division 2 Residual Heat Removal Service Water System (RHRSW) Inoperable Due to an Inoperable RHRSW Flow | 07-21-2017 | On May 22, 2017 at 05:10 am (EST), while placing Division 2 Residual Heat Removal Service Water (RHRSW) in service for biocide treatment of the Division 2 Residual Heat Removal (RHR) Reservoir, the Division 2 RHRSW Flow Control Valve (FCV) (E 1150F068B) failed to fully open. Troubleshooting discovered the direct cause was failure of the anti-rotation bushing stem key. The apparent cause was system operating conditions (high vibration) resulting in the failed tack welds. Previous troubleshooting on an indication issue on May 5, 2017 for the RHRSW FCV was i a n n a d d e s q u u b a se te q , u a e n n d tl y d i f d a i n le o d t i o d n e n th ti e f y n e th x e t f o a n i - lu d r e e m o an f t d h e s tr a o n k ti e - r a o t t a 5 t : i 1 o 0 n a k m ey o . n A M s a a y r e 2 s 2 u , l t, 2 0 th 1 e 7 . R H Se R v S e W nte e F n C V sim w il a a s r r M etu o r t n o e r d O t p o e s r e a r te v d ic e V a a l t v 2 e : s 5 0 (M p O m V o s n ) M we a r y e 7 in , s 2 p 0 e 1 c 7 te , d and no MOVs exhibiting the symptoms observed on the El 150F068B prior to the failure of the anti-rotation key were found, and all anti-rotation devices were found to be intact. The Past Operability determination for El 150F068B found that the MOV was unable to perform its design basis functions from May 3, 2017 at 5:48 am, when the RHRSW FCV was last successfully stroked under dynamic conditions, through May 24, 2017 at 4:04 pm, when the RHRSW FCV was returned to service. The Division 1 RHRSW was available throughout the event except on two occasions. Division 1 o 20 f 1 R 7 H a R t S 1 W 1:1 w 8 a p s m d . e c D la i r v e i d si o in n o p 1 e o r f a b R le H R fo S r W M e w c a h s a n ag ic a a i l n D d r e a c f l t a r C ed o o i l n in o g p e T ra o b w le e r f o ( r M M D D CT C ) T N N o o z z z z le le C C le le a a n n in in g g a a c c ti t v iv it i i t e ie s s o o n n M M a a y y 9 1 , 1 2 , 0 2 1 0 7 1 7 fr o a m t 8 8 :3 :4 5 1 a m am t h to ro M ug a h y 9, May 11, 2017 at 10:01 pm. The as found condition of the Division 2 RHRSW FCV is a condition prohibited by Technical Specification 3.7.1 and reportable under 10 CFR 50.73 (a)(2)(i)(B) "Operation or Condition Prohibited by Technical Specifications," and 10 CFR 50.73(a)(2)(v)(B) "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: Remove Residual Heat." NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/3112018 (06-2016) Estimated burdepner response toc omply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (L ER) l r e e s g s a o rd n i s n g l e b a u rn rd ea e dr en e s i t n im co a r t p e o r t a o t e th d e i n FO to I t A h , e l P ic ri e v n a s c i y n g a p n ro dI c n e f s o s r m a a n tio d n fe C db o a ll c e k c t t io o n i s n d B u r s a t n ry c . h S (T en -5 d F c 5 o 3 m ), m e U n . t S s . CONTINUATION SHEET Nuclear Regulatory CommissioWnas, hington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, andto t heD esk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management andB udget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used toi mpose ani nformatcioollenc tion does not displaayc u rrently valid OMB control number, the http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022r3/) NRC mayn otc onduct or sponsor, anda persoins notr equiretod r espond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Fermi 2 YEAR SEQUENTIAL REV 05000-341 NUMBER NO. 2017 -003 -00 | INITIAL PLANT CONDITIONS Mode-1 Reactor Power - 100 Reactor Pressure Vessel Temperature - 518 degrees Fahrenheit There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT On May 22, 2017, at 5:10 am, while placing Division 2 Residual Heat Removal Service Water (RHRSW) [BI] in service to support biocide treatment of the Division 2 Residual Heat Removal (RHR) [BO] Reservoir, the Division 2 RHR Heat Exchanger Service Water Flow Control Valve [(FCV)] (El 150F068B) did not completely open as expected when the push button was pressed. The Division 2 RHRSW Flow Control Valve (FCV) (El 150F068B) failed to fully open. The RHRSW FCV indicated dual position after 5 seconds of operation in the open direction. When the RHRSW pump was started, indicated flow would not go above 2800 Gallons Per Minute (gpm). After the initial flow spike RHRSW flow settled out at 2,800 gpm and would not continue to rise as expected while holding the open pushbutton for El 150F068B valve. The Division 2 RHRSW Pump B was placed in off and valve position remained in dual indication. The Operator pushed the close pushbutton and no change in valve position was observed. The operator then depressed the Thermal Overload reset and verified continuity for all fuses in 72F-4A Position 3A, MCC for El 150F068B. The FCV was verified closed locally by stem position and manually checking close with hand-wheel. Troubleshooting discovered the direct cause was failure of the anti-rotation bushing stem key tack welds. The welds were repaired and the key was replaced. Post Maintenance Testing (PMT) was satisfactorily completed. The RHRSW FCV was returned to service at 4:04 pm on May 24, 2017. Prior to the May 22, 2017, RHRSW FCV failure, troubleshooting did not identify cause of the failure. On May 5, 2017, during shutdown of the Division 2 RHRSW, with flow lowered to 8500 gpm, the E1150F068B improperly indicated full closed. The RHRSW pumps were shutdown and El 150F068B was then stroked and timed with local position verification. When the open pushbutton was pressed, the open light did not come on until after approximately 55 seconds and the valve indicated full open after 125 seconds. On the close stroke, the open light went out after approximately 56 seconds (indicated full closed in the Main Control Room) and the valve was seen to be full closed locally at 124 seconds. The stroke times were longer than expected but still within acceptance criteria. Troubleshooting activities were performed. The troubleshooting focused on the indication aspects of the Motor Page 2 of 6 | ML17202G758
Clinton Power Station | Unit 1 | Secondary Containment Inoperable During Mode Change Due to Doors Propped Open | 08-01-2017 | On June 2, 2017, plant personnel were performing welding activities on the 'B' Reactor Water Cleanup System (RT) pump while the plant was in operating Mode 4. The Operations Work Control Supervisor (WCS) had given maintenance personnel authorization to prop both 'B' RT pump room doors open so that welding cables could extend through both doors in support of maintenance activities. The doors are part of the plant secondary containment boundary. Authorization granted by the WCS was executed without utilizing the plant barrier impairment process (PSI) per plant procedures. Prior to the plant's transition to operating Mode 2, Operations personnel made a plant announcement requiring the establishment of primary and secondary containment. The plant then transitioned to operating Mode 2 at 0241. However, both RT Pump 'B' doors remained propped open during the plant mode change. This condition was discovered by shift personnel at 0300 (CDT) and secondary containment was declared inoperable. The loss of secondary containment was caused by personnel not following the PB! per plant procedure. Secondary containment was subsequently restored twenty four minutes after discovery of the open 'B' RT doors. Corrective actions taken and planned include implementing management action response checklist (MARC) principles for the responsible supervisor and completing a read and sign for planners and schedulers associated with the PBI process. NRC FORM 366 (04-2017) •.., NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET MEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Clinton Power Station, Unit 1 05000461 NUMBER NO. 2017 - 006 00 | PLANT AND SYSTEM IDENTIFICATION General Electric-Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX] EVENT IDENTIFICATION Secondary Containment Inoperable During Mode Change A. Plant Operating Conditions before the Event Unit: 1 Event Date: June 2, 2017 Event Time: 0241 Mode: 2 Mode Name: Power Operation Reactor Power: 000 percent B. DESCRIPTION OF EVENT On June 2, 2017, while the plant was in Mode 4, maintenance personnel were performing welding activities associated with the 'B' Reactor Water Cleanup System (RT) [CE] pump. In support of these activities, an Operations Work Control Supervisor (WCS) provided authorization to prop open both RT 'B' pump room doors (a Secondary Containment (SC) boundary) to allow welding cables to extend through the doors. The authorization was granted, however, without utilizing the plant barrier impairment process (PBI) per plant procedures. This process provides guidance on actions necessary to evaluate and compensate for an impaired barrier. As the plant prepared for startup and the transition to operating Mode 2 commenced, Operations personnel made a plant announcement requiring that primary and secondary containment be established. The announcement was not heard by personnel working on the 'B' RT pump. The plant entered Mode 2 at 0241. The doors were found propped open at 0300 shortly after the plant entered Mode 2 by Operations shift personnel. Technical Specification (TS) 3.6.4.1, Secondary Containment, actions were then entered to restore SC. Both 'B' RT doors were later closed and SC was restored twenty four minutes following discovery of the open RT doors. NRG FORM 366A (04-2017) Page _2_ of _3_ .• | ML17215A233
Brunswick Steam Electric Plant (BSEP) | Unit 1 | Control Room Air Conditioning and Emergency Ventilation Systems Rendered Inoperable | 08-02-2017 | On June 5, 2017, at 0930 Eastern Daylight Time (EDT), Unit 1 was in Mode 1 at 100 percent power, and Unit 2 was in Mode 1 at 87 percent power and was increasing power after a preplanned control rod improvement evolution. Maintenance personnel were inspecting dampers in the Control Room Air Conditioning (AC) system and Control Room Emergency Ventilation (CREV) system and disconnected an air supply to a damper. This resulted in the CREV system being inoperable due to interruption of the pneumatic supply. The CREV system was restored to operable status by 1009 EDT. At 1352 EDT, a second damper was inspected, and its pneumatic supply was disconnected. During the second occurrence, the Control Room AC system also tripped and was made inoperable. Affected systems were restored by 1407 EDT. The event is reportable as a loss of safety function per 10 CFR 50.73(a)(2)(v)(D). The event resulted from inadequate use of human performance tools and inadequate work instructions. Corrective actions for this event include restoring the affected pneumatic supply, revising work orders, and taking steps to emphasize proper use of human performance tools. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) E le s s t s im on a s te d le b a u rn rd e e d n a p r e e r r in e c s o p r o p n o s r e a t t e o d c o in m to p ly t h w e i th li c th e i n s s m ing a nd p a ro to c r e y s s c ol a le n c d t io f n e d r eq b u a e c s k t : t 8 o 0 i h n o d u u r s s tr . y R . e p S or e te n d d LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear CONTINUATION SHEET Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant (BSEP) YEAR 05000325 NUMBER NO. Unit 1 2017 - 003 - 000 | Energy Industry Identification System (EllS) codes are identified in the text as [XX]. Background Initial Conditions On June 5, 2017, at 0930 Eastern Daylight Time (EDT), Unit 1 was in Mode 1 at 100 percent power, and Unit 2 was in Mode 1 at 87 percent power and was increasing reactor power after a preplanned control rod improvement evolution. No inoperable equipment contributed to this event other than as specified in the event description below. Reportability Criteria In this event, the Control Room Air Conditioning (AC) system [NA] and the Control Room Emergency Ventilation (CREV) system [VI] were temporarily rendered incapable of performing their safety functions due to interruption of pneumatic pressure. Therefore, it is reportable per 10 CFR 50.73(a)(2)(v)(D) as a loss of safety function. The event was also reportable per 10 CFR 50.72(b)(3)(v)(D) for loss of safety function. This reporting requirement was fulfilled per Event Number 52788 on June 5, 2017, at 1940 EDT. Event Description On June 5, 2017, at 0930 EDT, Maintenance personnel were performing an inspection of damper seals in the Control Room AC and CREV systems. In the as-found condition, certain dampers were closed, which restricted the inspection to one side only. Thus, a complete inspection could not be performed. Craftsmen concluded that the particular damper being inspected needed to be stroked open so the inaccessible side could be viewed. They asked Operations personnel to open the damper. However, it was stated that due to the electrical logic configuration of these dampers, this single damper could not be actuated from the Control Room. Operations permission was given to the mechanics in the field to stroke the damper open locally. When initial efforts to open the damper manually were unsuccessful, craftsmen contacted the system engineer for guidance on opening the damper. The system engineer suggested the mechanics disconnect the normal instrument airline for the damper and reconnect a separate air source that would redirect air flow to allow the damper to cycle open. Therefore, the craftsmen removed the pneumatic supply from the damper port and connected a portable air tank to a port that channeled airflow to open the damper. The damper seals and the damper blade were then inspected and found to be satisfactory. The normal pneumatic supply was reconnected and restored to the original configuration by 1009 EDT. On the same day at 1352 EDT, the steps described above were repeated for a second damper. In this instance, the configuration of the system resulted in air porting from the pneumatic system, depressurizing it. Within about three minutes, pneumatic pressure decreased to the point where the two operating Control Room AC systems tripped, and the third was unable to start because of low pneumatic supply pressure. In | ML17215A760
Brunswick Steam Electric Plant (BSEP) | Unit 2 | Setpoint Drift in Main Steam Line Safety/Relief Valves Results in Three Valves Inoperable | 08-03-2017 | On June 5, 2017, BSEP received the results of testing of eleven main steam line safety relief valves (SRVs) removed from Unit 2 during the spring refueling outage. Three of the eleven valves were found to have as-found lift setpoints of their pilot valves outside the +/-3 percent tolerance required by Technical Specification (TS) 3.4.3. One SRV was 9.1 percent high. One SRV was 8.6 percent high, and one SRV was 5.0 percent high. Evaluation determined that the elevated lift pressures in two valves resulted from corrosion bonding of the SRV pilot valves which raised the breakaway force needed to open the pilot. The third valve experienced steam erosion. This event had no adverse impact on nuclear safety. Although the SRV setpoint limits required by the TS were exceeded, the plant condition was bounded by the Brunswick Unit 2 Cycle 22 Reload Safety Analysis, demonstrating that the SRVs could have performed their safety function of limiting reactor vessel overpressure. TS 3.4.3 requires ten of the eleven installed SRVs to be operable. Since less than ten SRVs were operable, this event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) for operation prohibited by the plant’s TS. The SRV pilot valves were replaced with certified spares before the startup of Unit 2. A procedure was revised to reduce corrosion bonding by improving surface preparation of SRV pilot valve discs. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) E le s s t s im on a s te d le b a u rn rd e e d n a p r e e r r in e c s o p r o p n o s r e a t t e o d c o in m to p ly t h w e i th li c th e i n s s m ing a nd p a ro to c r e y s s c ol a le n c d t io f n e d r eq b u a e c s k t : t 8 o 0 i h n o d u u r s s tr . y R . e p S or e te n d d LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear CONTINUATION SHEET Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant (BSEP) YEAR 05000324 NUMBER NO. Unit 2 2017 - 003 - 000 | Energy Industry Identification System (EllS) codes are identified in the text as [XX]. Introduction Initial Conditions At the time the condition was identified, Unit 2 was in Mode 1 at 87 percent of rated power and was increasing in power after a preplanned control rod improvement evolution. Reportability Criteria Unit 2 Technical Specification (TS) 3.4.3 requires at least 10 of 11 main steam [SB] line safety/relief valves (SRVs) to be operable. Per Surveillance Requirement (SR) 3.4.3.1, each valve is required to open within +/-3 percent of its opening setpoint. As-found testing of the valves indicated that three of the valves had lift setpoints outside this tolerance. Based on the causes of the inoperability described below, it was concluded that three SRVs were inoperable when the unit was in operation. Consequently, the plant operated in a condition which is prohibited by the TS, that is, with fewer than the required number of SRVs having lift setpoints within the +/-3 percent tolerance. Therefore, the condition is being reported per 10 CFR 50.73(a)(2)(i)(B) for operation in a condition prohibited by the plant TSs. Event Description During the spring 2017 Unit 2 refueling outage, all 11 Model 7657F Target Rock Two-Stage pilot valve assemblies in the SRVs were replaced with certified spares. The removed SRV pilot valves were sent to National Technical Systems (NTS) to determine the as-found set pressure. On June 5, 2017, test results were reported to BSEP. The test results showed that three of the 11 valves actuated at pressures outside of the +/-3 percent tolerance allowed by TS 3.4.3. The test data for the valves found out of tolerance are shown below: Valve TS Setpoint As-Found Lift Percent Identification (psig) Pressure (psig) Difference S/N 1098 1140 1244 +9.1 S/N 1109 1130 1227 +8.6 S/N 1106 1150 1208 +5.0 Event Cause The change in SRV lift setpoints resulted from corrosion bonding between the discs and seats of the pilot valves. Corrosion bonding between the pilot disc and seat is an inherent problem with the two-stage SRV | ML17215A990
Susquehanna Steam Electric Station | Unit 1 | Secondary Containment Declared Inoperable Due to Failure of an Exhaust Fan Breaker. | 03-31-2020 | On June 9, 2017 at approximately 0509 hours, Secondary Containment Zone 3 differential pressure was lost during a routine restoration due to the failure of the Unit 1 Zone 3 'A' Reactor Building Exhaust Fan. Technical Specification Surveillance Requirement (SR) 3.6.4.1.1 was not met. Zone 3 differential pressure was recovered to> 0.25" WG (Water Gage) by placing Unit 1 Zone 3 Filtered Exhaust to STOP and allowing Unit 2 Zone 3 to recover differential pressure. Zones 1 and 2 were not affected. This event is being reported under 10 CFR 50. 73(a)(2)(v)(C) as a condition that could have prevented the fulfillment of a safety function. The cause was determined to be a broken ring terminal on the breaker which prevented the fan from starting. Maintenance replaced the ring terminal and re-terminated the wire. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/3112020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43}, U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104}, Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1 022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http:/fw.Nw.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1 022/r30 NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station Unit 1 05000387 NUMBER NO. 2017 -004 - 00 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 3, approximately 0 percent Rated Thermal Power Unit 2 - Mode 1, approximately 100 percent Rated Thermal Power Unit 1 was in the process of starting up following a Scram on 6/8/17, however, this did not contribute to the event. There were no structures, systems, or components that were inoperable on Unit 2 that contributed to this event. EVENT DESCRIPTION On June 8, 2017 at approximately 2206, at the start of restoration of the Reactor Building HVAC [EllS Code: NG] Unit 1 Zone 3 ventilation post Unit 1 SCRAM, Operations placed the 'A' Reactor Building Zone 3 Filtered Exhaust Fan [EllS Code: FAN] in service. The 'A' Reactor Building Zone 3 Supply Fan [EllS Code: FAN] started but the 'A' Reactor Building Zone 3 Exhaust Fan [EllS Code: FAN] did not. With the Filtered Exhaust Fan in service, the supply air was greater than the exhaust air which resulted in a loss of differential pressure. 6/9/17 0441: Operations entered Technical Specification (TS) 3.6.4.1 due to Secondary Containment being inoperable during the start of the Zone 3 fan. 6/9/17 0449: Operations cleared TS 3.6.4.1. 6/9/17 0509: Secondary Containment Zone 3 differential pressure lowered to 0" WG as a result of the Reactor Building HVAC fans tripping and restarting several times. The required differential pressure per Surveillance Requirement 3.6.4.1.1 could not be maintained. Operations placed Unit 1 Zone 3 Filtered Exhaust in the STOP position. 6/9/17 0941: Operations entered LCO 3.6.4.1 due to Secondary Containment being inoperable while restoring Unit 1 Zone 3 HVAC. 6/9/17 1010: While restoring Unit 1 Zone 3 HVAC, a bell alarm for the Reactor Building Zone 3 Exhaust Fan supply breaker could not be reset. 6/9/17 1015: Operations placed the Unit 1 Zone 3 system in service using the 'B' Unit 1 Zone 3 fans. The 'A' Reactor Building Supply Fan and 'A' Reactor Building Filtered Exhaust Fans were placed in STANDBY. The 'A' Reactor Building Exhaust Fan was left in STOP. 6/9/17 11:11 The Maintenance investigation revealed that the terminal connection was broken in the supply breaker [EllS Code: BKR] for the 'A' Reactor Building Zone 3 Exhaust Fan. Maintenance replaced the ring terminal and re-terminated the wire. The exhaust fan was successfully placed in service. Zone 3 differential pressure was recovered to> 0.25"WG following the restart of Unit 2 Zone 3 Secondary Containment fans. Zones 1 and 2 were not affected. This event is being reported under 10 CFR 50.7 3(a)(2)(v)(C) as a condition that oculd have prevented the fulfillment of a safety function. NRC FORM 3668 (04-2017) Page 2 of 3 | ML17216A286
Pilgrim Nuclear Power Station 05000-293 1 OF 3 | Unknown Unit | Reactor Building Isolation Dampers Failed to Isolate | 07-17-2017 | On January 16, 2017, with the reactor at 100 percent power and the mode switch in RUN, Pilgrim Nuclear Power Station (PNPS) was performing surveillance testing of secondary containment isolation dampers when dampers IAO-N-82 and AO-N-83, refueling floor supply isolation dampers, failed to fully close when the control switches !Were taken to close. IThe failure of dampers AO-N-82 and AO-N-83 to fully close resulted in a loss of safety function for secondary containment, causing immediate entry into Limiting Condition for Operation (LCO) Action Statement (AS) 3.7.C.2.a, at 1155 hours. This LCO AS was exited at 1206 hours when the dampers were verified closed. !An 8-hour non-emergency notification was made in accordance with 10 CFR 50.72(b)(3)(v), any event or condition that at the time discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: (C) Control the release of radioactive material; or (D) Mitigate the consequences of an accident. In addition, this notification is being conservatively made by PNPS in accordance with 1O CFR 50. 73(a)(2)(i)(B), as a condition that was prohibited by Technical Specifications. The reactor building isolation dampers were cleaned, lubricated and post-work tested. PNPS has returned the dampers to operable status. Planned action to prevent recurrence is to revise the preventive maintenance strategy. There was no impact to public health and safetv from this condition. NRC FORM 366 (06-2016) NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) .. t>•it.e., Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported ':\. lessons learned are incorporated into the licensing process and fed back to industry. Send (}' \¥) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 ..... F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (LER) CONTINUATION SHEET used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR NUMBER NO. Pilgrim Nuclear Power Station 05000-293 2017 001 01 | BACKGROUND he Reactor Building Isolation and Control System (RBIS) safety objective is to limit the release to the nvironment of radioactive material so that offsite doses from a postulated design basis accident will be below he guideline values stated in 10 CFR 100_ The RBIS shall trip the Reactor Building supply and exhaust fans, isolate the normal ventilation system, and provide the initiation signals for the Standby Gas Treatment System in the event of a postulated Loss Of Coolant Accident (LOCA) in the drywell or a postulated fuel handling ccident in the Reactor Building. he Reactor Building Heating, Ventilation and Air Conditioning (HVAC) System includes the RBIS subsystem, hich supports the secondary containment function by automatically closing HVAC-related openings in econdary containment in the event of high drywell pressure, low reactor pressure vessel water level, or high irborne radiation levels in the refuel floor area, and Equipment Area Cooling System components, which upply supplemental cooling to the Core Standby Cooling Systems spaces within the reactor building and reject heat to the Reactor Building Closed Cooling Water System. Pilgrim Nuclear Power Station (PNPS) was performing surveillance testing for the secondary containment isolation supply dampers. During the performance of this test the refuel floor supply isolation dampers showed ual indication when the control switches were taken to close. This is indicative of a failure of dampers to close. EVENT DESCRIPTION On January 16, 2017, with the reactor at 100 percent power and the mode switch in RUN, PNPS was performing surveillance testing of secondary containment isolation dampers when dampers AO-N-82 and O-N-83, refueling floor supply isolation dampers, failed to fully close on demand as revealed by dual indication in the Control Room. n 8-hour non-emergency notification was made in accordance with 10 CFR 50.72(b)(3)(v), Any event or ondition that at the time discovery could have prevented the fulfillment of the safety function of structures or ystems that are needed to: (C) Control the release of radioactive material; or (D) Mitigate the consequences f an accident. he dampers were manually closed. The reactor building isolation dampers were then cleaned and lubricated. he dampers were then cycled five times with satisfactory closure time results. PNPS has returned the ampers to operable status. he root cause of this event is that the preventative maintenance strategy was inadequate for secondary ontainment isolation supply dampers AO-N-82 and AO-N-83 and was not sufficiently structured to prevent repetitive failures of high critical components. This caused the condition, since preventative maintenance ctions (which are intended to prevent repetitive failures of high critical components) were not adequate to ro erl maintain these com onents, resultin in a loss of safet function for seconda containment. NRc FORM 366 (06-2016) Page 2 of 3 NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported ~ #' " ~ ~ . ... , - , .~. ~ .' ".<.. c le o s m so m n e s n ts le a re rn g e a d rd in a g re b u in rd c e o n rp e o s ra ti t m ed a te i n to to th t e h e FO lic IA en , s P in r g iv a p cy ro c a e n s d s In a fo n r d m a f t e io d n b C a o ck lle c t t o io n i s n du B s r t a ry n . c h S ( e T n - d 5 ~ \ .....7 .1· F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to LICENSEE EVENT REPORT lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (LER) CONTINUATION SHEET used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR NUMBER NO. Pilgrim Nuclear Power Station 05000-293 2017 001 01 NARRATIVE CORRECTIVE ACTIONS The immediate corrective action was for the reactor building isolation dampers to be cleaned and lubricated and post-work tested and the dampers were then cycled five times with satisfactory closure time results. PNPS used compensatory measures to restore the dampers to operable status. The Corrective Action to Prevent Recurrence addresses revising the preventative maintenance strategy for secondary containment supply and exhaust isolation dampers as follows: Refurbish damper actuators in accordance with vendor recommendations; Perform annual inspection and maintenance of secondary containment dampers; and bench test and record torque values to verify the adequacy of the actuators prior to installation and after they have been removed and replaced. SAFETY CONSEQUENCES There were no consequences to the safety of the general public, nuclear safety, industrial safety, and radiological safety due to this event. The actual consequences were a loss of safety function for secondary containment and entry into Limiting Condition for Operation Action Statement 3.7.C.2.a. Per the guidance in NUREG-1022, Section 5.2.2 the event date is the date of discovery, January 16, 2017, since there is no firm evidence, based on a review of relevant information that the issue existed previously. The Limiting Condition for Operation Action Statement was entered at 1155 hours on January 16, 2017 and exited at 1206 hours on the same day. As such, the loss of safety function for secondary containment existed for a total duration of 11 minutes. There was no adverse impact on the public health or safety. REPORTA BILITY This event is reportable under 10 CFR 50. 73(a)(2)(v)(C) and 10 CFR .50. 73(a)(2)(v)(D), event or condition that could have prevented fulfillment of a safety function of structures or systems that are needed to: (C) Control the release of radioactive material; or (D) Mitigate the consequences of an accident. Subsequent to submission of the initial LER, based on NRC questions, it was concluded that this notification should also be conservatively made in accordance with 10 CFR 50.73(a)(2)(i)(B), as a condition that was prohibited by Technical Specifications. PREVIOUS EVENTS A review of PNPS Licensee Event Reports for the past five years did not identify any loss of safety function due to isolation dampers failing to isolate. REFERENCE CR-PNP-2017-00494 Page 3 of 3 NRC FORM 366 (06-2016) | ML17220A065
LaSalle County Station | Unit 1 | Low Pressure Core Spray System Inoperable due to Loss of Cooling | 08-18-2017 | On June 22, 2017, the Unit 1 Low Pressure Core Spray (LPCS) system was declared inoperable due to loss of corner room area cooling and loss of motor cooling. The common diesel generator cooling water pump received an automatic trip signal while being secured. The LPCS pump remained in standby during the event. Troubleshooting identified the most likely cause for the trip of the emergency cooling water pump breaker was a malfunction of the cooling water pump control switch or the cooling water supply fan control relay. Both suspected components were replaced. The causal investigation did not identify a specific cause; however, there is a high level of confidence that the failure modes were eliminated by the corrective actions taken during troubleshooting. This component inoperability is reportable in accordance with 10 CFR 50. 73{a){2)(v)(D) as an event or condition that could have prevented fulfillment of the safety function of structures or system that are needed to mitigate the consequences of an accident. This condition could have prevented the LPCS system, a single train safety system, from performing its design function. There was minimal safety consequences associated with the condition since other required emergency safety systems remained operable, there were no actual demands for Unit 1 LPCS, and safety margins were maintained. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: BO hours. Reported lessons learned are incOfporated into the licensing process and led back to industry. Send comments regarding burden estimate to the Information Services Branch (T·2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LEA) Regulatory Commission, Washington, DC 20555-0001, or by e·maif to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB·10202, (3150-0104), Office of Management and Budge!, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR LaSalle County Station, Unit 1 05000373 NUMBER NO. 2017 - 007 00 | PLANT AND SYSTEM IDENTIFICATION LaSalle County Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the Division 1 Low Pressure Core Spray (LPCS) system, one of the stand-by emergency core cooling systems (ECCS) credited for emergency injection into the reactor pressure vessel (RPV). The LPCS system is designed to provide sufficient cooling to the reactor core to prevent excessive fuel cladding temperatures following any break in the nuclear system piping. The affected support system was the diesel generator (DG) cooling water system, which provides cooling to the LPCS room equipment and the LPCS pump motor, from the Division 1 DG cooling water pump ODG01 P. CONDITION PRIOR TO EVENT Unit(s): 1 Date: June 22, 2017 Time: 2043 CDT Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 100 percent DESCRIPTION On June 22, 2017, the Unit 1 Low Pressure Core Spray (LPCS) system was declared inoperable due to loss of a supporting system for corner room area cooling and loss of motor cooling. The common (Division 1) diesel generator (DG) cooling water pump received an automatic trip signal while being secured. The LPCS pump remained in standby during the event. This condition could have prevented LPCS, a single train safety system, from performing its design function. The NRC was notified of the event on June 23, 2017, via emergency notification system (ENS) report 52821. Prior to the condition the station was preparing to shut down Unit 1 for a planned maintenance outage. The Division 1 residual heat removal (RHR) pump had been shut down, and its corner room fan had been verified to be secured. As neither Unit 1 nor Unit 2 required the use of the common DG cooling pump, the ODG01 P control switch was taken to the STOP position at the 1 PM01 J panel. When the switch was taken to the STOP position, the automatic trip light lit and 1 PM01 J-A215 0 DG trouble alarm annunciated. Operations re-verified that the associated pumps and fans were not required to be running and took the ODG01 P control switch to the NORMAL AFTER STOP position and the ODG01 P pump restarted. This operation was performed to ensure operability of the pump and minimize risk. Troubleshooting identified that the most likely reason for the malfunction of the ODG01 P pump breaker was a contact fault of either the OHS-DG001 A control switch or the 1 VY01 C control relay. Troubleshooting was performed, and both the control relay and the hand switch were replaced. Correct operation of the control circuit and breaker was verified, and the equipment was returned to operable status. CAUSE The most likely causes of the event were intermittent binding of the contact carriers internal to the switch or an intermittent failure of the control relay that contains the contact that provides the automatic start of the ODG01 P pump. The analysis of various potential failures of other components in the control logic did not identify any other component failures with the potential to cause the same type of behavior. Based on the review of the troubleshooting and failure analysis, both suspected failure modes were addressed by component replacements. | ML17230A288
Cooper Nuclear Station 05000298 1 of 3 | Unknown Unit | Traversing In-core Probe In-shield Limit Switch Mounting Failure Results in Common Cause lnoperability of Independent Trains or Channels and Condition Prohibited by Technical Specifications | 08-17-2017 | On June 21, 2017, Traversing In-core Probe {TIP) C failed to stop at its in-shield position when being withdrawn from the core. Cooper Nuclear Station (CNS) Operations personnel declared the associated TIP C ball valve inoperable as a Primary Containment Isolation Valve (PCIV) at 0524 and entered Technical Specification {TS) Limiting Condition for Operation (LCO) 3.6.1.3, Condition A. On June 22, 2017, TIP D failed to stop at its in-shield position when being withdrawn from the core. CNS Operations personnel declared the associated TIP D ball valve inoperable as a PCIV at 0445 and entered TS LCO 3.6.1.3, Condition A. Subsequent investigation determined the cause of the failures was inadequate mounting and securing of the in- shield limit switch to the chamber shield. Corrective actions included repair of the mounting of the in-shield limit switches for all TIP channels, and improved procedure guidance for properly mounting the in-shield limit switches. Both valves were declared operable on July 13, 2017, at 1133. There were no safety consequences associated with this condition. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a (See NUREG-1022, R 3 for instruction and guidance for completing this form means used to impose an information collection does not display a currently valid OMB control http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Cooper Nuclear Station 05000- 298 NUMBER NO. 2017 -005 -00 | PLANT STATUS Cooper Nuclear Station (CNS) was in Mode 1, Power Operations, 100 percent power, at the time of discovery; i.e., June 22, 2017. BACKGROUND The Traversing In-Core Probe (TIP) subsystem is a part of the Neutron Monitoring System [EllS:IG]. The TIP subsystem allows calibration of Local Power Range Monitor (LPRM) [EllS:MON] signals by correlating TIP signals to LPRM signals as the TIP is positioned in various locations in the core. A TIP drive mechanism [EllS:DRIV] uses an ionization chamber attached to a flexible drive cable, which is driven from outside Primary Containment [EllS:NH] and is contained by guide tubes that continue into the reactor core. A valve system is provided with a valve on each TIP guide tube entering the primary containment. A ball valve [EllS:V] and a cable shearing valve [EllS:V] are mounted in the TIP guide tubing just outside of the primary containment. The ball valve opens when the TIP is being inserted and closes automatically upon receipt of the proper signal and after the TIP cable and ionization chamber have been retracted. An in shield limit switch [EllS:33] actuates to stop withdrawal of the TIP detector and also provides a permissive for closing the ball valve. The shear valve is used in the event the ball valve should fail to close or the chamber drive cable should fail to retract during the time that primary containment isolation is required. CNS Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.6.1.3 requires each Primary Containment Isolation Valve (PCIV) to be operable. The TIP ball valves are PCIVs. EVENT DESCRIPTION On June 21, 2017, TIP C failed to stop at the designated in-shield position when being withdrawn from the core. The TIP machine was manually stopped approximately seven inches beyond the in-shield position, and was then manually moved to the correct position by Operations. The TIP C ball valve was declared inoperable as a PCIV due to the failure of the in-shield limit switch. TS LCO 3.6.1.3, Primary Containment Isolation Valves, Condition A, was entered at 0524 and the Required Actions taken. On June 22, 2017, TIP D failed to stop at the designated in-shield position when being withdrawn from the core. The TIP machine was manually stopped at approximately six inches past the in-shield position, and was then manually returned to in-shield location by Operations. The TIP D ball valve was declared inoperable as a PCIV due to failure of the in-shield limit switch. TS LCO 3.6.1.3, Primary Containment Isolation Valves, Condition A, was entered at 0445 and the Required Actions taken. In each case, the condition would have prevented the ball valve from automatically closing on initiation of a Group 2 containment isolation signal. Page 2 of3 | ML17236A166
Columbia Generating Station 05000 397 I OF 3 | Unknown Unit | Momentary loss of Secondary Containment due to Weather | 08-24-2017 | On June 6, 2017 at 1756 PDT hours Secondary Containment pressure exceeded the Technical Specification (TS) limit during a period of inclement weather. At 1756 PDT Secondary Containment was declared inoperable and operations personnel entered TS Action Statement 3.6.4.1.A and subsequently exited at 1800 PDT. Secondary Containment pressure was restored automatically by system response and operator action was not required. The direct cause of the momentary loss of Secondary Containment was due to slow system response to maintain a vacuum in Secondary Containment during a period of inclement weather. The interim planned co1Tective action is to verify proper operation and tuning of the Secondary Containment instrumentation. Additionally Columbia Generating Station is pursuing the change to TS requirements by adopting TSTF-55 l, Revise Secondary Containment Surveillance Requirements. This condition is being reported under 10 CFR 50.73(a)(2)(v)(C) and IO CFR 50.73(a)(2)(v)(D) for an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material and to mitigate the consequences of an accident. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 CONTINUATION SHEET F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocoUects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means {See NUREG·1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/l NRC may not conduct or sponsor, and a person is nol required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER DYE AR SEQUENTIAL REV 05000-1 I NUMBER NO. Columbia Generating Station 397 1-0 ~-I 003 | PLANT CONDITIONS At the time of the event, Columbia Generating Station (Columbia) was in Mode 1 operating at 98% reactor power. There were no structures, systems, or components that were inoperable that contributed to the event. EVENT DESCRIPTION On June 26, 2017 at 1756 PDT Secondary Containment (Reactor Building) [NG] pressure was not maintained at a vacuum greater than 0.25 inches water gauge (inwg) during a .period of inclement weather. The Secondary Containment alarm was received and Secondary Containment pressure peaked at 0.08 inwg. Secondary Containment vacuum was restored to greater than 0.25 inwg by system response and operator action was not required. EXTENT OF CONDITION The extent of condition for Secondary Containment vacuum momentarily dropping below the required value is specific to the Reactor Building Heating Ventilation and Air Cooling (HVAC) (VA] and Standby Gas Treatment (SGT) (BH] systems, and their capability to establish and maintain Secondary Containment vacuum. No other systems were affected as a result of this condition. IMMEDDIAT E CORRECTIVE ACTION The Reactor Building Exhaust Air (REA) flow in-service differential pressure controller (DPIC) automatically restored Secondary Containment vacuum to greater than 0.25 inwg. CAUSE The sudden change in wind speed and direction has been shown to cause pressure transients on the exterior walls of the Secondary Containment. When wind direction changes and wind speed increases, the auctioneering function designed into the Secondary Containment differential pressure controller will select the lowest differential pressure input. The direct cause was Secondary Containment HVAC not responding quickly enough to maintain a vacuum of greater than 0.25 inwg during a period of inclement weather. PLANNED CORRECTIVE ACTION The interim planned corrective action is to verify proper operation and tuning of Secondary Containment differential pressure controller. Additionally, Energy Northwest plans to submit a license amendment request to adopt TSTF-551, Revise Secondary Containment Surveillance Requirements, to address TS 3.6.4.1 Surveillance Requirement (SR) 3.6.4.1.1. ASSESSMENT OF SAFETY CONSEQUENCES This event resulted in an unplanned entry into Technical Specification (TS) Action Statement 3.6.4.1 Condition A, in which Secondary Containment vacuum was less than 0.25 inwg for approximately four minutes. The peak Secondary Containment pressure during this event was 0.08 inwg. While the actual vacuum was beyond the range allowed by TS the | ML17236A455
Columbia Generating Station 05000 397 1 OF 3 | Unknown Unit | Failure of Fan to Start Results in Momentary Increase in Secondary Containment Pressure | 08-29-2017 | On November 20, 2016 at 1402 PST, Secondary Containment [NH] (Reactor Building) became inoperable due to pressure increasing above the Technical Specification limit of -0.25 inches of water gauge (inwg). While the plant was ascending in power, the Reactor Building exhaust air fan unexpectedly failed to start in manual during post-maintenance testing. Prior to this event, Reactor Building Heating, Ventilation and Air Conditioning [VA] (HVAC) System A was running. Per station procedures, System A was stopped and System B was to start. The fan’s failure to start resulted in no Reactor Building fans running, and increased Reactor Building pressure. For a time period of less than one minute, Secondary Containment pressure was not maintained less than or equal to -0.25 inwg. Immediate recovery actions by Operations personnel included manually starting Reactor Building HVAC System A, which quickly restored Secondary Containment pressure to less than or equal to -0.25 inwg at 1403 PST. While TS limits were exceeded for this short time period, the resulting pressure excursion was bounded by analytical results; and thus, there were no safety consequences for this condition. This event was reported under reporting criteria 10 CFR 50.72(b)(3)(v)(C) and 10 CFR 50.72(b)(3)(v)(D) as Event Notification #52382. The cause of the exhaust fan's failure to start was degraded lubrication on the closing mechanism of the fan's circuit breaker [BKR]. Corrective actions for this event include replacement of the circuit breaker and updates to preventative maintenance dates of the station's 480 volt circuit breakers. There were no other event-related equipment malfunctions. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000- NUMBER NO. Columbia Generating Station 397 2016 - 003 - 01 | Plant Conditions At the time of the event, the plant was operating in Mode 1 at approximately 97% power, and ascending to 100% power. There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. Event Description On November 20, 2016 at 1402 PST, the Reactor Building [NG] exhaust air fan [FAN] (REA-FN-1B) failed to start in manual during a post-maintenance task on the fan. Prior to this event, Reactor Building Heating, Ventilation and Air Conditioning [VA] (HVAC) System A was running. Per station procedures, System A was stopped and System B was to start. The fan’s failure to start resulted in no Reactor Building fans running, and increased Reactor Building pressure. For a time period of less than one minute, Secondary Containment [NH] pressure was not maintained less than or equal to -0.25 inches of water gauge (inwg), resulting in Technical Specification (TS) 3.6.4.1 not being met. This event is reportable as an event that could have prevented fulfillment of safety functions needed to control the release of radiation, and mitigate the consequences of an accident per 10 CFR 50.73(a)(2)(v)(C) and 10 CFR 50.73(a)(2)(v)(D). This condition was reported under 10 CFR 50.72(b)(3)(v)(C) and 10 CFR 50.72(b)(3)(v)(D) via Event Notification #52382 for an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material. Immediate Corrective Actions Operations personnel manually started Reactor Building HVAC System A and quickly restored Secondary Containment pressure to less than or equal to -0.25 inwg. Secondary Containment was declared operable following successful start of the System A Reactor Building exhaust air fan. Assessment of Safety Consequences This event resulted in an unplanned entry into TS 3.6.4.1.A, in which Secondary Containment pressure was greater than -0.25 inwg for approximately one minute. The peak pressure during this event was -0.12 inwg. While the actual pressure was beyond the range allowed by Technical Specifications, the purpose of maintaining a slight vacuum is to assist in drawdown of secondary containment to support accident response of the safety related Standby Gas Treatment [BH] (SGT) system. Existing engineering analysis demonstrates that for this event, the drawdown credited in accident response could have been attained using either of the two available trains of the SGT system, thus there were no potential safety consequences. There was no actual safety consequence associated with this event since there was no loss of safety function and no potential for radiological release. Cause of Event The apparent cause of the unexpected failure to start of the Reactor Building exhaust air fan, and resultant loss of Secondary Containment was degraded lubrication on the closing mechanism of the fan's circuit breaker which prevented the fan from starting. The lubrication was degraded due to an error in calculating the preventative maintenance date. | ML17241A220
Oyster Creek Nuclear Generating Station 05000219 1 OF 3 | Unknown Unit | Automatic Scram while Subcriticai due to low Reactor level | 08-31-2017 | On July 3, 2017 at approximately 10:30 hours with the reactor subcritical after a manual scram, an automatic reactor scram occurred due to low Reactor Pressure Vessel (RPV) water level. Prior to this event, Main Control Room (MGR) Operators established reactor water letdown, reset the manual scram and were placing RPV water level control in automatic using a Low Flow Feedwater Regulator Valve (LFRV). Reactor pressure control was automatically being maintained with turbine bypass valves. A low reactor water level occurred when a bypass valve opened as expected to lower reactor pressure. Operations personnel had reset the scram signal without fully evaluating other plant conditions. Upon resetting the scram with reactor water level not yet stabilized, an automatic scram was received on low reactor water level. The automatic scram initiation signal occurred with the plant in a shutdown mod~. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06·2016)) Estimated burden per response to comply with this mandatory collection request 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently vaiid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr10221r3D collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Oyster Creek Nuclear Generating Station 05000219 YEAR NUMBER NO. 2017 - 003 - 00 | Plant Conditions Prior To Event Event Date: July 3, 2017 Event Time: 10:30 hours ET Unit 1 Mode: Hot Shutdown Power Level: 0% Description of Event On July 3, 2017 at approximately 10:30 hours a subcritical automatic reactor scram was received while stabilizing plant parameters after a manual scram. The automatic scram was due to low RPV water level. Prior to this, MCR operators established reactor water letdown, reset the manual scram and were placing RPV water level control in automatic using a LFRV. Reactor pressure control was automatically being maintained with turbine bypass valves. A low reactor water level occurred when a bypass valve opened as expected to lower reactor pressure. Operators reset the scram signal without fully evaluating other plant conditions. By resetting the scram signal with water level not yet stabilized, an automatic scram was received on low reactor water level. Operator fundamentals and human performance tools were not properly utilized prior to resetting the scram. Operations personnel did not ensure plant parameters of pressure and level were stable prior to resetting the scram. An expected pressure transient resulted in an automatic scram due to RPV level dropping below the scram setpoint. Cause of Event MCR Operators did not confer with the Unit Supervisor their intended actions nor did they provide an update to other control room personnel prior to resetting the scram. Operations personnel did not perform a thorough review of all system conditions prior to peer checking the scram reset. Additionally, the procedure did not provide details of conditions to verify prior to resetting the scram. Analysis of the Event The personnel involved did not display distinct thought to understand the impact that the action would have with reactor water level control in its current state. The operators should have taken the time to understand that resetting the scram at that time was not the correct action. The operators were not fully engaged and did not think about the consequences of resetting the scram prior to reactor water level stabilization. Their behavior represents a gap as described in SOER 10-2, Engaged, Thinking Organizations. Assessment of Safety Consequences Following the automatic scram actuation all systems responded as expected; therefore, this event is of low safety significance. | ML17249A123
Oyster Creek Nuclear Generating Station 05000219 1 OF 3 | Unknown Unit | Manual Reactor Scram due to Degrading Main Condenser Vacuum | 08-31-2017 | On July 3, 2017, at approximately 10:15 AM following a grid disturbance, a manual scram was inserted due to degrading main condenser vacuum because of an improper configuration of the Augmented Off-gas (AOG) System. The loss of main condenser vacuum resulted when Operations personnel failed to execute procedural requirement to align the AOG system into a shutdown lineup. The loss of vacuum was caused by degraded Steam Jet Air Ejectors (SJAE) performance due to a blocked discharge path. The AOG system tripped 11 hours earlier following a grid disturbance. During the trip, operations personnel failed to re-align the AOG treatment system to a shutdown lineup resulting in the AOG Flame Arrestor siphoning into the inlet piping which filled the lower section of the off-gas hold up line with water. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016)) Estimated burden per response to comply with this mandatory collection request 80 hours. Reported . . lessons learned are incorporated into the licensing process and fed back to industry. Send ~'>#f'. AECt.~.,>0,,, comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 ~. . i LICENSEE EVENT REPORT {LER) F53}, U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, 'lo CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means ~'9 ....... . used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond lo, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV Oyster Creek Nuclear Generating Station 05000219 YEAR NUMBER NO. 2017 - 002 - 00 | Plant Conditions Prior To Event Event Date: July 3, 2017 . Event Time: 10:15 hours ET Unit 1 Mode: Power Operation Power Level: 100% Description of Event On july 3, 2017 at 1015 hours a manual reactor scram was initiated due to degrading condenser vacuum. The loss of vacuum was initiated by the operations department failure to execute the procedural requirement to align the AOG system into a shutdown lineup. The SJAE discharge line was blocked by water from the AOG system. The AOG system tripped eleven hours earlier following a grid disturbance. During the trip, operations personnel failed to re-align the AOG system to a shutdown lineup resulting in the AOG Flame Arrestor siphoning into the lower section of the off-gas delay pipe. Cause of Event Operations failed to enter stop work criteria, made a non-conservative decision and did not execute a procedure in response to a trip of AOG. After the AOG system trip from the electrical transient, operations personnel misdiagnosed the AOG system lineup. The AOG system had partially isolated as designed with the recombiner blower still in service. To place the AOG system in a shutdown lineup, the system isolation valve had to be closed to separate the AOG building from the off-gas delay pipe. This isolation valve was left open and flame arrestor water siphoned back into the off-gas delay pipe causing a stall of the SJAEs and a subsequent loss of main condenser vacuum. · Analysis of Event Following the manual scram actuation, all systems responded as expected; therefore, this event is of low safety significance. An analysis did not determine an area where early detection via plant observable parameters would have stopped the event. An analysis of water usage and design is below. A known operating characteristic on the system results in the flame arrestor getting pressurized on the process side up to 5 psig, (stem pressurization air sub-system). This pressure will cause the flame arrestor to siphon back into the AOG inlet line. A siphon will continue to backfill the suction lines due to the automatic makeup from the demineralized water system. Failure to isolate the inlet line to the flame arrestor with the system not in service allows water back flow to the off-gas process piping and fill the delay pipe. The delay pipe is the discharge piping from the SJAE process gas flow. Water filling the line resulted in the stall of the SJAE's that started at 0919 hours on July 3, 2017. To block SJAE flow this line would have to fill up the lowest elevation of piping. This is approximately 8100 gallons of water. The earliest detection of changes in the plant would occur just as the pipe is filled with water blocking the flow and is consistent with operations observations at approximately 0825 hours on July 3, 2017. | ML17249A124
Salem Generating Station-Unit 2 05000 311 1 OF 4 | Unit 2 | Automatic Reactor Trip due to Main Turbine Trip | 03-31-2020 | On 2/4/16 at 11 :21, Salem Unit 2 automatically tripped from approximately 74% power. Power had been reduced at the beginning of dayshift to support a 500 KV transmission line outage. The reactor trip was due to a Main Turbine trip caused by a Main Generator Protection signal initiated by a main generator automatic voltage regulator (A YR) volts/hertz over excitation protection relay. All emergency core cooling systems and emergency safeguards feature systems functioned as expected. As found calibration data for the generator protection logic relay were found out of specification low. An evaluation determined the cause of the event to be that the organization failed to develop and implement corrective actions to resolve the previously identified cause of poor manufacturing/vendor quality identified in the causal evaluation following a similar Unit 1 trip on 12/21/2012 trip due to STV-1 relay setpoint drift. This report is being made in accordance with 10 CFR 50.73 (a)(2)(iv)(A), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)," specifically automatic actuation of the Reactor Protection System and the Auxiliary Feedwater System for this event. NRG FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are Incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear CONTINUATION SHEET Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to Impose an information collection does not display a currently valid OMB control number, the http://www.nrc.gov/readlng-rm/doc-collectlons/nuregs/staff/sr1022/r3/) NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Salem Generating Station - Unit 2 05000-1 311 I ~ NUMBER 0N O. 2~161 I I · - 002 | PLANT AND SYSTEM IDENTIFICATION Westinghouse-Pressurized Water Reactor {PWR/4} Main Generator System/Relay {TB/RL Y} *Energy Industry Identification System (EllS) codes and component function identifier codes appear as {SS/CCC}. IDENTIFICATION OF OCCURRENCE Event Date: 02/04/2016 Discovery Date: 02/04/2016 CONDITIONS PRIOR TO OCCURRENCE On 02/04/2016, Salem Unit 2 was operating in MODE 1. At 07:00, Salem Unit 2 commenced a load reduction at 30% per hour to approximately 73% rated thermal power (RTP) to support a 500 kV line outage. Power was stabilized at approximately 74% RTP at 07:50. DESCRIPTION OF OCCURRRENCE On 2/4/16 at 11 :21 Salem Unit 2 automatically tripped from approximately 7 4% power on Generator Protection, initiated by the main generator Automatic Voltage Regulator (AVR) STV1volts/hertz relay {TB/RLY}. At 11 :20:36 Overhead Annunciator (OHA) H21 - "Generator Voltage/Frequency High" was received, followed by OHA H27 - "Gen Vreg Trbl" at 11:21:19. At 11 :21 :25 OHA F47 - "Generator Protection" was received, coincident with the Unit 2 trip. The STV1 relay is an over excitation protection relay. Troubleshooting identified the STV1 as a contributor to the trip, so the calibration of the relay was checked. The as-found calibration data showed that the relay pick up setting was out of specification low. In the time period just prior to the Unit 2 trip, the generator was operating at approximately 26.1 KV, which corresponds to a 2.175 V/Hz sensed at the STV1 relay. The as found pick up for the STV1 relay was at 2.17 V/Hz, so the plant was operating above the relay's pick up set point. Once the set point was exceeded, the H21 OHA alarm was received in the Control Room. After the time delay of 45 seconds had elapsed, the trip relay picked up, starting the sequence of tripping the AVR on an external trip and dropping the generator field, causing the turbine trip on generator protection. The turbine trip resulted in a reactor scram. The Unit 2 AVR was replaced during the 2R21 refueling outage in Fall 2015. The STV1 was original plant design. A new relay was purchased, calibrated, and installed at the time of the AVR replacement. A four-hour NRC Event Notification (EN) was required by 10 CFR 50.72(b)(2)(iv)(B) for actuation of the reactor protection system (RPS) when the reactor is critical and an eight-hour NRC EN was required by 10 CFR 50.72(b)(3)(iv)(A) for a valid actuation of the auxiliary feedwater system. EN 51708 was completed at 13:33 on 02/04/2016. This LER is being submitted pursuant to the requirements of 1 OCFR50.73 (a)(2)(iv)(A), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)." | ML17250A152
Watts Bar Nuclear Plant | Unit 1 | Unanalyzed Condition Related to Dual Unit operation of the Essential Raw Cooling water System During a Design Basis Accident | 09-11-2017 | On July 12,2017, at 1238 Eastern Daylight Time (EDT), Watts Bar Nuclear Plant (WBN) determined that a pretiminary analysis shows adequate Essential Raw Cooling Water (ERCW) flow may not be available during dual unit limiting design basis conditions of one unit in Hot Shutdown on Residual Heat Removal (RHR) cooling when the other unit experiences a Loss of Coolant Accident (LOCA). Based on preliminary analysis, during a Unit 1 LOCA, Unit 1 receives adequate flow when following existing procedural guidance. However, Unit 2 may not receive adequate flow to meet cool-down requirements with design basis maximum temperatures. During a Unit 2 LOCA, however, current procedural guidance is not adequate to ensure the proper system alignment to establish correct ERCW Component Cooling Water (CCS) Heat Exchanger A and B flow rates for either unit's cool down requirements. At the time of the event, Unit 2 had been shutdown for an extended period of time such that the flow delivered by ERCW was adequate to serve both Unit 1 in a LOCA and Unit 2 in Mode 4 or 5. lmmediate corrective actions included procedure changes to ensure adequate ERCW flow for all possible plant situations in both units. The causes of this issue are a failure to address cross train elements of the ERCW system in the design analysis and a failure to address procedural impacts when the plant transitioned to dual unit operation. The procedure errors were corrected. NRC FORM 366 (O4-2O17) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 ExptRES: 0il11t2020 (0/-2017)) Estimated burden per response to comply with this mandatory collection request 80 hours. Reported lessons leamed are incorprated into the licensing process and fed back to industry. Send LTGENSEE EVENT REPORT (LER) c R o e m g m u e l n a b to re ry ga r C di o n m g m bu i r s d s e i n o n es , tim w a a te s h to in t g h t e o l n n , fo r D ma C tion 2 S 0 e s rv s ic s e - s 0 0 Br 0 a 1 nc , h o ( r T -2 b F4 y 3) , U e . - S m . N a u i c t l ea to r CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, ffice of lnformation and Regulatory Afiairs, NE0&10202, (315G0104), Office of Management and Budget, Washington, DC 20503. lf a nreans used to impose an information collection does not display a cunenfly valid OMB contol number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Watts Bar Nuclear Plant, Unit 05000390 NUMBER NO. 1 r -00 2017 009 | I. PLANT OPERATING CONDITIONS BEFORE THE EVENT Watts Bar Nuclear Plant (WBN) Unit 1 was at 100 percent rated thermal power (RTP) . WBN Unit 2 was in Mode 5. II. DESCRIPTION OF EVENT A. Event Summary On July 12,2017, at 1238 Eastern Daylight Time (EDT), Watts Bar Nuclear Plant (WBN) determined that a preliminary analysis shows adequate Essential Raw Cooling Water (ERCW) {EllS:Bl} flow may not be available during dual unit limiting design basis conditions of one unit in Hot Shutdown on Residual Heat Removal (RHR) cooling when the other unit experiences a Loss of Coolant Accident (LOCA). Based on preliminary analysis, during a Unit 1 LOCA, Unit 1 receives adequate flow when following existing procedural guidance. However, Unit 2 may not receive adequate flow to meet cool-down requirements with design basis maximum temperatures. During a Unit 2 LOCA, however, current procedural guidance was found not adequate to ensure the proper system alignment to establish correct ERCW Component Cooling Water (CCS) {EllS:CC} Heat Exchanger {EllS:HX} A and B flow rates for either unit's cool down requirements. This event is being reported to the Nuclear Regulatory Commission (NRC) under 10 CFR 50.73(a)(2)(ii)(B) as an unanalyzed condition that significantly degraded plant safety and under 10 CFR 50.73 (a)(2)(v)(B) and (D) as an event or condition that could have prevented fulfillment of a safety function. B. lnoperable Structures, Components, or Systems that Contributed to the Event No inoperable equipment contributed to this event. C. Dates and Approximate Times of Occurrences Date Event 10t20t15 WBN Unit 1 receives license Amendment 104 to revise the Technical Specifications (TS) for CCS and ERCW to support Dual Unit Operation. 10t22t15 WBN Unit 2 receives operating license 11t19t15 Post lssuance Change (PlC) 65699 revises Design Change Notice (DCN) 62151to address ERCW alignment for Dual Unit Operation. Emergency procedure impacts not properly addressed. 5t23116 WBN Unit 2 is critical for the first time 7112t17 condition Report (GR) 1316395 is generated to document ERCW design issue. 7114t17 Procedures 1-E-0 and 2-E-0, Reactor Trip or Safety lnjection, are revised to address proper position of ERCW outlet valves from the CCS heat exchangers. D. Manufacturer and Model Number of Components that Failed During the Event There were no failed components that contributed to this event. | ML17254A762
Oconee Nuclear Station | Unit 1 | : | 08-09-2017 | On June 16, 2017, during implementation of a modification to Keowee Hydroelectric Station Governor Actuator Cabinets 1 and 2, breakers were inadvertently repositioned in each of the governor control system for Keowee Hydroelectric Units 1 and 2 (KHU1 and KHU2), rendering both units inoperable. The condition was discovered following an unsuccessful start of KHU2 for commercial operation. The KHUs are the onsite emergency power source for the Oconee Nuclear Station. It was concluded that this constituted a loss of safety function from the time when both KHUs were inoperable until the dedicated offsite power source was aligned to the emergency busses; a period of approximately 7 hours. This condition is reportable pursuant to 10 CFR 50. 73(a)(2)(v)(A-D). ·Technical Specifications (TS) were followed based on time of discovery; however, a subsequent review of c:omputer logs provided firm evidence that both KHUs were inoperable for longer than allowed by TSs based cm "past inoperability," requiring this event to be reported pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. The direct cause of this event was attributed to the reposition due to inadvertent contact of two 24 VDC breakers. The risk impact of this event was determined to be insignificant and corrective actions are planned ti:> prevent recurrence. NFtC FORM 366A (04-2017) U.S. NUCLEAR REGULATORY COMMISSION . APPROVED BY OMB: NO. 3150-0104 EXPIRES 3/3112020 LICENSEE EVENT REPORT (LER) .. (See form 366 above for burden estimate) CONTINUATION SHEET 1. FACILITY NAME 2. DOCKET NUMBER 6. LER NUMBI ER Oconee Nuclear Station Unit 1 5000269 YEAR I SE N Q U U M E B N E T R IA L R N E Q V 2017 - 001 .. 00 | BACKGROUND At Oconee Nuclear Station {ONS), the Keowee Hydroelectric Station (KHS) [EllS:EK] serves the emergency power function typically performed by diesel generators [EllS: DG] at other nuclear facilities. The KHS consists of two (2) hydroelectric turbine/generator units (KHUs) and associated support equipment and auxiliaries. Each KHU is provided with its own automatic start equipment and both · KHUs undergo simultaneous automatic emergency starts during an emergency. Either KHU may be aligned to either of two emergency power paths, with the underground path being preferred if only one KHU is available. In addition to Keowee, a 100 kV transmission line from a nearby plant with dedicated combustion turbines [EllS: TUR] can provide power to the Stand-by Buss (the emergency buss that supplies emergency loads on all three Oconee units). Governor [EllS: 65] Actuator Cabinets [EllS: CAB] GAC1 and GAC2 contain control circuitry and components for KHU1 and KHU2 respectively, including breakers [EllS: 52] K1 GCS BK0001 and K2 GCS BK0001 as part of the Governor Control System for KHU1 and KHU2 respectively. These breakers are small, 'plug in' type, 10 amp breakers with the actuating power switches [EllS: JS] protruding into an open space inside their respective cabinets. These breakers provide 24 VDG to a distributing valve [EllS: V] assembly and shutdown solenoid valve [EllS: SV] which are both required to actuate for Keowee to start. The shutdown solenoid is a fail-safe valve that requires energization to open during turbine operation. Without power, the solenoid valve closes. EVENT DESCRIPTION On June 16, 2017, at approximately 0740 hours, workers were implementing a modification to Governor Actuator Cabinets 1 and 2 located within the Keowee Hydroelectric Station. The investigation showed thatat approximately 0907 hours, Operator Aid Computer (OAC) alarm [EllS: ALM] indications for K1 GCS BK0001 breaker for KHU1 Channel A and B Governor Critical Alarm were received on the OAC alarm screens located in the Keowee Control Room (KCR). These alarms were not observed by the Keowee operator since he was still on rounds and not in the KCR. Normally, when a Governor Critical Alarm is received, Stat-Alarms in both the Keowee and Oconee ~unit 2 Control Rooms are generated. Additionally, a governor critical alarm condition triggers an emergency lock-out of the unit, which would also normally generate Stat-Alarms. However• . in this-instance, no Stat-Alarms were !generated and no emergency lock-out conqition was triggered due to the failure mode design of the repositioned breaker defeating the signal sent to the Stat-Alarms. Had a Stat-Alarm been received, the !Protocol of Stat-Alarm management would have been followed by the Oconee Unit 2 Control Room, the Oconee Unit 2 Senior Reactor Operator and the Keowee Control operators, potentially reducing the probability for this single incident to have escalated further. At 1020 hours, similar OAC alarm indications were received in the KCR associated with the KHU2 K2 GCS BK0001 breaker. · ;!\t 1321 hours, while attempting to start KHU2 for commercial generation, an "incomplete start" alarm was received in the KCR. Investigation into the matter subsequently revealed that the two (2) repqsitioned breakers were open and both KHUs were non-functional. Each KHU was declared inoperable at 1635 hours. In Mode 1, KHU operability is required by TS 3.8.1, "AC Sources-Operating," and TS 3.7.10, "Protected Service Water." The appropriate TS conditions were .entered and the Required Actions completed within the allowed Completion Times. As required by TS Limiting Condition for Operation (LCO) 3.8.1, Condition I, due to the loss of both KHUs, Standby Buses were energized from a Page2 of 5 | ML17256A516
Limerick Generating Station | Unit 2 | HPCI lnoperability during Post Maintenance Testing | 09-25-2017 | On July 27, 2017, during Post Maintenance Testing (PMT) following a relay replacement activity, the Unit 2 High Pressure Coolant Injection (HPCI) system was inoperable when an undesirable valve alignment was established as per the PMT instructions resulting in a loss of suction path for the HPCI pump. Work was stopped and Operations and Instrument & Controls (l&C) supervision were notified. HPCI was inoperable for approximately 20 minutes until Operations restored a HPCI suction path to the Unit 2 Suppression Pool. This event is significant because it resulted in an unplanned inoperability of a single train safety system. An eight (8) hour ENS notification to the NRG was completed on July 27, 2017 at 1854 hours. NRC FORM 366 (04·2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03131/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the lnfonnation Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LEA) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of lnfonnation and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an infonnation collection dces not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/stall/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR Limerick Generating Station, Unit 2 05000353 NUMBER NO. 2017 - 006 - 00 | I. Unit Conditions Prior to the Event Limerick Generating Station (LGS) Unit 2 was operating in Operational Condition (OPCON) 1 at 100 percent power at the time of the event. There were no other structures, systems, or components inoperable at the time of the event that contributed to the event. 11. Description of the Event On July 27, 2017, during Post Maintenance Testing (PMT) following a relay replacement activity, the Unit 2 High Pressure Coolant Injection (HPCI) system was inoperable when an undesirable valve alignment was established as per the PMT instructions resulting in a loss of suction path for the HPCI pump. Work was stopped and Operations and l&C supervision were notified. On July 27, 2017 at 1335 hours, Operations personnel restored a HPCI suction path to the Unit 2 Suppression Pool. HPCI was inoperable for approximately 20 minutes. This event is significant because it resulted in an unplanned inoperability of a single train safety system. An eight (8) hour ENS notification to the NRC was completed on July 27, 2017 at 1854 hours. A condition existed that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident and is reportable under 1 O CFR 50.73(a)(2)(v)(D). Ill. Analysis of the Event In 2004 a modification was implemented for both Unit 1 and Unit 2 to increase margin for the HPCI suction Primary Containment Isolation Valve (PCIV) stroke time. This modification had taken a normally de-energized relay and changed the relay to a normally energized relay for the HPCI suction valves. Preventative Maintenance tasks were created to replace the normally energized relays. Similar work packages were developed for both the Unit 1 and Unit 2 Preventative Maintenance tasks. The Unit 1 relay replacement was completed in June 2015 during a HPCI system outage window (SOW) with the system inoperable. The PMT closed the suction valves which isolated both HPCI suction sources. The Unit 2 relay replacement was planned to be performed with HPCI inoperable; however, the work was rescheduled to perform the relay replacement with HPCI operable. In July 2017, prior to performing the work, Station Maintenance and Operations personnel performed a review of the work package. The review identified that the work package required revision to maintain the system operable during the relay replacement. The review did not identify that the PMT also required a revision. | ML17268A272
Columbia Generating Station 05000 397 1 OF 3 | Unknown Unit | Valve Closure Results in Momentary Increase in Secondary Containment Pressure | 09-27-2017 | On October 3, 2016 at 1008 PDT, the Secondary Containment (Reactor Building) became inoperable due to pressure increasing above the Technical Specification limit of -0.25 inches of water gauge (inwg). While the plant was at 100% power, a Reactor Building exhaust valve (REA-V-1) unexpectedly closed, resulting in a loss of Secondary Containment vacuum for approximately four minutes. Operations personnel manually started the Standby Gas Treatment System A and quickly restored Secondary Containment to less than -0.25 inwg. While Technical Specification limits were exceeded for this short time period, the resulting pressure excursion was bounded by analytical results; and thus, there were no safety consequences for this condition. This event was reported under reporting criterion 10 CFR 50.72(b)(3)(v)(C) as Event Notification #52276. The cause of the REA-V-1 closure was a loose termination point on the termination board, resulting in an intermittent loss of power to the valve. The corrective action for this event was to tighten the loose termination point screw. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000- NUMBER NO. Columbia Generating Station 397 2016 - 002 - 01 | Plant Conditions At the time of the event, the plant was operating in Mode 1 at 100% power. Event Description On October 3, 2016 at 1008 PDT, Operations personnel received an annunciator alarm for high Secondary Containment [NH] differential pressure when the Reactor Building [NG] exhaust inboard isolation valve [V] (REA-V-1) failed shut. For a time period of approximately four minutes, Secondary Containment differential pressure increased above -0.25 inches of water gauge (inwg), resulting in Technical Specification (TS) 3.6.4.1 not being met. This event is reportable as an event that could have prevented fulfillment of safety functions needed to control the release of radiation, and mitigate the consequences of an accident per 10 CFR 50.73(a)(2)(v)(C) and 10 CFR 50.73(a)(2)(v)(D). This condition was reported under 10 CFR 50.72(b)(3)(v)(C) via Event Notification #52276 for an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material. Immediate Corrective Actions Per plant procedure, Operations personnel manually started Standby Gas Treatment [BH] (SGT) System A and Secondary Containment was restored to less than -0.25 inwg at 1012 PDT. Assessment of Safety Consequences This event resulted in an unplanned entry into TS 3.6.4.1.A, in which Secondary Containment pressure was greater than -0.25 inwg for approximately four minutes. The peak pressure during this event was +4.17 inwg. While the actual pressure was beyond the range allowed by Technical Specifications, the purpose of maintaining a slight vacuum is to assist in drawdown of secondary containment to support accident response of the safety related SGT system. Existing engineering analysis demonstrates that for this event, the drawdown credited in Columbia's accident analysis could have been attained using either of the two available trains of the SGT system, thus there were no potential safety consequences. There was no actual safety consequence associated with this event since SGT did in fact restore Secondary Containment, and there was no loss of safety function or potential for radiological release. Cause of Event The apparent cause of the unexpected failure of REA-V-1 was a loose termination point on the termination board, resulting in an intermittent loss of power to the valve. | ML17270A195
clinton power station | Unknown Unit | Automatic Reactor Scram During the Performance of Scram Time Testing As a Result of an Invalid Oscillation Power Range Monitor Growth Rate Trip | 09-28-2017 | On May 30, 2017 at 2038 CDT, with the reactor at approximately 28% thermal power Clinton Power Station (CPS) experienced an automatic reactor scram while conducting scram time testing (STT). Plant systems responded as expected and functioned properly following the automatic scram. The automatic scram signal was generated by the Oscillation Power Range Monitor (OPRM) Growth Rate Algorithm (GRA). An evaluation confirmed that the reactor was operating in a very stable core condition and that the event did not occur due to an actual core thermal hydraulic instability. The cause of the event was that the OPRM GRA trip function design is unable to distinguish between plant response to system perturbations and onset of thermal-hydraulic instabilities. Interim actions were implemented to increase operating margin to trip setpoints to support reactor startup and completion of STT. They included a revision to a plant procedure to establish an operating strategy when performing STT in the OPRM enabled region, implementing a monitoring strategy to assess the effectiveness of the operating strategy and monitoring for expected plant response, and raising OPRM Amplitude and GRA set points. Planned corrective actions include working with the industry, as needed, to develop and implement an industry solution for the design of the OPRM GRA to prevent false, spurious trip signals. The automatic scram is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in a manual or automatic actuation of the reactor protection svstem. NRG FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: BO. hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/readinq-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Clinton Power Station, Unit 1 05000461 NUMBER NO. 2017 - 005 - 01 | PLANT AND SYSTEM IDENTIFICATION General Electric-Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX] EVENT IDENTIFICATION Automatic Reactor Scram During the Performance of Scram Time Testing As a Result of an Invalid Oscillation Power Range Monitor Growth Rate Trip A. Plant Operating Conditions before the Event Unit: 1 Event Date: May 30, 2017 Event Time: 2038 Mode: 1 Mode Name: Power Operation Reactor Power: 028 percent 8. DESCRIPTION OF EVENT On May 30, 2017 at 2038 hours CDT, Clinton Power Station (CPS) experienced an automatic reactor scram from 28 percent thermal power while performing control rod scram time testing (STT) per CPS procedure, CPS 9813.01, Control Rod Scram Time Testing, during startup from refueling outage C1R17. The automatic scram signal was generated by the Oscillation Power Range Monitor (OPRM) Growth Rate Algorithm. Following the event, General Electric Hitachi (GEH) performed an evaluation of CPS .reactor conditions and determined that the core decay ratio, a measure of reactor core stability, was very low (<0.3) which is indicative of a very stable core condition and consistent with the observed data. A review of OPRM data concluded that the event did not occur due to actual core thermal hydraulic instability. It is also concluded that core thermal limits were not challenged by this event. CPS is licensed with the Detect and Suppress Option Ill reactor core stability solution which utilizes the Period Based Detection Algorithm. This provides detection of a power instability based on occurrence of a fixed number of consecutive neutron flux period confirmations and a relative power signal exceeding a specific set point. For CPS, the number of period confirmation counts is 14 and relative power set point is 1.12. Furthermore, the Option Ill stability solution includes a Growth Rate Algorithm (GRA) and an Amplitude Based Algorithm (ASA) that offer defense in depth by providing protection against unexpected power oscillation characteristics. NRG FORM 366A (04-2017) Page _2_ of _4_ | ML17275A173
Susquehanna Steam Electric Station | Unit 1 | Automatic Reactor Protection System Trip on High Neutron Flux | 00-04-2017 | On June 8, 2017 at 1527 hours, the reactor automatically scrammed due to a loss of Main Turbine- Electro-Hydraulic Control (EHC) logic power causing a high neutron flux, Reactor Protection System (RPS) trip. The safety systems operated as expected. Secondary Containment differential pressure lowered to 0" WG due to a trip of the normal operation of the Reactor Building Ventilation system. The differential pressure was restored by the initiation of Standby Gas Treatment System. The scram was caused directly by a DC+ (direct current, positive) test lead (Maxi Grabber) that inadvertently contacted with the grounding screw, causing a short and momentary loss of EHC logic power. Immediate action was taken to validate that there was no damage to the +30 VDC (volts DC) EHC logic. I The root cause for this event is an insufficient focus on the High Risk Activity of adjusting the EHC power supply, and inadequate risk mitigating actions for that activity. The condition is being reported in accordance with 10 CFR 50.7 3(a)(2)(iv)(A) as an event that resulted in an automatic actuation of the RPS, including reactor scram. Although no safety system functional failure occurred, this event is also reportable pursuant to 10CFR 50.73(a)(2)(v)(C) as a condition that could have prevented fulfillment of a safety function. There were no actual, or potential consequences to the health and safety of the public as a result of this event. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1 022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http://www. nrc.gov/readinq-rm/doc-collections/n u regslstaff/sr1 0221r30 NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station Unit 1 05000387 NUMBER NO. 2017 -005 - 01 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, approximately 10 0 percent Rated Thermal Power Unit 2 - Mode 1, approximately 100 percent Rated Thermal Power There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. EVENT DESCRIPTION On June 8, 2017, at 1527 hours, the reactor automatically scrammed due to a loss of Main Turbine Electro Hydraulic Control (EHC) [EllS System Code TG] logic power causing a high neutron flux, Reactor Protection System (RPS) trip. Workers were restoring from making a power supply swap for the EHC, from permanent Magnetic Generator (PMG) to a house power supply. A Maxi Grabber was being removed from the PMG positive lug and came in contact with a grounding screw, resulting in a short and causing a loss of EHC pressure control. After the momentary short cleared, the meter indications showed the power supply returned to the normal operating voltage. The 30 VDC (volts DC) bus voltage transient resulted in temporary saturation of the pressure regulatory output and caused the bypass valve fast open logic to actuate and closure of the control valves. Once the control valves closed beyond the bypass valve capacity, the reactor pressure increased resulting in the high neutron flux reactor scram. All control rods inserted and both reactor recirculation pumps tripped due to reaching reactor water low level 2. Reactor water level lowered to -49 inches causing Level 3 (+13 inches) and Level 2 (-38 inches) isolations. High Pressure Coolant Injection (HPCI) '[EllS System Code BJ] and Reactor Core Isolation Cooling (RCIC) [EllS System Code BN] automatically initiated and were overridden by control room operations after reactor pressure vessel water level was restored to the normal band with feedwater. HPCI and RCIC injected to the Reactor Coolant System during reactor level stabilization. Division 1 RHR was manually placed in suppression pool cooling. All isolations and initiations occurred as expected. No main steam relief valves opened. Pressure was controlled via main turbine bypass valve operation. The safety systems operated as expected. Secondary Containment [EllS System Identifier: NG] Zone 1, 2, and 3 differential pressure lowered to 0" WG due to a trip of the normal operation of the Reactor Building Ventilation system that resulted from the Unit 1 Level 2 isolation. The differential pressure was restored to Zones 1, 2, and 3 by the initiation of Standby Gas Treatment System on the Unit 1 Level 2 initiation. NRC FORM 3668 (04-2017) Page 2 of 4 | ML17277A320
Fermi2 05000 341 1 OF 6 | Unknown Unit | Inadequate Procedural Guidance for Residual Heat Removal Complex Ventilation Systems Leads to Condition Prohibited by Technical Specifications and Loss of Safety Function | 10-09-2017 | On August 10, 2017, it was determined that inadequate procedural guidance for determining operability for ventilation support systems was being utilized. The Residual Heat Removal (RHR) switchgear and pump rooms have ventilation systems to maintain operability of the equipment in the rooms. Fermi 2 procedures had directed personnel to declare the supported equipment in the rooms inoperable due to nonfunctionality of the ventilation systems only if the room temperature exceeded the operability limit. Following discovery, a review of the RHR switchgear and pump room ventilation systems for the past three years was performed. The review identified multiple instances where the ventilation systems were nonfunctional and should have resulted in entry into applicable Technical Specifications (TS). Many of these instances resulted in operations or conditions prohibited by TS, since TS Required Actions were not completed within the Completion Times for restoration of affected equipment and plant shutdown. In addition, one instance was identified where the plant configuration was such that it could have prevented the fulfillment of the safety function to remove residual heat following a design basis accident. An engineering evaluation of this specific instance was performed and verified that the plant remained within its analyzed design basis. All other instances maintained one fully operable division of heat removal equipment such that no loss of safety function existed. There were no radiological releases associated with this event. The safety significance was determined to be very low. The cause of the event was inadequate procedural guidance. Immediate actions were taken to provide interim guidance related to the procedure. Corrective actions to revise the affected procedure have been completed. NRC FORM 366 (04-20171 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported ""*N< E N lessons learned are Incorporated into the licensing process and fed back to Industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear CONTINUATION SHEET Regulatory Commission, Washington, DC 20555-0001, or by e-mail to infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, ***** NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC2 0503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http://www.nrc.cov/reading-rm/doc-collections/nureqs/staff/sr022/r3/) NRC may not conduct or sponsor, and a person is not required to respond to, the Information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Fermi 205000- NUMBER NO. 2017 - 004 - 00 | INITIAL PLANT CONDITIONS Mode -1 Reactor Power - 100 percent There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT At approximately 1200 EDT on August 10, 2017, while operating in Mode 1 at 100 percent power, the DTE Electric Company (DTE) procedural guidance pertaining to the Residual Heat Removal (RHR) [BO] switchgear [SWGR] room ventilation system was questioned by the NRC Senior Resident Inspector. Technical Specification (TS) 3.8.7 requires Division I and Division II alternating current (AC) and direct current (DC) electrical power distribution subsystems [EB and EJ] to be operable in Modes 1, 2, and 3. The AC distribution system in TS 3.8.7 consists of two divisions with four 4160 V buses [BU] and four 480 V buses each. The Division I 4160 V buses 11 EA and 12EB, the Division I 480 V buses 72EA and 72EB, the Division II 4160 V buses 13EC and 14ED, and the Division II 480 V buses 72EC and 72ED are all located in the RHR complex. Specifically, each bus is located in the RHR switchgear room associated with its corresponding Emergency Diesel Generator (EDG) [DG]. As described in the Updated Final Safety Analysis Report (UFSAR) Section 9.4.7.2, the four RHR switchgear rooms are each equipped with a ventilation system to dissipate the heat produced by the switchgear room equipment (e.g., the 4160 V and 480 V buses) and limit the inside ambient temperature to 104 degrees Fahrenheit (F) under all plant operating conditions. Each switchgear room ventilation system consists of an intake air duct [DUCT], high efficiency filter [FLT], and two 50 percent-capacity fans [FAN] in parallel. Thus the switchgear room ventilation systems are design features and their functionality impacts the operability of the 4160 V and 480 V buses and therefore the AC distribution subsystems. Contrary to this, a DTE procedure directed personnel to declare the 4160 V and 480 V buses inoperable per TS 3.8.7 due to nonfunctionality of the RHR switchgear room ventilation system only if the room temperature exceeded 104 degrees F. At the time of discovery of this procedural inadequacy on August 10, 2017, all the RHR switchgear room ventilation systems were functional and the associated 4160 V and 480 V buses were operable. With a correct understanding of the applicable TS, a past operability review was performed for the three years prior to the date of discovery. This review identified 50 occurrences where an RHR switchgear room ventilation system was not functional due to maintenance activities. For each occurrence, the associated 4160 V and 480 V buses were considered operable at the time and no entry to TS 3.8.7 was made based on the unavailability of the RHR switchgear room ventilation system. Limiting Condition for Operation (LCO) 3.8.7 Condition A Required Action A.1 requires restoration of the AC electrical power distribution subsystems (i.e. the buses) to operable status within 8 hours. LCO 3.8.7 Condition C Required Action C.1 requires the reactor to be in Mode 3 in 12 hours if the Required Action and associated Completion Time of Condition A is not met. Of the 50 total occurrences described above, 25 exceeded the combined restoration Completion Time and the shutdown Completion Time (i.e. 20 hours) and therefore represent instances of an "operation or condition which was prohibited by the plant's Technical Specifications" reportable under 10 CFR 50.73(a)(2)(i)(B). Note that there is no corresponding reporting requirement under 10 CFR 50.72 and therefore no telephone notification to the NRC was made. The longest occurrence was a Division 1 RHR switchgear room ventilation system associated with EDG 11 out of service for approximately 158 hours. The 4160 V and 480 V buses described above directly provide power for the safety-related RHR service water (RHRSW) [BI] pumps [P], Mechanical Draft Cooling Tower (MDCT) [CTW] fans [FAN], and Emergency Equipment Service Water | ML17282A004
YEAR SEQUENTIAL REV | Unknown Unit | MANUAL REACTOR SCRAM DUE TO HIGH MAIN CONDENSER BACK PRESSURE | 10-18-2017 | On August 20, 2017 at 1605 PDT, Columbia Generating Station was manually scrammed due to a rise in Main Condenser back pressure. The rise in back pressure was due to the spurious closure of the Main Condenser Air Removal Suction Valve (AR-V-1) as a result of the failure of it's associated solenoid pilot valve. Following the reactor scram and depressurization of the reactor a Level 3 actuation occurred. In addition a startup flow control valve failed which necessitated throttling of the Feedwater start-up level control isolation valve to control Reactor Pressure Vessel level. All other safety systems functioned as expected and all control rods were fully inserted. Reactor decay heat was removed via bypass valves to the main condenser. The apparent cause was the plant modification to address the single point vulnerability of the closure of AR-V-1 was not implemented in time to prevent a plant shutdown. A temporary modification has been installed to maintain AR-V-1 open for the remainder of the operating cycle. These events are reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear CONTINUATION SHEET Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000- NUMBER NO. Columbia Generating Station 397 2017 - - 004 00 | PLANT CONDITIONS At the time of the event, Columbia Generating Station (Columbia) was in Mode 1 operating at 100% reactor power. There were no safety related systems out of service prior to the event. EVENT DESCRIPTION On August 20, 2017 at 1605, in response to rising main condenser [SG] backpressure due to the Main Condenser Air Removal Suction Valve [SH] [V] (AR-V-1) failing closed, control room operators initiated a manual reactor scram after reducing reactor power to 80%. The main turbine [TA] and generator [TB] tripped due to the main condenser backpressure transient and both Reactor Recirculation (RRC) Pumps [AD] [P] tripped when an automatic signal was generated by the main turbine trip. All rods fully inserted and the Main Steam Isolation Valves [SB][V](MSIVs) stayed open. Following the initial transient a subsequent Reactor Pressure Vessel [AB] [RPV] (RPV) low water level (Level 3) actuation occurred due to operator action per plant procedure to reduce RPV pressure, and level restored automatically with no operator action. Startup Flow Control Valve [SK] [V] (RFW-FCV-10B) then failed to automatically control RPV water level resulting in a RPV high water level (Level 8) trip and level was restored by throttling Reactor Feedwater Flow Control Valve [SK] [V] (RFW-V-118) per plant procedure. All other safety systems operated as designed. All other plant systems responded as expected with the following exceptions: The Mode Switch [JC] [HS] was reportedly difficult to turn but did not impede the capability to scram. Reactor Feedwater Turbine Turning Gear [TA] [TGR] (RFT-DT- A) would not stay engaged; operator action was required to keep it engaged. These equipment issues did not impact the safety significance of the event. IMMEDIATE CORRECTIVE ACTION A temporary modification to gag open AR-V-1 for the remainder of the operating cycle has been implemented. CAUSE The direct cause of the shutdown was failure of Solenoid Pilot Valve [SK] [V] (AR-SPV-1/1) due to thermal aging which resulted in unexpected closure of AR-V-1. The apparent cause was a plant modification to address the known single point vulnerability (closure of AR-V-1) was not implemented in time to prevent a plant shutdown. The contributing cause was the management decision to not include the maintenance task to replace AR-SPV-1/1 in the most recent refueling outage. EXTENT OF CONDITION A review of all single point vulnerable components was conducted. The scope of the review included all normally energized components that could change state and cause a plant trip if electrical power were lost. The review revealed three relays that are in a normally energized state but were within their required replacement frequency. | ML17291A391
Nine Mile Point | Unit 2 | Automatic Reactor Scram due to High Reactor Pressure | 10-04-2017 | On August 5, 2017, at approximately 2235, the Nine Mile Point Unit 2 (NMP2) reactor scrammed on an automatic scram signal during performance of quarterly turbine stop valve surveillance testing. The automatic Reactor Protection System (RPS) actuation and reactor scram is reportable per 10 CFR 50.73(a)(2)(iv)(A). The definitive root cause of the equipment failure was not located but was bound to spurious actuation of load limit relays KL 186 and KL 187. The spurious action was caused by an intermittent ground and/or an induced voltage within the load limit circuit. This is a result of the non-fault tolerant original design of the Electro-hydraulic Control (EHC) system. The corrective action planned is replacement of the current single point vulnerable NMP2 Turbine EHC system with a fault tolerant Digital EHC system. Interim actions have also been developed to mitigate risk associated with testing of the current system until replacement can be accomplished during the 2018 refueling outage. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and led back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear. LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www. nrc. gov/readi nq-rm/doc-collections/nureqs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Nine Mile Point Unit 2 05000410 NUMBER NO. 2017 - 001 00 | I. DESCRIPTION OF EVENT A. PRE-EVENT PLANT CONDITIONS: Prior to the event, Nine Mile Point Unit 2 (NMP2) was in Mode 1 and operating at 84% reactor power. Turbine controls troubleshooting and overspeed trip system repairs had been completed, followed by power ascension from 20% power to 84% power. The plant was stabilized at 84% power to support quarterly turbine valve testing. B. EVENT: On August 5, 2017, at approximately 2235, during performance of quarterly turbine valve testing, an automatic Reactor scram occurred. The RPS system actuation was due to high reactor pressure. The pressure increase occurred when the turbine control valves (TCV) began closing while stroking turbine stop valves (TSV) 1 and 2. All systems responded as expected to the reactor scram signal. Based on the turbine bypass valves (TBV) fast opening and TCVs ramping closed, a loss of control valve demand was determined to be the initiator of the event. The TSV limit switch circuit was tested for grounds or stuck limit switches after the scram but none could be found. Troubleshooting identified an erroneous control valve demand signal resulting in fast closure of the control valves and subsequent increase in reactor pressure. After instrumenting the load control circuit, an anomaly on the load limit amplifier card was identified. The card was replaced and sent out for failure analysis. To further protect against latent failures, a temporary modification to lift the leads on the stop valve load limit switches was implemented. Lifting the leads minimizes the risk of fast closure of the TCVs in the event of a stuck load limit switch during future turbine valve testing. The failure analysis of the load limit amplifier card determined the card was functioning properly and was not the cause of the event. This further supports that the spurious actuation of load limit relays KL 186 and KL 187 was caused by an intermittent ground and/or an induced voltage within the load limit circuit. Nine Mile Point Unit 1 (NMP1) was unaffected by the scram at NMP2. The event has been entered into the plant's corrective action program as IR 4039435. C. INOPERABLE STRUCTURES, COMPONENTS, OR SYSTEMS THAT CONTRIBUTED TO THE EVENT: No other systems, structures, or components contributed to this event. NRG FORM 366A (04-2017) Page _2_ of _5_ | ML17296A158
Browns Ferry Nuclear Plant | Unit 3 | Inoperable Residual Heat Removal Pump Results in Condition Prohibited by Technical Specifications | 10-31-2017 | On September 1, 2017, at approximately 1006 Central Daylight Time (CDT), Browns Ferry Nuclear Plant (BFN) Unit 3 3A Residual Heat Removal (RHR) system pump failed to start during performance of Surveillance 3-SR-3.5.1.6 (RHR I), Quarterly RHR System Rated Flow Test Loop I. The apparent cause was the Electrical Preventive Maintenance Instruction for 4kV Wyle/Siemens Horizontal Vacuum Circuit Breaker (Type-3AF) and Compartment Maintenance was revised to include steps to secure the breaker’s mounting hardware which caused internal binding of the indication flag. Binding of the indication flag prevented the closing spring of the breaker from charging and the breaker from closing on demand. As a result, automatic start of the 3A RHR pump was prevented. On September 1, 2017, at approximately 1633 CDT, the 3A RHR Pump was declared operable following lubrication and testing of the breaker’s indication flag mounting bolt. A Past Operability Evaluation concluded that the 3A RHR Pump was inoperable from July 26, 2017 to September 1, 2017, which exceeded the Technical Specification allowed outage time. During this time, the 3B, 3C, and 3D RHR pumps would have started automatically upon receipt of an Emergency Core Cooling System (ECCS) initiation signal or from an Operator manual start demand from the Control Room. Based on results from the Probability Risk Assessment and Engineering inspections, there was no significant risk to the health and safety of the public or plant personnel for this event. The Corrective Action to reduce the probability of similar events occurring in the future will be addressed by revising the Electrical Preventive Maintenance Instruction for 4kV Wyle/Siemens breakers to ensure freedom of movement of the indication flag is present during the breaker inspection. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Browns Ferry Nuclear Plant, Unit 3 05000-296 2017 - 001 - 00 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Unit 3 was in Mode 1 at 100 percent power. II. Description of Event A. Event Summary On September 1, 2017, at approximately 1006 Central Daylight Time (CDT), BFN Unit 3 3A Residual Heat Removal (RHR)[BO] system pump [P] failed to start during the performance of Surveillance, 3-SR-3.5.1.6 (RHR I), Quarterly RHR System Rated Flow Test Loop I. Maintenance troubleshooting revealed that the 3A RHR pump motor breaker’s [BKR] closing spring failed to charge preventing the breaker from closing on demand. Malfunction of the 3A RHR pump motor breaker resulted in 3A RHR pump failing to start during manual or automatic actuation. Operations personnel declared 3A RHR pump inoperable. A Past Operability Evaluation (POE) was performed for the 3A RHR pump failure. The POE concluded that the 3A RHR pump was inoperable from July 26, 2017 to September 1, 2017. BFN Technical Specifications (TS) Limiting Condition of Operability (LCO) 3.5.1 Required Action A.1 requires, with one required Emergency Core Cooling System (ECCS) injection/spray subsystem inoperable, that the required ECCS injection/ spray subsystem be restored to operable status within seven days. Additionally, BFN TS LCO 3.6.2.3 Required Action A.1 requires, with one RHR suppression pool cooling subsystem inoperable, restore the RHR suppression pool cooling subsystem to operable status within 30 days. The 3A RHR pump was inoperable for a time longer than allowed by TS. Therefore, The Tennessee Valley Authority (TVA) is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant’s TS. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event No inoperable systems, structures, or components contributed to this event. Page 2 of 8 | ML17304B088
Watts Bar Nuclear Plant | Unit 1 | Multiple Unreported Potential Loss of Safety Function Events Associated with Inoperable Single Train Systems Due to Misinterpretation of Reporting Guidance 5. EVENT DA TE 6. LER NUMBER 7. REPORT DAT E 8. OTHER FACILITIES INVOLVED I I FACILITY NAME DOCKET NUMBER SEQUENTIAL REV MONTH DAY YEAR YEAR MONTH DAY YEAR Watts Bar Nuclear Plant, Unit 2 05000391 NUMBER NO. 06 09 2017 2017 - 007 - 01 11 03 2017 FACILITY NAME DOCKET NUMBER 9. OPERATING MODE 11. THIS REPORT IS SUBMITTED PURSUANT TO THE REQUIREMENTS OF 10 CFR §: (Check all that apply) D D D D 20.2201 (b) 20.2203(a)(3)(i) 50.7 3(a)(2)(ii)(A) 50.7 3(a)(2)(viii)(A) D D D D 20.2201 (d) 20.2203(a)(3)(ii) 50. 73(a)(2)(ii)(B) 50. 73(a)(2)(viii)(B) 1 D D D D 20.2203(a)(1) 20.2203(a)(4) 50.73(a)(2)(iii) 50. 73( a )(2)(ix) (A) D D D D 20.2203(a)(2)(i) 50.36(c)(1 )(i)(A) 50. 73(a)(2)(iv)(A) 50.73(a)(2)(x) D D D D 10. POWER LEVEL 20.2203(a)(2)(ii) 50.36(c)(1 )(ii)(A) 50.7 3(a)(2)(v)(A) 73.71 (a)(4) D D D D 20.2203(a)(2)(iii) 50.36(c)(2) 50.73(a)(2)(v)(B) 73.71 (a)(5) D D f8J D 20.2203(a)(2)(iv) 50.46(a)(3)(ii) 50. 73(a)(2)(v)(C) 73.77(a)(1) 76 D 20.2203(a)(2)(v) D 50.73(a)(2)(i)(A) f8J 50.7 3(a)(2)(v)(D) D 73.77(a)(2)(i) D D D D 20.2203(a)(2)(vi) 50.73(a)(2)(i)(B) 50. 73(a)(2)(vii) 73.77(a)(2)(ii) D D 50. 73(a)(2)(i)(C) OTHER Specify in Abstract below or in NRC Form 366A 12. LICENSEE CONTACT FOR THIS LER LICENSEE CONTACT rELEPHONE NUMBER (Include Area Code) Dean Baker, Licensing Engineer 423-452-4589 13. COMPLETE ONE LINE FOR EACH COMPONENT FAILURE DESCRIBED IN THIS REPORT MANU- REPORTABLE MANU- REPORTABLE CAUSE SYSTEM COMPONENT CAUSE SYSTEM COMPONENT FACTURER TO EPIX FACTURER TO EPIX 14. SUPPLEMENTAL REPORT EXPECTED 15. EXPECTED MONTH DAY YEAR D YES (If yes, complete 15. EXPECTED SUBMISSION DA TE) (8J NO SUBMISSION DATE ABSTRACT (Limit to 1400 spaces, i.e., approximately 15 single-spaced typewritten lines) On June 9, 2017, Watts Bar Nuclear Plant (WBN) personnel determined that the reporting requirements of 10 CFR 50.72(b)(3)(v) and 10 CFR 50.73(a)(2)(v), as clarified by guidance in NUREG-1022, Revision 3, were being incorrectly applied for certain events associated with single train safety systems. When events occurred that resulted in these systems not meeting Technical Specification (TS) Limiting Conditions for Operation (LCO), the short duration of these events relative to their required action completion time, coupled with prompt return to allowable values, were not considered a loss of safety function by Operations and Licensing personnel. As a result, multiple potential loss of safety function events were not reported as required. These events were related to Refueling Water Storage Tank (RWST) level, Containment and Shield Building pressure, and Control Room Envelope integrity. A review of these events indicate, when considering the actual system capability and the response of equipment and personnel, a loss of safety function capability impacting public health and safety did not occur for events associated with the RWST, Containment, Shield Building, or Control Room. Corrective actions include briefing personnel on the regulatory impact of these events, and the importance of the control room boundary. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Watts Bar Nuclear Plant, Unit 1 05000390 NUMBER NO. 2017 007 01 NARRATIVE I. PLANT OPERATING CONDITIONS BEFORE THE EVENT Watts Bar Nuclear Plant (WBN) Unit 1 was at 76 percent rated thermal power (RTP) . WBN Unit 2 was in Mode 5. II. DESCRIPTION OF EVENT A. Event Summary On June 9, 2017, Watts Bar Nuclear Plant (WBN) personnel determined that the reporting requirements of 10 CFR 50. 72(b)(3)(v) and 10 CFR 50. 73(a)(2)(v), as clarified by guidance in NUREG-1022, Revision 3, were being incorrectly applied for certain events associated with single train safety systems. When events occurred that resulted in these systems not meeting Technical Specification (TS) Limiting Conditions for Operation (LCO) for these systems, the short duration of these events relative to their required action completion time, coupled with prompt return to allowable values, were not considered a loss of safety function by Operations and Licensing personnel. As a result, multiple potential loss of safety function events were not reported as required. This event is being reported to the Nuclear Regulatory Commission (NRC) under 10 CFR 50. 73(a)(2)(v)(C) and (D) as an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material and to mitigate the consequences of an accident. B. Inoperable Structures, Components, or Systems that Contributed to the Event Various equipment issues and personnel errors did contribute to the events described in Section VIII of this report. C. Dates and Approximate Times of Occurrences Date Time Event EDT 3/13/17 N/A Condition Report (CR)1273873 generated for Potential Failure to Report Loss of Safety Function 6/09/17 N/A Extent of Condition for CR 1273873 completed for period of 3/17/14 to 3/17 /17. This review incorrectly concludes no failure to report. 6/22/17 N/A Condition Report 1310096 generated to address position on loss of safety function reporting. WBN licensing determines that multiple examples of failure to report have occurred and that the event/discovery date for reporting is 6/09/17. D. Manufacturer and Model Number of Components that Failed During the Event Not applicable. NRC FORM 366A (04-2017) Page _2_ of _9_ NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Watts Bar Nuclear Plant, Unit 1 05000390 NUMBER NO. 2017 007 01 NARRATIVE E. Other Systems or Secondary Functions Affected No other systems or secondary functions were affected. F. Method of discovery of each Component or System Failure or Procedural Error The failure to report these potential loss of safety function events was discovered during an on-going evaluation of this issue by WBN licensing personnel with assistance from other offsite licensing personnel who had been involved in the development of NUREG-1022 Revision 3. G. Failure Mode and Effect of Each Failed Component Individual failures for each event are summarized in Section VIII. H. Operator Actions No operator actions were required at the time, as there were no on-going events. I. Automatically and Manually Initiated Safety System Responses Not applicable. Ill. CAUSE OF THE EVENT A The cause of each component or system failure or personnel error, if known. The cause of the failure to report was an incorrect understanding of the regulation associated with events or conditions that could have prevented fulfillment of a safety function. B. The cause(s) and circumstances for each human performance related root cause. The cause of the failure to report was an incorrect understanding of the regulation associated with events or conditions that could have prevented fulfillment of a safety function in addition to the individual human performance and equipment failures attributed to each event. IV. ANALYSIS OF THE EVENT When events occurred that resulted in single train systems not meeting TS LCO requirements; the short duration of these events relative to their required action completion time were not considered a loss of safety function by Operations and Licensing personnel. During evaluation of this issue, with input from offsite sources, WBN licensing personnel became aware of a letter transmitted by the Nuclear Regulatory Commission (NRG) staff to Exelon Corporation in January 2015 that provides an NRG position on loss of safety function related to single train type systems. This resulted in a reassessment of those events that should have been reported as a potential loss of safety function, considering the guidance of NUREG- 1022 that a report is required when: NRC FORM 366A (04-2017) Page _3_ of _9_ NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Watts Bar Nuclear Plant, Unit 1 05000390 NUMBER NO. 2017 007 01 NARRATIVE "1) there is a determination that the SSC is inoperable in a required mode or other specified condition in the TS Applicability, 2) the inoperability is due to one or more personnel errors, including procedure violations; equipment failures; inadequate maintenance; or design, analysis, fabrication, equipment qualification, construction, or procedural deficiencies, and 3) no redundant equipment in the same system was operable." Reassessment using these criteria identified a number of events related to single train systems. WBN had not reported events related to Refueling Water Storage Tank (RWST) {EllS:TK} level, shield building {EllS: NH} pressure being outside TS limits, containment pressure being outside TS limits, and the control room envelope {EllS:NA} being inoperable due to a boundary door {EllS:DR} inadvertently left open. Each event is described in Section VIII of this report. WBN's assessment of the safety impacts of these events is provided below. 1. With respect to RWST level, three events occurred where the RWST level went below the TS 3.5.4 allowed value. While the level was below that permitted by the TS, the level reduction was very small with respect to the tank volume. The safety function capability of the tank was determined to have been met for design basis events (DBEs). 2. The WBN containment design includes a free standing steel pressure vessel surrounded by a reinforced concrete shield building. The shield building is maintained at a negative pressure during normal operation by non-safety related ventilation systems required to be in operation in Modes 1 -4. In the event of an accident, safety related ventilation systems would filter the exhaust from the shield building, reducing the offsite dose to members of the public from postulated leakage of the containment pressure vessel. On multiple occasions, the pressure in the shield building went outside of TS 3.6.15 allowable limits as a result of equipment failures. While these events are reportable as a potential loss of safety function, evaluation of these events shows that the safety function capability of the shield building, the containment pressure vessel, and the associated ventilation systems would not have been lost. The Emergency Gas Treatment System (EGTS), which would function to filter the exhaust from the shield building, is capable of performing its safety function assuming the shield building is not at a negative pressure as documented in the dose analysis in the UFSAR. In addition, such testing or equipment malfunctions also has impacted containment pressure TS 3.6.4 which specifies the relative pressure limits between the containment and the annulus. The design of the containment pressure vessel bounds any minor pressure transient that may occur during ventilation system transients and its safety function capability would not be lost. 3. The control room envelope (CRE) is required to be operable in Modes 1 through 6. Operability requires integrity of the control room envelope such that it will have a low unfiltered in leakage during accident conditions to maintain the dose to operators within the requirements of 1O CFR 50, General Design Criterion 19. TS allows the CRE boundary to be opened intermittently under administrative control, normally to allow personnel ingress and egress from the control room. Administrative controls in the case of boundary doors are that an individual is in control of the door when it is opened. On multiple occasions, personnel entering and leaving the control room left one of the boundary doors open. This resulted in operations personnel entering TS LCO 3.7.10, Control Room Emergency Ventilation System (CREVS), Condition B for one or more CREVS trains inoperable due to an inoperable CRE boundary. Low positive pressure (less than 0.2 inches of water gauge (WG)) in the control room for 90 seconds results in a control room alarm. Upon receipt of the alarm, operations personnel promptly closed the CRE door. For these events, the time that the CRE boundary was open was approximately four minutes for each event, includin the alarm dela time. The licensin basis at WBN for a loss of coolant accident LOCA assumes NRC FORM 366A (04-2017) Page _4_ of _9_ NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Watts Bar Nuclear Plant, Unit 1 05000390 NUMBER NO. 2017 007 01 NARRATIVE instantaneous core damage and release, and therefore, a potential loss of safety function event for each case occurred. The physics of such an event are that core damage and a containment release would take some period of time much greater than a few minutes. The CRE door would be expected to be closed with high confidence well in advance of an actual radiological release. Most of the door events involved the door being ajar, and under these circumstances simplified, non-surveillance testing has shown that a positive control room pressure would be present. V. ASSESSMENT OF SAFETY CONSEQUENCES The failure to report potential loss of safety function events represents a significant concern from a regulatory standpoint. A review of these events indicate, when considering the actual system capability and the response of equipment and personnel, a loss of safety function capability impacting public health and safety did not occur with respect to the RWST, Shield Building, Containment or the Control Room. A Availability of systems or components that could have performed the same function as the components and systems that failed during the event Availability of systems to perform the required functions is described in Section IV. B. For events that occurred when the reactor was shut down, availability of systems or components needed to shutdown the reactor and maintain safe shutdown conditions, remove residual heat, control the release of radioactive material, or mitigate the consequences of an accident Availability of systems to perform the required functions is described in Section IV. C. For failure that rendered a train of a safety system inoperable, an estimate of the elapsed time from the discovery of the failure until the train was returned to service The time period that systems and equipment were outside of specified TS limits is described in Section VIII of this LER. VI. CORRECTIVE ACTIONS This event was entered into the Tennessee Valley Authority (TVA) Corrective Action Program and is being tracked under Condition Report (CR) 1310096. A Immediate Corrective Actions Upon determining that previous events were reportable, this LER was initiated and developed for submittal. Communication of this reporting issue has occurred within operations and licensing. B. Corrective Actions to Prevent Recurrence or to Reduce Probability of Similar Events Occurring in the Future WBN will brief personnel, including supplementary staff, on the regulatory and nuclear safety impacts related to failure to close the control room boundary doors, and will post door watches as needed. NRG FORM 366A (04-2017) Page _5_ of _9_ NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, '~. .f .t NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means »:t·jc~~ used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR · Watts Bar Nuclear Plant, Unit 1 05000390 NUMBER NO. 2017 007 01 NARRATIVE VII. PREVIOUS SIMILAR EVENTS AT THE SAME SITE On November 11, 2015, WBN Unit 1 failed to enter TS 3.1.8 Condition A which was required when WBN Unit 1 experienced a rod drop event. This was subsequently reported to the NRC as a condition prohibited by TS in LER 390-2016-007 on June 20, 2016. This event is similar in that licensing personnel incorrectly interpreted requirements related to how to comply with TS 3.1.8. VIII. POTENTIAL LOSS OF SAFETY FUNCTION EVENTS FOR PREVIOUS THREE YEARS A summary of potential loss of safety function events over the last three years is provided below: Events related to TS LCO 3.5.4 for the Refueling Water Storage Tank less than 370,000 gallons Date Time Condition Summary Report 3/24/14 0435 864251 Entry into TS LCO 3.5.4.B when level in the RWST went below TS minimum of 370,000 gallons with Unit 1 in Mode 4. Exited LCO when Unit 1 entered Mode 5 at 0620 on March 24, 2014. Due to other equipment issues, a decision was made to use the RWST to provide a Reactor Coolant System (RCS) makeup water source during cooldown. 7/7/14 1255 907544 Entry into TS LCO 3.5.4.B when level in the RWST went below TS minimum of 370,000 gallons. A leak from the suction side of the Refueling Water Purification Pumps was isolated and the Unit 1 RWST was refilled. The LCO condition was exited on July 7, 2014 at 1320. 6/5/16 1230 1317307 Entry into TS LCO 3.5.4 Condition B when level in the RWST went below TS minimum of 370,000 gallons due to a reactor trip with safety injection (SI) on WBN Unit 2. Exited TS LCO 3.5.4 Condition B on June 5, 2016 at 1622 when the RWST was above TS minimum level. The trip with SI was reported to the NRC in LER-391-2016-004 on August 4, 2016. Events related to TS LCO 3.6.4 for Containment Pressure outside range of greater than of equal to -0.1 psid and less than or equal to +0.3 psid relative to the annulus Date Time Condition Summary Report 7/14/16 1307 1317307 Entry into TS LCO 3.6.4 condition A when the containment pressure was less than -0.1 psid relative to the annulus following the loss of power to the annulus vacuum fans. TS LCO 3.6.4 Condition A was exited on July 14, 2016 at 1354. This was subsequently determined to not be reportable because this occurred during a planned evolution performed using approved plant procedures. 3/13/17 1558 1273873 Entry into TS LCO 3.6.4 condition A when the containment pressure was less than -0.1 psid relative to the annulus during Auxiliary Building Gas Treatment System (ABGTS) Pressure Test of Train B. TS LCO 3.6.4 Condition A was exited On March 13, 2017 at 1613. NRC FORM 366A (04-2017) Page _6_ of _9_ NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR NUMBER NO. Watts Bar Nuclear Plant, Unit 1 05000390 2017 - 007 - 01 NARRATIVE Events related to TS LCO 3.6.15 Condition B for annulus pressure requirement not met for the Shield Building. SR 3.6.15.1 requires annulus to be greater than -5 inches WG with respect to atmosphere Date Time Condition Summary Report 3/12/15 1133 998890 Entry into TS 3.6.15 Condition B for annulus pressure not within limits (more negative than -5 inches WG) due to dropping below -5.5 inches WG because 1-FC0-65-49 Annulus Vacuum normal control damper not controlling properly. Annulus pressure restored at 1305. 9/13/15 1025 1317307 Entry into TS 3.6.15 Condition B for annulus pressure not within limits due to pressure transient from initiating an Auxiliary Building Isolation (ABI) for U2 testing. LCO 3.6.15 was exited at 1031. This was subsequently determined to not be reportable because this occurred during a planned evolution performed using approved plant procedures. 6/2/16 1512 1177619 Entry into TS 3.6.15 Condition B for annulus pressure not within limits due to failure of 2-FC0-65-45 to open during 2-Sl-99-303-B. Exited LCO 3.6.15 at 1518. 6/5/16 1240 1317307 Shield building pressure less than -5 in WG due to U2 Reactor Trip with SI. Exited condition at 1242 on June 5, 2016. The trip with SI was reported to the NRG in LER-391-2016-004 on August 4, 2016. 7/14/16 1303 1317307 Shield building pressure less than -5 in WG due to Loss of Power Power Ascension Test (PAT). TS LCO 3.6.15 Condition B not entered into plant logs. Exited condition at 1438 on July 14, 2016 when annulus pressure was greater than -5 in WG. This was subsequently determined to not be reportable because this occurred during a planned evolution for power ascension performed using approved plant procedures. -14-45- -·3/1117- - --1317307 Entry into TS LCO 3.6.15 Condition A and B for annulus not more negative than -5 inches WG due to transient caused by storm front moving through area. Exited TS LCO 3.6.15 Condition A and B on March 1, 2017 at 1446. 3/13/17 1558 1272164/ Shield building pressure less than -5 in WG due to ABGTS testing (No 1272224 entry into LCO 3.6.15 Condition B logged). Exited condition at 1812 on March 13, 2017. Events related to TS LCO 3.7.1O for the Control Room Emergency Ventilation System (CRE boundary breached) Note: The control room pressure alarm comes in after a 90 second delay. Date Time Condition Report Summary (Alarm) 3/23/14 0424 862708 Boundary door closed by 0427 3/30/14 0951 866226 Boundary door closed by 0953 5/31/14 0157 894134 Boundary door closed by 0159 6/14/14 0915 899633 Boundary door closed by 0917 6/23/14 1135 903067 Boundary door closed by 1140 7/10/14 1255 909000 Boundary door closed by 1257 7/11/14 1014 910194 Boundary door closed by1016 NRC FORM 366A (04-2017) Page _7_ of _9_ NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send ,f~,-~·f· ""'"'·~\ comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to ~· ~ lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, o '-<; . -;,...~~**~"'./ii - > ~ : CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Watts Bar Nuclear Plant, Unit 1 05000390 NUMBER NO. 2017 - 007 - 01 NARRATIVE Date Time Condition Report Summary (Alarm) 7/19/14 0822 912154 Boundary door closed by 0823 8/22/14 1740 1317307 /132644 7 Boundary door closed by 17 43 8/23/14 2240 1317307 /132644 7 Boundary door closed by 2246 10/21/14 0708 948571 Boundary door closed by 0710 11 /7/14 1722 1317307 /132644 7 Boundary door closed by 1725 12/15/14 1245 967964 Boundary door closed by 1247 1/18/15 0703 979264 Boundary door closed by 0705 2/3/15 1305 985860 Boundary door closed by 1306 2/8/15 0726 986637 Boundary door closed by 0727 2/11 /15 0603 988464 Boundary door closed by 0605 3/15/15 1242 1000413 Boundary door closed by 1244 3/25/15 1924 1317307/1326447 Boundary door closed by 1925 6/15/15 1502 1040054 Boundary door closed by 1504 7/21 /15 1918 1317307 /132644 7 Boundary door closed by 1922 7/22/15 2100 1061510 Boundary door closed by 2103 8/18/15 0427 1071973 Boundary door closed by 0429 10/13/15 0751 1092726 Boundary door closed by 0753 10/31/15 0240 1099526 Boundary door closed by 0242 10/31 /15 1358 1099592 Boundary door closed by1360 11/14/15 0728 1104089 Boundary door closed by 0731 12/5/15 2207 1112234 Boundary door closed by 2210 1/ 4/16 1053 1121123 Boundary door closed by 1055 1/22/16 0332 1127775 Boundary door closed by 0334 1/ 22/16 2247 1128181 Boundary door closed by 2250 1/26/16 0550 1129073 Boundary door closed by 0552 1/26/16 2005 1129477 Boundary door closed by 2007 2/15/16 1102 1137634 Boundary door closed by 1104 4/20/16 1827 1162773 Boundary door closed by 1830 4/27/16 2334 1317307 /132644 7 Boundary door closed by 2337 5/12/16 2134 1170567 Boundary door closed by 2141 6/29/16 1951 1187273 Boundary door closed by 1954 7/ 30/16 0404 1197627 Boundary door closed by 0406 10/21/16 1409 1225143 Boundary door closed by 1412 3/20/17 0120 1274363 Boundary door closed by 0122 3/21 /17 0900 1275203 Boundary door closed by 0902. The Control room door was undergoing minor maintenance. Maintenance personnel were in control of the door durinq this activity. 4/6/17 1620 1281767 Boundary door closed by 1623 5/13/17 1408 1295376 Boundary door closed by 1410 IX. ADDITIONAL INFORMATION None. NRC FORM 366A (04-2017) Page _8_ of _9_ NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Watts Bar Nuclear Plant, Unit 1 05000390 NUMBER NO. 2017 007 01 NARRATIVE X. COMMITMENTS None. NRC FORM 366A (04-2017) Page _9_ of _9_ | 11-03-2017 | On June 9, 2017, Watts Bar Nuclear Plant (WBN) personnel determined that the reporting requirements of 10 CFR 50.72(b)(3)(v) and 10 CFR 50.73(a)(2)(v), as clarified by guidance in NUREG-1022, Revision 3, were being incorrectly applied for certain events associated with single train safety systems. When events occurred that resulted in these systems not meeting Technical Specification (TS) Limiting Conditions for Operation (LCO), the short duration of these events relative to their required action completion time, coupled with prompt return to allowable values, were not considered a loss of safety function by Operations and Licensing personnel. As a result, multiple potential loss of safety function events were not reported as required. These events were related to Refueling Water Storage Tank (RWST) level, Containment and Shield Building pressure, and Control Room Envelope integrity. A review of these events indicate, when considering the actual system capability and the response of equipment and personnel, a loss of safety function capability impacting public health and safety did not occur for events associated with the RWST, Containment, Shield Building, or Control Room. Corrective actions include briefing personnel on the regulatory impact of these events, and the importance of the control room boundary. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Watts Bar Nuclear Plant, Unit 1 05000390 NUMBER NO. 2017 007 01 | I. PLANT OPERATING CONDITIONS BEFORE THE EVENT Watts Bar Nuclear Plant (WBN) Unit 1 was at 76 percent rated thermal power (RTP) . WBN Unit 2 was in Mode 5. II. DESCRIPTION OF EVENT A. Event Summary On June 9, 2017, Watts Bar Nuclear Plant (WBN) personnel determined that the reporting requirements of 10 CFR 50. 72(b)(3)(v) and 10 CFR 50. 73(a)(2)(v), as clarified by guidance in NUREG-1022, Revision 3, were being incorrectly applied for certain events associated with single train safety systems. When events occurred that resulted in these systems not meeting Technical Specification (TS) Limiting Conditions for Operation (LCO) for these systems, the short duration of these events relative to their required action completion time, coupled with prompt return to allowable values, were not considered a loss of safety function by Operations and Licensing personnel. As a result, multiple potential loss of safety function events were not reported as required. This event is being reported to the Nuclear Regulatory Commission (NRC) under 10 CFR 50. 73(a)(2)(v)(C) and (D) as an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material and to mitigate the consequences of an accident. B. Inoperable Structures, Components, or Systems that Contributed to the Event Various equipment issues and personnel errors did contribute to the events described in Section VIII of this report. C. Dates and Approximate Times of Occurrences Date Time Event EDT 3/13/17 N/A Condition Report (CR)1273873 generated for Potential Failure to Report Loss of Safety Function 6/09/17 N/A Extent of Condition for CR 1273873 completed for period of 3/17/14 to 3/17 /17. This review incorrectly concludes no failure to report. 6/22/17 N/A Condition Report 1310096 generated to address position on loss of safety function reporting. WBN licensing determines that multiple examples of failure to report have occurred and that the event/discovery date for reporting is 6/09/17. D. Manufacturer and Model Number of Components that Failed During the Event Not applicable. | ML17310A105
YEAR SEQUENTIAL REV | Unknown Unit | Non-Functional Mechanical Draft Cooling Tower Fan Brakes Leads to HPCI Being Declared Inoperable and Loss of Safety Function | 11-03-2017 | At 1000 EDT on September 9, 2017, the Division 2 Mechanical Draft Cooling Tower (MDCT) fans were declared inoperable due to loss of output from the over speed fan brake inverter. The MDCT fans are required to support operability of the Ultimate Heat Sink (UHS) and the Emergency Equipment Cooling Water (EECW) system. The Division 2 EECW system cools the High Pressure Coolant Injection (HPCI) system room cooler. As a result, the non-functionality of the fan brakes lead to an unplanned HPCI inoperability. Since HPCI is a single train system designed to mitigate the consequences of a loss of coolant accident (LOCA), this event could have prevented the fulfillment of a safety function. The cause of the event was the failure of the Division 2 fan brake inverter. Corrective Actions were taken to replace the inverter and returning the MDCT fans, the UHS, EECW and HPCI to service on September 9, 2017 at 2351 EDT. A failure modes evaluation was performed by the vendor with no direct cause of the failed output determined. The fan brake system is only required for a design basis tornado and there was no credible tornado threat during this event. The HPCI system is not required to mitigate a design basis tornado. The safety significance of this event is very low and there were no radiological releases associated with this event. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000- NUMBER NO. Fermi 2 341 2017 - 005 - 00 | INITIAL PLANT CONDITIONS Mode – 1 Reactor Power – 100 percent There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT At 1000 EDT on September 9, 2017, the Division 2 Mechanical Draft Cooling Tower (MDCT) [CTW] fans [FAN] were declared inoperable due to loss of output from the over speed fan brake [BRK] inverter [INVT]. The brakes prevent the fans from experiencing over speed from a design basis tornado as described in Updated Final Safety Analysis Report (UFSAR) Section 9.2.5.2.2. The MDCT fans are required to support operability of the Ultimate Heat Sink (UHS) [BS]. The UHS is required to support operability of the Division 2 Emergency Equipment Cooling Water (EECW) system. The EECW system cools various safety related components, including the High Pressure Coolant Injection (HPCI) [BJ] system room cooler [CLR]. As a result, the non-functionality of the fan brakes lead to an unplanned HPCI inoperability based on the inoperability of the EECW to the HPCI room cooler. Following restoration of the brake inverter, HPCI was declared operable on September 9 at 2351 EDT. Therefore, the single train HPCI system was inoperable for approximately 14 hours. This report is being made pursuant to 10CFR50.73(a)(2)(v)(D) as a condition that could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident. Technical Specification 3.7.2 requires the UHS reservoir to be operable in Modes 1, 2, and 3. The UHS operability requirements in Modes 4 and 5 are determined by the systems the UHS supports. The UHS reservoir is divided into two one-half capacity reservoirs, corresponding to Division 1 and Division 2. Each reservoir is the cooling source for that division's service water subsystems, including the service water for the Emergency Diesel Generators (EDGs) [[DG]]. A two-cell MDCT is located above each of the one-half capacity reservoirs. Each cell is equipped with a MDCT fan. Two MDCT fans above each one-half capacity reservoir are required for it to be considered operable. The "A" and "C" MDCT fans are in Division 1 and the "B" and "D" fans are in Division 2. The MDCT fans have a brake system to prevent overspeed from a design basis tornado as described in UFSAR Section 9.2.5.2.2. Thus the fan brakes are a design feature of the fans and their functionality impacts the operability of the MDCT fans and therefore the UHS. The brake mechanism senses the speed of the motor and blades and uses nitrogen pressure to activate a brake system to slow the fan speed. The control power for this braking control module is powered by the R1700S011B (Division 2 Residual Heat Removal (RHR) MDCT Fans overspeed Brake Inverter). Without this inverter being energized, neither of the Division 2 MDCT fan brakes would perform their design function. Therefore, this inverter failure renders both of the Division 2 MDCT fans inoperable. A past operability review was performed and concluded that the MDCT Brake Inverter Panel R1700S011B was discovered to be indicating no AC Volts or Amps during daily rounds on September 9, 2017 at 1000. An Operator records the output voltage daily and it was observed that the output voltage was within acceptable limits on September 8, 2017 at 0958. This measurement is consistent with the readings for the previous 4 days. Thus, the inverter was observed to be functioning 24 hours before discovery and the maximum possible period of inverter failure prior to discovery is approximately 24 hours. A review verified that the Division 1 UHS and RCIC systems were operable during the possible period of inverter failure, as well as during the period when Division 2 UHS and HPCI were declared inoperable. Therefore, there was not a violation of Technical Specifications and Licensing Basis due to this condition. TS 3.7.2 Condition B allows for 72 hours of | ML17310A167
YEAR SEQUENTIAL REV | Unknown Unit | Valve Closure Results in Momentary Increase in Secondary Containment Pressure | 11-09-2017 | On September 12, 2017 at 1227 PDT, Secondary Containment became inoperable due to pressure increasing above the Technical Specification limit of -0.25 inches of water gauge. While the plant was at 100% power, a Reactor Building exhaust valve and supply valve unexpectedly lost power and closed, resulting in a loss of Secondary Containment for approximately one minute. While Technical Specification limits were exceeded for this short time period, the resulting pressure excursion was bounded by analytical results; and thus, there were no safety consequences for this condition. This event was reported under 10 CFR 50.72(b)(3)(v)(C) and 10 CFR 50.72 (b)(3)(v)(D) as Event Notification #52966. The apparent cause of the event was that station personnel did not deliberately and conservatively perform work tasks. Workers failed to update work instructions when work was rescheduled, and did not verify power sources at the work site. Corrective actions for this event include conducting a workshop on management expectations of Maintenance, increased management oversight, and addressing human performance issues. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000- NUMBER NO. Columbia Generating Station 397 2017 - 005 - 00 | Plant Conditions At the time of the event, the plant was operating in Mode 1 at 100% power. There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. Event Description On September 12, 2017 at 1227 PDT, Operations personnel received trouble alarms for the Off Gas System [WF], Fuel Pool Cooling System [DA], and Condensate Blowdown System [SD]. A Reactor Building [NG] exhaust valve [ISV] and supply valve [ISV] closed due to a loss of power. Concurrently, station electricians called to report an electrical spark while replacing the motor control center bucket [MCC] for the Reactor Core Isolation Cooling [BN] vacuum pump [P]. For a time period of approximately one minute, Secondary Containment differential pressure increased above -0.25 inches of water gauge (inwg), resulting in Technical Specification (TS) Surveillance Requirement 3.6.4.1.1 not being met. This event is reportable as an event that could have prevented fulfillment of safety functions needed to control the release of radiation, and mitigate the consequences of an accident per 10 CFR 50.73(a)(2)(v)(C) and 10 CFR 50.73(a)(2)(v)(D). This condition was reported under 10 CFR 50.72(b)(3)(v)(C) and 10 CFR 50.72(b)(3)(v)(D) via Event Notification #52966 for an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material, and needed to mitigate the consequences of an accident. Immediate Corrective Actions Operations personnel took manual control of the Reactor Building exhaust air controller [DCC] and restored Reactor Building differential pressure to normal. Both the supply and exhaust valves were re-opened, and the Reactor Building exhaust air controller was then returned to automatic function. Assessment of Safety Consequences This event resulted in an unplanned entry into TS Action Statement 3.6.4.1.A, in which Secondary Containment pressure was greater than -0.25 inwg for approximately one minute. The peak pressure during this event was -0.18 inwg. While the actual pressure was beyond the range allowed by Technical Specifications, the purpose of maintaining a slight vacuum is to assist in drawdown of secondary containment to support accident response of the safety related Standby Gas Treatment [BH] (SGT) system. Existing engineering analysis demonstrates that for this event, the drawdown credited in Columbia's accident analysis could have been attained using either of the two available trains of the SGT system, thus there were no potential safety consequences. There was no actual safety consequence associated with this event since there was no loss of safety function and no potential for radiological release. Cause of Event The apparent cause of the event was that station personnel did not deliberately and conservatively perform work tasks. Workers failed to update work instructions when work was rescheduled, and did not verify power sources at the work site. | ML17313A741
Browns Ferry Nuclear Plant | Unit 1 | Safety System Functional Failures Due to the lnoperability of Both Unit 1 and 2 Control Bay Chillers | 11-09-2017 | On September 9, 2017, at 1520 Central Daylight Time (CDT), Operations personnel declared Unit 1/2 Control Bay (CB) Chiller (CHLR) A inoperable after observing that its outlet water temperature exceeded its specified limits. On September 10, 2017, at 1151 CDT, the Unit 1/ 2 CB CHLR B was declared inoperable after failing to start and providing a flashing error code to an operator in the field. The concurrent inoperability of both Unit 1/ 2 CB CHLRs required Browns Ferry Nuclear Plant (BFN) to declare the immediate inoperability of the electrical equipment in the affected electric board rooms, including all four Unit 1/ 2 4160 V Shutdown Boards, resulting in a Safety System Functional Failure, and entry into Technical Specifications (TS) Limiting Conditions for Operation (LCO) 3.0.3 for BFN, Units 1, 2, and 3. On September 10, 2017, at 2110 CDT, the Unit 1/2 CB CHLR B was restored to operable status following a capacitor replacement, and LCO 3.0.3 was exited. The Unit 1/2 CB CHLR A failure was caused by a thermistor failure, likely due to a break in the cable system. The Unit 1/2 CB CHLR B failure was due to a capacitor failing to hold its charge. Corrective actions include changing the preventive maintenance frequency interval for CB CHLR capacitor replacement from 10 years to 4 years. In addition, the concurrent Unit 1/2 CB CHLR failures were caused by a design which lacked defense-in- depth, where removing one Unit 1/2 CB CHLR from service for unplanned corrective maintenance created a single-point failure risk. A design change has been proposed to install a cross-tie between the Unit 3 Chillers and the Unit 1/2 Chillers to provide cooling in the event that Unit 1/2 CB CHLR A and B were to both become inoperable. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Browns Ferry Nuclear Plant, Unit 1 05000-259 2017 -004 - 00 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Units 1, 2, and 3, were in Mode 1 at 100 percent power. II. Description of Event A. Event Summary On September 9, 2017, at 1520 Central Daylight Time (CDT), Operations personnel observed that the outlet water temperature on Unit 1/2 Control Bay (CB) Chiller (CHLR) [CHU] A exceeded its specified limits. Unit 1/ 2 CB CHLR A was then declared inoperable for troubleshooting on September 9, 2017. The inoperability of Unit 1/2 CB CHLR A required BFN, Units 1 and 2, to enter Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.4, Control Room Air Conditioning (AC) System, Condition A. On September 10, 2017, at 1151 CDT, Unit 1/2 CB CHLR B failed to start, and an operator in the field noted a flashing error code. Operations personnel noted that the A Compressor on Unit 1/ 2 CB CHLR B was not running, and was not warm to the touch. Operations personnel declared Unit 1/ 2 CB CHLR B inoperable at this time. The concurrent inoperability of both Unit 1/2 CB CHLRs required Browns Ferry Nuclear Plant (BFN) to declare the immediate inoperability of the electrical equipment in the affected electric board rooms, including all four Unit 1/2 4160 V (4kV) Shutdown Boards (SD BDs) [ECBD]. This resulted in multiple TS LCO and Technical Requirements Manual (TRM) LCO entries and a Safety System Functional Failure for safety systems on all three Units. The concurrent inoperability of Unit 1/2 CB CHLRs A and B also required BFN, Units 1 and 2, to enter TRM LCO 3.7.6, Electric Board Room Air Conditioning (AC) System, Condition B. This LCO requires the unit, with two Unit 1/2 electric board room AC subsystems inoperable, to declare the electrical equipment in the electric board rooms inoperable immediately. In particular, this event resulted in the loss of two trains of Standby Gas Treatment (SGT) [BH], which required entry into TS LCO 3.0.3 for BFN, Units 1, 2, and 3. As a result of the unplanned entry into TS LCO 3.0.3, all three BFN Units were required to be in Mode 2 by 2151 CDT on September 10, 2017. The NRC Headquarters Office granted BFN an Enforcement Discretion from complying with TS LCO 3.0.3, Condition A, which extended the time to shutdown by 12 hours and 9 minutes, such that all three Units were now required to either exit TS LCO 3.0.3 or be in Mode 2 by 1000 CDT on September 11, 2017. On September 10, 2017 at 1945 CDT, the Tennessee Valley Authority (TVA) submitted an 8-hour event notification (EN) to the NRC in accordance with 10 CFR 50.72(b)(3)(v)(A)/(B)/(C)/(D), as any event or condition that could have prevented the fulfillment of the safety function of structures or | ML17313A848
YEAR SEQUENTIAL REV | Unknown Unit | CONDITION PROHIBITED BY TECHNICAL SPECIFICATIONS DUE TO INCOMPLETE ACTION STATEMENT | 11-09-2017 | On September 21, 2017 at 0800 PDT, Columbia Generating Station declared number 2 Diesel Generator inoperable for maintenance and entered Technical Specification Action Statement (TSAS) 3.8.1, Condition B for One Required Diesel Generator inoperable. At 0821 PDT and again at 1537 PDT Surveillance Requirement 3.8.1.1 was performed per action statement B.1. At 2315 PDT it was noted by operations that a page was missing from the surveillance procedure for both occurrences and determined that the action statement was not met within the required action time. Operations entered TSAS 3.8.1, Condition F for Required Action and associated Completion Time of Condition B not being met. AT 2321 PDT SR 3.8.1.1 was performed satisfactorily and Condition F was exited. The apparent cause was a failure to page check the surveillance procedure prior to use. Initiatives have been developed to reinforce existing standards and improve human performance. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) Operation or Condition Prohibited by Technical Specifications. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear CONTINUATION SHEET Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000- NUMBER NO. Columbia Generating Station 397 2017 - - 006 00 | PLANT CONDITIONS At the time of the event, Columbia Generating Station (Columbia) was in Mode 1 operating at 100% reactor power. Number 2 Diesel Generator [EK] [DG] (DG2) was out of service. EVENT DESCRIPTION On September 21, 2017 at 0800 PDT, Columbia declared DG2 inoperable for maintenance and entered Technical Specification Action Statement (TSAS) 3.8.1, Condition B for One Required Diesel Generator inoperable. At 0821 PDT and again at 1537 PDT Surveillance Requirement (SR) 3.8.1.1 was performed to satisfy TSAS 3.8.1, Condition B action statement B.1. At 2315 PDT it was noted by operations that a page was missing from the surveillance procedure used to satisfy SR 3.8.1.1. For both occurrences the action statement was not met within the required action time. Operations entered TSAS 3.8.1, Condition F for Required Action and Associated Completion Time of Condition B not being met. AT 2321 PDT SR 3.8.1.1 was performed satisfactorily and TSAS 3.8.1 Condition F was exited. CAUSE The direct cause was due to pages sticking together when the surveillance procedure was being copied for use. The apparent cause was the failure to perform a page check of the procedure prior to use. The contributing cause was the reviewing supervisors failure to verify completeness and accuracy of the surveillance once it was completed. EXTENT OF CONDITION A review of recently performed on demand procedures was conducted and no instances of missing pages was noted. COMPLETED CORRECTIVE ACTIONS Missing pages were added, the procedure was performed, and SR 3.8.1.1 was completed satisfactorily. Individual contributor culpability was evaluated and initiatives were developed to reinforce existing standards for performing page checks and to improve human performance. PLANNED CORRECTIVE ACTIONS Brief operations personnel on lessons learned from the event. ASSESSMENT OF SAFETY CONSEQUENCES The off site power alignment surveillance is performed to ensure the electrical system will function as designed when required. The missing page of the surveillance contains steps that must be performed to satisfy a TS surveillance requirement. Since these steps were not performed within the required time frame, the station did not meet the required action of the Limiting Condition for Operation (LCO) to perform SR 3.8.1.1. Compliance with LCOs is necessary to ensure | ML17313A938
Brunswick Steam Electric Plant (BSEP) | Unit1 | Emergency Diesel Generator and Primary Containment Isolation System Actuations | 11-15-2017 | On September 17, 2017, at 0938 Eastern Daylight Time (EDT), a momentary power interruption to Emergency Bus E4 occurred during planned surveillance activities involving Emergency Diesel Generator (EDG) 4. This occurred when EDG 4 was disconnected from Emergency Bus E4 and offsite power was not supplying the bus. EDG 4 automatically transferred from manual mode to automatic control and reconnected to Emergency Bus E4. Normal frequency and voltage were restored with EDG 4 in automatic control. The momentary power interruption to Emergency Bus E4 resulted in various Unit 2 Primary Containment Isolation System (PCIS) actuations. The affected equipment responded as designed. The direct cause of this event was that Operators were not aware that, at the time of the event, Emergency Bus E4 was being supplied solely by EDG 4. As a result of a failed under-frequency relay, the incoming line and feeder breakers from Balance of Plant (BOP) Bus 2C to Emergency Bus E4 had opened during the performance of the EDG 4 surveillance, leaving only EDG 4 to power Emergency Bus E4 in the manual mode of operation. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant (BSEP) YEAR 05000325 NUMBER NO. Unit 1 2017 - 004 - 00 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. Background Initial Conditions At the time of the event, Unit 1 and Unit 2 were in Mode 1 at approximately 100 percent of rated thermal power (RTP). Reportability Criteria This event resulted in the automatic actuation of Emergency Diesel Generator (EDG) 4 [EK] and various Primary Containment Isolation System (PCIS) [JM] actuations. As such, this event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in valid actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B). The NRC was initially notified of this event on September 17, 2017 (i.e., Event Number 52974). Due to the shared configuration of the onsite AC Electrical Distribution System [EB], this event is applicable to both Units 1 and 2. Event Description On September 17, 2017, Unit 2 Operators were conducting a surveillance of EDG 4 in accordance with 0PT-12.2D, No. 4 Diesel Generator Monthly Load Test. As part of this surveillance, EDG 4 was started in the manual mode of operation and synchronized to the grid via Emergency Bus E4. Operators observed unexpected loading and drops in frequency and voltage following closure of the EDG 4 output breaker. As a result, the decision was made to back out of the ongoing surveillance. When the EDG 4 output breaker was opened, at 0938 Eastern Daylight Time (EDT), a momentary power interruption to Emergency Bus E4 occurred. EDG 4 automatically transferred from manual mode to automatic control and reconnected to Emergency Bus E4. Normal frequency and voltage were restored with EDG 4 in automatic control. The momentary power interruption to Emergency Bus E4 resulted in the partial actuation of Unit 2 PCIS Group 1, Group 2, Group 8, and Group 10; and a full actuation of PCIS Group 3 and Group 6. The affected equipment responded as designed. In addition, Unit 2 Reactor Building Ventilation System [VA] isolation (i.e., Secondary Containment isolation), and the automatic start of Standby Gas Treatment System [BH] occurred. These systems functioned as designed. Per design, no Unit 1 PCIS actuations occurred. Unit 1 Conventional Service Water (CSW) System [KG] pump 1A and Unit 2 CSW pump 2B, which are powered from Emergency Bus E4, tripped, which resulted in the automatic start of CSW pump 1B. These systems functioned as design. EDG 4 continued to supply power to Emergency Bus E4 while troubleshooting was conducted to determine the cause of the electrical transient. Offsite power was restored to Emergency Bus E4 at 0023 EDT on September 18, 2017. | ML17319A432
Point Beach Nuclear Plant | Unit 1 | Control Room Barrier Inadvertently Disabled | 11-16-2017 | At 1724 [COT] on 9118117 Door-061, South Control Room Door (DR) was inadvertently disabled. The door became wedged open against its backstop during control room ventilation testing. Door-061 is a barrier that functions to maintain the control room envelope (NA). The barrier was subsequently disengaged from the backstop allowing it to close. The door was inspected and returned to operable status at 1750 [COT]. While the door was stuck open, the control room was in an unanalyzed condition, a condition that could have prevented fulfillment of a safety function, and a common cause inoperability of independent trains or channels. This event is being reported pursuant to 10 CFR 50. 73(a)(2)(ii)(B), 10 CFR 50. 73(a)(2)(v)(A), 10 CFR 50. 73(a)(2)(v)(D), and 10 CFR 50.7 3(a)(2)(vii) for a degraded barrier that affected the control room envelope. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported /~··~"·'·;;~_ lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) • 'i comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear \~. ....~ ~ Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http://www.nrc.gov/reading-rm/doc-collectionslnureqs/staff/sr1 022/r3D NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Point Beach Nuclear Plant Unit 1 05000266 NUMBER NO. 2017 001 00 | Description of the Event: At 1724 [COT] on 9/18/17 Door-061, South Control Room Door was inadvertently disabled. Door-061 is a barrier that functions to maintain the control room envelope during design basis accidents, events, and conditions (Safe Shutdown I High Energy Line Break I Fire I Flood). The barrier became wedged open against its backstop during control room ventilation testing. The barrier was subsequently disengaged from the backstop allowing it to close. The door was inspected and returned to operable status at 1750 [COT]. While the door was stuck open, the control room was in an unanalyzed condition, a condition that could have prevented fulfillment of a safety function, and a common cause inoperability of independent trains or channels. This event is being reported pursuant to 10 CFR 50.73(a)(2)(ii)(B), 10 CFR 50.73(a)(2)(v)(A), 10 CFR 50.73(a)(2)(v)(D), and 10 CFR 50.73(a)(2)(vii) for a degraded barrier that affected the control room envelope. This 60 day licensee event report is being submitted in accordance with the following requirements; 10 CFR 50. 73(a)(2)(ii)(B), any event or condition that results in the condition of the nuclear power plant being in an unanalyzed condition; 10 CFR 50.7 3(a)(2)(v)(A) and 10 CFR 50. 73(a)(2)(v)(D), any event or condition that could have prevented fulfillment of a safety function of structures or systems needed to shut down the reactor and maintain it in a safe shutdown condition or mitigate the consequences of an accident; 10 CFR 50.73(a)(2)(vii), any event where a single cause or condition caused at least one independent train or channel to become inoperable in multiple systems or two independent trains or channels to become inoperable in a single system; Where, the functions supported by the disabled barrier could not be found acceptable under all design basis accidents, events or conditions. Cause of the Event: The cause of the inadvertent degraded barrier was a less than adequate door stop design to control the barrier during ingress/egress activities of the control room envelope with a simultaneous differential pressure transient of the control room ventilation during testing. Analysis of the Event: Technical Specifications permit intermittent opening of the control room envelope boundaries under administrative controls. While the barrier was disabled, the boundary was unable to be rapidly closed. An engineering evaluation of the inadvertently disabled barrier determined the functions supported by the barrier could not be found acceptable under all design basis accidents, events and conditions. The less than adequate door stop design led to inadequate administrative control of the barrier during ingress/egress activities of the control room envelop with the simultaneous differential pressure transient of the control room ventilation during testing. The disabled barrier was promptly enabled, restoring the control room envelope support function. Corrective Actions: The disabled barrier was promptly enabled, restoring the control room envelope support function, and the door stop was modified with a more robust design. Additionally, an extent of condition review was completed and | ML17320A010
Quad Cities Nuclear Power Station | Unit 1 | Control Room Emergency Ventilation Air Conditioning Piping Refrigerant Leak Due to High Cycle Fatigue | 11-17-2017 | On 09/21/2017 at 1550, Operations started Control Room Emergency Ventilation (GREV) Air Conditioning (AC) for Tracer Gas Testing. Per Operations instructions, Mechanical Maintenance went to inspect the Control Room Emergency Ventilation system for refrigerant leaks before Tracer Gas Testing was started. Mechanical Maintenance reported a refrigerant leak on the discharge piping of the compressor, right above the inlet to the condenser. The leak was at the expansion joint of a fitting. The safety significance of this event was minimal. The cause of the refrigerant leak on the Control Room Emergency Ventilation compressor discharge pipe fitting into the condenser was due to high cycle fatigue. The corrective action was to replace the failed Control Room Emergency Ventilation compressor discharge pipe fitting. The GREV AC system is a single train system. Given the impact on the GREV AC system, this report is submitted in accordance with the requirements of 10 CFR 50.73(a)(2}(v}(D}, which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mai to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currentty valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-colfections/nureqs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Quad Cities Nuclear Power Station Unit 1 05000254 NUMBER NO. 2017 - 003 - 00 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Control Room Emergency Ventilation Air Conditioning Compressor Discharge Pipe Fitting Refrigerant Leak A. CONDITION PRIOR TO EVENT Unit: 1 Event Date: September 21, 2017 Event Time: 1550 hours Reactor Mode: 1 Mode Name: Power Operation Power Level: 100% B. DESCRIPTION OF EVENT On 09/21/2017 at 1550, Operations started Control Room Emergency Ventilation (CREV) Air Conditioning (AC)[CMP] for Tracer Gas Testing. Per Operations instructions, Mechanical Maintenance went to inspect the Control Room Emergency Ventilation system for refrigerant leaks before Tracer Gas Testing was started. Mechanical Maintenance reported a refrigerant leak on the discharge piping [PSF] of the compressor, right above the inlet to the condenser [COND]. The leak was at the expansion joint of a fitting. Operations declared the refrigeration condensing unit (RCU) of Train B of Control Room HVAC inoperable at 1730 and entered Technical Specification (TS) 3.7.5 Condition A. The refrigerant leak was minimal, which allowed the Air Conditioning Compressor to run and maintain Control Room Temperature before it was secured. This event is a Maintenance Rule Functional Failure for the Control Room Emergency Ventilation system. C. CAUSE OF EVENT The cause of the refrigerant leak on the Control Room Emergency Ventilation Air Conditioning compressor discharge pipe fitting was due to a high cycle fatigue crack that initiated at the root of expansion joint transition on the outer surface. No material anomalies were associated with the crack origin. The compressor discharge piping is approximately five linear feet in length with two 90-degree bends and enters the condenser at a 45-degree angle. Adding a support to the short length of pipe would not reduce the vibrations or stress acting on the pipe. A contributing factor to the high cycle fatigue was that the lifespan (20 yrs) of the fitting was reduced because of high vibration conditions it experienced during a portion of its installed life. Three previous compressor failures (2005, 2009 & 2011) caused the high vibration conditions. D. SAFETY ANALYSIS System Design The purpose of the Control Room Emergency Ventilation system is to maintain the proper air environment for instrumentation and personnel in the Control Room. The Train B CREV AC system is a single train safety-related system that is designed to maintain design temperature in the Control Room Envelope (CRE) under post-accident NRC FOAM 366A (04-2017) Page _2_ of _4_ | ML17321A065
Pilgrim Nuclear Power Station 05000293 1 OF 3 | Unknown Unit | Supplement to Suppression Pool Declared Inoperable Due to High Water Level | 11-13-2017 | On March 31, 2017, at 1155 [EDT], with the reactor at 97 percent core thermal power and steady state conditions, operators were restoring a valve lineup after performing planned operations when a pathway was created through ~alve manipulation that allowed water in the Condensate Storage Tank to be diverted to the suppression pool. The rise in suppression pool water level exceeded the maximum water level specified in Technical Specifications (TS) and caused a lowering of the drywall to suppression pool differential pressure. With suppression pool water level and differential pressure both outside of TS limits, Limiting Condition for Operation !Action Statements 3.7.A.5 and 3.7.A.8.c were both entered and investigation into the cause of diverting water into the suppression pool was initiated. Water level was restored to within TS limits at 1540 [EDT]. An 8-hour non-emergency notification was made in accordance with 10 CFR 50. 72(b )(3)(v)(D), any event or condition ~hat at the time discovery had the potential to have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. !The initial LER was submitted under 10 CFR 50.73(a)(2)(i)(B), operation or condition prohibited by TS, but it was subsequently determined it should have been submitted under 10 CFR 50.73(a)(2)(v)(D), any event or condition that at he time of discovery had the potential to have prevented the fulfillment of the safety function of structures or systems hat are needed to mitigate the consequences of an accident, to more precisely describe this condition. There was no impact to public health and safety from this condition. NRC FORM 366 (04-2017) NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington,; DC 20555-0001, or by internet e-mail to :,· ~ lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, "'ttet• NEOB-10202, (3150-0104), Office of Management and B~dget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid 0MB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR NUMBER NO. Pilgrim Nuclear Power Station 05000-293 2017 003 · 01 I | BACKGROUND The suppression pool water provides the heat sink for the reactor primary system energy release following a postulated rupture of the system. The suppression pool water volume must absorb the associated decay and structural sensible heat released during primary system blow-down. The design volume of the suppression pool (water and air) was obtained by considering that the total volume of reactor coolant to be condensed is discharged to the suppression pool and that the drywell volume is purged to the suppression.pool. The suppression pool is designed to absorb the sudden input of heat from the primary system. In the long . term, the pool continues to absorb residual heat generated by fuel in the reactor core. EVENT DESCRIPTION On March 31, 2017, at 1155 [EDT], with the reactor at 97 percent core thermal power and steady state conditions, operators were.restoring a valve lineup after performing planned operations when a pathway was created through valve manipulation that allowed water in the Condensate Storage Tank to be diverted to the suppression pool. The rise in suppression pool water level to(+) 6.3 inches exceeded the maximum suppression pool water level specified in Technical Specification (TS) and the TS limit for differential pressure was lowered to less than 1.17psid between the drywell and suppression pool. With suppression pool water level and differential pressure outside of TS limits, both Limiting Condition for Operation Action Statement (LCOAS) 3.7.A.5 and 3.7.A.8.c were entered. In addition, Emergency Operating Procedures-03, Primary Containment Control, was also entered due to high suppression pool water level. Investigation into the cause of diverting water to the suppression pool was initiated. Appropriate procedural guidance was followed to begin lowering suppression pool water level below the limit specified in the TS. With suppression pool water level and differential pressure both returned to within TS limits, LCOAS 3.7.A.8.c and 3.7.A.5 were both exited at 1515 and 1540 respectively. The direct cause of the condition was that the control room operator opened the Core Spray Pump A Suppression Pool Suction Valve prior to verifying closed the Core Spray Pump Suction Valve from the Condensate Storage Tank and the Condensate Supply to Core Spray System Valve. CORRECTIVE ACTIONS Upon discovery of the suppression pool high water level condition, Operations returned the suppression pool water level to the required level using appropriate procedural guidance. The Control Room Supervisor and the Reactor Operator were disqualified. NRG FORM 366A (04-2017) Page 2 of 3 NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BYOMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported /"'""',!lo lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 {~) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to 'f ~ lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, •!!•!· NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid 0MB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR NUMBER NO. Pilgrim Nuclear Power Station 05000-293 2017 003 01 NARRATIVE SAFETY CONSEQUENCES The safety function of the suppression pool system was not adversely affected due to the high water level condition in the suppression pool. A preliminary assessment has demonstrated that the suppression pool water level was within a volume range that will accommodate all normal, transient, emergency, and accident events within the design capabilities of the primary containment system. As such, there are no consequences to general safety of the public, nuclear safety, industrial safety and radiological safety from this condition. Maintaining a drywell to suppression pool pressure differential to keep the downcomer legs clear of water significantly reduces suppression pool post LOCA hydrodynamic loads. A pressure of 1.17psid is required to sufficiently clear the water legs of the downcomers without bubbling nitrogen into the suppression pool at the 3.00 ft. downcomer submergence level. The suppression pool remained available and functional and capable of performing its intended safety function during the event. As such, there was no actual loss of safety function. The engineering evaluation that was performed concluded that this event did not constitute a Safety System Functional Failure. (Reference NEI 99-02, Revision 7, Regulatory Assessment Performance Indicator Guideline, Section 2.2, Mitigating Systems Cornerstone, Safety System Functional Failures, Clarifying Notes, Engineering Analyses.) As such, this event will not be reported in the NRC Performance Indicator for Safety System Functional Failures since an engineering evaluation was performed which determined that the system was capable of performing its safety function during this event. REPORT ABILITY This event was initially reported under 10 CFR 50. 73(a)(2)(i)(B), as a condition that was prohibited by TS. Subsequent to submission of the initial Licensee Event Report, based on NRC questions, it was concluded that this notification should have more precisely been made in accordance with 10 CFR 50. 73(a)(2)(v)(D), event or condition that could have potentially prevented fulfillment of a safety function of structures or systems that are needed to mitigate the consequences of an accident. PREVIOUS EVENTS A review of PNPS Licensee Event Reports for the past five years did not identify any similar occurrences of declaring the suppression pool inoperable due to a high water level condition. REFERENCE CR-PNP-2017-02785 NRG FORM 366A (04-2017) Page 3 of 3 | ML17325A984
Nine Mile Point | Unit 1 | Automatic Reactor Scram due to Reactor Vessel Low Water Level | 11-02-2017 | On September 6, 2017 at 1157, Nine Mile Point Unit 1 experienced an automatic reactor scram due to reactor vessel low water level. The automatic Reactor Protection System (RPS) actuation and reactor scram is reportable per 10 CFR 50.72 (b)(2)(iv)(B) and 10 CFR 50.73(a)(2)(iv)(A) as any event or condition that resulted in a manual or automatic actuation of any of the systems listed in 10 CFR 50. 73(a)(2)(iv)(B). Following the automatic scram all plant systems responded per design including High Pressure Coolant Injection (HPCI) System automatic initiation. HPCI is a flow control mode of the normalfeedwater systems, and is not an Emergency Core Cooling System. The root cause of the scram was a failed power supply within the Proportional Amplifier, PAM-ID23E. This power supply failure resulted in the output from the module dropping out causing the #13 Feedwater Pump Flow Control Va.Ive to close. The corrective action taken was the replacement of the failed Feedwater Level Control module, PAM- ID23E. ; NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per. response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503.. If a means used to impose an information collection does not display a currently valid 0MB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www. nrc. gov/reading-rm/doc-collections/nu regs/staff/sr1 022/r3Q collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Nine Mile Point Unit 1 05000220 NUMBER NO. 2017 003 00 | I. DESCRIPTION OF EVENT A. PRE-EVENT PLANT CONDITIONS: Prior to the event, Nine Mile Point Unit 1 (NMP1) was in Run and operating at 100% reactor power. B. EVENT: On 9/6/2017, at approximately 11 :57, NMP1 experienced a reactor scram due to reactor water low level. Following the scram Unit 1 also experienced a low-low reactor water level condition causing automatic Reactor Pressure Vessel (RPV) and containment isolation. Significant automatic responses that occur due to low-low reactor water level conditions include Main Steam Isolation Valve (MSIV) isolation, Reactor Water Clean Up (RWCU) isolation, core spray initiation signal, reactor recirculation pump trip, and emergency condenser vent and drain valve isolation. The HPCI mo9e of feed water first initiated on the reactor water low level signal. Following this HPCI initiation, vessel level continued to lower until low-low level was received. Due to the scram, trip of recirculation pumps, and HPCI initiation, vessel level rose to greater than 85" requiring Reactor Operators to perform procedurally driven actions for securing the feed water pumps. Additionally, following MSIV isolation on low-low level, vessel pressure control was established on the emergency condenser system briefly by manually placing the 11 emergency condenser in service. This resulted in an expected rise in vessel level. Approximately five minutes after placing the 11 emergency condenser in service Reactor Operations reopened MSIVs, transferred pressure control from the 11 emergency condenser to the turbine bypass valves, and removed 11 emergency condenser from service. Following the restoration of RWCU, opening of the MS IVs, and recovery of RPV water level, the HPCI mode of feed water was reset and feed water level control was transferred to the manual mode. Troubleshooting following the scram identified a failed power supply within Proportional Amplifier PAM ID23E which caused the Flow Control Valve for #13 Feedwater Pump to close. The module was sent for failure analysis. During this analysis, it was identified that a Schottky diode internal to the power supply of the Proportional Amplifier had failed, resulting in the output from the module to drop out. Nine Mile Point Unit 2 (NMP2) was unaffected by the scram at NMP1. Operations performed the ENS notification (#52950) required by 10 CFR 50. 72(b )(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) for the manual reactor scram and specified system activations. This event has been entered into the plant's corrective action program as JR 4049445. NRG FORM 366A (04-2017) Page _2_ of _5_ | ML17325A994
i | Unknown Unit | Potential Loss of Safetv Function of Secondarv Containment due to Unsecured Personnel Door | 11-13-2017 | On September 27, 2017, at approximately 10:00 a.m. CDT, with the plant operating at 85 percent power, a door in the auxiliary building pressure boundary was left unsecured by an employee entering the building. The employee failed to fully close the door, and then did not properly challenge the door to confirm its security prior to leaving the area. A security officer responded to the resulting alarm, and fully closed the door approximately four minutes later. Since the worker had sufficient experience with watertight doors to know their proper operation, this event is considered a skill-based error caused by over-confidence and improper assumptions. Having successfully used such doors numerous times, the worker was confident in the ability to do so. The effort to check the door's security by pushing it failed, likely due to its heavy mass. A briefing memorandum was issued from the general manager to site personnel. Tamper alarms were installed on all watertight doors in the secondary containment boundary to provide an audible indication that the door is open. ~dministrative controls have been instituted to schedule routine battery replacements. ' NRG FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 . EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collecUon request: 80 hours. R~ported ;/',,,,,..11..,c,, ..> _lessons learned are . incorporated into . the licensing process and fed back to industry. Send LICENSEE. EVENT REPORT (LER) · - f - ' \ . . \ i . comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, . .DC · 20555,0001, . . or by . e-mail . to •. ..., , CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Offic.er, Office of Information an·d Regulatory Aflairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid 0MB control number, !he http://www. nrc. gov/reading-rm/doc~collections/n ur egs/staff/sr1 022/r3i) .NRG may not conpuct or sponsor; and a person is not required to respond to, the information collection. . . . . ' . 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER YEAR SEQUENTIAL REV River Bend Station - Unit 1 05000-458 NUMBER NO. 2017 009 00 | REPORTED CONDITION On September 27, 2017, at approximately 10:00 a.m. CDT, with the plant operating at 85 percent power, a door (**DR**) in the auxiliary building [NF] pressure boundary was left unsecured by an employee entering the building. The employee failed to fully close the door, and then did not properly challenge the door to confirm its security prior to leaving the area. A security officer responded to the resulting alarm, and fully closed the door approximately four minutes later. \ This event is being reported in a.ccordance witr 10 CFR 50.73(a)(2)(v)(C) as·an event that could have caused the.loss of ~he safety function of the secondary containment pressure boundary. BACKGROUND The auxiliary building is part of the secondary containment pressure boundary. The event for which credit is taken for secondary containment is a loss of coolant accident. The secondary containment performs no active function in response to this event. However, its leak tightness is required to ensure that the release of radioactive materials from the primary containment is restricted to those leakage paths and associated leakage rates assumed in the accident analysis, aryd that fission products entrapped within the secondary containment structures will be treated prior to discharge to the environment. lfhe access doors in the auxiliary building pressure boundary have no redundancy: That is, each passageway contains only one door, not two doors in an airlock arrangement. As such, one unsecured do<;>r compromises the integrity of the pressure boundary. CAUSAL ANALYSIS lfhe door was mis-operated by a contract worker with significant experience at River Bend, who had successfully traversed such doors in the past. The pre-job brief for the work to be performed in the auxiliary building did not include a specific discussion of secondary containment doors. Four workers were traversing the door sequentially. The first worker swiped the card reader to open the door, and all the following workers swiped the card reader before entering the building to assure security accountability. The last person entering the door is responsible for closing it properly to secure the boundary. In this instance, the last person was being assisted by the previous worker who pulled on the door handle, while the last worker pulled on the door lock hand wheel. The worker pulling on the hand wheel inadvertently rotated it, causing the latch bolts to extend slightly. The latch bolts contacted the door frame outside of their receivers, preventing the door from being closed completely. Thinking that the door was properly closed, the worker holding the hand wheel rotated it fully, and the worker pulling the handle failed to notice that the door was not in contact with the seating surface in the frame. The worker then made an effort to assure the door's security by pushing in the open direction, but failed to move it. They then departed the area, leaving the door unsecured. NRG FORM 366A (04-2017) Page 2 of 4 | ML17325A996
Limerick Generating Station | Unit 2 | Reactor Mode Switch Change During RCIC Testing | 11-28-2017 | On May 26, 2017, during the Limerick Unit 2 reactor startup from a refueling outage, the reactor mode switch was placed in the RUN position (OPCON 1) with Reactor Core Isolation Cooling (RCIC) inoperable for required surveillance testing due to the Control Room Supervisor (CRS) failing to maintain adequate control of plant evolutions prior to placing the Mode switch to RUN. The station initially determined this operation was permitted based on TS 3.0.4.c. On September 29, 2017, it was subsequently determined TS 3.0.4.c was inappropriately used for this evolution. Therefore, changing the Reactor Mode Switch from Startup to Run while RCIC was inoperable for testing was a TS violation and therefore reportable as an Operation or Condition Prohibited by TS under 10 CFR 50.73(a)(2)(i)(B). Operations will revise the 'Normal Plant Startup' procedure to incorporate lessons learned from this event. Additionally, a Shift Training Notification will be developed and distributed to ensure gaps and lessons learned are shared with the Operations organization. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: BO hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send c."""""'ov, ( t.., .:·. .. 1,, comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear !(·~ LICENSEE EVENT REPORT (LEA) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to \f.~.~..~.; CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Attairs, NEOB-10202, (3150-0104), Office of Managemenl and Budget, Washington, DC 20503. If a means used to impose an Information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/readinq-rm/doc-collectionslnuregslstafflsr10221r3/) collect1on. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Limerick Generating Station, Unit 2 05000353 NUMBER NO. 2017 - 007 - 00 | I. Unit Conditions Prior to the Event Limerick Generating Station (LGS) Unit 2 was in Startup and being placed in the Run (Operational Condition (OPCON) 1) position at the time of the event. Reactor Core Isolation Cooling (RCIC) was inoperable for testing. There were no other structures, systems, or components inoperable at the time of the event that contributed to the event. There were no component failures as part of the event. 11. Description of the Event During the Reactor startup from the 2017 Refueling Outage, 2R14, the Reactor Mode Switch was placed iri the Run position while RCIC was inoperable for surveillance testing. The following is a timeline of events. On May 26, 2017 at 16: 10, Unit 2 RCIC was inoperable to perform the RCIC Comprehensive Surveillance Test, in accordance with Technical Specification (TS) 4.7.3.b. On May 26, 2017 at 16:37, Unit 2 Reactor Mode Switch was placed in the RUN position. Subsequently, the NRG questioned if TS allowed the station to change OPCONs while RCIC was inoperable. The station initially determined the condition was allowed based on TS 3.0.4.c, but that conclusion was later determined to be an inappropriate usage of the TS for the evolution. On September 29, 2017, the Station determined that changing the Reactor Mode Switch from Startup to Run while RCIC was inoperable was a TS violation. This evolution was determined to be an Operation or Condition Prohibited by TS and is reportable under 1O CFR 50.73(a)(2)(i)(B). This Licensee Event Report (LER) is being submitted within 60 days from the date of determination that this operation was prohibited by TS. Additionally, the NRG inspectors issued a Green Non-Cited Violation (NCV) as a result of this event. Specifically, a mode change from Startup to Run was made while TS 3.7.3 for RCIC was not met, and none of the allowances of TS 3.0.4 were met to allow the OPCON change. This NCV was issued as part of the third quarter integrated inspection, as documented in inspection report number 05000353/2017003. 111. Analysis of the Event During the Unit 2 startup, RCIC was inoperable to perform the RCIC comprehensive test in accordance with TS 4.7.3.b. TS 4.7.3.b has an allowance that states the provisions of TS 4.0.4 are not applicable provided the surveillance is performed within 12 hours after reactor steam pressure is adequate to perform the test. TS 4.0.4 requires that the entry into an operating condition shall only be made when the TS LCO surveillance requirements have been met within their surveillance time interval. During the performance of the test, the plant OPCON was changed from Startup to Run. The Station initially determined that the change was permitted by applying TS 3.0.4.c, since the TS LCO for RCIC was not met solely to perform the surveillance testing. Subsequent review concluded | ML17332A077
Columbia Generating Station 05000 397 1 OF 3 | Unknown Unit | Valve Closure Results in Momentary Increase in Secondary Containment Pressure | 11-30-2017 | On October 3, 2017 at 0800 PDT, Secondary Containment (Reactor Building) became inoperable due to pressure increasing above the Technical Specification (TS) limit of -0.25 inches of water gauge (inwg). While the plant was at 100% power, a Reactor Building exhaust valve unexpectedly closed, resulting in a loss of Secondary Containment for approximately two minutes. Secondary Containment was declared inoperable and TS Action Statement 3.6.4.1.A was entered. The Control Room operators reopened the Reactor Building exhaust valve and pressure returned to within limits automatically. Secondary Containment was declared operable at 0810 PDT and TS Action Statement 3.6.4.1.A was exited. The event was reported under 10 CFR 50.72(b)(3)(v)(C) and 10 CFR 50.72 (b)(3)(v)(D) as Event Notification #52999. The apparent cause of the event is a surface degradation on the lower stab of an electrical disconnect causing a momentary high resistance when the cubicle door is opened. This event occurred during performance of thermography in the cubicle. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000- NUMBER NO. Columbia Generating Station 397 17 - 007 - 00 | Plant Conditions At the time of the event, the plant was operating in Mode 1 at 100% power. The division 1 emergency diesel generator [EK] [DG] (DG1) was out of service for maintenance but did not contribute to this event. There were no other structures, systems, or components that were inoperable at the start of the event that contributed to the event. Event Description On October 3, 2017 at 0800 PDT, Operations personnel received an annunciator alarm for high Secondary Containment [NH] differential pressure when the Reactor Building [NG] exhaust inboard isolation valve [V] failed shut. For a time period of approximately two minutes, Secondary Containment differential pressure increased above -0.25 inches of water gauge (inwg), resulting in Technical Specification (TS) 3.6.4.1 not being met. The pressure rise was due to unexpected isolation of the Reactor Building inboard exhaust isolation valve during electrical switchgear inspections. This event is reportable as an event that could have prevented fulfillment of safety functions needed to control the release of radiation, and mitigate the consequences of an accident per 10 CFR 50.73(a)(2)(v)(C) and 10 CFR 50.73(a)(2)(v)(D). This condition was reported under 10 CFR 50.72(b)(3)(v)(C) and 10 CFR 50.72(b)(3)(v)(D) via Event Notification #52999 for an event or condition that could have prevented fulfillment of a safety function needed to control the release of radioactive material and accident mitigation. Immediate Corrective Actions Control Room operators reopened the Reactor Building exhaust inboard isolation valve and pressure was restored within TS limits. Assessment of Safety Consequences This event resulted in an unplanned entry into TS 3.6.4.1.A, in which Secondary Containment pressure was greater than -0.25 inwg for approximately two minutes. The peak pressure during this event was +3.7 inwg. While the actual pressure was beyond the range allowed by Technical Specifications, the purpose of maintaining a slight negative pressure is to assist in drawdown of secondary containment to support accident response of the safety related SGT system. Existing engineering analysis demonstrates the drawdown credited in Columbia's accident analysis could have been attained using either of the two available trains of the SGT system. There was no actual safety consequence associated with this event since opening the Reactor Building exhaust inboard isolation valve restored Secondary Containment, and there was no loss of safety function or potential for radiological release. Cause of Event The apparent cause of the event is a surface degradation on the lower stab of an electrical disconnect causing a momentary high resistance when the cubicle door is opened. This event occurred during performance of thermography in the cubicle. Further Corrective actions Cleaning and inspection of the disconnect switches including the stab to bus connection on the electrical disconnects and correction of any deficiency found will be performed in the next available outage. As an interim corrective action, thermography on the electrical panels associated with the degraded electrical disconnects will be discontinued until after the cleaning and inspection of the electrical disconnect is completed. NRC FFOORRMM 366A (04-2017) Page 2 of 3 | ML17334B440
Nine Mile Point | Unit 2 | Secondary Containment Inoperable Due to Wind Conditions | 11-28-2017 | On September 30, 2017 at 0134, Nine Mile Point Unit 2 declared Secondary Containment inoperable due to Secondary Containment vacuum decreasing below the technical specification limit. The condition is reportable under 1O CFR 50.72 (b)(3)(v)(C) and 1O CFR 50.73(a)(2)(v)(C) as any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. The change in Secondary Containment vacuum was the result of changing wind conditions. Secondary Containment was declared operable at 0135 when Secondary Containment vacuum was restored to greater than 0.25 inches of vacuum water gauge. The event described in this LER is documented in the plant's corrective action program as IR# 04057558. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: BO hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid 0MB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information l1ttp://www.nrc.gov/reading-rm/doc-col lections/nu regs/stafl/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. L0ER NUMBER SEQUENTIAL REV YEAR Nine Mile Point Unit 2 05000410 NUMBER NO. 2017 - 002 - 00 | I. DESCRIPTION OF EVENT A. PRE-EVENT PLANT CONDITIONS: Prior to the event, Nine Mile Point Unit 2 (NMP2) was operating at 100 percent power. B. EVENT: On September 30th, 2017 at approximately 0130 the Unit 2 Main Control Room was notified by the building rounds operator of Reactor Building differential pressure (0/P) fluctuations · observed at the local ventilation control panel. All Reactor Building fans and dampers were found in a normal configuration. Reactor building 0/P readings in the control room were noted as less than .25 inches vacuum water gauge (WG) and remaining negative as compared to atmospheric pressure. Secondary Containment was declared inoperable due to exceeding the Technical Specification (TS) allowed value of .25 inches vacuum WG and TS Limiting Condition for Operation (LCO) 3.6.4.1 Condition A was entered. One minute later Operations started Standby Gas Treatment (GTS) Train "B" per procedure. Secondary Containment vacuum was restored to greater than 0.25 inches of vacuum WG, TS LCO 3.6.4.1 Condition A was exited and Secondary Containment was declared Operable. Nine Mile Point Unit 1 (NMP1) was unaffected by the inoperability of Secondary Containment at NMP2. The event has been entered into the plant's corrective action program as IR# 04057558 C. INOPERABLE STRUCTURES, COMPONENTS, OR SYSTEMS THAT CONTRIBUTED TO THE EVENT: There were no inoperable systems, structures, or components that contributed to this event. D. DATES AND APPROXIMATE TIMES OF MAJOR OCCURRENCES AND OPERATOR ACTIONS: The dates, times, and major occurrences and operator actions for this event are as follows. All times are 09/30/2017. 0130 Reactor Building Operator reports the Reactor Building 0/P fluctuating at the local control panel. 0134 Control Room Operator observes control room indicators for Reactor Building pressure reading above -0.25 inches water gauge, Secondary Containment was declared inoperable and Technical Specification 3.6.4.1 was entered. NRG FORM 366A (04-2017) Page _2_ of _5_ | ML17346A745
Cooper Nuclear Station 05000298 1 of 5 | Unknown Unit | De-Energized High Pressure Coolant Injection Auxiliary Lube Oil Pump Caused by Relay Failure Results in Loss of Safety Function, a Condition Prohibited by Technical Specifications, and a 10 CFR Part 21 Report | 12-15-2017 | On April 25, 2016, while performing a walkdown of Control Room panels, it was noticed that the green indication light for High Pressure Coolant Injection (HPCI) auxiliary lube oil pump (ALOP) was not illuminated. A non-licensed operator was dispatched to the HPCI ALOP starter and reported that the local indication lights were not illuminated. HPCI was declared inoperable at 2117 Central Daylight Time (CDT) resulting in entry into Technical Specifications (TS) Limiting Condition of Operation 3.5.1, Condition C, HPCI System Inoperable. Investigation determined that the coil in the electrical relay for the ALOP, which had recently been replaced during a preventive maintenance window, had failed after 133 hours of service. The cause of the failure was determined to be the prior pre-installation checks performed by NuTherm on the relay were inadequate to prevent the type of infant mortality failure that occurred in this case. HPCI was declared operable at 1314 CDT on April 26, 2016, after the coil was replaced. This event is being reported as a loss of safety function due to HPCI being a single-train safety system, as a condition prohibited by TS and in accordance with 10 CFR Part 21. The potential safety consequences of this event were minimal due to both the limited duration the condition existed and the redundant/diverse core cooling systems which remained operable. l~. --- -NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-20.1,7,),,, .- Estimated burden per response to comply with this mandatory collection request: 80 hours, .... Reported lessons learned are incorporated into the licensing process and fed back to industry. Send \ ·~ ~.. ' . , .. , ) ~ LICENSEE EVENT REPORT (LER) c N o u m cl m ea e r n t R s e r g e u g l a a r to d r in y g C b o u m rd m e i n s si e o s n t , i m W at a e s h to in g t t h o e n , In D fo C r m 2 a 0 ti 5 o 5 n 5 - S 00 e 0 rv 1 i , c e o s r B b ra y n e c - h m a (T il - t 2 o F43), U.S. CONTINUATION SHEET lnfocollects,Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a (See NUREG-1022, R 3 for instruction and guidance for completing this form means used to impose an information collection does not display a currently valid 0MB control http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection, 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Cooper Nuclear Station 05000- 298 NUMBER NO. 2016 -001 -02 | PLANT STATUS Cooper Nuclear Station (CNS) was in Mode 1, Power Operation, at 100 percent steady state power at the time the condition was identified. Service Water Pump "B" and Service Water Booster Pump "B" were inoperable when High Pressure Coolant Injection (HPCI) was inoperable. No other emergency core cooling systems were inoperable during the event. BACKGROUND The HPCI System (EIIS:BJ) provides protection to the core for the case of a small break in the reactor coolant pressure boundary which does not result in rapid depressurization of the reactor vessel (EIIS:RPV). The HPCI System permits the nuclear plant to be shutdown while maintaining sufficient reactor vessel water inventory until the reactor vessel is depressurized. The HPCI System continues to operate until reactor vessel pressure is below the pressure at which Low Pressure Coolant Injection (EIIS:BO) operation or Core Spray System (EIIS:BM) operation can be used to maintain core cooling. HPCI consists of a steam turbine assembly (EIIS:TRB) driving a multi-stage booster and main pump assembly (EIIS:P) and system piping, valves, controls and instrumentation. The HPCI turbine is driven by steam from the reactor which is generated by decay and residual heat. A control governor (EIIS:65) receives a HPCI flow signal and adjusts the turbine steam control valve (EIIS:SCV) so that HPCI design pump discharge flow rate is obtained. The flow signal used for automatic control of the HPCI turbine is derived from a differential pressure measurement across a flow element (EIIS:FE) in the HPCI pump discharge pipeline. The governor controls the pressure applied to the hydraulic operator of the turbine control valve, which, in turn, controls the steam flow to the HPCI turbine. Upon receipt of the actuation signal, the auxiliary oil pump starts, providing hydraulic pressure for the turbine stop valve and turbine control valve hydraulic operator. The flow signal will ramp the control governor until rated flow is achieved. As hydraulic oil pressure is developed, the turbine stop valve and the turbine control valve open simultaneously and the turbine accelerates toward the speed setting of the control governor. As HPCI flow increases, the flow signal adjusts the control governor setting so that design flow is maintained'. EVENT DESCRIPTION On April 25, 2016, while performing a walkdown of Control Room panels, a licensed operator noticed that the green indication light for the HPCI auxiliary lube oil pump (ALOP) was not illuminated. The bulb in the Control Room panel was replaced, but did not illuminate. A non-licensed station operator was subsequently sent to the HPCI ALOP starter to verify local indications and found the local indication lights were not illuminated on the starter rack, indicating that the ALOP starter had lost power. The ALOP is required to start in order to open the steam admission valves for the HPCI turbine. An attempt was made in the Control Room to start the ALOP, but it did not start. | ML17354A149
Cooper Nuclear Station 05000298 1 of 4 | Unknown Unit | Residual Heat Removal Minimum Flow Valves Out of Position Results in Loss of Safety Function and Condition Prohibited by Technical Specifications | 12-15-2017 | On February 5, 2017, during a quarterly sealed valve log audit, Residual Heat Removal (RHR) Valves RHR-V-58 and RHR-V-60 were discovered sealed closed. Normal configuration for these valves is sealed opened. Consequently, Operations declared RHR pumps A and C Inoperable at 0756 hours and entered Technical Specifications (TS} Limiting Condition for Operation (LCO) 3.5.1 Condition A, LCO 3.6.1.9 Condition A, and LCO 3.6.2.3 Condition A. Subsequently, the operating crew opened RHR-V-58 and RHR-V-60, independently verified the position of the valves and applied seals to the valves. As such, RHR pumps A and C were declared Operable at 1041 hours on February 5, 2017, and TS LCO 3.5.1 Condition A, LCO 3.6.1.9 Condition A, and LCO 3.6.2.3 Condition A were exited. The root cause is Operations Department standards related to Operator Human Performance and Configuration Control are inadequate and do not meet industry expectations. Licensed and Non-Licensed Operators completed training focused on Standards and Expectations related to attention to detail and configuration control. To prevent recurrence, expectations will be established and institutionalized for Operations Leadership to reinforce consistent application of operator fundamentals and to identify and correct performance gaps for the operating crews. This is a Safety Svstem Functional Failure. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BYOMB: NO. 3150-0104 EXPIRES: 03/31/2020 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments .regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a (See NUREG-1022, R.3 for instruction and guidance for completing this form means used to impose an information collection does not display a currently valid 0MB control http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Cooper Nuclear Station 05000- 298 1---------------.....___ ________ ....___2_0_11_...__ __-_ 00_1_ _. ____· _01----111 | PLANT STATUS Cooper Nuclear Station (CNS) was in Mode 1, Power Operations, at 100 percent power, at the time of discovery. BACKGROUND The safety objective of the Residual Heat Removal (RHR) system [EIIS:BO] is to provide core cooling, in conjunction with other Emergency Core Cooling Systems, and to provide containment cooling as required during abnormal operational transients and postulated accidents. The RHR system consists of two heat exchangers [EIIS:HX], four main system pumps [EIIS:P] in two divisions, and associated piping, valves, controls and instrumentation. The motor-operated minimum flow valves automatically provide the necessary flow through the pump in order to prevent pump overheating. The manual isolation valves for the motor-operated minimum flow valves, RHR-V-58 and RHR-V-60, are normally configured open and sealed. RHR pumps A and C provide RHR Loop A safety functions associated with Low Pressure Cooling Injection (LPCI) and Containment Cooling. These pumps also provide RHR Loop A Shutdown Cooling (SDC) function during outage conditions. EVENT DESCRIPTION On September 29, 2016, during Refueling Outage 29 (RE29), RHR-V-58 and RHR-V-60 were closed and danger tagged in accordance with a clearance order to support the RHR Loop A Maintenance Window. On October 7, 2016, the danger tags for RHR-V-58 and RHR-V-60 were released and the clearance order directed that both valves be restored to their normal configuration. The danger tags were removed and seals applied to the valves. However, the valves were not opened before placing the seals. Second verification incorrectly verified that the valves were sealed open, when they were sealed closed. A quarterly sealed valve log audit was performed on November 29, 2016, and the seals were verified to be intact. The audit required only that the seals be verified, the audit did not require the valve configuration be checked. On February 5, 2017, during a quarterly sealed valve log audit, it was discovered that RHR-V-58 and RHR-V-60 were sealed closed. Consequently, Operations declared RHR pumps A and C Inoperable at 0756 hours and entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.5.1 Condition A, LCO 3.6.1.9 Condition A, and LCO 3.6.2.3 Condition A. | ML17354A150
Watts Bar Nuclear Plant | Unit 05000390 | Main Control Room Boundary Door Left Open Leading to a Loss of Safety Function | 12-20-2017 | 12. LICENSEE CONTACT FOR THIS LER ICENSEE CONTACT TELEPHONE NUMBER (lnclude Area Code) Dean Baker, Licensing Engineer 423-452-4589 13. COMPLETE ONE LINE FOR EACH COMPONENT FAILURE DESCRIBED IN THIS REPORT cAUSE I svsruru lcorr,rroNENrl.#+U[;- REP T O O R E T P A I B X LE CAUSE SYSTEM I COMPONENT FA M C A TU N R U E - R I I REP T O O R E T P A I B X LE 14. SUPPLEMENTAL REPORT EXPECTED 15. EXPECTED MONTHI DAY I YCNN I vrS (ff yes, comptete 15.EXPECTED SU BMt SS/O/V DATE) X NO SUB D M A IS T S E ION ABSTMCT (Limit to 1400 spaces, i.e., approximately 15 single-spaced typewitten tines) On October 30, 2017, at 0942 Eastern Daylight Time (EDT) Watts Bar Nuclear Plant (WBN) operations personnet received a Main Control Room (MCR) alarm for low control room positive pressure. At 0943 EDT, a Control Room Envelope (CRE) door was found ajar and immediately closed. Technical Specification 3.7.10 Control Room Emergency Ventilation System (CREVS) was declared not met for both trains, and Limiting Conditions for Operation (LCO) Condition B was entered for Unit 1 (Mode 1) and Condition G was entered for Unit 2 (Mode 5). At 0945 EDT the alarm cleared, CREVS was declared operable and LCO 3.7.10, Conditions B and G were exited. The loss of the control room envelope is being reported as a loss of safety function needed to mitigate the consequences of an accident. The cause of this issue is a human performance error in that an individual leaving the control building complex failed to confirm closure of the MCR envelope boundary door. Corrective actions have been generated to develop and install an engineering feature to inform personnel closing the door that it is fully shut and latched. NRC FORM 366 (O4-2O17) NRG FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED By OMB: NO.3150-0104 EXptRESz 03t3itZO20 (04-2017)) Estimated burden per response to comply with this mandatory collection request 80 hours. Reported R.cu(4b-. lessons learned are incorporated into the licensing process and fed back to industry. Send fb *o , *^ . o , i i : t, i . r .t y li L i* IC '' E NSEE EVENT REPORT (LER) c R o e m g m u en la ts t o re r g y a r C di o n m g m bu i r s d s e i n o n es , tim w a a te s h to in t g h t e o l n n , fo r D ma c tio n 2 S 0 e s rv 5 ic 5 e - s 0 0 B 0 ra 1 n , c h o ( r T -2 b F4 y 3) , U e .S m . N a u i c l le a to r coNrrNUArroN sHEEr lnfocollects,Resource@nrc.gov, and to the Desk Officer, ffice of lnformailon and Regulatory Affairs, NE0B-10202, (3150-0104), ffice of Management and Budget, Washington, DC 20503. lf a means used to impose an information collection does not display a cunently valid OMB conhol number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Watts Bar Nuclear Plant, Unit 05000390 NUMBER NO. 1 - r00 2017 014 | I. PLANT OPERATING CONDITIONS BEFORE THE EVENT Watts Bar Nuclear Plant (WBN) Unit 1 was in Mode 1 at 100 percent rated thermat power (RTP) . WBN Unit 2 was in Mode 5. It. DESCRIPTION OF EVENT A. Event Summary On October 30,20'17, a¦0942 Eastern Daylight Time (EDT) Watts Bar Nuclear Plant (WBN) operations personnel received a Main Control Room (MCR) alarm for low control room positive pressure. At 0943 EDT, a Gontrol Room Envelope (CRE) door {EllS:DR} was found ajar and immediately closed. Technical Specification (TS) 3.7.10 Control Room Emergency Ventilation System (CREVS) {EllS:Vl} was declared not met for both trains and Limiting Conditions for Operation (LCO) Condition B was entered for Unit 1 (Mode 1) and Condition G was entered for Unit 2 (Mode 5). At 0945 EDT the alarm cleared, CREVS was declared operable and LCO 3.7.10, Conditions B and G were exited. This event is being reported to the Nuclear Regulatory Commission (NRC) under 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident. B. lnoperable Structures, Components, or Systems that Contributed to the Event No inoperable equipment contributed to this event. C. Dates and Approximate Times of Occurences Date Time Event (EDT) 10130t17 0942 A MCR alarm was received for low control room positive pressure. 10130t17 0943 A CRE door was found ajar and immediately closed. TS 3.7.1 0 CREV= was declared not met for both trains, and Conditions B (Unit 1) and G (Unit 2) were entered. 10130t17 0945 The MCR alarm cleared, CREVS was declared operable and LCO 3.7.10, Conditions B and G were exited. D. Manufacturer and Model Number of components that Failed During the Event There were no failed components that contributed to this event. E. Other Systems or Secondary Functions Affected No other systems or secondary functions were affected. | ML17354A230
Peach Bottom Atomic Power Station | Unit 3 | Reactor Pressure Boundary Leakage Due to Weld Failure in One-Inch Diameter Instrument Line | 12-20-2017 | On 10/23/2017, during a walkdown of containment at the start of the Unit 3 refueling outage, a leak was identified in a socket weld for a 1-inch diameter instrument line. The line is connected to discharge piping for the 'B' recirculation pump and is part of the reactor coolant system pressure boundary. Because the leak was misting, the leakage rate could not be quantified. However, the reactor coolant system unidentified leakage prior to plant shutdown was 0.18 gpm. RCS pressure boundary leakage while in Mode 1 is a violation of Technical Specification 3.4.4 and is a reportable condition. The cause of the event was a lack of fusion defect in the weld when it was done in the late 1980's. Normal vibration of the line since it was installed resulted in the crack initiating at the weld defect and propagating to the surface. The section of pipe and associated fitting were replaced, along with welds in similar sections of piping. There were no actual safety consequences as a result of this event. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and led back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NAG may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rmldoc-colleclionslnuregslstall/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV VEAR Peach Bottom Atomic Power Station Unit 3 05000278 NUMBER NO. 2017 - 001 00 | Unit Conditions Prior to Discovery of the Event Unit 3 was in Mode 3, Hot Shutdown, when the condition was discovered on 10/23/2017 at approximately 4:00 am. The unit entered Mode 3 at 1: 08 am in preparation for the planned refueling outage. There were no structures, systems, or components out of service that contributed to this event. Description of the Event On 10/23/2017, with the Unit in Mode 3, at the beginning of a refueling outage, personnel entered the drywell to perform an inspection. At approximately 4:00 am, leakage was identified on a one-inch diameter instrument line socket (EIIS:PSF) weld. The instrument line is for a pressure transmitter from the 'B' Recirculation Pump (EIIS:AD) discharge. Because the leak was misting, the leakage rate could not be quantified. However, the reactor coolant system unidentified leakage prior to plant shutdown was 0.18 gpm. This line is part of the ASME Class 1 primary coolant pressure boundary. Technical Specification (TS) 3.4.4 does not allow any pressure boundary leakage in Modes 1, 2 or 3. As a result, TS 3.4.4 Condition C was entered, which requires the plant to be in Mode 3 in 12 hours and Mode 4 in 36 hours. The plant was in Mode 3 at the time of discovery and entered Mode 4, Cold Shutdown, at 12:54 pm on 10/23/2017 (approximately 9 hours after time of discovery). Prompt notification to the NRC was made in accordance with 10 CFR 50.72(b)(3)(ii)(A) on 10/23/2017 at 9:35 am (Event Notification #53031). Analysis of the Event The leak was determined to be from a crack in the weld connecting the pipe to a tee fitting. The crack extended approximately 60 degrees around the circumference of the weld. Although it could not be determined when the crack developed, it is assumed it existed while operating in Mode 1, prior to shutdown. During such time, the leakage would have been contributing to the total unidentified leakage of 0.18 gpm. This is well below the 5 gpm limit for unidentified leakage as stated in TS 3.4.4. This event is being reported in accordance with the following: 1. 10 CFR 50.73(a)(2)(i)(B) - Conditions Prohibited by Technical Specifications - TS Limiting Condition for Operation (LCO) 3.4.4 requires there to be no RCS pressure boundary leakage while in Modes 1, 2 and 3. If leakage exists, TS 3.4.4 Condition C requires the unit to be in Mode 3 in 12 hours and Mode 4 in 36 hours. Since the leak existed while in Mode 1 for greater than 36 hours, a condition prohibited by TS existed. NRG FORM 366A (04-2017) Page _2_ of _3_ | ML17355A003
Grand Gulf Nuclear Station | Unit 1 | Outside-of-Tech-Spec-Allowable-Value Automatic Depressurization System Initiation Timer Relay due to Inadequate Procedures | 12-18-2017 | On May 26, 2017, while performing the Automatic Depressurization System (ADS) quarterly surveillance, the time delay on the Trip System A (Division 1) ADS initiation timer relay was found outside of its Technical Specification (TS) Allowable Value of :5 115 seconds. Specifically, the ADS timer requirements in TS 3.3.5.1, Emergency Core Cooling System Instrumentation, Table 3.3.5.1-1, Emergency Core Cooling System Instrumentation, Function 4, Sub-function c. ADS Initiation Timer, Allowable Value was not met. The cause was determined to be inadequate preventive maintenance and review of the previous test results. This event is reportable as a license event report (LER) in accordance with 1 OCFR50.73(a)(2)(i)(B), as a "condition prohibited by Technical Specifications" because the same relay failed its previous test and could not be considered as OPERABLE during the full inteNal between tests. Corrective actions included replacement of the defective timer relay and planned actions to replace the corresponding timer relays in ADS and the Feedwater Control System. In addition, the applicable preventive maintenance procedures were revised. The event posed no threat to the health and safety of the general public or to nuclear safety as ADS would have performed as designed. No Technical Specification safety limits were challenged or violated. Page 1 of4 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 3/31/2020 (4-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to ~~,.<>•••••,,, LICENSEE EVENT REPORT (LER) industry. Send comments regarding burden estimate to the Information Services Branch (T-2 . 0 CONTINUATION SHEET F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to /~ ~";' lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and· \;; " Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, <;, (See NUREG-1022. R.3 for instruction and guidance for completing this form Washington, DC 20503. If a means used to impose an information collection does not -.;~~ "** •• ~ http://www.nrc.gov/reading-rm/doc-collections/nureqs/staff/sr1022/r3/) display a currently valid 0MB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 3. LER NUMBER YEAR SEQUENTIAL I REV. I Grand Gulf Nuclear Station, Unit 1 NUMBER NO. 05000 416 2017 -004-01 | DESCRIPTION On May 26, 2017, while performing Automatic Depressurization System (ADS) [AD][C23] quarterly surveillance, the time delay on the Trip System A ADS initiation timer relay [RL Y2] was found outside of its Technical Specification (TS) Allowable Value of :5 115 seconds. Specifically, the ADS timer requirements that are specified in Technical Specifications 3.3.5.1, Emergency Core Cooling System (ECCS) Instrumentation, Table 3.3.5.1-1, Emergency Core Cooling System Instrumentation, Function 4, Sub-function c. ADS Initiation Timer, Allowable Value were not met. The failure mechanism is degradation of the timing function in the ADS initiation timer relay (Agastat Model TR14D3EC750) that delays initiation of ADS in order to allow time for high pressure injection to restore reactor water level. The TS Allowable Value for this timer is less than or equal to 115 seconds. The as found value was beyond this value. This surveillance is performed on a quarterly basis. This same condition was found during the last surveillance performed on February 23, 2017. This condition was not found during the surveillance performed prior to that on November 18, 2016. The Automatic Depressurization System is required in Modes 1, 2, and 3 with the reactor above 150 psig. Between November 18, 2016 and January 30, 2017, the plant was in Mode 4. Therefore this function was not required from November 18, 2016 to January 30, 2017, which is when the reactor reached 150 psig in Mode 2. The ADS was required to be Operable from January 30, 2017, until May 26, 2017. ADS initiation is accomplished by energization of either the Trip System A (Division 1) or Trip System B (Division 2) solenoids [FSW] associated with each of the ADS valves. The logic for each Trip System is separate and either trip system will cause all the ADS relief valves to open. Therefore, the automatic safety function would still be accomplished within the allowable time provided that the Trip System B was Operable. Trip System B initiation logic was taken out of service on March 10, 2017, to support performance of the quarterly ADS channel calibration surveillance procedure. An additional review was performed to determine if the Trip System A logic would have initiated within the allowable time during the period when the Trip System B logic was out of service. The average rate of change of the setpoint between surveillances was 0.402 seconds/day for the first interval (November 18, 2016 - February 23, 2017) and 0.424 seconds/day for the second interval (February 23, 2017 - May 26, 2017). Use of the larger rate of change is conservative, and therefore a rate of 0.424 seconds/day was assumed for the second interval. Linearly extrapolating from an as left condition of 104 seconds on February 23, 2017, it is concluded that the setpoint would have been approximately 110.4 seconds on March 10, 2017. This value is within the 115 second TS AV. Therefore, it is I concluded that no loss of safety function occurred for this condition. REPORT ABILITY This event is reportable as a license event report (LER) in accordance with NUREG-1022, Section 3.2.2, and 1O CFR50.73(a)(2)(i)(B), as a "condition prohibited by Technical Specifications" because the same relay failed its previous test and could not have been considered operable for the full interval between tests. The timer relay would have been considered inoperable for a time period such that the Technical Specification 3.3.5.1 completion time would not have been met. Page2of4 NRG FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 3/31/2020 (6-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to ,,.po•••••,.> LICENSEE EVENT REPORT (LER) industry. Send comments regarding burden estimate to the Information Services Branch (T- i, / 0 ~. CONTINUATION SHEET 2 ln f F o 4 c 3 o ) l , l e U c . t S s. . R N e u s c o l u e r a c r e R @ e n g r u c l . a g t o o v ry , a C n o d m t m o i t s h s e i o D n e , s W k a O s f h fi i c n e g r t , o n O , f f D ic C e 2 o 0 f 5 In 5 f 5 o - r 0 m 0 a 0 ti 1 o , n o a r n b d y e-mail to i Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, ~ (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. If a means used to impose an information collection does not ~.,,4 •-. *" • http:/Jwww.nrc.gov/reading-rm/doc-collections/nureqs/stafflsr1022/r30 display a currently valid 0MB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 3. LEA NUMBER YEAR I SEQUENTIAL I REV. Grand Gulf Nuclear Station, Unit 1 NUMBER NO. 05000 416 2017 -004 - 01 NARRATIVE CAUSE The direct cause of the failure is the degradation of timing function for ADS initiation timer relay 1 B21-K5A, most likely due to the electrolytic capacitor degradation. ·. ''" The cause of the failure was an inadequate preventive maintenance task and inadequate procedural guidance. The procedures did not require periodic replacement of the relay nor did they require an engineering review of the test results. CORRECTIVE ACTIONS Immediate: The defective timer relay in Trip System A was replaced. Completed: Preventive maintenance tasks were revised to require periodic replacement of the relays. Surveillance testing was revised to require timely engineering review of the completed quarterly surveillance tests. Planned: The corresponding relays in ADS and the Feedwater Control System will be replaced. This action has been entered in the corrective action program and may be modified in accordance with that program. SAFETY SIGNIFICANCE Initiation of the ADS is accomplished by energizing either the Trip System A or Trip System B solenoids associated with each of the ADS valves. Each separate trip system will cause all the ADS relief valves to open. Therefore, the automatic safety function would still be accomplished within the allowable time with Trip System A inoperable provided that Trip System B was Operable. Trip System B initiation logic was taken out of service on March 10, 2017, to support performance of the quarterly ADS Channel B calibration surveillance procedure. An additional review was performed to determine if the Trip System A logic would have initiated within the allowable time during the period when the Trip System B logic was out of service. The conclusion was that the "A" setpoint would have been approximately 110.4 seconds on March 10, 2017. This value is within the 115 second TS AV. Therefore, at least one division of ADS was always available to perform the safety function. In addition, manual actuation was available, and operators are trained on the conditions requiring manual actuation and the associated procedures. The ADS acts as a backup to High Pressure Core Spray System [BG] for a small break loss of coolant accident. The High Pressure Core Spray System was not impacted by the degraded condition of ADS. The event posed no threat to the health and safety of the general public or to nuclear safety as ADS would have performed as designed. No Technical Specification safety limits were challenged or violated. Industrial safety was not challenged, and there was no potential or actual radiological release during the event. Page3 of4 PREVIOUS SIMILAR OCCURRENCES LER 2017-001-00 High Pressure Core Spray Jockey Pump Trip · LER 2009-002-00 Emergency Diesel Actuation Caused By Degraded DC Control Battery The identified licensee event reports were attributed to inadequate maintenance procedures. The events were reviewed and it has been determined that the causes and corrective actions were sufficiently different that they could not have predicted or prevented the occurrence of this event. Page 4 of4 . | ML17360A154
Dresden Nuclear Power Station | Unit 3 | Unit 3 Standby Liquid Control System Inoperable Due to a Manufacturing Defect Causing a Piping Leak | 12-27-2017 | On September 12, 2017 at 1131 hours (CDT), at Dresden Nuclear Power Station (DNPS), both Unit 3 Standby Liquid Control system subsystems were declared inoperable when control room personnel were notified of a through wall leak on the common discharge piping. Technical Specification (TS) 3.1.7, "Standby Liquid Control System," Condition B was entered. The pipe repair schedule projected that the work could not be completed within the allowed Completion Time of TS 3.1.7 and DNPS requested a Notice of Enforcement Discretion (NOED) to allow Unit 3 to remain at power during the repair. The NRC granted the NOED on September 12, 2017, at 1746 hours. The system was restored to operable status by replacing the piping on September 12, 2017, at 2035 hours within the time allowed by the NOED. This event is reportable under 1O CFR 50.73(a)(2)(i)(B), as a condition prohibited by TS. The cause of the event was a manufacturing defect. Corrective actions include replacing the failed piping (completed) and performing extent of condition pipe inspections. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send ~r,~fl!at,'-f comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear ! ~ LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to ;. lnfoco/lects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, '" CONTINUATION SHEET ~"'., ............ . NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid 0MB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http://www. nrc. gov/read in g-rm/doc-c?llections/nuregs/staff/sr1 022/r3l) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Dresden Nuclear Power Station, Unit 3 05000249 NUMBER NO. 001 01 | PLANT AND SYSTEM IDENTIFICATION Dresden Nuclear Power Station (DNPS), Unit 3, is a General Electric Company Boiling Water Reactor with a licensed maximum power level of 2957 megawatts thermal The Energy Industry Identification System codes used in the text are identified as [XX]. A. Plant Conditions Prior to Event: Unit: 03 Event Date: 09/12/17 Event Time: 1131 CDT Reactor Mode: 1 Mode Name: Power Operation Power Level: 100 percent B. Description of Event: On September 10, 2017, during Equipment Operator (EO) rounds, the EO found crystalized boron on Dresden, Unit 3 Standby Liquid Control System (SLC) [BR] discharge piping [PSF]. There was no active leak at the time of discovery and the source of the boron crystals was unknown. Work activities began to determine the source of the boron deposits. On September 12, 2017, the Division 1 SLC pump [P] was started to pressurize the system to the normal In-Service Testing test pressure as directed by station procedures. With the system pressurized, a leak of approximately one drop per minute was identified on the common discharge line of the SLC pumps. The leak was characterized as a through wall leak from an American Society of Mechanical Engineers (ASME), Class 2 pressure boundary of the SLC system. This leak was treated as a structural integrity issue; therefore, the affected piping was isolated in accordance with station procedures. Isolating the failed piping resulted in both divisions of SLC being declared Inoperable. This action led to entering Technical Specification {TS} Limiting Condition for Operation (LCO) 3.1.7, "Standby Liquid Control (SLC) System," Condition B, "Two SLC subsystems inoperable," and Required Action B.1, "Restore one SLC subsystem to OPERABLE status," with a Completion Time of eight hours. DNPS requested a Notice of Enforcement Discretion (NOED) to exceed the TS 8 hours Completion Time to complete the pipe repair and replace the pipe. The NRG verbally granted the NOED on September 12, 2017 at 1746 hours. At 2035 hours, the failed piping was replaced in accordance with station work instructions, thereby restoring the Unit 3 SLC system to Operable status within the time allowed by the NOED. The piping through-wall flaw did not meet ASME Code structural integrity requirements. Therefore, Dresden determined that since there was boron buildup identified on September 1O and later confirmed leakage on September 12, the system was inoperable for longer than allowed by TS and is-reportable under 10 CFR 50.73{a)(2)(i)(B) for a condition prohibited by TS. NRG FORM 366A (04-2017) Page_2_ of~ L___ - | ML17363A214
Browns Ferry Nuclear Plant | Unit 3 | 4kV Shutdown Board Potential Transformer Primary Fuses Do Not Coordinate with Secondary Fuses | 12-29-2017 | On November 1, 2017, at approximately 1425 Central Daylight Time, during an extent of condition review, a fuse coordination issue was discovered. Four Potential Transformer (PT) 10 amp secondary fuses on Unit 3 4kV Shutdown Boards (SD BO) do not selectively coordinate with upstream 0.5 amp primary fuses for fault currents greater than 30 amps on the 120 V secondary. Cable fire damage could cause an affected SD BO to spuriously disconnect from off-site power, and could cause a spurious, maintained under-voltage trip signal. The under-voltage trip signal would prevent motor load operation on the board whether on off-site power or Emergency Diesel Generator power. If a fire were to occur in fire areas 03-03 or 16, all four Unit 3 4kV SD BDs could be affected. In fire area 21, 4kV SD BDs 3EA and 3EB could be affected. This condition was determined to be a legacy issue dating to the original design of the plant. The most likely cause is lack of rigorous oversight of the vendor during the preparation and subsequent issuance of the fuse evaluation for the four Unit 3 4kV SD BDs. The required coordination studies have since been performed and a vendor oversight process has been added to TVA procedures. Compensatory measures (hourly fire ·watches) have been put in place for affected fire areas. Additional corrective actions include issuing an Engineering Change Package to replace the Unit 3 4kV SD BDs primary 0.5 amp PT fuses with 1 amp fuses of the same type. NRG FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget. Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. L..ER NUlllBER YEAR SEQUENTIAL REV NUMBER NO. Browns Ferry Nuclear Plant, Unit 3 05000-296 2017 - 002 - 00 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Unit 3, was in Mode 1 at approximately 100 percent rated thermal power. II. Description of Event A. Event Summary On November 1, 2017, at approximately 1425 Central Daylight Time (CDT), during an extent of condition review, a fuse [FU] coordination issue was discovered. Four Potential Transformer (PT) [XPT] 10 amp secondary fuses on Unit 3 4kV Shutdown Boards (SD BO) [ECBD] do not selectively coordinate with upstream 0.5 amp primary fuses for fault currents greater than 30 amps on the 120 V secondary. Cable [CBL] fire damage could cause an affected SD BO to spuriously disconnect from off-site power, and could cause a spurious, maintained under-voltage trip signal. The under-voltage trip signal would prevent motor load operation on the board whether on off-site power or Emergency Diesel Generator (EOG) [DG] power [EK]. If a fire were to occur in fire areas 03-03 or 16, all four Unit 3 4kV SD BDs could be affected. In fire area 21, 4kV SD BDs 3EA and 3EB could be affected. On November 1, 2017, at approximately 2126 CDT, Event Notification (EN) 53049 was made to the NRC. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event. There were no systems, structures, or components inoperable at the time of discovery which contributed to this condition. C. Dates and approximate times of occurrences November 1, 2017, Unanalyzed condition discovered during an extent of condition review. 1425 CDT November 1, 2017, Event Notification 53049 made to the NRC. 2126 CDT D. Manufacturer and model number of each component that failed during the event There were no failed components associated with this condition. Page 2 of 5 NRG FORM 366A (04-2017) | ML17363A295
Quad Cities Nuclear Power Station | Unit 1 | Unit 1 HPCI Did Not Trip Due to Wear Debris in the Turbine Stop Valve Oil Resetting Solenoid | 01-05-2018 | During performance of the High Pressure Coolant Injection (HPCI) Pump Operability Test, the Unit 1 HPCI turbine did not trip when the Remote HPCI Turbine Trip pushbutton was depressed. Operations shut down HPCI by isolating the steam supply valves to trip the HPCI turbine. The Unit 1 HPCI system was declared inoperable, but remained available. The cause was determined to be accumulation of wear debris within the HPCI turbine stop valve oil resetting solenoid valve causing the valve to stick in the energized position. This wear debris was a result of a manufacturing deficiency. The immediate corrective action was to replace the turbine stop valve oil resetting solenoid valve. Follow-up corrective action is to evaluate the preventative maintenance frequency tor the HPCI turbine stop valve oil resetting solenoid valve. The safety impact of this condition was minimal. The HPCI system was still available to function, despite the issue with the HPCI Turbine Stop Valve oil resetting solenoid. The event is being reported because HPCI is a single train system and the loss of HPCI could potentially impact the plant's ability to mitigate the consequences of an accident. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimaled burden per response lo comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means CONTINUATION SHEET used to impose an information collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. (See NUREG-1022, R.3 for instruction and guidance for completing this form htto://www.nrc.aov/readino-rm/doc-collections/nureas/staff/sr1022/r3/l 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Quad Cities Nuclear Power Station Unit 1 05000254 NO. NUMBER 2017 004 00 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Unit 1 HPCI Did Not Trip Due to Wear Debris in the Turbine Stop Valve Oil Resetting Solenoid A. CONDITION PRIOR TO EVENT Unit: 1 Event Date: November 7, 2017 Event Time: 18:10 hours Reactor Mode: 1 Mode Name: Power Operation Power Level: 100% B. DESCRIPTION OF EVENT On November 7, 2017 at 1810 hours, during performance of the quarterly High Pressure Coolant Injection (HPCI) [BJ] Pump Operability test, the Unit 1 HPCI turbine [TRB] failed to trip when the remote HPCI Turbine Trip pushbutton [HS] was depressed. Operations directed the shutdown of the Unit 1 HPCI system by isolating the HPCI steam supply valves [ISV], causing HPCI flow to reduce to 0 GPM. After the isolation was completed, Unit 1 HPCI was declared inoperable but available. There were no other structures, systems or components (SSC) inoperable during this event time period that could have contributed to this event. After troubleshooting, the internal HPCI stop valve oil resetting solenoid [PSV] was replaced. Following the replacement of the solenoid valve, the HPCI system was declared operable on November 8, 2017 at 2335 hours. C. CAUSE OF EVENT The cause of the HPCI turbine failure to trip was determined to be accumulation of wear debris within the HPCI stop valve oil resetting solenoid valve causing the solenoid valve to stick in the energized position. The wear debris was caused by a manufacturing deficiency. D. SAFETY ANALYSIS System Design According to the Quad Cities Nuclear Power Station (QCNPS), Units 1 and 2 Updated Final Safety Analysis Report (UFSAR) Section 6.3.2.3, the HPCI subsystem is designed to pump water into the reactor vessel under Loss of Coolant Accident (LOCA) conditions which do not result in rapid depressurization of the pressure vessel. The loss of coolant might be due to a loss of reactor feedwater or to a small line break which does not cause immediate depressurization of the reactor vessel. The sizing of the HPCI subsystem is based upon providing adequate core cooling during the time that the pressure in the reactor vessel decreases to a value that the Core Spray [BM] subsystem and/or the Low Pressure Coolant Injection (LPCI) [BO] subsystem become effective. The HPCI subsystem is designed to pump 5600 gallons per minute into the reactor vessel within a reactor pressure range of | ML18005A276
Clinton Power Station | Unit 1 | Trip of Emergency Reserve Auxiliary Transformer Static VAR Compensator Causes Positive Secondary Containment Pressure Following Voltage Transient on 138 kV Offsite Source. | 01-04-2018 | On November 5, 2017, at approximately 1240 CDT, the Main Control Room (MCR) received numerous annunciators that indicated a trip of the Emergency Reserve Auxiliary Transformer (ERAT) Static VAR Compensator (SVC) caused by a voltage transient on the 138 kV offsite supply. Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1, AC Sources-Operating, Required Action A.1 and A.2 were entered. As a result of the voltage transient, the Division 1 Fuel Building ventilation (VF) system isolation dampers closed causing a trip of VF supply and exhaust fans. With no operating VF fans, Secondary Containment (SC) vacuum rose to slightly greater than O inches water gauge (WG) at 1241 CDT which exceeded the TS requirement of greater than 0.25 inches vacuum WG. The MCR entered Emergency Operating Procedure (EOP)-8, Secondary Containment Control and TS LCO 3.6.4.1, Secondary Containment, Required Action A.1. The cause of the SC differential pressure becoming positive is that the circuit design of VF is not adequately robust to withstand loss of the 138 kV feed. At the time, the Division 1 safety bus was being fed from the ERAT. Secondary Containment vacuum was restored within TS requirements at 1242 CDT by starting the Standby Gas Treatment System. A modification will be installed to prevent tripping VF during a momentary loss of power. Installation of a 138 kV Ring Bus is scheduled that is intended to improve the reliability of the radial feed of the 138 kV line. This event is being reported as a condition that could have prevented fulfillment of a safety function under 10 CFR 50. 73(a)(2)(v)(C). NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: BO hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid 0MB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) · collection. · 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Clinton Power Station, Unit 1 05000461 NUMBER NO. 2017 • 009 • 00 | PLANT AND SYSTEM IDENTIFICATION General Electric -- Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in text as [XX]. EVENT IDENTIFICATION Trip of Emergency Reserve Auxiliary Transformer Static VAR Compensator Causes Positive Secondary Containment Pressure Following Voltage Transient on 138 kV Offsite Source. A. Plant Operating Conditions before the Event Unit: 1 Event Date: 11 /05/17 Event Time: 1240 CDT Mode: 1 Mode Name: Power Operation ReaciorPowe~98peme~ B. Description of Event On November 5, 2017, at approximately 1240 hours CDT the Emergency Reserve Auxiliary Transformer (ERAT)[XFMR] Static VAR Compensator (SVC)[COMP] tripped due to a voltage transient on the 138 kV line owned and maintained by Ameren Illinois. The Main Control Room (MCR) entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1, AC Sources-Operating, Required Actions A.1 and A.2. As a result of the voltage transient, the Division 1 Fuel Building Ventilation (VF) system isolation dampers closed causing a trip of the VF supply and exhaust fans. Ameren stated that the voltage transient was possibly due to weather. The effect of this condition was that Secondary Containment (SC) vacuum rose to slightly greater than O inches water gauge (WG) and exceeded the TS limit of -0.25 inch WG. Operations personnel entered Emergency Operating Procedure (EOP) -8, Secondary Containment Control, and TS LCO 3.6.4.1, Secondary Containment, Required Action A.1. As a result of the momentary loss of power, the following additional system actuations occurred: • Division 1 MCR Ventilation Chiller tripped, • Division 1 Diesel Generator Room Exhaust Fan 1V D02CA tripped, • Division 1 Shutdown Service Water Pump auto started, • Fission Product Monitoring (FPM) skid isolation valves shut, • Division 1 Hydrogen Monitoring system isolation valves shut, • Containment Service Air System Outboard Isolation valve 1S A029 shut, ' • Nuclear Systems Protection System (NSPS) Inverter Trouble alarms (due to loss of synchronization) 0 NRG FORM 366A (04-2017) Page _2_ of _4_ | ML18008A062
Watts Bar Nuclear Plant | Unit 1 | Failure to Enter Limiting Condition of Operation Action Statement Results in a Condition Prohibited by Technical Specifications | 01-08-2017 | On November 9, 2017, an issue was identified where Technical Specification (TS) Limiting Conditions of Operation (LCOs) were not entered when non-TS Engineered Safety Feature (ESF) area coolers were removed from service for maintenance. The Watts Bar Nuclear Plant (WBN) had been performing maintenance on ESF coolers serving Auxiliary Building areas without entering the TS LCO Action Statements associated with equipment present in those areas. Specific areas of concern identified were the general areas of the 713 foot and 737 foot elevations of the Auxiliary Building. These coolers were taken out of service for time periods longer than allowed for ESF equipment (typically 72 hours), which would represent a condition prohibited by the TS. At this time, WBN has not confirmed that for those cases where a cooler was taken out of service without entering a TS LCO if an actual adverse impact on safety function would have occurred if an accident with a single failure had occurred during those time periods. Those details, and the cause and corrective actions related to a 2010 guidance change, will be provided in a supplement to this report. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send +"'&~""' Fr~(;'-tro.,. comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to ~.. ~ :;, lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means ... ,.,, *** .... used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Watts Bar Nuclear Plant, Unit 1 05000390 NUMBER NO. 2017 - 015 00 | I. PLANT OPERATING CONDITIONS BEFORE THE EVENT Watts Bar Nuclear Plant (WBN) Unit 1 was in Mode 1 at 100 percent rated thermal power (RTP) . WBN Unit 2 was defueled (No Mode). II. DESCRIPTION OF EVENT A. Event Summary On November 9, 2017, an issue was identified where Technical Specification (TS) Limiting Conditions of Operation (LCOs) were not entered when non-TS Engineered Safety Feature (ESF) area coolers {EllS:CLR} were removed from service for maintenance. The Watts Bar Nuclear Plant (WBN) had been performing maintenance on ESF coolers serving Auxiliary Building ventilation {EllS:VF} areas without entering the TS LCO Action Statements associated with equipment present in those areas. Specific areas of concern identified were the general areas of the 713 foot and 737 foot elevations of the Auxiliary Building. These coolers were taken out of service for time periods longer than allowed for ESF equipment (typically 72 hours). This event is being reported to the Nuclear Regulatory Commission (NRC) under 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. B. Inoperable Structures, Components, or Systems that Contributed to the Event No inoperable equipment contributed to this event. C. Dates and Approximate Times of Occurrences Date Event 4/5/2002 NRC issues letter to Perry plant related to application of Generic Letter 80- 30 guidance to an inoperable non-technical specification support subsystem. 4/5/2010 WBN adopts the Perry guidance into plant documents via an engineering chanoe. 11/9/2017 CR 1357258 generated questioning the need for TS LCO Action Statement entry requirements for removing a redundant, non-TS ESF cooler from service. D. Manufacturer and Model Number of Components that Failed During the Event There were no failed components that contributed to this event. E. Other Systems or Secondary Functions Affected No other systems or secondary functions were affected. F. Method of discovery of each Component or System Failure or Procedural Error NRG FORM 366A (04-2017) Page _2_ of _5_ | ML18008A215
Watts Bar Nuclear Plant | Unit 05000390 | lncorrectly Adjusted Auxiliary Building Gas Treatment System Damper Leads to a Condition Prohibited by Technical Specifications | 01-24-2018 | On September 6,2017, Watts Bar Nuclear Plant (WBN) identified that the vacuum relief line airflows did not meet acceptance criteria for the Auxiliary Building Gas Treatment System (ABGTS) for Train A during the performance of 0- Sl-30-7-A, ABGTS Pressure Test. Troubleshooting of the low airflows identified an Auxiliary Building Secondary Containment Enclosure (ABSCE) Unit 2 General Ventilation intake damper 2-FCO-30-108 with approximately one inch gaps in the blade seals with the damper in the closed position. Preliminary investigation found that the damper linkage appeared to not be adjusted correctly to allow full closure of the damper blades following maintenance in May of 2017. The low vacuum relief line airflows resulted in the Train A ABGTS being inoperable, based on identified open ABSCE breaches, from July 7,2017 to September 5,2017. This time period is longer than that allowed by Technical Specification (TS) 3.7.12 for ABGTS, and is therefore a condition prohibited by TS. The cause of this event was an incorrectly adjusted damper linkage after replacement of the damper actuator. A training needs analysis will be performed to evaluate training solutions for damper linkage adjustments. Damper preventative maintenance activities will be revised to address smooth operation and absence of mechanical binding. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO.3150-0104 ExptRESz 0tt31t2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request 80 hours. Reported rffi lessons learned are incorporated into the licensing process and fed back to industry. Send LTCENSEE EVENT REPORT (LER) c R o e m g m u en la ts t o re ry ga r c d o in m g m bu i r s d s en io e n s , t im w a a te s h to in t g h t e o l n nf , o r D ma c tio n 2 S 0 e s rv s ic s e - s 0 0 B 0 ra 1 n , ch o ( r T -2 b F4 y 3) , U e . - S m . N a u i c l l ea to r CONTINUATION SHEET lnfocollects.Resource@nrc,gov, and to the Desk Officer, Office of lnformation and Regulatory Affairs, NE0&10202, (315G0104), Office of Management and Budget, Washington, DC 20503. lf a means used to impose an information collection does not display a currently valid OMB oontrol number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Watts Bar Nuclear Plant, Unit 05000390 NUMBER NO. 1 - - 2017 013 01 | t. PLANT OPERATING CONDITIONS BEFORE THE EVENT Watts Bar Nuclear Plant (WBN) Unit 1 was at 100 percent rated thermal power (RTP) . WBN Unit 2 was also in Mode 1 at 100 percent power. il DESCRIPTION OF EVENT A. Event Summary On September 6,2017, Watts Bar Nuclear Plant (WBN) identified that the vacuum relief line airflows did not meet acceptance criteria for the Auxiliary Building Gas Treatment System (ABGTSXEIIS:VF) for Train A during the performance of 0-Sl-30-7-A, ABGTS Pressure Test. Troubleshooting of the low airflows identified an Auxiliary Building Secondary Containment Enclosure (ABSCE) Unit 2 General Ventilation intake damper 2-FCO-30-108 {EttS:CDMP} with approximately one inch gaps in the blade seals with the damper in the closed position. Preliminary investigation found that the damper linkage appeared to not be adjusted correcfly to allow full closure of the damper blades following maintenance in May of 2017. The low vaouum relief line airflows resulted in the Train A ABGTS being inoperable, based on identified open ABSCE breaches, from July 7,2017 at 2030 Eastern Daylight Time (EDT) to September 5,2017 at 1645 EDT. This time period is longer than that allowed by Technical Specification (TS) 3.7.12 for ABGTS, and is therefore a condition prohibited by TS. This event is being reported to the Nuclear Regulatory commission (NRC) under 10 cFR 50.73(a)(2)(i)(B) as a condition prohibited by Technicat specifications. B. lnoperable structures, components, or systems that contributed to the Event No inoperable equipment contributed to this event. C. Dates and Approximate Times of Occurrences Date Time Event 5119t17 Actuator associated with damper 2-FCO-30-108 replaced to address air leaks. A visual inspection of the damper by inspecting the blade seals through the ventilation manway was not performed. Only external checks yvere performed. 7 t07 t17 2030 ABSCE breach exceeds 63.9 square inches for Train A. 9105t17 1 645 ABSCE breach is less than 63.9 square inches for Train A . 9t06t17 During performance of 0-Sl-30-7-A, Auxiliary Building Gas Treatment System Pressure Test Train A, the vacuum relief line airflows obtained did not meet the required acceptance criteria of greater than or equal to 1370 cubic feet per minute (cfm). 9t19t07 1 609 Damper issue corrected by work order 1 19015649 10t06t17 A Past Operability Evaluation (POE) performed for this event determined that the A Train of ABGTS was inoperable from July 7,2017 at 2030 EDT until September 5,2017 at 1645 EDT. | ML18024A360
Watts Bar Nuclear Plant | Unit 1 | Error in Plant Emergency Procedures Leads to a condition Prohibited by the Technical specifications | 01-30-2018 | 12. LICENSEE CONTACT FOR THIS LER LICENSEE CONTACT TELEPHONE NUMBER (lnclude Area Code) Dean Baker, Licensing Engineer 423-452-4589 13. coMpLETE oNE LINE FoR EAcH coMpoNENT FATLURE DESCRTBED rN THrs neponi cAUSE I svsrervr lcor',reoNENr I ,^t+[H;- l*t?31$,.:Lt CAUSE SYSTEM I conapoNENT FA M C A TU N R U E - R I I REP T O O R E T P A I B X LE 14. SUPPLEMENTAL REPORT EXPECTED 15. EXPECTED MoNTHI ony I yenn x f] vrs (f yes, comptete 15.EXPECTED SU BMt SS/O/V DATE) NO SUBMISSION DATE ABSTMCT (Limit to 1400 spaces, i.e., approximately 1S singte-spaced typewitten lines) On August 23,2017, Watts Bar Nuclear Plant (WBN) identified that procedures 1-E-1 and 2-E-1, Loss of Reactor or Secondary Coolant, contained steps to manually open 1-FCV-67-458 in the event of a Train A or B power failure. Opening 1-FCV-67-458 would result in the crosstie of Essential Raw Cooling Water (ERCW) Headers 2A and 1B, which would lead to providing flow to equipment not operating due to the loss of a train of power. On October 6,2017, it was determined that for certain time periods, if a design basis accident had occurred on Unit 2 with a loss of offsite power concurrent with a train failure and with 1-FCV-67-458 opened, inadequate ERCW flow would have been available to remove decay heat after transfer to cold leg recirculation. This condition only atfected operability of ERCW Train A. This is reportable as a condition prohibited by Technical Specification 3.7.8. The issue associated with this incorrect procedural step to cross-tie the ERCW trains in 1-E-1 and 2-E-1 was addressed as part of actions to resolve an ERCW design and procedure issue documented in Licensee Event Report (LER) 390-2017-009. This report, while related, identifies an issue that was not addressed in the prior LER. The cause was determined to be the incorrect application of a cross tie requirement associated with 1O CFR 50 Appendix R. Corrective action will be to include engineering in the review of procedures affected by complex design changes. NRC FORM 366 (04-2017) 366A NRC FORM U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3is0-0104 (04-2017n Estimated burden per response to comply with ilris mandatory collection request 80 hours. Reported lessons learned are. incorporated into the licensing process and fed back to industry. Send LTCENSEE EVENT REPORT (LER) c R o e m g m u en la ts t o re ry ga r C di o n m g m bu i r s d s e i n o n es , tim w a m te h t i o n g th to e n ln , f or D ma C tion 2 S 0 e 5 rv s ic 5 e - s 0 0 B 0 ra 1 n , c h o ( i T -2 b F4 y 3) , U e , - S m . N a u i c l l ea to r CONTINUATION SHEET lnfocollects.Resource@lrc.gov, and to the Desk Officer, Office of lnformation and Regulatory Affairs, NEOB-10202, (315G0104), ffice of Managenrent and Budget, Washington, DC 20503. lf i means ys_e! to impose an information collection does not display a cunently viliO OUg control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Watts Bar Nuclear Plant, Unit 05000390 NUMBER NO. 1 - 2017 012 r 01 | I PLANT OPERATING CONDITIONS BEFORE THE EVENT Watts Bar Nuclear Plant (WBN) Unit 1 was at 100 percent rated thermal power (RTp) . WBN Unit 2 was also in Mode 1 at 100 percent power. il. DESCRIPTION OF EVENT A. Event Summary On August 23,2017, WBN identified that procedures 1-E-1 and 2-E-1, Loss of Reactor or Secondary Coolant, contained steps to manually open 1-FCV{7-458 {EllS:FCV} in the event of a Train A or Train B power failure. Opening 1-FCV-67458 would result ih the crosstie of Essential Raw Cooling Water (ERCW {EllS:Bl} Headers 2Aand 1B, which woutd lead to providing flow to equipment not operating due to the loss of a train of power. On October 6,201i, it was determined that for certain time periods, if a design basis accident had occurred on Unit 2 with a loss of offsite power concurrent with a train failure and with 1-FCV-674S8 opened, inadequate ERCW flow would have been available to remove decay heat after transfer io cold leg recirculation. This condition only affected operability of ERCW Train A. The issue associated with this incorrect procedural step to cross-tie the ERCW trains in 1-E-1 and 2-E-1 was addressed as part of actions to resolve an ERCW design and procedure issue documented in Licensee Event Report (LER) 390-2017-009. This report, while related, identifies an issue that was not addressed in the prior LER. This event is being reported to the Nuclear Regulatory Commission (NRC) under 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical SpeiiRcations. B. lnoperable Structures, Components, or Systems that Contributed to the Event No inoperable equipment contributed to this event. C. Dates and Approximate Times of Occurrences Date Event 10t20t15 WBN Unit 1 receives license Amendment 104 to revise tfre Tecfrnical specifications (TS) for ccs and ERCW to support Dual Unit operation. 10t22t15 WBN Unit 2 receives operating license 10t08t15 Procedure 2-E-1, Loss of Reactor or Secondary Coolant, Rev. 0 issued including steps to open 1-lSV-67458, ERCW Cross tie. 12t28t15 Procedure 1-E-1, Rev. 7 issued including steps to open 1-lSV-67459, ERCW Cross tie. 5t23t16 WBN Unit 2 is critical for the first time 7 112t17 condition Report (cR) 1316395 is generated to document ERCW design issue. 7114t17 Procedures 1-E-0 and 2-E-o, are revised to address proper position or encw outlet valves from the ccs heat exchangers. Additionally, procedures 1-E-1 and 2-E-1 are revised to remove action to cross tie ERCW headers. | ML18030A583
Limerick Generating Station | Unit 1 | D12 EDG Inoperable for Greater than 30 Days Resulting in Condition Prohibited by TS | 02-05-2018 | On December 7, 2017, during performance of the D12 Emergency Diesel Generator (EDG) Surveillance Test (ST), it was recognized that Scavenging Air temperatures were abnormally high. An investigation revealed a deficiency in the air pressure control valve. Because of this deficiency, the Air Cooler Temperature Indicating Controller was not performing correctly. The D12 EDG had run unloaded for approximately two hours, then fully loaded for approximately one hour when the condition was identified. This condition results in inoperability/ unavailability of the affected EDG and entry into a 30-day shutdown Limiting Condition for Operation (LCO). On December 12, 2017, the D12 EDG was declared operable and the LCO was exited. A past operability review determined that the D12 EDG was inoperable since the last D12 EDG 24-hr endurance run, which was began on November 6, 2017. The D12 EDG was inoperable for a period of greater than 30 days and the LCO 3.8.1.1.a actions were not completed in the required time frames provided in Technical Specifications (TS). Therefore, an Operation or Condition Prohibited by TS existed and is reportable under 10 CFR 50.73(a)(2)(i)(B). NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Limerick Generating Station, Unit 1 05000352 NUMBER NO. 2018 - 001 - 00 | I. Unit Conditions Prior to the Event Limerick Generating Station (LGS), Unit 1 was operating in Operational Condition (OPCON) 1 at 100 percent power at the time of the event. There were no other structures, systems, or components inoperable that contributed to the event. II. Description of the Event On December 7, 2017, during the performance of the D12 Emergency Diesel Generator (EDG) [EIIS: EK] Loss of Coolant Accident (LOCA)/Load Reject Testing and Fast Start Operability Surveillance Test (ST) Run, it was recognized that Air Cooler Discharge Air temperatures were abnormally high (220°F), with an expected band of 115°F-145°F. The cooling water controller’s setpoint was found set at 200°F. The required setpoint is 130°F. The D12 EDG had run unloaded for about two hours, then fully loaded for about one hour when the condition occurred. D12 EDG was declared inoperable and Limiting Condition for Operation (LCO) 3.8.1.1 was entered. As part of troubleshooting, the Temperature Indicating Controller (TIC) was removed, bench tested satisfactorily, re-installed and recalibrated to a setpoint temperature of 130°F. On December 12, 2017, the D12 EDG was declared operable and the LCO was exited. On December 11, 2017, a past operability review determined that the past functionality of the D12 EDG had been impacted since performance of the 24-hour endurance run that began on November 6, 2017, when an intermittent equipment deficiency caused incorrect indication and control resulting in subsequent high temperature conditions. Testing performed on January 10, 2018, during the monthly D12 EDG ST run, identified an equipment deficiency associated with the Pressure Control Valve (PCV). The air pressure control issue causes the TIC to not indicate or perform correctly. The D12 EDG was inoperable for a period of greater than 30 days and the LCO 3.8.1.1.a actions were not completed in the required time frames provided in Technical Specifications (TS). Therefore, an Operation or Condition Prohibited by TS existed. This LER is being submitted in accordance with 10 CFR 50.73(a)(2)(i)(B). III. Analysis of the Event On November 6, 2017, while performing a routine running check of engine operation, an equipment operator identified that the air cooler temperature controller setpoint was not at 130°F and process temperatures were off-scale low (known condition with existing Issue Report (IR)). An adjustment was made to the temperature controller setpoint to control jacket water coolant engine discharge temperature, in accordance with procedure. However, intermittent malfunction of the PCV in the supply air line to the temperature controller would have prevented that adjustment from taking effect until the next engine run on December 7, 2017 (lower air pressure prevents the air cooler control loop from operating throughout its full span and results in a lower indicated setpoint and process temperature). | ML18036A983
Oyster Creek | Unit 1 | Technical Specification Prohibited Condition Caused by One Electromatic Relief Valve Inoperable for Greater than Allowed Outage Time | 09-22-2011 | On September 19, 2016, after achieving Cold Shutdown for the 1 R26 Refuel Outage, as found testing was performed on all five (5) Electromatic Relief Valves (EMRVs). The "E" EMRV did not open from the Main Control Room (MCR), and no change in indication was observed. Per the work activity, technicians were dispatched to the Drywell to verify that the valve did not move upon receiving an open signal from the MCA. A cutout switch in the valve actuator was stuck in the open position, thereby preventing a solenoid from actuating to open the valve. The cutout switch did not operate as required because the hinge pin lock star washers were not installed in the cutout switch assembly. Without the lock star washers installed, the hinge pins interfered with the solenoid frame holes creating mechanical binding. Based on this information it is suspected that the "E" EMRV would have been inoperable for longer than the Technical Specification Allowed Out of Service Time (AOT) of 24 hours. Therefore, this issue is reportable under 1O CFR 50. 73(a)(2)(i)(B) as an Operation or Condition which was Prohibited by the plant's Technical Specifications. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016)) Estimated burden per response to comply with this mandatory coHection request: BO hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555·0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currenUy valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/@ collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV Oyster Creek, Unit 1 05000- 0219 YEAR NUMBER NO. 2016 - 005 - 01 | Plant Conditions Prior To Event Event Date: September 19, 2016 Event Time: 1500 EDT Unit 1 Mode: Cold Shutdown Power Level: 0% Description of Event On September 19, 2016 after achieving Cold Shutdown for the 1 R26 Refuel Outage, as found testing was performed on all five (5) Electromatic Relief Valves (EMRVs). The "E" EMRV did not open from the Main Control Room (MGR), and no change in indication was observed. Per the work activity, technicians were dispatched to the Drywell to validate that the valve did not move upon receiving an open signal from the MGR. Troubleshooting was developed and determined that the cutout switch in the valve actuator was stuck in the open position, thereby preventing the actuator pickup solenoid from energizing to open the valve. The cutout switch did not operate as required because the hinge pin lock star washers were not installed in the cutout switch assembly. Without the lock star washers installed, the hinge pins interfered with the solenoid frame holes creating mechanical binding. During each refueling outage, all five (5) EMRV actuators are removed from the plant, refurbished, and reinstalled during the following refueling outage. By Oyster Creek Nuclear Generating Station (OCNGS) process, the EMRV actuators are refurbished with new springs, posts, guides, and microswitches every 24 months during refueling outages. The actuator inspection/refurbishment frequency of 24 months is more frequent than the manufacturer's (Dresser Industries) recommended frequency of 36 months (per Vendor Manual VM-OC-0030, Installation and Maintenance Manual for Electromatic Relief Valves, Revision 1, Section VII, Ref. 4.5). Equipment Description The EMRVs are Type 6" 1525-VX relief valves manufactured by Dresser Industries. They are installed on the two (2) main steam lines that carry steam from the reactor vessel to the main turbine. Actuation signals from either the Automatic Depressurization System or the individual EMRV pressure switches, as well as from the manual control switches will open the valves to lower reactor pressure, thereby allowing the low pressure Core Spray System to provide makeup water to the reactor core during accident I transient conditions. The main valve is operated by a pilot valve that is controlled by energizing a DC operated solenoid actuator. When energized, the solenoid develops an electromagnetic field that enables the downward travel of a plunger, which strikes the pilot valve lever pushing it down. In that position, the lever opens the exhausVventing path of the main valve, which subsequently opens the EMRV. The solenoid actuator is equipped with two solenoid coils (a pickup, low resistance - 50 coil, and a hold, high resistance - 3000 coil) in series. The hold coil has a parallel cutout switch, which is normally closed, thus bypassing the hold coil during the initial solenoid actuation. The initial pickup current in that configuration (-20 amps) is capable of developing the force required by the plunger for striking down the pilot valve lever and opening the EMRV. During its downward travel, the plunger tail will also strike down the cutout switch lever, which opens the cutout switch and connects the hold coil into the circuit. The low current developed (- 0.5 Amps) in that configuration is required to allow the EMRV to remain open, as needed, without the risk of burning out the pickup coil. NAC FOAM 366A (06-2016) Page _2_ of _4_ | ML18037A091
Limerick Generating Station | Unit 2 | HPCI lnoperability due to Discharge Check Valve Failure to Close | 02-06-2018 | On December 8, 2017, when the Unit 2 High Pressure Coolant Injection (HPCI) System was being secured following a quarterly surveillance test, the Main Control Room (MGR) received indications that the HPCI pump suction piping was pressurizing. The HPCI pump discharge check valve failed to fully close following turbine shutdown causing repeated cycling of the HPCI pump minimum flow bypass valve. The motor operated HPCI pump discharge valve located immediately downstream of the pump discharge check valve was closed to terminate pressurization of the pump suction piping. With the pump discharge check valve in an indeterminate state and the motor operated pump discharge valve closed, the Unit 2 HPCI System was declared inoperable. This condition is reportable under 1O CFR 50.73(a)(2)(v)(D) as an event that could have prevented fulfillment of a safety function of a system that is needed to mitigate the consequences of an accident. An eight (8) hour Emergency Notification System (ENS) notification (#53108) was completed on December 8, 2017 at 1725 hours. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04·2017)) Estimated burden per response to comply with this mandatory collection request: BO hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send -lr... .' -"'""lo(l',.,.. 0 comments regarding burden estimate to the Information Services Branch (T·2 F43). U.S. Nuclear {t~.:·.J.\ LICENSEE EVENT REPORT (LEA) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to ..... lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, \~1~~; CONTINUATION SHEET NEOB-10202, (3150-0104), Office ol Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1 D22, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Limerick Generating Station, Unit 2 05000353 NUMBER NO. 2018 - 001 - 00 | I. Unit Conditions Prior to the Event Limerick Generating Station (LGS) Unit 2 was operating in Operational Condition (OPCON) 1 at 100 percent power at the time of the event. There were no other structures, systems, or components inoperable at the time of the event that contributed to the event. 11. Description of the Event At approximately 1300 hours on December 8, 2017, when the Unit 2 High Pressure Coolant Injection (HPCI) [EllS: BJ] system was being secured following a quarterly surveillance test, the Main Control Room (MCA) received indications that the HPCI pump suction piping was pressurizing. Failure of the HPCI pump discharge check valve to fully close caused repeated cycling of the HPCI pump minimum flow bypass valve. The motor operated pump discharge valve located immediately downstream of the pump discharge check valve was closed to terminate pressurization of the pump suction piping. With the HPCI pump discharge check valve in an indeterminate state and the motor operated pump discharge valve closed, the Unit 2 HPCI System was declared inoperable. Following repair of the pump discharge check valve, satisfactory post-maintenance testing, and surveillance testing, the Unit 2 HPCI system was declared operable at 1140 hours on December 11, 2017. This condition is reportable under 1O CFR 50.73(a)(2)(v)(D) as an event that could have prevented fulfillment of a safety function of a system that is needed to mitigate the consequences of an accident. An eight (8) hour Emergency Notification System (ENS) notification (#53108) was completed at 1725 hours on December 8, 2017. 111. Analysis of the Event Inspection of the Unit 2 HPCI pump discharge check valve identified that the disc was stuck in the full open position. Repeated contact between the disc and sides of the valve body over time resulted in wear of the disc and the formation of notches in the side of the valve body. During the December 8, 2017 surveillance test, the disc became lodged in the notches and prevented disc closure when the system was secured. Normal wear of the valve internal parts and the formation of the notches in the valve body are both time dependent failure modes that occurred over the life of the valve. IV. Safety Significance The HPCI pump discharge piping includes a pump discharge check valve upstream of the system keep fill connections from the Condensate Transfer and the Safeguard Piping Fill systems. The check valve maintains the HPCI pump discharge piping filled with water above the elevation of normal Condensate Storage Tank (CST) water level. The pump discharge check valve performs an active safety function in the open direction to provide an injection flow path for the HPCI pump and a NRC FOAM 366A (04-20171 Page _2_ of _4_ | ML18037A914
I | Unknown Unit | : | 02-13-2018 | On December 22, 2017 at 2348 hours, the High Pressure Core Spray (HPCS) system was declared inoperable due to a through-wall leak on the minimum flow line piping. The leak was on the outside bend of the first elbow downstream of the minimum flow restricting orifice and was leaking approximately 60 drops per minute. Technical Specification (TS) Limiting Condition of Operation (LCO) 3.5.1 Condition B was entered. The piping was repaired, the TS LCO exited, and HPCS was declared operable on December 25, 2017 at 2213 hours. The cause was pipe wall loss due to a combination of cavitation and mechanical erosion wear. The safety significance of this event is considered to be very small. This event is being reported in accordance with 10 CFR50. 73(a)(2)(v)(D) as an event or condition that could have prevented the fulfilment of a safety function. NRC FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43}, U.S. Nuclear CONTINUATION SHEET Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid 0MB control number, the http://www. nr c.gov/readi ng-rm/doc-collections/n uregs/staff/sr1 022/r3/ NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Perry Nuclear Power Plant Unit 1 05000-440 YEAR NUMBER NO. 2017 007 00 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. INTRODUCTION On December 22, 2017 at 2348 hours, the High Pressure Core Spray (HPCS) [BG] system was declared inoperable due to a piping [PSP] leak. Limiting Condition of Operation (LCO) 3.5.1 Condition B was entered for HPCS inoperability. This resulted in a loss of safety function for a single train system. EVENT DESCRIPTION On December 22, 2017 at 2348 hours, the HPCS system was declared inoperable due to discovery of a through-wall leak on the minimum flow line piping. The leak was on the outside bend of the first elbow downstream of the minimum flow restricting orifice [OR] and was leaking at approximately 60 drops per minute. TS LCO 3.5.1 Condition B was entered for HPCS inoperability. On December 23, 2017 at 0500 hours, event notification EN# 53137 was made to the NRC Operations Center in accordance with 50.72(b)(3)(v)(D). The flaw was characterized as thinning across an approximateiy one square inch area. Pipe wall thickness outside the. thinned area was at or above nominal wall thickness of 0.438 inches for a 4-inch diameter schedule 120 pipe. High water flow concentrated to the center-line of the upstream piping (caused by the restricting orifice) would impact directly to the thinned area of the elbow. A weld overlay (approximately 3-inch circle and 0.50 inches thick) was added over the thinned elbow area in accordance with ASME Code Case N-561-2, "Alternative Requirements for Wall Thickness Restoration of Class 2 and High Energy Class 3 Carbon Steel Piping Section XI, Division 1." The TS LCO was exited and the HPCS system was declared operable on 12/25/2017 at 2213 hours. CAUSE The cause was pipe wall loss due to a combination of cavitation and mechanical erosion wear. EVENT ANALYSIS A Probabilistic Risk Assessment (PRA) evaluation was performed. While the associated maintenance activity resulted in unplanned unavailability hours and was assessed via 10 CFR 50.65 (a)(4) requirements, a bounding analysis to account for "the event or condition that could have prevented the fulfillment of a safety function" condition conservatively indicates that the given event resulted in a very small change to overall plant risk with a change (delta) in core damage frequency (CDF) of 6.11 E-07/yr, and a change (delta) in the large early release frequency (LERF) of 3.52E-09/yr. The delta CDF and delta LERF values are well below the acceptable thresholds of 1.0E-06/yr and 1.0E-07/yr, respectively, as discussed in Regulatory Guide 1.174. The risk of this event is therefore considered very small in accordance with the Regulatory Guidance. | ML18045A057
Oyster Creek Nuclear Generating Station 05000219 1 OF 3 | Unknown Unit | Reactor Protection System Channel Disabled During Test Box Use | 02-16-2018 | On August 31, 2017, during a review of industry Operating Experience (FERMI 2, LER 2017-001) for the use of a Reactor Protection System (RPS) test box during main turbine surveillance testing, it was determined that Oyster Creek station procedures failed to implement the required action specified by Technical Specifications (TS) section 3.1, 1. note (nn) during testing. The surveillance tests associated with the Turbine Trip and Generator Load Rejection functions were revised in 2013 to use an RPS test box in order to minimize operational risks associated with the receipt of half scram signals during testing. The installation of the RPS test box caused two of the four required instrument channels for the Turbine Trip Scram function to be bypassed during testing. In accordance with station Technical Specifications, the required action to verify sufficient channels remained operable was not documented as complete within the action time specified in TS Table 3.1.1, note (nn). This issue was identified under normal operating conditions, and is reportable under 1O CFR 50.73(a)(2)(i)(B). NRG FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means ? ..... used to impose an information collection does not display a currently valid 0MB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-nn/doc-colleclions/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Oyster Creek Nuclear Generating Station 05000219 YEAR NUMBER NO. 2017 - 004 01 | Plant Conditions Prior To Event Event Date: August31,2017 Event Time: 10:30 hours ET Unit 1 Mode: Run Power Level: 100% Description of Event On August 31, 2017, during a review of industry Operating Experience (FERMI 2 2017-001) for the use of a Reactor P~otection System (RPS) test box during main turbine surveillance testing, it was determined that the Oyster Creek station procedures failed to implement the required action specified by Technical Specifications (TS) Section 3.1, 1. note (nn) during testing. The surveillance tests associated with the Turbine Trip and Generator Load Rejection functions were revised in 2013 to use an RPS test box to minimize operational risks associated with the receipt of half scram signals during testing. With the RPS test box installed, two of the four required Turbine Trip Scram inputs were bypassed. The action to verify sufficient channels remained operable was not documented as complete within one (1) hour as specified in TS Table 3.1.1, note (nn). TS Table 3.1.1, Function 11, Turbine Trip Scram, specifies the minimum number of operable channels as four per trip system. The test directed the RPS test box to be installed around the relay that actuates the specific channel in the RPS division that would receive a trip signal when the turbine stop valves closed or the pressure switch that senses low trip system oil pressure for the main turbine was tested. Cause of Event The cause has been determined to be insufficient technical rigor during the development of the procedure revision, and the failure to obtain an independent technical review of the procedure changes. The procedure preparer and approver did not identify that installation of the RPS test box resulted in the need to execute the TS action. Consequently, the Turbine Trip and Generator Load Rejection surveillance test procedures did not direct the performance of the required action. Analysis of the Event Since May 2013, Oyster Creek has used an RPS test box to perform the Turbine Trip and Generator. Load . Rejection surveillance tests. Each RPS division contains two logic channels that receive inputs from the turbine stop valve limit switches. Two stop valve limit switches are assigned to each RPS logic channel. The assignment of stop valve limit switches varies between the two channels in RPS division 1 and RPS division 2. When the turbine stop valves are less than 90 percent open, a limit switch associated with that valve opens in the RPS logic. When two stop valve limit switches in one trip channel open, a relay in the RPS logic system (relay 1K 11, 1 K12, 2K11, or 2K12) is deenergized, causing a half scram signal to be initiated. Installation of the RPS test box during the Turbine Trip and Generator Load Rejection surveillance tests would prevent the relays in the RPS channel from initiating causing the two stop valves assigned to that channel to be rendered inoperable. | ML18046A076
Susquehanna Steam Electric Station | Unit 2 | Secondary Containment Declared Inoperable Due to Trip of Zone II Equipment Exhaust Fan | 03-31-2020 | On September 16, 2017 at approximately 13:30, when performing a swap to place the Unit 2 "A" Reactor Building Equipment Compartment Exhaust fan (2V206A) in service, the fan tripped unexpectedly after being placed in service. Reactor Building differential pressure lowered to < 0.25 inches water gauge (WG) due to the unexpected trip of 2V206A. As a result, Technical Specification 3.6.4.1 Surveillance Requirement 3.6.4.1.1 was not met due to loss of Secondary Containment differential pressure. The 2V206B fan was placed back in service and Reactor Building differential pressure was restored to above 0.25 inches WG. The condition is being reported in accordance with 10 CFR 50. 73(a)(2)(v)(C) as an event or condition that could have prevented fulfillment of a safety function. The failure was not able to be replicated during investigation. The direct cause is inconclusive. A failure modes analysis was completed to identify the likely cause of the fan trip. Potential causes include one of the following: the flow control damper linkages binding, the low flow switch failing to reset, or the "A" and "B" fans running in parallel long enough to result in a low flow trip. A corrective action was identified to address each of these potential causes including greasing the linkages, testing the low flow switch reset and replacing the switch if necessary, and enhancing the affected procedures. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1 022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMS control number, the http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station Unit 2 05000388 NUMBER NO. 2017 -009 -o1 I | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, approximately 100 percent Rated Thermal Power Unit 2 -Mode 1, approximately 100 percent Rated Thermal Power There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. EVENT DESCRIPTION On September 16, 2017, a plant operator identified belts associated with the Unit 2 "B" Reactor Building Equipment Compartment Exhaust fan (2V206B) [EllS System/Component Identifier: VA/FAN] slipping and a hot burnt rubber smell in the area. The operator recommended swapping fans to place the "A" fan (2V206A) in service. At approximately 13:30, when performing the swap to place the 2V206A fan in service, the 2V206A fan ) tripped unexpectedly after being placed in service. Reactor Building [EllS System Code: NG] differential pressure lowered to < 0.25 inches water gauge (WG). As a result, Technical Specification 3.6.4.1 Surveillance Requirement 3.6.4.1.1 was not met due to loss of Secondary Containment differential pressure. The 2V206B fan was placed back in service and Reactor Building differential pressure was restored to above 0.25 inches WG. On September 16, 2017, at 15:53, this condition was reported (ENS #52973) in accordance with 10 CFR 50.72(b)(3)(v)(C) as an event or condition that, at the time of discovery, could have prevented the fulfillment of the safety function to mitigate the consequences of an accident by controlling the release of radioactive material. Susquehanna Steam Electric Station (SSES) has no redundant Secondary Containment System. CAUSE OF EVENT The failure was not able to be replicated during investigation. The direct cause is inconclusive. A failure modes analysis was completed to identify the likely cause of the fan trip. Potential causes include the following: 1. Linkages on Flow Control Damper PDD27522A [EllS System/Component Identifier: VA/CDMP] could have been binding and prevented the damper from going open. 2. Low Flow Switch FSL27522A [EllS System/Component Identifier: VA/FS] could have failed to reset during the 2V206A start. NRC FORM 3666 (04-2017) Page 2 of 4 | ML18046A861
Fermi 2 05000 341 1 OF 4 | Unknown Unit | Secondary Containment Pressure Exceeded Technical Specification Due to Reactor Building HVAC System Manipulation | 02-23-2018 | On January 11, 2018, at 1041 EST, a planned train swap of the Reactor Building Heating Ventilation and Air Conditioning (RBHVAC) system resulted in the Technical Specification (TS) for secondary containment (SC) pressure boundary not being met for less than one minute. The maximum secondary containment pressure recorded during that time was approximately 0.116 inches of vacuum water gauge. Secondary containment pressure was restored to within TS limits by starting Division 1 of the Standby Gas Treatment System (SGTS). There were no safety consequences or radiological releases associated with this event. The cause of this momentary loss of SC was determined to be the effect of the RBHVAC West Exhaust Fan Modulating Damper failing to fully open. For corrective actions, Fermi 2 has repaired the damper. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/3112020 (04-2017 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learneda re incorporated intot he licensinpgr ocesasn df ed back to industry. Send I LICENSEE EVENT REPORT (LER) comments regardinbugr den estimate to theI nformation Services Branch (T-2 F43), U.S. Nuclear CONTINUATION SHEET Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, andto t heD esk Officer, Office of InformaatinodnR e gulatory Affairs, " *. NEOB-10202, (3150-0104), Office of Managemeanntd B udgeWt,a shington, DC2 0503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose ani nformatcioolnle ction does not display a currently valid OMB control number, the http://www.nrc.govlreading-rm/doc-collections/nureas/staff/sr1022/r3) NRC may not conduct or sponsor, anda persoins not required to respond to, thei nformation collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000- NUMBER NO. Fermi 2 341 2018 - 0 1 - 00 | INITIAL PLANT CONDITIONS: Mode -1 Reactor Power - 100 percent There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT: On January 11, 2018, while in Mode 1 at 100 percent power, a planned train swap of the Reactor Building Heating Ventilation and Air Conditioning (RBHVAC) [[VA]] system in support of troubleshooting vibrations on the East Supply Fan was initiated. Following shutdown of the Center Supply and East Exhaust Fans [[FAN]], secondary containment (SC) [[NH]] pressure began to rise. At 1041 EST, the Technical Specification (TS) for SC pressure boundary was exceeded. Division 1 of the Standby Gas Treatment System (SGTS) [[BH]] was started and restored SC vacuum to within the TS operability limit of greater than or equal to 0.125 inches of vacuum water gauge per TS Surveillance Requirement (SR) 3.6.4.1.1. The duration of the TS not being met was less than one minute and the maximum SC pressure observed within the Control Room during the event was 0.117 inches of vacuum water gauge. SC was declared OPERABLE at 1045 EST. There are two recorder divisions to monitor SC pressure. Review of the pressure recorder [[PR]], following January 11, identified the highest pressure was 0.116 inches of vacuum water gauge. During the transient, the Division 1 recorder indicated that the TS operability limit had been exceeded for less than one minute. The Division 2 recorder indicated that the TS operability limit was maintained throughout the transient, with the lowest observed vacuum of 0.164 inches of vacuum water gauge. Recorder data deltas were reviewed with no notable trend. An 8-hour event notification (EN 53165) was made to the NRC based on meeting the reporting criteria of Title 10 Code of Federal Regulations (10 CFR) 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. This Licensee Event Report (LER) is being made under the corresponding requirement in 10 CFR 50.73(a)(2)(v)(C). SIGNIFICANT SAFETY CONSEQUENCES AND IMPLICATIONS: There were no safety consequences or radiological releases associated with this event. At no time during this event was there a potential for endangering the public health and safety. The specified safety function of the SC is to contain, dilute, and hold up fission products that may leak from primary containment following a Design Basis Accident (DBA). In conjunction with operation of the SGTS and closure of certain valves [[V]] whose lines penetrate the SC, the SC is designed to reduce the activity level of the fission products prior to release to the environment and to isolate and contain fission products that are released during certain operations that take place inside primary containment, when primary containment is not required to be OPERABLE, or that take place outside primary containment. It is possible for the pressure in the control volume to rise relative to the environmental pressure (e.g., due to pump [[P]] and motor [[MO]] heat load additions). To prevent ground level exfiltration while allowing the SC to be designed as a conventional structure, the SC requires support systems to maintain the control volume pressure at less than the external pressure. For the SC to be considered OPERABLE, it must have adequate leak tightness to ensure that the required vacuum can be established and maintained. | ML18054A752
i | Unknown Unit | 121 Motor Driven Cooling Water Pump Auto Start due to Smoking Packing on 11 Cooling Water Pump | 00-07-2018 | On January 8, 2018, Prairie Island Nuclear Generating Plant (PINGP) staff were running the 11 Cooling Water (CL) pump for post-maintenance testing. At 1437 CST, operators stopped 11 CL pump following a report from Maintenance staff that the inboard pump packing was smoking. Shortly after operators secured 11 CL pump the 121 Motor Driven Cooling Water Pump (MDCLP) auto-started and supplied the CL header. This event is reportable under 10 CFR 50. 73(a)(2)(iv)(A) as an event that resulted in automatic actuation of an emergency service water system. The cause of the 121 MDCLP auto-start was determined to be low CL header pressure after 11 CL pump was secured. Operators secured the 11 CL pump when they received the report that the inboard pump packing was smoking. Investigation found the most likely cause of the smoking pump packing was due to inadequate procedural guidance regarding packing replacement criteria. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 {04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to Industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43}, U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-1 0202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this used to impose an information collection does not display a currently valid OMB control number, the form http://www.nrc.gov/reading-rm/doc- NRC may not conduct or sponsor, and a person is not required to respond to, the information collections/nuregs/staff/sr1 022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Prairie Island Nuclear Generating Plant 05000-282 NUMBER NO. Unit 1 2018 -001 -00 | DESCRIPTION OF EVENT On January 8, 2018, Prairie Island Nuclear Generating Plant (PINGP) Unit 1 and Unit 2 were both operating at 100% in MODE 1 and PINGP staff were running the 11 Cooling Water (CL) pump 1 for post-maintenance testing. The 11 CL pump is a nonsafety-related pump manufactured by Worthington Pump Corporation model number 16-LN-28. At 1437 CST, operators stopped 11 CL pump following a report from Maintenance staff that the inboard pump packing was smoking. Shortly after operators secured 11 CL pump the 121 Motor Driven Cooling Water Pump (MDCLP) auto-started and supplied the CL heade~. The 121 MDCLP is designed to start automatically if CL header pressure drops to 80 pounds per square inch gauge (psig). EVENT ANALYSIS The PINGP CL System is a shared system for Units 1 and 2 and provides a heat sink for the removal of process and operational heat from safety-related components during a design basis accident or transient. During normal operation and shutdown, the CL System also provides this function for various safety-related and nonsafety-related components. PINGP Units 1 and 2 share five CL pumps: one motor-driven and two diesel-driven vertical pumps that take a suction from the safeguards bay and two nonsafety-related motor-driven cooling water pumps. All five pumps are connected to a common pump discharge that directs CL flow into a header that splits into two trains upon · receipt of a Safety Injection signal. The 121 MDCLP can function as a safeguards replacement when either safeguards diesel-driven cooling water pump is taken out of service. In this configuration, the pump is aligned manually to the appropriate train of safeguards power and motor:-operated valves are administratively disabled in accordance with Technical Specifications. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of an emergency service water system. SAFETY SIGNIFICANCE There was no radiological, environmental, or industrial impact associated with the 121 MDCLP auto-start, and the health and safety of the public were not affected. The auto-start of the 121 Motor Driven Cooling Water Pump did not challenge nuclear safety as all plant systems responded as designed; therefore, this event does not represent a safety system functional failure for Unit 1 or Unit 2. 1 EllS Component Identifier: P 2 EllS System Code: 81 NRC FORM 3668 (04-2017) Page 2 of 4 | ML18068A028
Browns Ferry Nuclear Plant | Unit 3 | Separated Pressure Switch Sensing Line Causes Unit 3 SCRAM | 03-12-2018 | On January 10, 2018, at approximately 0926 Central Standard Time (CST), with Unit 3 at 74 percent power, Browns Ferry Nuclear Plant (BFN) received an automatic scram on Reactor Protection System (RPS) Turbine Control Valve (TCV) fast closure trip. The support bracket for Unit 3 TCV #2 Electro- Hydraulic Control (EHC) pressure switch separated from TCV #2 allowing the mass of the pressure switch to break the hydraulic sense line. As a result, the EHC pressure switch sensed low pressure and triggered a half scram. With a half-scram previously in place due to an unrelated issue from closure of TCV #3, the additional half-scram resulted in an automatic scram on Unit 3 which is a reportable condition. Safety systems responded as designed and the reactor scram was uncomplicated. The apparent cause of this event was determined to be high cycle fatigue failure of the Unit 3 TCV #2 EHC pressure switch support bracket. This failure was corrected by replacing the failed mounting bracket with a newly designed mounting bracket. The corrective action to reduce the probability of recurrence is to install viscoelastic dampeners on the steam piping to reduce the overall piping vibration on the area components. The dampeners are expected to reduce overall piping vibration and the probability of future vibration induced failures of various components in the moisture separator rooms. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Browns Ferry Nuclear Plant, Unit 3 05000-296 2018 -001 -00 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Unit 3 was in Mode 1 at 74 percent power. II. Description of Event A. Event Summary On January 10, 2018, at approximately 0926 Central Standard Time (CST), with Unit 3 at 74 percent power, BFN received an automatic scram on Reactor Protection System (RPS) Turbine Control Valve (TCV)[PCV] fast closure trip. Unit 3 was operating at reduced power because TCV #3 failed closed due to Linear Variable Differential Transformer (LVDT) failure resulting in a half scram condition on the A2 RPS channel. Subsequently, Unit 3 TCV #2 failed due to the Electro-Hydraulic Control (EHC)[JI] relay emergency trip supply (RETS) pressure dropping because of a high cycle fatigue failure of TCV #2's associated pressure switch (3-PS-047-0144). The pressure switch on the TCV #2 fast acting solenoid valve (FASV)[PSV] disconnected and tripped the 81 RPS channel. A Unit 3 automatic reactor scram was initiated, since the A2 RPS channel was already tripped. All safety systems functioned as expected. This event was reported by the Tennessee Valley Authority (TVA) in Event Notification (EN) 53162 on January 10, 2018, at 1353 ET, under the four- and eight-hour non-emergency reporting requirements pursuant to Title 10 of the Code of Federal Regulations (10 CFR) 50.72(b)(2)(iv)(B) for an event that resulted in actuation of the RPS when the reactor is critical and 10 CFR 50.7 2(b )(3)(iv)(A) for a valid actuation of RPS when the actuation results in a reactor scram or trip. This event is also reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A), as an event that resulted in an automatic actuation of the RPS, including reactor scram or reactor trip. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, components, or systems that were inoperable at the start of the event that contributed to the event. NRG FORM 366A (04-2017) Page 2 of 6 | ML18071A123
Limerick Generating Station | Unit 1 | Core Spray Failed to Start Resulting in Condition Prohibited by TS | 03-13-2018 | On October 5, 2017, when the 1C Core Spray pump breaker hand switch was placed in start, the breaker failed to close. The 1C Core Spray Pump was declared inoperable and Limiting Condition for Operation (LCO) Action 3.5.1.a.1 was entered. An initial investigation identified that the breaker limit switch which energizes the closing springs charging motor became dislodged inside the control device. With the contact unable to complete the circuit, the charging motor could not energize to charge the closing springs. An Exelon Power Labs analysis identified the cause of the failure to be associated with welding of the limit switch contacts eventually resulting in displacement of the limit switch. This condition existed since the last time the 1C Core Spray Pump was in service, July 17, 2017, until the discovery on October 5, 2017. Although this event was not considered to be within the Station's ability to foresee and correct, the LCO Actions were not completed in the required time frames provided in Technical Specification (TS). Therefore, an Operation or Condition Prohibited by TS existed and is reportable under 1O CFR 50. 73(a)(2)(i)(B). NRG FORM 366 (04·2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Seivices Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required lo respond to, the information http:/lwww.nrc.gov/readinq-rm/doc-collectionslnuregslstafflsr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR Limerick Generating Station, Unit 1 05000352 NUMBER NO. 2017 - 004 - 00 | I. Unit Conditions Prior to the Event Limerick Generating Station (LGS) Unit 1 was operating in Operational Condition (OPCON) 1 at 100 percent power at the time of the event. There were no other structures, systems, or components inoperable that contributed to the event. II. Description of the Event On October 5, 2017 at 03:45, LGS, Unit 1 commenced a Pump Valve and Flow (PV&F) test for 1A Core Spray [BM] in accordance with Technical Specifications (TS) Surveillance Requirement 4.5.1.b.1. On October 5, 2017 at 04:00, when the 1C Core Spray pump breaker hand switch was placed in start, the breaker failed to close. Investigation at the breaker [BKR] showed that the closing springs on 1C Core Spray Pump did not indicate as charged. Therefore, the 1C Core Spray Pump was declared inoperable due to failure to start when demanded from the Main Control Room (MCA) hand switch and Limiting Condition for Operation (LCO) Action 3.5.1.a.1 was entered due to one Core Spray Subsystem (CSS) being inoperable. On October 5, 2017 at 23:00 the LCO was exited when 1C Core Spray breaker was repaired and the PV&F test was completed. Investigation of the 4KV breaker identified that the breaker closing springs were not fully charged which prevented the breaker from closing. A faulty control device was determined to be the cause and the device was replaced. The 1C Core Spray pump was last in service on July 17, 2017 to support motor testing. It was determined that the 1C Core Spray pump had been inoperable from July 17, 2017 to the time of discovery of this condition on October 5, 2017. Exelon Power Labs analysis revealed that during the previous operation of the breaker, on July 17, 2017, the breaker retaining spring became dislodged as a result of multiple breaker operations and welding action that was occurring with the limit switch contact closed. Although this event was not considered to be within the Station's ability to foresee and correct, the LCO Actions were not completed in the required time frames provided in TS. Therefore, an Operation or Condition Prohibited by TS existed and is reportable under 1O CFR 50.73(a)(2)(i)(B). Ill. Analysis of the Event When the breaker is initially racked into the switchgear, the closing springs will be discharged. As the breaker reaches the test position, 125 VDC is applied to the breaker control device and the closing springs charging motor will energize due to the closing springs limit switch being closed. After the closing springs are charged, the limit switch will open to de-energize the charging motor. The closing springs remain charged as the breaker is racked into the connected position. With the closing springs NAC FORM 366A (04-2017) Page _2_ of _4_ | ML18072A022
Oyster Creek Nuclear Generating Station 05000219 1 OF 3 | Unknown Unit | Failure of the Emergency Diesel Generator #2 During Surveillance Testing due to a Broken Electrical Connector | 03-12-2018 | On 10/09/17, during the bi-weekly Emergency Diesel Generator (EDG) #2 Load Test, a Generator Lockout signal (86G) was received which tripped the EDG output breaker. This failure resulted in EDG #2 being declared inoperable, and entry into an unplanned 7-day Limiting Condition for Operation (LCO) at 0312. Troubleshooting identified a broken electrical ring lug connector on a current transformer that provides an input to the protective relay logic. The investigation determined the connector failure was due to fatigue cracking that was initiated by stresses caused by bending and twisting of the electrical lug. The ring lug was most likely distressed during initial installation in the 1990's. The condition that led to the EDG #2 trip existed for greater than the allowed outage time in the plant's Technical Specification (TS) and is reportable under 1O CFR 50. 73(a)(2)(i)(B). NRG FORM 366 {06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016)) Estimated burden per response to comply with this mandatory collection request 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid 0MB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the infonnation http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/@0 collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Oyster Creek Nuclear Generating Station 05000219 YEAR NUMBER NO. 2017 - 005 01 | Plant Conditions Prior To Event Event Date: October 09, 2017 Event Time: 03:12 hours ET Unit 1 Mode: Run Power Level: 100% Description of Event On 10/09/17, during the bi-weekly EDG #2 Load Test (station procedure 636.4.013), a Generator Lockout (86G) signal was received which tripped the EDG output breaker. The diesel had run for 4 minutes loaded in the procedurally prescribed band of 2600-2800 KW prior to receiving the 86G lockout signal. The EDG #2 trip is documented under Issue Report (IR) 04060815. This failure resulted in EDG #2 being declared inoperable, and entry into an unplanned 7-day LCO (TS Section 3.7.D) at 0312. Troubleshooting identified a broken electrical ring lug connector on one current transformer (CT5) that provides an input to a differential current relay (87G). When the ring lug connector became detached fmm the terminal point, the relay sensed a current imbalance and the protective relay logic actuated. The differential current relay (87G) provided an input to the Generator Lockout circuit, causing the lockout relay (86G) to trip the EDG#2 output breaker. Repairs were completed on 10/10/17 at 0557. EDG #2 was satisfactorily tested and declared operable at 0805, and the 7-day LCO was exited. Cause of Event The investigation determined the electrical ring lug connector failure was due to fatigue cracking that was initiated by stresses caused by bending and twisting of the electrical lug. Analysis of the Event The ring lug that failed was sent to a metallurgical lab for failure analysis. The metallurgical analysis determined the ring lug had failed due to fatigue cracking. The investigation performed for the EDG#2 trip concluded the fatigue cracking was initiated by historical stresses caused by bending and twisting of the electrical lug beyond limits specified in industry guidelines. Based on a review of recent maintenance records for EDG#2 and a review of plant procedures and work practices, the investigation concluded the ring lug was most likely distressed during initial installation in the 1990's. Assessment of Safety Consequences Two EDG units serve as the Standby Power Supply for Oyster Creek Nuclear Generating Station (OCNGS) by providing an emergency source of power to the .4.16 kV buses 1C and 1 D in the event of a loss of normal power. The EDG units are designed to start and load automatically, if required. Non-essential loads are automatically shed by under-voltage sensing devices on loss of offsite power to ensure that the EDG units are not overloaded. The capacity of the EDG units is sufficient to sequentially energize for starting all safety-related pumps and auxiliaries required for a safe shutdown of the reactor in the event of a Design Basis Accident. The EDG units are independent of each other, except for a common bulk fuel storage supply, and are provided with auxiliary systems to ensure reliable starting and continuous operation with no Operator attention. Power to start the EDG units is self-contained and is not dependent on the availability of any other source of normal plant power at the moment of initiation. NRG FORM 366A (06-2016) Page _2_ of _3_ | ML18078A296
River Bend Station | Unit 1 | Loss of HiQh Pressure Core Spray Safety Function Durinq Surveillance Due to Malfunction of Test Return Valve | 03-15-2018 | On March 23, 2017, at 0028 CDT, with the plant operating at 100 percent power, the high pressure core spray system (HPCS) was declared inoperable due to a malfunction of a motor-operated valve (MOV) in the system. During a scheduled test, the HPCS pump est return valve to the suppression pool was given a "close" signal after having been opened for the test. The valve position lights indicated that it fully closed, but system flow parameters did not respond as expected. An operator went to the valve and reported hat it appeared that the anti-rotation device on the valve actuator had failed, and that the valve was not fully closed. This valve is a primary containment isolation valve. An examination of the MOV found that a set screw on the actuator had loosened, allowing the anti-rotation device to slip down the valve stem. When the anti-rotation device slipped far enough, the retainer keys fell out, allowing the valve stem to disengage from the anti-rotation device. The maintenance history of the valve was investigated, and it was found that in 1996, the anti-rotation device was loosened during a scheduled maintenance task. A review of the work documentation package and the vendor manual found that no torque value was specified for the set screw. The Flowserve Vendor was contacted and recommended the set screw be torqued to 60 ft.-Ibs. lAW Entergy procedure EN-MA-14S, MAINTENANCE STANDARD FOR TORQUE f,PPLICATIONS. This condition is being reported in accordance with 10 CFR SO.72(b)(3)(v) as a potential loss of safety function of the HPCS system and the primary containment isolation function. An evaluation of the as-found condition has concluded that the HPCS system and primary containment isolation would have been able to perform their design safety function had an actual design basis event occurred during the test. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported / .......' 1\ lessons learned are incorporated into Ihe licensing process and fed back to industry. Send I - LICENSEE EVENT REPORT (LER) • i comments regarding burden estimale to the Information Services Branch (T-2 F43), U.S. Nuclear ~ ~ Regulatory Commission, Washington, DC 20555-0001, or bye-mail to CONTINUATION SHEET Infocoliects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-l 022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http://WNW.nrc.gov/reading-rm/doc-collections/nureqs/staff/srl0221@O NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER MJMBER YEAR SEQUENTIAL REV River Bend Station - Unit 1 05000-458 NUMBER NO. 2017 004 01 | REPORTED CONDITION On March 23, 2017, at 0028 COT, with the plant operating at 100 percent power, the high pressure core spray system (HPCS) [BGlwas declared inoperable due to a malfunction of a motor-operated valve (MOV) in the system. During a scheduled test, the HPCS pump test return valve (**TV**)to the suppression pool was given a "close" signal after having been opened for the test. The valve position lights indicated that it fully closed, but system flow parameters did not respond as expected. An operator went to the valve and reported that it appeared that the anti-rotation device on the ~alve actuator had failed, and that the valve was not fully closed. This valve is a primary containment isolation valve and has a design safety function to close automatically upon receipt of a system actuation signal. IThis condition is being reported in accordance with 10 CFR SO.73(a)(2)(v)(B) and 10 CFR SO.73(a)(2)(v)(C) as a potential loss of safety function of the HPCS system and the primary containment isolation function. INVESTIGATION Operators diagnosing the condition of the valve determined that the anti-rotation device had become dislocated. An examination of the MOV found that a set screw on the actuator had loosened, allowing the anti-rotation device to slip down the valve stem. When the anti-rotation device slipped far enough, the retainer keys fell out, allowing the valve stem to disengage from the anti-rotation device. The valve limit switches were also displaced by this action, resulting in an erroneous indication in the main control room that the valve was fully closed. In terminating the test, the MOV was given a "close" signal for at least five seconds in accordance with operations administrative guidelines. At this time, system flow parameter returned to normal, and the operator at the MOV reported that it was fully closed. This MOV is a throttle valve, and the extra amount oftime under a "close" signal resulted in the valve actually going fully closed. The maintenance history of the valve was investigated, and it was found that in 1996, the anti-rotation device was loosened during a scheduled maintenance task. A review of the work documentation package found that no torque value was specified for the set screw, whereas the Flowserve Vendor recommends the torque values in EN-MA-14S which requires the set screw to be torqued to 60 ft.-Ibs. An extent-of-condition was performed, and two other similar valves in the HPCS system test return line are susceptible to the same failure mechanism. During work in 2014, the anti-rotation devices for those valves were loosened_ The applicable work packages did not incorporate the EN-MA-14S specification to torque the set screw to 60 ft.-Ibs. The work instructions only directed that the set screw should be "snug tight." | ML18081A024
grand gulf nuclear station | Unknown Unit | Loss of Secondary Containment and lnoperability of the Standby Gas Treatment Systems as a result of a damages power supply. | 03-22-2018 | On March 24, 2017 the A Standby Gas Treatment System (SGTS) was not operating as expected. The investigation revealed the Single Nest Power Supply was damaged, resulting in loss of flow control. The power supply had been replaced on February 23, 2017. SGTS A was not run between replacement of the power supply and the time of discovery condition on March 24, 2017. Additionally, SGTS B was removed from service for_planned maintenance on February 28, 2017, and returned to service on March 3, 2017. The cause of this event has been determined to be an inadequate design that allowed the standby gas treatment system filter train to not provide annunciation and indication upon power loss to the control room. The power supply was replaced and tested satisfactorily. Implementation of a design modification to ensure the standby gas treatment system filter train will provide annunciators/indication upon power loss to the control room. There were no actual nuclear safety consequences or radiological consequences. Page 1 of 3 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (4-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 LICENSEE EVENT REPORT (LER) F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, a·nd to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not (See NUREG-1022, R.3 for instruction and guidance for completing this forin display a currently valid OMB control number, the NRC may not conduct or sponsor, and a http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3() person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 3. LER NUMBER YEAR I SEQUENTIAL I REV. Grand Gulf Nuclear Station, Unit 1 NUMBER NO. 05000 416 2017-002-01 | DESCRIPTION On March 24, 2017, while performing a surveillance on the A train of Standby Gas Treatment System (SGTS) [BH] the SGTS Flow Recorder [FR] was indicated a downscale reading. The Plant Data System [ID] computer points indicated a flow mismatch of approximately 5000 cubic feet per minute (CFM) between the available 'indications. Due to the mismatch indications and the downscale reading the surveillance was terminated and Standby Gas 11A11 was returned to standby. The investigation determined a damaged Single Nest Power Supply [ED] (Bailey Model 771111AAAA1) for SGTS A was replaced on February 23, 2117. Subsequent testing determined that the replacement power SL!PP!Y was not fully functional at the time it was installed, resulting in a loss of the associated train's flow control. This damaged condition was not identified until March 24, 2017, when the A SGTS was tested. The A SGTS was in a standby configuration between the time the damaged power supply was installed and the time of discovery condition. Prior to the power supply being replaced the system had been successfully tested and therefore it was determined that this condition could only have been present since th~ installation of the new Power Supply was completed on February 23, 2017 and the time of detection on March 24, 2017. I The investigation further revealed that the B SC:3TS was removed from service for planned corrective and _preventive maintenance on·February 28, 2017, and returned to service on March 3., 2017. The above described condition rendered the ASGTS inoperable between February 23, 2017 and March 24, 2017. The B SGTS was inoperable between February 28, 2017 and March 3, 2017. Therefore, both trains were inoperable between February 28, 2017 and March 3, 2017. REPORTA BILITY This condition is reportable as an event that could have prevented the fulfillment of a safety function in accordance -with -1 O· CFR 50:73(a)(2)(v)(C) -for the time -period when -both -the A and B SGTSs were -inoperable. The condition is also reportable as a condition prohibited by technical specifications in accordance with 1O CFR 50. 73(a)(2)(i)(B) for the A SGTS train being inoperable for a period longer than allowed by technical specifications. CAUSE The cause of this event has been determined to be an inadequate design that allowed the standby gas treatment system filter train to not provide annunciation and indication upon power loss to the control room. Page 2 of 3 | ML18081B210
Grand Gulf NuclearStation | Unit 1 | Reactor Core Isolation Cooling System lnoperability Due to Lockout Circuit Settings | 10-31-2018 | On December 12, 2017, at approximately 0918 hours, Grand Gulf Nuclear Station (GGNS) was in_ , MODE 1 and increasing. power when the unit experienced an essential transformer (ESF-11) lockout. Concurrent with the lockout the Reactor Core Isolation Cooling (RCIC) system received a Division I isolation signal. The cause-of the-RC IC -isolation -is -determined -to -be -installation -of-temperature -switches in -the-RC IC isolation initiation circuits with unrecognized response times. The power bus monitor time delay relays were adjusted from a one second delay to a 10-second delay to account for the response of the terr:1perature switches. Additionally, a review of engineering change testing involving applicable temperature switch installations was performed to verify the post modification testing requirements of the Entergy testing philosophies are met. There was no ·increase to any accident consequences, and no ·impact on plant safety or the sa·fety of the public, Page 1 of 3 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (6-2016} Estimated burden per response to comply with this mandatory collection request: 80 hours.'' Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or bye LICENSEE EVENT REPORT (LER} mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and CONTINUATION SHEET Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection.. · 1. FACILITY NAME 2. DOCKET 3. LER NUMBER YEAR I SEQUENTIAL I REV. Grand Gulf Nuclear Station, Unit 1 05000 416 NUMBER NO. 2017-009-00 | DESCRIPTION On December 12, 2017, at approximately 0918 hours, Grand Gulf Nuclear Station (GGNS) experienced an essential transformer (ESF-11) lockout. Concurrent with the ESF-11 transformer lockout, the Reactor Core Isolation Cooling (RCIC) [BN] system received a Division I isolation signal. Leak detection NUS [NUS] temperature switches (NUS switches) for the main steam line tunnel installed in 2007 were discovered to actuate and de-actuate instantaneously upon both loss of power and upon restoration of power. The initialization sequence which occurs upon restoration of power resulted in a RCIC isolation signal. Because the condition persisted for a period of time greater than the existing logic time delay, RCIC isolation occurred. The RCIC isolation circuits have a one second time delay to prevent spurious isolation of RCIC. Because the sequence duration of 1.58 seconds exceeded the existing logic time delay of one second, RCIC isolation occurred. RCIC was placed back in standby at 1440 hours on December 12, 2017. Analysis of the RCIC isolation initiation circuits has determined that RCIC received the isolation signal only upon restoration of power. The direct cause of RCIC isolation was the response of temperature switches to power restoration. The response, which testing has confirmed, is that the NUS temperature switches remain in the tripped state for a brief period of time when their power is restored. Because of this response the leak detection circuit begins a one second time delay to prevent spurious isolation of RCIC. Because the described condition persists for approximately 1.58 seconds, the existing one second time delay setpoint is exceeded, thereby permitting RCIC isolation. Although the event occurred in December 2017, the final reportability was not determined until February 20, 2018, due to the time required to analyze the condition. REPORTABILITY STATEMENT This event is reportable as a licensee event report in accordance with 1O CFR50.73(a)(2)(i)(B) as an operation or condition which was prohibited by the plant Technical Specifications. The plant configuration that could have prevented the RCIC system from being available under all expected plant conditions existed for a time longer than allowed by Technical Specification Completion Time for the system. This event was included in ENS notification 53115. CAUSE In 2007 the subject RCIC temperature switches were changed from a Riley brand to a NUS brand. Discussion with the vendor determined that the observed response to loss and restoration of power to NUS switches is a design feature. Page2of3 ' | ML18085A078
Surry Power Station | Unit 1 | Loss of 4160 Volt Emergency Bus and Start of Emergency Diesel Generator due to Opening Emergency Bus Potential Transformer Drawer 5. EVEI\JT DATE 6. ILE R NUMBEIR 7. REPORT DATE 8. OTHER FACILITIES INVOLVED MONTH DAY YEAR YEAR SE N Q U U M E B N E T R IA L R N E O V . MONTH DAY YEAR S F u A r C r I y LIT Y P N o A w ME e r Station, Unit 2 05 D 0 O 0 C 0 K ET NU 2 M 8 B 1 ER - - FACILITY NAME DOCKET NUMBER 01 17 2018 2018 001 00 03 19 2018 05000 9. OPERATING MODE 11. THIS REPORT IS SUBMITTED PURSUANT TO THE REqUIREMENTS OF ·IO CFR §: (Check all that apply) D D · D 20.220·1 (b) 20.2203(a)(3)(i) 50.73(a)(2)(ii)(A) D 50.73(a)(2)(viii)(A) ··o . , N ..,., · -- · 20.2201(d) ,··· D ;zci.2203(a'i<3J(H). ·D so.73(a}(2)(ii)(B) · . ' ~ ·· D 50.73(a)(2)(Viii)(B) ' D 20.2203(a)(1) D 20.2203(a)(4) · D so.1~(a)(2)<rni: · ' [J 50'.73(a)(2)(ix)(A) .. .. ... D 20.2203(a)(2)(i) · D 50.36(c)(1)(i)(A) l:ZJ so.73(a)(2)(iv)(A) · .. · D 50.73(a)(2)(x) ·o D 1'0. POWER LEVEL 20.2203(a)(2)(ii) D 50.36(c)(1)(ii)(A) 50.73(a)(2)(v)(A) D 73.71(a)(4) I D 20.22o~(a)(2)(rn) . D .so.3a(c)(2) D 50.73(a)(2)(v)(B) D 73.71(a)(5) D D 29.2203(a)(2)(iv) D so.4a(a)(3)(ii) · D 50.73(a)(2)(v)(C) 73.77(a)(1) 100 D .20.2203(a)(2)(v) D 50.73(a)(2)(i)(A) D 50.73(a)(2)(v)(D) D 13.77(a)(2)(i) D 20.2203(a)(2)(vi) D 50.73(a)(2)(i)(B) D 50.73(a)(2)(vii) D 13.77(a}(2)(ii) ,• {'.,i?~I};'.,.tI~ ::;,:}:·0c.:::i,i:,tf f > D 50.73(a)(2)(i)(C) D OTHER Specify in Abstract below or in NRC Form 366A 12. LICENSEE CONTACT FOR THIS LER LICENSEE CONTACT .. . . . . TELEPHONE NUMBER (Include Area Code) Barry Ga'rb~r (757) 365:2725 ,13. COMPLETE ONE LINE FOR EACH COMPONENT FAILURE DESCRIBED IN THIS REPORT CAUSE ... SYSTEM·· COMPONENT FA M C A 'rU N R U E - R RE T P O OR E T P A IX B LE 1a• CAUSE SYSTEM COMPONENT FA M C A TU N R U E - R RE T P O O R E T P A IX B LE A .EK DR G080 .Y .. ,;,. ri;; ' 14. SUPPLEMENTAL REPORT EXPECTED 15. EXPECTED MONTH . DAY. VEAR ' DYES (ff yes, complete 1,5. ·EXPECTED SUBMISSION DATE) [Z]· NO SUB D M A IS TE S ION .. ABSTRACT (Limit to ·1400 spaces, i .. e., approximately 15.single-spaced typewritten lines) .. .. , . On January 17, 2018, at 09:52 hours, with Units 1 and 2 at 100% power, the 1·J emergency bus p·otential transformer drawer located inside the 1J 4160 Vemergency bus uhdervolfage (UV) ·relaying cubicle was opened inadvertently, generating a 1J .emergency bus UV signal. The signal caused the normal 1J emergency bus supply·breaker to open and also caused the automatic start· of the #3 Emergency Diesel Generator (EOG). The #3 EOG energized the 1J emergency . bus, and all 1J emergency bus loads were verified to be in correct alignment.. . . . After proper re-installation of the bus potential. transformer drawer was verified, normal alignment of. the #3 EOG and normal alignment of the prima.ry, off-site power supply to the 1J emergency bus were reestablished. Both Units 1 and 2 remained at 100% pqwer during the event. All equipment operated as designed .. '. It was determined that the Operations team, while reyiewing an electrical tag-out walkdciwn task, did not adequately perceive and manage the risk of opening the:1J bus potential transformer drawer. Also, the operator who opened the . drawer did not understand the impact to the UV sensing circuit by opening the bus potential transformer drawer. · of The condition was reported as an event or condition that results in a valid actuation an emergency electrical power system, pursuant to 10 CFR. 50. 72(b)(3)(iv)(A). This event is being reported as an event.or <::or:,dition that results in a. valid actuation of an emergency electrical power system, pursuant to 50.73(a)(2)(iv)(A). NRC FORM 366 (04-2017) Page 1 3 NRC FORM 366A U.s;·NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB:. NO: 3.150-0104 EXPl~ES: 03/31/2020 (04-2017) Estimated burden per response ici ·c omply with' this mandatory collection request: 80 hours. Reported ..l essons learned are incornorated. into the licensing process .and le.a back to industry, LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear. Regulatory Commission, Washington, DC 2055q-0001, or by e-mail to lnfocollects. CONTINUATION SHEET Resource@nrc.gov, and to the Desk Officer, Office of .Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Managemen(and Budget, Washington, DC 20503. If a (See NUREG-1022·, R.3 for instruction and guidance for completing this form means_ u~ed to imJ)Ose an information collection does not display.a currently valid 0MB control · number, the· NRG may not conduct or sponsor, and a person is not required to respond to, the http://www.nrc.gov/reading-rm/doc-collectio~s/nuregs/staff/sr1022/r3/) information collection. · · · 1. FACILITY NAME .. 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Surry Power Station, Unit 1 · 05000- 280 NUMBER NO. 2018 • 001 00 NARRATIVE 1,.0 DESCRIPTION OF.THE EVE.NT On Ja~uary 17, 2018, at 09:52 hours, with Units 1 and 2 oper~ting at 100% power, the 1 J bus potential transformer drawer [EIIS£i<~DR]. located inside the tJ 4.160V Emergency Bus UV relaying cubicle.was inadvertently opened while performing an electrical tag-out walkdown. The 1J 4160 V emergency bus UV potential transformers [EIIS-EK-XPT] and fuses [El IS-EK-FU] are attached to the inner panel of the drawer which, when opened, disconnected the UV sensing circuit and generated a UV signal. Emergency bus 1J [El IS-EK-BU] was de-energized due to the normal bus supply breaker [EIIS-EK-BKR] opening on the UV signal. The UV signal also initiated the start sequence for the #3 EDG [EIIS-EK-DG]. The #3 EDG started normally and energiz.ed the 1J bus, as designed. Also as designed, the UV signal tripped the 1 J stub bUs breaker [EIIS-EK-BKRJ and the running component cooling (CC) water pump breaker · powered by the 1 J bus. The standby CC water pumps [EIIS-CC-P] automatically started when a low CC system pressure signal was received as a result of the power loss to the running CC water pump. All 1J emergency bus loads were verified to be in proper alignment by the Operations team. All equipment performed as expected, and there were no unexplained occurrences. · At 10:47. hours, normal CC pump alignment was restored. At 11 :56 hours; the 1J 4160 V emergency bus potential transformer fuses were verified to be installed properly, and restoration of emergency bus normal configuration was commenced. At 12:54 hours, after the 1J 4160 V emergency bus normal supply breaker had been closed, the #3 EDG was secured and returned to normal automatic standby alignment. · An eight-hour non-emergency event notification was made to the NRC pursuant to 10 CFR 50.72(b)(3)(iv)(A) due a valid actuation of the #3 EDG, This report is being made pursuant to 10 CFR 50.73(a)(2)(iv)(A) due a valid actuation of the #3 EDG. 2.0 SIGNIFICANT SAFETY CONSEQUENCES AND 11\/lPLICATIONS During the. event, the redundant 1H 4160 V emergency bus was supplied by normal off-site power. Also, the Unit 2 4160 V emergency busses, 2H and 2J, were supplied by normal off-site power. The #1, #2, and #3 Emergency Diesel Generators.remained available to supply power to emergency b_us loads. All equipment performed as designed, and the normai equipment alignment was restored by. the Operations team in a timely manner. Therefore this event is of minimal safety significance. 3.0 CAUSE OF THE EVENT An apparent cause evaluation was conducted, and it was determined that the Operations team, whiie reviewing the electrical tag-out walkdown task, did not adequately perceive and manage the risk of opening the. 1 J emergency bus potential transformer drawer under the existing plant conditions. Therefore, contingendes, stop criteria, arid other risk mitigation actions were not established. Additionally, the operator who opened the drawer did not understand the impact to the 1J emergency bus UV sensing circuit when opening the 1J emergency bus potential transformer drawer. 4.0 IMMEDIATE CORRECTIVE ACTIONS All operator qualifications were immediately removed for the operator and approving Operations supervisor, and a remediation plan was developed. A department stand-down was held, and expectations were communicated by station management. A human performance review board was established to document.facts, determine lessons learned, and define further actions. NRG FORM 366A (04-2017) Page 2 of 3 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with. this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulato·ry Commission, Washington, DC 20555-0oo·1, or by e-mail to lnfocollects. CONTINUATION SHEET Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a (See NUREG-1022, R.3 for instruction and guidance for completing this form means used to impose an information collection does not display a currently valid 0MB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the http://www.nrc.gov/reading-rm/doc-co11ections/nuregs/staff/sr1022/r3/) information collection. 1. FACILITY NAME 2. DOCKET NUMBER . 3. LER NUMBER SEQUENTIAL REV YEAR NUMBER NO. Surry Power Station, Unit 1 05000- 280 2018 - 001 00 NARRATIVE 5.0 ADDITIONAL CORRECTIVE ACTIONS Expectations concerning potential risk and consequences of entry into electrical enclosures were established, communicated, and documented by Operations management. The associated ·electrical industrial safety requirements were included in the communications. 6.0 ACTIONS TO PREVENT RECURRENCE Further training will be conducted for licensed and .non-licensed operators concerning knowledge of bus potential transformer UV circuitry and the impact of opening associated drawers. Also, training will address industrial safety aspects of working near 4 KV equipment. All corrective actions determined by the apparent cause evaluation will be implemented in accordance with the station corrective action program. 7.0 SIMILAR EVENTS LER 95-009-00, Personnel Error Results in. Loss of 4160 V Transfer Bus and Start of Emergency Diesel Generators 8.0 MANUFACTURER/MODEL NUMBER G080 I GE JVM-3 bus potential transformer drawer 9.0 ADDITIONAL INFORMATION Unit 2 remained at 100 percent power during this event. While #3 EDG was loaded on the 1J 4160 V emergency bus, Technical Specification (TS) action statements associated with Unit 2 emergency electrical systems were reviewed, and associated TS clocks were entered. The event did not cause any additional reportable condition. All Unit 2 TS action statements associated with Unit 2 emergency electrical systems were exited when the #3 EDG was returned to normal alignment at 12:54 hours on 1/17/2018. · There were no other structures, systems, or components that were inoperable at the start of the event that contributed to the event. NRG FORM 366A (04-2017) Page 3 of 3 | 03-31-2020 | On January 17, 2018, at 09:52 hours, with Units 1 and 2 at 100% power, the 1·J emergency bus p·otential transformer drawer located inside the 1J 4160 Vemergency bus uhdervolfage (UV) ·relaying cubicle was opened inadvertently, generating a 1J .emergency bus UV signal. The signal caused the normal 1J emergency bus supply·breaker to open and also caused the automatic start· of the #3 Emergency Diesel Generator (EOG). The #3 EOG energized the 1J emergency . bus, and all 1J emergency bus loads were verified to be in correct alignment.. . . . After proper re-installation of the bus potential. transformer drawer was verified, normal alignment of. the #3 EOG and normal alignment of the prima.ry, off-site power supply to the 1J emergency bus were reestablished. Both Units 1 and 2 remained at 100% pqwer during the event. All equipment operated as designed .. '. It was determined that the Operations team, while reyiewing an electrical tag-out walkdciwn task, did not adequately perceive and manage the risk of opening the:1J bus potential transformer drawer. Also, the operator who opened the . drawer did not understand the impact to the UV sensing circuit by opening the bus potential transformer drawer. · of The condition was reported as an event or condition that results in a valid actuation an emergency electrical power system, pursuant to 10 CFR. 50. 72(b)(3)(iv)(A). This event is being reported as an event.or <::or:,dition that results in a. valid actuation of an emergency electrical power system, pursuant to 50.73(a)(2)(iv)(A). NRC FORM 366 (04-2017) Page 1 3 NRC FORM 366A U.s;·NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB:. NO: 3.150-0104 EXPl~ES: 03/31/2020 (04-2017) Estimated burden per response ici ·c omply with' this mandatory collection request: 80 hours. Reported ..l essons learned are incornorated. into the licensing process .and le.a back to industry, LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear. Regulatory Commission, Washington, DC 2055q-0001, or by e-mail to lnfocollects. CONTINUATION SHEET Resource@nrc.gov, and to the Desk Officer, Office of .Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Managemen(and Budget, Washington, DC 20503. If a (See NUREG-1022·, R.3 for instruction and guidance for completing this form means_ u~ed to imJ)Ose an information collection does not display.a currently valid 0MB control · number, the· NRG may not conduct or sponsor, and a person is not required to respond to, the http://www.nrc.gov/reading-rm/doc-collectio~s/nuregs/staff/sr1022/r3/) information collection. · · · 1. FACILITY NAME .. 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Surry Power Station, Unit 1 · 05000- 280 NUMBER NO. 2018 • 001 00 | 1,.0 DESCRIPTION OF.THE EVE.NT On Ja~uary 17, 2018, at 09:52 hours, with Units 1 and 2 oper~ting at 100% power, the 1 J bus potential transformer drawer [EIIS£i<~DR]. located inside the tJ 4.160V Emergency Bus UV relaying cubicle.was inadvertently opened while performing an electrical tag-out walkdown. The 1J 4160 V emergency bus UV potential transformers [EIIS-EK-XPT] and fuses [El IS-EK-FU] are attached to the inner panel of the drawer which, when opened, disconnected the UV sensing circuit and generated a UV signal. Emergency bus 1J [El IS-EK-BU] was de-energized due to the normal bus supply breaker [EIIS-EK-BKR] opening on the UV signal. The UV signal also initiated the start sequence for the #3 EDG [EIIS-EK-DG]. The #3 EDG started normally and energiz.ed the 1J bus, as designed. Also as designed, the UV signal tripped the 1 J stub bUs breaker [EIIS-EK-BKRJ and the running component cooling (CC) water pump breaker · powered by the 1 J bus. The standby CC water pumps [EIIS-CC-P] automatically started when a low CC system pressure signal was received as a result of the power loss to the running CC water pump. All 1J emergency bus loads were verified to be in proper alignment by the Operations team. All equipment performed as expected, and there were no unexplained occurrences. · At 10:47. hours, normal CC pump alignment was restored. At 11 :56 hours; the 1J 4160 V emergency bus potential transformer fuses were verified to be installed properly, and restoration of emergency bus normal configuration was commenced. At 12:54 hours, after the 1J 4160 V emergency bus normal supply breaker had been closed, the #3 EDG was secured and returned to normal automatic standby alignment. · An eight-hour non-emergency event notification was made to the NRC pursuant to 10 CFR 50.72(b)(3)(iv)(A) due a valid actuation of the #3 EDG, This report is being made pursuant to 10 CFR 50.73(a)(2)(iv)(A) due a valid actuation of the #3 EDG. 2.0 SIGNIFICANT SAFETY CONSEQUENCES AND 11\/lPLICATIONS During the. event, the redundant 1H 4160 V emergency bus was supplied by normal off-site power. Also, the Unit 2 4160 V emergency busses, 2H and 2J, were supplied by normal off-site power. The #1, #2, and #3 Emergency Diesel Generators.remained available to supply power to emergency b_us loads. All equipment performed as designed, and the normai equipment alignment was restored by. the Operations team in a timely manner. Therefore this event is of minimal safety significance. 3.0 CAUSE OF THE EVENT An apparent cause evaluation was conducted, and it was determined that the Operations team, whiie reviewing the electrical tag-out walkdown task, did not adequately perceive and manage the risk of opening the. 1 J emergency bus potential transformer drawer under the existing plant conditions. Therefore, contingendes, stop criteria, arid other risk mitigation actions were not established. Additionally, the operator who opened the drawer did not understand the impact to the 1J emergency bus UV sensing circuit when opening the 1J emergency bus potential transformer drawer. 4.0 IMMEDIATE CORRECTIVE ACTIONS All operator qualifications were immediately removed for the operator and approving Operations supervisor, and a remediation plan was developed. A department stand-down was held, and expectations were communicated by station management. A human performance review board was established to document.facts, determine lessons learned, and define further actions. NRG FORM 366A (04-2017) Page 2 of 3 | ML18085A156
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Safety ReliefValves Out of Tolerance 5. EVENTDATE 6. LERNUMBER 7. REPORTDATE 8. OTHERFACILITIESINVOLVED SEQUENTIAL REV FACILITYNAME DOCKETNUMBER MONTH DAY YEAR YEAR MONTH DAY YEAR NUMBER NO N/A N/A FACILITYNAME DOCKETNUMBER 11 21 2017 2017 - 004 - 01 03 30 2018 N/A N/A 9. OPERATING MODE 11.THIS REPORTISSUBMITTED PURSUANTTO THE REQUIREMENTS OF 10 CFR§: (Checkallthatapply) El [] [] El 20.2201(b) 20.2203(a)(3)(i) 50.73(a)(2)(ii)(A) 50.73(a)(2)(viii)(A) El El El El 20.2201(d) 20.2203(a)(3)(ii) 50.73(a)(2)(ii)(B) 50.73(a)(2)(viii)(B) 1 [1 El [] [] 20.2203(a)(1) 20.2203(a)(4) 50.73(a)(2)(iii) 50.73(a)(2)(ix)(A) . [] [] j] [] 20.2203(a)(2)(i) 50.36(c)(1)(i)(A) 50.73(a)(2)(iv)(A) 50.73(a)(2)(x) JO. POWERLEVEL El 20.2203(a)(2)(ii) El 50.36(c)(1)(ii)(A) El 50.73(a)(2)(v)(A) El 73.71(a)(4) El 20.2203(a)(2)(iii) 50.36(c)(2) 50.73(a)(2)(v)(B) 73.71(a)(5) jJ j 20.2203(a)(2)(iv) 50.46(a)(3)(ii) 50.73(a)(2)(v)(C) 73.77(a)(1) 100 [] 20.2203(a)(2)(v) [] 50.73(a)(2)(i)(A) 50.73(a)(2)(v)(D) [J 73.77(a)(2)(i) El 20.2203(a)(2)(vi) 50.73(a)(2)(i)(B) 50.73(a)(2)(vii) El 50.73(a)(2)(i)(C) OTHER SpecifyinAbstractbeloworin NRCForm366A 12. LICENSEE CONTACT FORTHIS LER LICENSEECONTACT TELEPHONENUMBER(IncludeAreaCode) Mr. William Drews, RegulatoryAssurance Manager 315-349-6562 13. COMPLETEONE LINE FOREACH COMPONENTFAILURE DESCRIBED IN THIS REPORT MANU- REPORTABLE MANU- REPORTABLE CAUSE SYSTEM COMPONENT FACTURER TOEP1X CAUSE SYSTEM COMPONENT FACTURER TOEPIX B SB RV T020 Y 14.SUPPLEMENTALREPORTEXPECTED 15. EXPECTED MONTH DAY YEAR SUBMISSION YES (Ifyes, complete 75. EXPECTEDSUBMISSIONDATE) NO DATE ABSTRACT (Limitto 7400spaces,i.e., approximately15single-spacedtypewrittenlines) The As-Found test results forthe eleven Safety/ReliefValve (S/RV) pilot assemblies removed and replaced during the 2017 Refueling Outage at James A. FitzPatrick Nuclear Power Plant (JAF) identified ten (10) S/RV pilot assemblies that lifted outside of the allowable tolerance required by Technical Specification Surveillance Requirement 3.4.3.1. Nine (9) two-stage S/RV’s were found out oftolerance high, and one three-stage was found out oftolerance low. The ten S/RV pilot assemblies are assumed to have been inoperable at some point in the operating cycle that preceded the 2017 Refueling Outage resulting in a condition reportable pursuantto 10 CFR 50.73(a)(2)(i)(B). The S/RV design features an electric actuation capability that provides a diversified means of opening the S/RV’s despite the out oftolerance condition. However, the electric lift function is considered a backup to the mechanical S/RV’s and is not credited in the accident analysis. Therefore, the TS inoperability ofthe ten (10) S/RV’s also resulted in a condition reportable pursuant to 10 CFR5O.73(a)(2)(v)(D). The cause ofthe two-stage failures has been identified as corrosion bonding; the cause ofthe three-stage failure is attributed to calibration and subsequent setpoint drift. The safety consequences associated with this event are considered low due to the electric actuation capability. NRCFORM366(06-2016) NRC FORM 366A U.S. NUCLEARREGULATORYCOMMISSION APPROVEDBY0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimatedburdenpetresponsetocomplywiththismandatorycollectionrequest:80hours. Reported ..n-RE ‘ LICENSEE E1ENT REPORT (LER) lessonslearnedareincorporatedintothelicensing processandfedbacktoindustry. Sendcomments “g’ CONTINUATION SHEET regardingburdenestimatetothe FOIA, PrivacyandInformation Collections Branch (1-5 F53), U.S. ., Nuclear Regulatory Commission, Washington, DC 20555-0001,. or by e-mail to ‘‘ c lnfocollects.Resourcenrc.gov,andtotheDeskOfficer,OfficeofInformationand RegulatoryAffairs, ‘s” NEOB-10202, (3150-0104),OfficeofManagementand Budget,Washington, DC 20503. Ifa means ‘‘ usedtoimposeaninformationcollectiondoesnotdisplayacurrenfyvalid0MB controlnumber, the (See NUREG-1022, R.3forinstruction and gui.danceforcompletingthisform NRCmaynotconductorsponsor,andapersonisnotrequiredtorespondto, theinformationcollection. http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/srl0221r3/) 1. FACILITYNAME 2. DOCKETNUMBER 3. LERNUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 333 NUMBER NO. — 2017 —004 —01 NARRATIVE Background The ASME Boiler and Pressure Vessel Code requires the reactor pressure vessel be protected from overpressure during upset conditions by self-actuated safety valves. As part ofthe nuclear pressure relief system, the size and number of SIRVs are selected such that peak pressure in the Reactor Coolant Pressure Boundary (RCPB) will not exceed the ASME Code limits. The James A. FitzPatrick Nuclear Power Plant (JAF) used ten (10) two-stage and one (1) three-stage Target Rock Safety/ReliefValves (S/RV) [EIIS Identifier: SB] for emergency pressure relief during operating Cycle 22. These valves are located on the main steam lines between the reactor vessel,and the first isolation valve within the drywell. Each S/RV discharges steam through a discharge line to a point below the minimum water level in the suppression pool. The S/RVs can actuate by either oftwo modes: the safety mode or the relief mode. In safety mode (or spring mode of operation), the spring-loaded pilot valve opens when steam pressure at the valve inlet overcomes the spring force holding the pilot valve closed. Opening the pilot valve allows a pressure differential to develop across the main valve piston and opens the main valve. This satisfies the code requirement. Each S/RV can be opened manually in the relief mode from the control room by its associated two-position switch. If one ofthese switches is placed in the open position the logic output will energize the associated S/RV solenoid control valve directing the pneumatic supply to open the valve. Seven ofthe installed S/RV solenoid control valves can also be energized by the relay logic associated with the Automatic Depressurization System (ADS). During each refueling outage all eleven ofthe pilot assemblies are removed and replaced with vendor tested and certified components. The pilots that are removed are sent to a vendor facility for testing, refurbishment, and certification. The test results for pilot assemblies removed in 2017, during Refueling Outage 22, identified ten (10) S/RV pilot assemblies that were out of allowable tolerance. Nine (9) of the pilots (all two-stage) lifted at greater than the allowable setpoint range, and one (three-stage) lifted at less than the allowable setpoint range. In order to address the concerns with corrosion bonding, JAF will commence replacement of two-stage with three-stage Target Rock S/RVs in the next Refueling Outage (RO). Industry experience has shown that the three stage S/RVs are less susceptible to corrosion bonding. The design ofthe three-stage S/RVs produces a greater mechanical force on opening, resulting in a greater likelihood of overcoming any potential effects of corrosion bonding that might occur. Event Description As-Found testing was performed on all eleven main S/RV pilot assemblies removed in 2017, during R022. The testing was conducted by NWS Technologies. The TS setpoint for each S/RV is 1145 +1- 34.3. During the initial lift test, ten ofthe eleven pilot assemblies failed to open within the allowable range (1110.7 to 1179.3). Nine of the ten two-stage and the three-stage S/RV pilot failed high and low outside the allowable range, respectively. As-Found failed test results are tabulated below. Page 2 of 4 NRCFORM366A(06-2016) NRC FORM 366A U.S. NUCLEARREGULATORYCOMMISSION APPROVEDBY0MB: NO. 3150-0104 EXPIRES: 03131/2020 (04-2017) Estimatedburdenperresponsetocomplywiththismandatorycollectionrequest:80hours. Reported LICENSEE EVENT REPORT (LER) ,“ “., lessonslearnedareincorporatedintothelicensingprocessandfedbacktoindustry. Sendcomments CONTINUATION SHEET regardingburdenestimatetothe FOIA, PrivacyandInformation Collections Branch (1-5 F53),U.S. ‘‘‘ Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to / lnfocoIlects.Resourcenrc.gov,andtotheDeskOfficer,OfficeofInformationand RegulatoryAffairs, NEOB-10202,(3150-0104),OfficeofManagementand Budget,Washington, DC 20503. Ifa means usedtoimposeaninformationcollectiondoesnotdisplayacurrentlyvalid0MB controlnumber, the (See NUREG-1022, R.3for.instructi.on and gui.danceforcompletingthisform NRCmaynotconductorsponsor,andapersonisnotrequiredtorespondto, theinformahoncollechon. http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/srl022Ir3I) 1. FACILITYNAME 2. DOCKETNUMBER 3. LERNUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 333 NUMBER NO. — 2017 —004 —01 Table 1 As-Found Test Results — In-service Pilot Serial First Test Acceptance Range Location Number (psig) (1110.7— 1179.3 psig) O2RV-71A 1088 1184 Unsat—High O2RV-71B 1080 1254 Unsat—High 02RV71C(a) 51 1103 Unsat—Low O2RV-71E 1235 1245 Unsat—High O2RV-71F 1195 1183 Unsat—High O2RV-71G 1194 1202 Unsat—High O2RV-71H 1111 1228 Unsat—High O2RV-71J 1192 1242 Unsat—High O2RV-71K 1193 1239 Unsat—High O2RV-71L 1056 1214 Unsat-High (a)Three.Stage Cause JAF has extensive internal Operating Experience with the S/RVs failing higher than the allowable setpoint. Causal evaluations identified corrosion bonding as the cause for the upward setpoint drift on the two-stage S/RVs. The As-Found test results shown above in conjunction with the successful second lift of all two-stage valves support this conclusion. Corrosion bonding is a crevice corrosion phenomenon that occurs between highly polished metals in a wetted solution in close proximity to each other. This close proximity (usually a gap of between 0.1 and 100 iJm) creates a crevice-like condition between the two wetted surfaces setting up the conditions for crevice corrosion to occur. An oxygen rich environment is created by the accumulation of oxygen in the area ofthe pilot disc due to the breakdown ofwater into hydrogen and oxygen. Susceptible material in the tight geometry with exposure to oxygen and high temperatures are the conditions which cause corrosion bonding in JAF S/RVs. There is extensive industry experience with corrosion bonding in the Target Rock two-stage S/RVs pilot assemblies. As stated above, the three-stage S/RV pilot valve failed the As-Found testing low. Disassembly and testing was performed by NWS Technologies to determine cause. NWS concluded that the three-stage S/RV pilot was originally calibrated within the lower half of the acceptance range in the OEM specification. Calibration within the lower half of the acceptance range resulted in a greater setpoint drift, which ultimately resulted in the S/RV pilot being outside the allowable range. Page 3 of 4 NRCFORM366A(06-2016) NRC FORM366A U.S. NUCLEARREGULATORYCOMMISSION APPROVED BY0MB: NO. 3150-0104 EXPIRES: 0313112020 (04-2017) Estimatedburdenperresponsetocomplywiththismandatorycollectionrequest:80hours, Reported RE LICENSEE EVENT REPORT (LER) “ “i., lessonslearnedareincorporatedintothelicensingprocessandfedbacktoindustry. Sendcomments ‘*, CONTINUATION SHEET regardingburdenestimatetothe FOIA, PrivacyandInformation Collections Branch (T-5 F53),U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocolIects.Resourcenrc.gov,andtotheDeskOfficer,OfficeofInformationand RegulatoryAffairs, NEOB-10202,(3150-0104),OfficeofManagementand Budget,Washington, DC 20503. Ifa means ** usedtoimposeaninformationcollectiondoesnotdisplayacurrentlyvalid0MB controlnumber, the (See NUREG-1022, R.3for.instructi.on and guidanceforcompleting thisform NRCmaynotconductorsponsor,andapersonisnotrequiredtorespondto, theinformationcollection. http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITYNAME 2. DOCKETNUMBER 3. LERNUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 333 NUMBER NO. — 2017 —004 —01 Similar Events Internal • JAF LER-15-002 “Safety ReliefValve Upward Setpoint Drift,” June 1, 2015 • JAF LER-1 1-003 “Safety ReliefValve Setpoints Outside ofAllowable Tolerances,” August 8, 2011 • JAF LER-09-005 “Safety ReliefValve Setpoints Outside ofAllowable Tolerances,” June 22, 2009 • JAF LER-07-001 “Safety ReliefValve Setpoints Outside of Allowable Tolerances,” August 6, 2007 External • Edwin I. Hatch Nuclear Plant, Unit 1: LER-16-004 “Safety Relief Valves As Found Settings Resulted in Not Meeting Tech Spec Surveillance Criteria,” May 26, 2016 • Edwin I. Hatch Nuclear Plant, Unit 2: LER-08-004 “Safety Relief Valves Allowable Test Range Exceeded Due to Setpoint Drift,” August 12, 2008 Corrective Actions Future Corrective Actions • Commence replacement of S/RVs with redesigned three-stage (R023) Previous Corrective Actions • Installed Stellite 21 discs in all eleven S/RV pilot assemblies during refurbishment at the vendor facility • Installed the S/RV Electric Lift System recommended by the Boiling Water Reactor Owner’s Group • Installed enhanced insulation on the S/RVs Safety Significance Nuclear Safety Actual Consequences There were no actual consequences to the general safety ofthe public, nuclear safety, industrial safety, or radiological safety associated with this event. Potential Consequences The potential consequences ofthis event are associated with the over-pressurization ofthe Reactor Coolant Pressure Boundary. The S/RVs provide overpressure protection forthe Reactor Coolant Pressure Boundary as required by the ASME Boiler and Pressure Vessel Code. Events similar to the one reported herein may be significant if design limits are challenged. The potential consequences of this event are considered low based on the operation and availability of the Electric Lift System. Radiological Safety There was no radiological safety impact associated with this event. Industrial Safety There was no industrial safety impact associated with this event. References • Issue Report No. 04077124, R22 SRV As-Found Testing Failures • Issue Report No. 04082823, R22 3-Stage SRV As-Found Testing Failure • JAF Technical Specifications Page 4 of4 NRCFORM366A(06-2016) | 03-30-2018 | The As-Found test results forthe eleven Safety/ReliefValve (S/RV) pilot assemblies removed and replaced during the 2017 Refueling Outage at James A. FitzPatrick Nuclear Power Plant (JAF) identified ten (10) S/RV pilot assemblies that lifted outside of the allowable tolerance required by Technical Specification Surveillance Requirement 3.4.3.1. Nine (9) two-stage S/RV’s were found out oftolerance high, and one three-stage was found out oftolerance low. The ten S/RV pilot assemblies are assumed to have been inoperable at some point in the operating cycle that preceded the 2017 Refueling Outage resulting in a condition reportable pursuantto 10 CFR 50.73(a)(2)(i)(B). The S/RV design features an electric actuation capability that provides a diversified means of opening the S/RV’s despite the out oftolerance condition. However, the electric lift function is considered a backup to the mechanical S/RV’s and is not credited in the accident analysis. Therefore, the TS inoperability ofthe ten (10) S/RV’s also resulted in a condition reportable pursuant to 10 CFR5O.73(a)(2)(v)(D). The cause ofthe two-stage failures has been identified as corrosion bonding; the cause ofthe three-stage failure is attributed to calibration and subsequent setpoint drift. The safety consequences associated with this event are considered low due to the electric actuation capability. NRCFORM366(06-2016) NRC FORM 366A U.S. NUCLEARREGULATORYCOMMISSION APPROVEDBY0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimatedburdenpetresponsetocomplywiththismandatorycollectionrequest:80hours. Reported ..n-RE ‘ LICENSEE E1ENT REPORT (LER) lessonslearnedareincorporatedintothelicensing processandfedbacktoindustry. Sendcomments “g’ CONTINUATION SHEET regardingburdenestimatetothe FOIA, PrivacyandInformation Collections Branch (1-5 F53), U.S. ., Nuclear Regulatory Commission, Washington, DC 20555-0001,. or by e-mail to ‘‘ c lnfocollects.Resourcenrc.gov,andtotheDeskOfficer,OfficeofInformationand RegulatoryAffairs, ‘s” NEOB-10202, (3150-0104),OfficeofManagementand Budget,Washington, DC 20503. Ifa means ‘‘ usedtoimposeaninformationcollectiondoesnotdisplayacurrenfyvalid0MB controlnumber, the (See NUREG-1022, R.3forinstruction and gui.danceforcompletingthisform NRCmaynotconductorsponsor,andapersonisnotrequiredtorespondto, theinformationcollection. http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/srl0221r3/) 1. FACILITYNAME 2. DOCKETNUMBER 3. LERNUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 333 NUMBER NO. — 2017 —004 —01 | Background The ASME Boiler and Pressure Vessel Code requires the reactor pressure vessel be protected from overpressure during upset conditions by self-actuated safety valves. As part ofthe nuclear pressure relief system, the size and number of SIRVs are selected such that peak pressure in the Reactor Coolant Pressure Boundary (RCPB) will not exceed the ASME Code limits. The James A. FitzPatrick Nuclear Power Plant (JAF) used ten (10) two-stage and one (1) three-stage Target Rock Safety/ReliefValves (S/RV) [EIIS Identifier: SB] for emergency pressure relief during operating Cycle 22. These valves are located on the main steam lines between the reactor vessel,and the first isolation valve within the drywell. Each S/RV discharges steam through a discharge line to a point below the minimum water level in the suppression pool. The S/RVs can actuate by either oftwo modes: the safety mode or the relief mode. In safety mode (or spring mode of operation), the spring-loaded pilot valve opens when steam pressure at the valve inlet overcomes the spring force holding the pilot valve closed. Opening the pilot valve allows a pressure differential to develop across the main valve piston and opens the main valve. This satisfies the code requirement. Each S/RV can be opened manually in the relief mode from the control room by its associated two-position switch. If one ofthese switches is placed in the open position the logic output will energize the associated S/RV solenoid control valve directing the pneumatic supply to open the valve. Seven ofthe installed S/RV solenoid control valves can also be energized by the relay logic associated with the Automatic Depressurization System (ADS). During each refueling outage all eleven ofthe pilot assemblies are removed and replaced with vendor tested and certified components. The pilots that are removed are sent to a vendor facility for testing, refurbishment, and certification. The test results for pilot assemblies removed in 2017, during Refueling Outage 22, identified ten (10) S/RV pilot assemblies that were out of allowable tolerance. Nine (9) of the pilots (all two-stage) lifted at greater than the allowable setpoint range, and one (three-stage) lifted at less than the allowable setpoint range. In order to address the concerns with corrosion bonding, JAF will commence replacement of two-stage with three-stage Target Rock S/RVs in the next Refueling Outage (RO). Industry experience has shown that the three stage S/RVs are less susceptible to corrosion bonding. The design ofthe three-stage S/RVs produces a greater mechanical force on opening, resulting in a greater likelihood of overcoming any potential effects of corrosion bonding that might occur. Event Description As-Found testing was performed on all eleven main S/RV pilot assemblies removed in 2017, during R022. The testing was conducted by NWS Technologies. The TS setpoint for each S/RV is 1145 +1- 34.3. During the initial lift test, ten ofthe eleven pilot assemblies failed to open within the allowable range (1110.7 to 1179.3). Nine of the ten two-stage and the three-stage S/RV pilot failed high and low outside the allowable range, respectively. As-Found failed test results are tabulated below. Page 2 of 4 NRCFORM366A(06-2016) | ML18089A040
Susquehanna Steam Electric Station | Unit 1 | Core Spray Inoperable due to not meeting Seismic requirements as a result of a Human Performance Error | 00-02-2018 | On December 3, 2017, at approximately 1030, Operations identified materials staged in the Susquehanna Steam Electric Station (SSES) Unit 1 Division 2 Core Spray Room near the "B" Core Spray Pump Room Unit Cooler. The replacement piping materials were located on pipe roller stands approximately 6 inches from the unit cooler and were not seismically restrained. At the time of this condition, the SSES Unit 1 Division 2 Residual Heat Removal (RHR) Low Pressure Core Spray (LPCI) Swing Bus MG voltage regulator was being replaced. As such, Unit 1 Technical Specification 3.5.1 condition A for the voltage regulator replacement had already been entered. With the U1 "B" Core Spray Unit Cooler inoperable due to the presence of the improperly stored materials, this would have required entry into TS 3.5.1 condition I which requires entry into TS LCO 3.0.3 immediately. The cause of the condition was determined to be less than adequate procedure use and adherence. The staged piping was removed immediately and a communication was performed with site personnel on this issue. This condition is being reported in accordance with 10 CFR 50.7 3(a)(2)(i)(B) as a condition prohibited by Technical Specifications. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366 (02-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43}, U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1 022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1 022/r3D NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station Unit 1 05000387 NUMBER NO. 2017 -008 -00 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, approximately 100 percent Rated Thermal Power Unit 2 - Mode 1, approximately 100 percent Rated Thermal Power There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. EVENT DESCRIPTION On December 3, 2017, Operations identified materials staged in the Susquehanna Steam Electric Station (SSES) Unit 1 Division 2 Core Spray [EllS: BG] Room near the "B" Core Spray Pump Room Unit Cooler [IEEE: CLR]. The replacement piping materials were located on pipe roller stands approximately 6 inches from the unit cooler and were not seismically restrained. At the time of this condition, the Unit 1 Division 2 Residual Heat Removal (RHR) Low Pressure Core Spray (LPCI) [EIS: BO] Swing Bus MG voltage regulator [IEEE: RG] was being replaced. As such, Unit 1 Technical Specification (TS) 3.5.1 condition A for the voltage regulator replacement had already been entered. The following timeline demonstrates the sequence of events: 12/1/17-1300: Supplemental work force improperly staged replacement piping for upcoming work in the Unit 1 Division 2 Core Spray Room near the "B" Core Spray Pump Room Unit Cooler. 12/2/17-0748: Unit 1 TS 3.5.1 condition A was entered in support of the Division 2 RHR Low Pressure Core Spray Swing Bus MG voltage regulator replacement. 12/3/17 -1030: Operations identified the unrestrained replacement piping staged in the Unit 1 Division 2 Core Spray Room. A condition report was generated and Engineering was contacted. 12/3/17 -1335: Unit 1 TS 3.5.1 condition A was exited upon completion of the Division 2 RHR Low Pressure Core Spray Swing Bus MG voltage regulator replacement. 12/3/17 -1600: Maintenance removed the unrestrained replacement piping from the Core Spray Room. Based on Engineering review of the information available with respect to the positioning of the materials staged in the Core Spray Room, it was determined that under a seismic event, the piping could potentially make contact with the Core Spray Pump Room Unit Cooler conduit resulting in a loss of power to the cooler and inoperability of one of the Core Spray Pumps in the room. With the U1 "B" Core Spray Unit Cooler inoperable due to the presence of the improperly stored materials, this would have required entry into TS 3.5.1 condition I which requires entry into TS LCO 3.0.3 immediately. This condition is being reported in accorance with 10 CFR 50. 73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 3668 (04-2017) Page 2 of 3 | ML18092B513
Grand Gulf Nuclear Station | Unit 1 | BOTH 208 CONTAINMENT AIR LOCK DOORS SIMULTANEOUSLY INOPERABLE | 04-04-2018 | On February 10, 2018, at 1835 hours, while in MODE 1 at 68 percent power, the Grand Gulf Nuclear Station . entered Technical Specification (TS) 3.6.1.2 Condition C for both 208 foot upper containment air lock doors being inoperable. The upper containment inner door was determined to be inoperable while the air lock outer door was tagged-out for planned maintenance. A seal air system leak test performed on the air lock inner door on February 6, 2018, had been deemed satisfactory. The outer door was subsequently taken out of service for planned maintenance and, while the outer door was out of service, an additional review of the paperwork determined that the test on the inner door was actually unsatisfactory. TS 3.6.1.2 Condition C was entered at that time. Maintenance of the outer door was completed, the air lock was returned to operable status, and ACTION C was exited at 0835 on February 11, 2018, prior to exceeding the TS action completion time of 24 hours. The cause was determined to be human error in transcribing data and interpreting test results. Analyses of test results for inner doors demonstrated that in all cases the doors and air locks remained functional and capable of maintaining containment integrity in the event of an accident. The inner doors and the air locki remained functional, containment integrity was assured throughout the events, and there was no significant impact on the health and safety of the public. Page 1 of 5 NRG FORM 366AU.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (4-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 LICENSEE EVENT REPORT (LER) F ln 4 fo 3 c ), o U lle .S c . t s N .R u e c s le o a u r r c R e e @ gu n l r a c t . o g r o y v C , o a m nd m t i o s s th io e n , D W es a k s h O i f n fi g c t e o r n , , O D ff C ic e 2 0 o 5 f 5 I 5 n - fo 0 r 0 m 01 at , i o o n r b a y n d e -mail to CONTINUATION SHEET Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not (See NU REG-1022, R.3 for instruction and guidance for completing this form display a currently valid OMB control number, the NRC may not conduct or sponsor, and a http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr10221r3D person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 3. LER NUMBER YEAR I SEQUENTIAL I REV: NUMBER NO. Grand Gulf Nuclear Station, Unit 1 05000 416 2018-002-00 | A. PLANT CONDITIONS PRIOR TO THE EVENT At the time of discovery, Grand Gulf Nuclear Station (GGNS) Unit 1 was in Mode 1 at 68% reactor power, and in Technical Specification (TS} 3.6.1.2, "Primary Containment Air Locks," Condition A with the 208 foot upper air lock outer door tagged o_ut for planned maintenance. There were. no other structures,. systems or· components out of service that contributed to this event. B. DESCRIPTION February 6, 2018, GGNS completed the door seal air system leak test, TS Surveillance Requirement (SR) 3.6.1.2.4, on the upper containment air lock inner door [EIIS:NH][AL][DR] and the acceptance criteria were determined to be met. On February 9, 2018, TS 3.6.1.2 Condition A was entered when the .upper containment air lock outer door was taken out of service for maintenance and testing. At 1835 hours central standard time (CST) on February 10, while the outer door was tagged out, an additional review of the paperwork for the inner door determined that the s~rveillance test on the inner door was actually unsatisfactory. Technical Specification 3.6.1 .2 Condition C was entered for both doors being inoperable for reasons other than those stated in Conditions A and B. ' Technical Specification ·3.6.1.2 Action C requires restoration of the air lock to operable status within 24 hours or comply with Condition D and be in Mode 3 within the next 12 hours. Maintenance of the outer door was completed, the air lock was returned to operable status, and Condition C was exited at 0835 on February 11, 2018, prior to exceeding the Technical Specification required action completion time of 24 hours. The unit remained in TS 3.6.1.2 Condition A while maintenance and testing was performed on the inner door, which was completed on February 18, 2018. Condition A was exited and full operability restored at that time. When the surveillance test on the inner door was completed on February 6, TS 3.6.1.2 Condition A should have been entered, and the outer door should have been verified closed within 1 hour and locked closed within 24 hours. With Condition A required actions not met, Condition D requires the plant be in Mode 3 within the following 12 hours. This requirement was not met and therefore the pla.nt was in a condition prohibited by the Technical Specifications. In addition, from 2045 hours on February 7 until 0835 hours on February 11, while the outer door was out of service, both doors were inoperable concurrently with no redundant equipment in the same system operable, which constitutes a condition that could have prevented ·fulfillment of a safety function. Page 2 of 5 | ML18094A172
Clinton Power Station | Unit 1 | Manual Reactor SCRAM due to Loss of Feedwater Heating | 04-05-2018 | On June 10, 2017, at 2256 CDT, Clinton Power Station (CPS) experienced a complete loss of the 'A' feedwater (FW) heater string. The operators received numerous FW trouble alarms on FW string 'A' and low pressure heater 1A /1 B bypass opened (1 CB004). The operators entered procedure CPS 4005.01, "Loss of FW Heating," which directs the operators to restore and maintain power at or below the original power level. The operators lowered core flow and inserted all CRAM rods, and then observed that FW temperature had dropped greater than 100°F. As directed by CPS 4005.01, at 2306 hours the reactor mode switch was placed into the shutdown position and Procedure 4100.01, "Reactor Scram," was entered. All systems operated as expected following the scram. At 0100 EDT on June 11, 2017, Event Notification 52800 was made. The loss of FW heating transient was caused by a loss of power to Moore trip units caused by a shorted condition on the Moore trip unit associated with the Hi-Hi level in the 4A FW heater. The root cause is that the design of the FW heater level control trip circuitry was not adequate to prevent scrams due to an unevaluated single point vulnerability. Prior to startup, CPS modified the circuit card locations and thereby diversified the power supplies so that the trip units have less dependency on common fuses. Additional corrective actions include performing an engineering evaluation to determine if there are additional single component failures, operator errors, or events for the FW heating system that could result in a drop in FW temperature of greater than 100°F. NRG FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid 0MB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information httpJ/www.nrc.gov/readinq-rm/doc-collections/nureqs/staff/sr1022/r30 collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR NUMBER NO. Clinton Power Sta,tion, Unit 1 05000461 2017 - 007 - 02 | PLANT AND SYSTEM IDENTIFICATION General Electric -- Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in text as [XX]. EVENT IDENTIFICATION Manual Reactor SCRAM due to Loss of Feedwater Heating A. Plant Operating Conditions before the Event Unit: 1 Event Date: 6/10/17 Event Time: 2256 CDT Mode: 1 Mode Name: Power Operation Reactor Power: 98 percent 8. Description of Event On June 10, 2017, at 2256 CDT, Clinton Power Station (CPS) experienced a complete loss of the 'A' feedwater (FW) heater [HX] string. The operators received numerous FW trouble alarms on FW string 'A' and low pressure (LP) heater [HTR] 1A /1 B bypass valve (1 CB004) automatically opened. The operators entered procedure CPS 4005.01, "Loss of FW Heating," which directs the operators to restore and maintain reactor power at or below the original power level and within stability control and power/flow map limits by adjusting reactor recirculation flow, control rods, or CRAM array. The operators lowered core flow and inserted all CRAM rods. The operators observed that FW temperature had dropped by greater than 100°F. Procedure CPS 4005.01 directs the operators to place the reactor mode switch [JS] into the shutdown position and enter procedure CPS 4100.01, "Reactor Scram." With the unit at approximately 93 percent power, the operators placed the mode switch in shutdown at 2306 on June 10, 2017 and entered procedure CPS 4100.01. The components of the CPS power conversion system are designed to produce electrical power utilizing the steam generated by the reactor [RCT], condense that steam into water, and return the water to the reactor as heated feedwater. A portion of the main turbine [TRB] steam is extracted for FW heating. CPS has two trains of cascading FW heaters. Under normal, full power conditions, the extraction steam valves [V] to each of the FW heaters are open such that steam is condensed in the body of the heater. In addition, the normal heater drain valves are normally open and the emergency FW heater drain valves to the main condenser [COND] are closed. A high-high level in a FW heater will isolate the input sources to the heater (i.e., extraction steam valve(s) and the. upstream normal FW heater drain valve(s)), reducing the reactor FW temperature. A walkdown of panel [PL] 1 PA08J (Miscellaneous Sensors & Transducers Power Supply Cabinet), which houses Moore trip units for both the 'A' and 'B' FW heating strings, identified that there were no lights on rack CA-1 and the indicator for fuse [FU] FU-89 was open. | ML18099A066
LaSalle County Station | Unit 1 | Unanalyzed Condition Affecting Accident Mitigation for Tornado Generated Missile Protection Non-Conformances | 04-16-2018 | On February 15, 2018, during evaluation of protection for Technical Specifications (TS} equipment from the damaging effects of tornado generated missiles, LaSalle County Station (LSCS) identified non-conforming conditions in the plant design such that specific TS equipment is considered inadequately protected from tornado generated missiles. Specifically, tornado generated missiles could strike the components supporting the operation of the main control room ventilation (VC) and auxiliary electric equipment room ventilation (VE) systems, and the Unit 2 Division 2 480-volt motor control center 236X-1 (2AP78E). The VCNE systems provide a protected environment for occupants to control the unit following an uncontrolled release of radioactivity, hazardous chemicals, or smoke if a tornado were to occur. This condition is a legacy design issue that has existed since the original licensing of the plant. This condition is reportable under multiple reporting criteria in accordance with 10CFR50.73 requirements indicated above. This condition is being addressed in accordance with NRC enforcement guidance provided in Enforcement Guidance Memorandum (EGM) 15-002, Revision 1, "Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance," and DSS-ISG- 2016-01, Revision 1, "Clarification of Licensee Actions in Receipt of Enforcement Discretion per Enforcement Guidance Memorandum EGM 15-002." Compensatory measures have been implemented in accordance with these documents. NRC FORM 366 (02-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with tilis mandatory collection request: BO hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarcing burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LEA) Regulatory Commission, Washington, DC 20555·0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Otticer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used lo impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nureqs/staff/sr1022/r3/l collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR LaSalle County Station, Unit 1 05000373 NUMBER NO. 2018 - 001 00 | PLANT AND SYSTEM IDENTIFICATION LaSalle County Station (LSCS) Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected systems are common (both units) ventilation required for the main control room (MCA) and auxiliary electric equipment room (AEER). These systems provide necessary ventilation and a protected environment for occupants to control the unit(s) following an uncontrolled release of radioactivity, hazardous chemicals, or smoke if a tornado were to occur. In addition, the Unit 2 division 2 480V power supply motor control center (MCC) 236X-1 was affected, which impacted various loads on Unit 2 including Unit 2 standby gas treatment, Unit 2 post-LOCA, "B" MGR area filtration system supply and exhaust fan, reactor building division 2 isolation dampers control logic, Unit 2 battery room exhaust fan, and Unit 2 24/48VDC battery rooms exhaust fans. CONDITION PRIOR TO EVENT Unit(s): 1 / 2 Date: February 15, 2018 Time: 1100 CST Reactor Mode(s): 1 I 1 Mode(s) Name: Power Operation I Power Operation Power Level: 95 percent I 100 percent DESCRIPTION On February 15, 2018, during evaluation of protection for Technical Specifications (TS) equipment from the damaging effects of tornado generated missiles, LSCS identified non-conforming conditions in the plant design such that specific TS equipment is considered inadequately protected from tornado generated missiles. Specifically, tornado generated missiles could strike the components supporting the operation of MCA ventilation (VC) and AEER ventilation (VE) systems. This could result in inoperable VCNE systems, which provide a protected environment for occupants to control the unit(s) following an uncontrolled release of radioactivity, hazardous chemicals, or smoke if a tornado were to occur. Station personnel entered this condition into the corrective action program and notified the NRG via Event Notification 53213 on February 15, 2018. There were no structures, systems, or components (SSCs) out of service that contributed to this condition. The specific SSCs found to be non-conforming relative to tornado-missile design basis requirements are: • Unit 1 (2) VC "A" train (19 components) • Unit 1 (2) VC "B" train (19 components) • Unit 1 (2) VE "A" train (12 components) • Unit 1(2) VE "B" train (12 components) • Division 2 480V MCC 236X-1 (2AP78E) CAUSE The cause of the non-conforming conditions is a legacy design issue that was identified as part of r-esponse to Regulatory Issue Summary (RIS) 2015-06, "Tornado Missile Protection," and Enforcement Guidance Memorandum (EGM) 15-002, "Enforcement Discretion for Tornado Generated Missile Protection Noncompliance." These conditions were part of the original plant design and have existed since the initial construction and licensing of the plant. LSCS received its operating licenses for Unit 1 (NPF-11) and Unit 2 (NPF-18) on April 17, 1982. These operating licenses were issued based, in part, on the design as described in the Final Safety Analysis Report (FSAR). REPORTABILITY AND SAFETY ANALYSIS This condition was previously reported in accordance with 10 CFR 50.72(b)(3)(ii)(B) as a condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety and 10 CFR 50.72(b)(3)(v)(D) as a condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. This condition was reported to the NRG via Event Notification System (ENS) report number 53213 on February 15, 2018. There were no actual consequences resulting from these identified non-conforming conditions. NAC FORM 366A (04-2017) Page _2_ of _s_ | ML18106A105
grand gulf nuclear station | Unknown Unit | Potential Loss of Safetv Function Due to Concurrent lnooerabilitv of Two Diesel Generators | 04-17-2018 | On February 14, 2018, the Grand Gulf Nuclear Station Division 2 diesel generator (DG) was removed from service for maintenance. On February 18, 2018, at 0006 hours, while in Mode 1 at 97 percent power, the Division 3 DG -experienced a lockout and was declared inoperable. Technical Specification 3;8.1 Condition E was entered for two DGs inoperable at that time. On February 18, 2018, at 0355 hours, Division 2 DG maintenance was completed, the ·diesel-was· returned -to-service, and ·Condition -E was exited. Division 3 DG was -restored -to -operable status-on February 18, 2018, at 1257 hours. The Division 3 DG lockout was caused by inadequate operation procedures, which failed to detect an elevated jacket water temperature condition. The elevated jacket water temperature was caused by a malfunctioning jacket water temperature control switch. Corrective actions include replacement of the temperature control s.~itch, and revision of the operation· procedures. -Division-1-DG, which -power-s -one low :pressure core -injection -pump and -one -low pressure ·core -spray -pump, -remained operable. An evaluation of Chapter 15 accident analyses demonstrated that, with just Division I, peak cladding temperatures and cladding oxidation remained within the Cycle 21 licensing basis of <1730 degrees F and <3%, respectively. NRC FORM 366 (02-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT {LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. ' 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Grand Gulf Nuclear Station 05000-00416 NUMBER NO. 2018 -004 -00 | A. PLANT CONDITIONS PRIOR TO THE EVENT Prior to the event Grand Gulf Nuclear Station (GGNS) Unit 1 was operating in Mode 1 at approximately 97 percent power in steady state conditions. The division 2 diesel generator (DG) [EIIS: DG] was inoperable due to preplanned maintenance and c·ontributed to the event. The division 2 electrical service was being supplied with offsite power and remained available and functional. There were no other structures, systems, or components that were known to be inoperable that contributed to the event. B. DESCRIPTION On February 17, 2018, at 2353 hours, the high pressure core spray (HPCS) diesel [EIIS: BG][DG] trouble alarm was received in the control room. At 0006 hours, while operators were in route to the diesel, control room operators received diesel engine trip and not ready for start alarms. Investigation revealed that the r· Division 3 HPCS DG was tripped and not available for autostart. Division 3 DG was declared inoperable and Technical Specification 3.8.1 Condition E, for two required DGs inoperable, was entered on February 18, 2018, at 0006 hours. Division 3 electrical service was being supplied with offsite power and remained available and functional. Operations personnel detected a local jacket water temperature alarm due to high jacket water temperature. Operators assumed manual control of the Division 3 diesel jacket water temperature, restored the temperature to an acceptable level, cleared the Division 3 DG trips, and restored the DG to available status on February 18, 2018, at 0037 hours. The Division 2 DG was returned to service and made operable on February 18, 2018 at 0355 hours. Technical Specification 3.8.1 Condition E was exited at that time. The Division 3 diesel generator high jacket water temperature was caused by a malfunctioning temperature control switch [EIIS: TSl Investigation indicated the temperature switch had failed approximately 7 days prior to the event, and it took that long for the system temperature to reach trip setpoint. Operations procedures were inadequate to detect the temperature increase prior to reaching the trip setpoint. The switch was replaced and retested satisfactorily, and the Division 3 diesel generator was returned to operable status on February 18, 2018 at 1240 hours. · C. REPORT ABILITY This report is made pursuant to 1O CFR50.73(a)(2)(v)(D) for any event or condition that could have prevented fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. This event was reported under 10CFR50.72(b)(3)(v)(D) in ENS notification 53227. NRG FORM 3668 (02-2018) Page 2 of 4 | ML18107A152
Dresden Nuclear Power Station | Unit 2 | Non-conformances to Design for Tornado Missile Protection | 04-13-2018 | On February 12, 2018, Dresden Nuclear Power Station identified a non-conforming condition with the three Emergency Diesel Generator Main Fuel Oil Storage Tank Vents with respect to tornado missile protection. All three Emergency Diesel Generators were declared inoperable. Compensatory measures were implemented and verified in accordance with the NRG Enforcement Guidance Memorandum (EGM) 15-002. All three Emergency Diesel Generators were returned to an operable but non-conforming status, and an eight-hour Event Notification was made to the NRG. This condition has been in existence since original plant design. It is not known if it was overlooked or considered acceptable at the time of the original licensing process. This event is reportable under 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications, under 1O CFR 50.73(a)(2)(ii)(B) as an event that resulted in the plant being in an unanalyzed condition that significantly degraded plant safety, 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfillment of a safety function of a system that is needed to mitigate the consequences of an accident; and 1 O CFR 50.73(a)(2)(vii)(D) as an event where a single condition caused at least two independent trains to become inoperable in a single system designed to mitigate the consequences of an accident. NRG FORM 366 (02-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, _W ashington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid 0MB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR Dresden Nuclear Power Station, Unit 2 05000237 NUMBER NO. 2018 • 001 • 00 | Dresden Nuclear Power Station (DNPS), Unit 2, is a General Electric Company Boiling Water Reactor with a licensed maximum power level of 2957 megawatts thermal. The Energy Industry Identification System codes used in the text are identified as [XX]. A. Plant Conditions Prior to Event: Unit: 02 Event Date: 02/12/2018 Event Time: 1200 CST Reactor Mode: 1 Mode Name: Power Operation Power Level: 100 percent B. Event Description: On February 12, 2018, DNPS identified a non-conforming condition exists regarding the three Emergency Diesel Generator (EOG) [EK-DG] Main Fuel Oil Storage [DE] Tank [TK] Vents [VTV] with respect to tornado missile protection. Since the vents are an integral component of the EDGs and are not protected against tornado missiles, the design does not meet the licensing basis and a non conforming condition exists. DNPS entered this condition into the corrective action program and notified the NRG via Event Notification 53204 on February 12, 2018. An extent of condition review identified no other items that are non-conforming to the design for tornado missile protection. This event is reportable in accordance with 1O CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications; 10 CFR 50.73(a)(2)(ii)(B) as an event that resulted in the plant being in an unanalyzed condition that significantly degraded plant safety; 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfillment of a safety function of a system that is needed to mitigate the consequences of an accident; and 10 CFR 50.73(a)(2)(vii)(D) as an event where a single condition caused at least two independent trains to become inoperable in a single system designed to mitigate the consequences of an accident. C. Cause of Event: These conditions were part of the original plant design and have existed since the construction and licensing of the plant. Following the review of the Systematic Evaluation Program, DNPS, Unit 2, received its operating license on February 20, 1991. DNPS, Unit 3, received its operating license on January 12, 1971. | ML18107A210
LaSalle County Station | Unit 1 | Damaged Bus Bar Identified Potentially Affecting High Pressure Core Spray System | 04-18-2018 | On February 17, 2018, during troubleshooting for an issue with the Unit 1 "B" diesel generator (DG) oil circulating pump, station personnel identified. damage of a bus bar at the breaker that supplies the DG auxiliaries, One of the loads fed from this breaker is the Division 3 DC Battery Charger. Station personnel determined that the degradation of the bus bar may have prevented the Division 3 DC battery charger from performing its function, which could have prevented the High Pressure Core Spray (HPCS) system, which is a single-train safety system, from performing its design safety function. This condition is reportable in accordance with 10 CFR 50. 73(a)(2)(v)(D) as a condition that could have prevented the fulfillment of the safety function of structures or systems that are required to mitigate the consequences of an accident. Based on a subsequent review of the loads powered by the 2B cubicle, loss of any of those loads would not have prevented the 1 B DG from being able to start and perform its design function. The condition of the motor control center (MCC) 143-1 (1AP79E) bus-bar was the result of a degraded connection between the "A" phase bus bar and the "A" phase bus clip (stab) associated with the breaker cubicle 2B. The apparent cause of the degraded bus bar to clip connection is due to relaxation of the bucket clip over time. The condition was exacerbated by long-term continuous ohmic heating caused by the normal currents of the loads supplied by this molded case circuit breaker. Corrective actions included replacement of the degraded clip assembly with one obtained from a spare cubicle, relocating loads to alternative spare cubicles in the affected MCC, visual inspection of all bucket-to-bus connections and repairs as necessary, and performance of a causal investigation including component failure analysis. This model of MCC used at the station is limited to Division 3 on both operating units; therefore, the extent of condition does not apply to other safety-related divisions. NRC FORM 366 (02-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: BO hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T·2 F43). U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Jnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Re~atDrJ Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http://www. nrc. gov/ reading-rm/doc-collections/nu regs/staffl s r1 022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR LaSalle County Station, Unit 1 05000373 NUMBER NO. 2018 - 002 00 | PLANT AND SYSTEM IDENTIFICATION LaSalle County Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected component was the Division 3 480-volt motor control center (MCC) 143-1 (1AP79E) that is powered by the Division 3 4160-volt 143 switchgear. This MCC provides power to components that are used to support operation of the High Pressure Core Spray (HPCS) system, which is part of the Emergency Core Cooling System (ECCS). In accident situations, switchgear 143 is powered by the 18 diesel generator (DG). Specifically, the connection of the "A" phase of the 28 cubicle to MCC 143-1 bus bar was discovered degraded. This cubicle feeds Division 3 battery charger and several auxiliary components that support operation of the 18 DG. CONDITION PRIOR TO EVENT Unit(s): 1 Date: February 17, 2018 Time: 0200 CST Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 94 percent DESCRIPTION On February 16, 2018, at approximately 1418 CST the main control room (MCA) received Plant Process Computer (PPC) alarms associated with the Division 3 1B DG, including an alarm for the 1 B DG oil pump. Approximately 15 minutes later the 1B DG trouble alarm annunciated, and the local panel alarm for low oil pressure was identified. Field investigations determined the 1 B DG oil circulating pump had not been rotating. In accordance with an engineering evaluation, the alternate current (AC) circulating oil pump is not required for 1 B DG operability provided oil and water temperatures remain above 85 degrees Fahrenheit (F). A special Jog was started to verify temperatures remained above 85 degrees F. On February 16, 2018, at approximately 2129 CST, the 1B DG was placed into maintenance, and the HPCS system was declared inoperable to support troubleshooting associated with the cubicle for 1B DG auxiliaries. During troubleshooting for the failure of the 1 B DG Oil Circulating Pump to rotate, the Electrical Maintenance Department (EMO) technicians identified low voltage on one phase of the motor. Specifically, EMO removed the MCC bucket from the bus, and the inspection identified that the "A" phase of the bus had localized damage in the location where the MCC 143-1 cubicle 28 bucket (1AP79E-2B) connects to the bus-bar. The bus bar degradation occurred at the first clip connection point from the top of the bus bar. The damaged area was toward the forward edge (i.e., cubicle side) of the bus bar and extended back approximately 0.557-inches on both sides of the bar. The damaged area was approximately 1-inch long, which is the approximate length of the clip. On February 17, 2018, at approximately 0200 CST (time of discovery) the station determined that the degradation of the bus bar may have prevented the Division 3 DC battery charger from performing its function, which could have prevented the HPCS system, a single-train safety system, from performing its design safety function. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented the fulfillment of the safety function of structures or systems that are required to mitigate the consequences of an accident. [Reference ENS 53219.] Station Response The "A" phase clip of the sliding disconnect assembly mounted on the bucket was also found to be have degraded clip connection (i.e., relaxation) and determined to have caused the degradation of the "A" phase bus bar. This condition was determined to have resulted in a single-phasing condition which prevented the 1 E22-S001-C oil circulating pump from rotating. This MCC cubicle provides power for seven 1 B DG components: AC oil circulating pump, DC battery charger, immersion heater, 1B starting air compressor, 1 B refrigerated air dryer, generator space heater, and AC soak back oil pump. A temporary modification was initially implemented to supply temporary power to 1 AP79E-2B loads utilizing a spare cubicle in MCC 143-1 (1AP79E). Post-maintenance verifications were performed to ensure proper equipment function was restored. Subsequently, the relocation of this cubicle was made permanent by another modification package. NAC FORM 366A (04-2017) Page _2_ of _4_ | ML18108A020
Point Beach Nuclear Plant | Unit 1 | Inadequate Protection from Tornado Missiles Identified Due to Nonconforming Conditions | 04-26-2018 | On March 1, 2018, with Units 1 and 2 operating at 100% power, during evaluation of safe shutdown equipment lfor protection from the damaging effects of tornado missiles, Point Beach personnel initiated a condition report documenting a potential vulnerability for the turbine driven auxiliary feedwater pumps due to steam supply piping that is not routed through a Class I structure. Operations declared the affected equipment inoperable, implemented Enforcement Guidance Memorandum (EGM) 15-002, Enforcement Discretion for Tornado- Generated Missile Protection Noncompliance, Revision 1, and the required compensatory measures; and, returned the equipment to an operable-but-nonconforming status. Subsequent to the condition identified on March 1, 2018, an extent of condition review documented additional equipment not fully protected by Class I structures, that are potentially vulnerable to tornado missiles. The additional equipment was declared inoperable, and returned to an operable-but-nonconforming status using EGM 15-002, Revision 1. The identified nonconformances are legacy issues associated with the original plant design. Point Beach is !pursuing a license amendment request to address tornado missile protection adequacy. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, CONTINUATION SHEET ~ ~ the Desk Officer, Office of Information and Regulatory Affairs, NEOB-1 0202, (3150-010 4), Office of (See NUREG-1 022, R.3 for instruction and guidance for completing this form Management and Budget, Washington, DC 20503. If a means used to impose an information http:/fw.Nw.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1 022/r3D collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Point Beach Nuclear Plant Unit 1 05000-266 NUMBER NO. 2018 -001 -00 | Description of the Event: On March 1, 2018, with Units 1 and 2 operating at 100% power, during evaluation of safe shutdown equipment for protection from the damaging effects of tornado missiles, Point Beach personnel initiated a condition report documenting a potential vulnerability for the turbine driven auxiliary feedwater pumps due to steam supply piping that is not routed through a Class I structure. Subsequent to the condition identified on March 1, 2018, on March 8, 2018, an extent of condition review documented additional equipment, required for safe shutdown, that is not fully protected by Class I structures that are potentially vulnerable to a tornado missile. The equipment identified as potentially vulnerable to tornado missile damage includes: • Unit 1 and 2 turbine driven auxiliary feedwater pump system [BA] -for unprotected steam supply piping and unprotected turbine exhaust stacks • Unit 1 and 2 Train B emergency diesel generators G03 and G04 [DG]- for unprotected fuel oil storage tank (T- 175B) vent [DR] [TK] • Unit 1 and 2 main steam isolation valves [SB] [ISV], main steam safety valves [SB] [RV] and atmospheric dump valves [SB] [PCV] -for lack of protection Operations declared the affected equipment inoperable, implemented EGM 15-002, Revision 1, and the required compensatory measures; and, returned the affected equipment to an operable-but-nonconforming status within the Technical Specification Action Condition completion times. Cause of the Event: The identified nonconformances are legacy issues associated with original plant design. Due to the historical nature of this vulnerability, a specific cause has not been identified. Analysis of the Event and Safety Significance: During a postulated design basis tornado, the conditions documented could have resulted in a loss of safety function for the Unit 1 and 2 turbine driven auxiliary feedwater pump systems, main steam systems, and emergency diesel generators G03 and G04. The affected systems/components are used to achieve and maintain safe shutdown, remove decay heat, and mitigate the effects of postulated design-basis accidents. As documented in EGM 15-002, Revision 1, tornado missile scenarios do not represent an immediate safety concern because their risk is bounded by the initiating event frequency and safety-related systems/structures/components are typically designed to withstand the effects of tornadoes. For a tornado missile induced scenario to occur, a tornado would have to strike the site and result in the generation of missiles that would hit and fail vulnerable, unprotected safety shutdown equipment and/or unprotected safety shutdown subcomponents in a manner that is non-repairable and non-recoverable. In addition, because plants are designed with redundancy and diversity, the tornado missiles would have to affect multiple trains of safety systems and/or means of achieving safe shutdown. | ML18116A140
grand gulf nuclear station | Unknown Unit | Inoperable Reactor Protection Functions During Main Steam Isolation Valve and Turbine Stop Valve Channel Functional Tests due to Use of a Test Box | 04-27-2018 | On March 6, 2018, during a review of industry operating experience, it was determined that use of the Reacto.r Protection System (RPS) test box described in station procedures would potentially result in the loss of two RPS reactor scram safety ·functions. Technical Specification (TS) ·3:3.1.1 requires that RPS instrumentation for Table -3.-3.1.1-1 Function 6 for Main Steam Isolation Valve - Closure (MSIV) and Fun~tion 9 for Turbine Stop Valves Closure (TSV) remain OPERABLE. It was concluded that an isolation of three of four Main Steam Lines or Turbine Stop Valves would not necessarily have resulted in a full Scram during testing, as required the TS bases, depending on the combination of closed valves occurring while the test box was in u~e. Modifications were approved in 2014 to accommodate the test box and surveillance procedures were revised to incorporate the use of the test box in May and June of 2016. Between May 2016 and February 2018, the MSIV Closure and TSV Closure procedures were each performed 6 times using the test box. While it did not meet the TS bases, the RPS remained functional at all times. The failure to recognize the impact ofthe modification and procedure revisions is considered a ·human performance error by engineering personnel. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (4-2017) Estimated_ burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch.(T-2 LICENSEE EVENT REPORT (LER) F43}, U.S. Nuclear Regulatory Commission; Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not (See NUREG-1022, R.3 for instruction and guidance for completing this form display a currently valid OMB control number, the NRC may not conduct or sponsor, and a http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3t) person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 3. LER NUMBER YEAR SEQUENTIAL REV. Grand Gulf Nuclear Station, Unit 1 05000 416 NUMBER NO. 2018-003-00 | A. PLANT CONDITIONS PRIOR TO THE EVENT On March 6, 2018, Grand Gulf was operating in Mode 1 at 78% Power. There were no structures, systems, or components that were inoperable at the start of this event that contributed to this event. B. DESCRIPTION On March 6, 2018, engineering personnel identified that the use of the Reactor Protection System (RPS) [EIIS: JC] test fixture as implemented in some surveillance test procedures could result in the loss of two RPS reactor scram safety functions. Use of the test fixture in surveillance test procedures unintentionally resulted in the loss of Technical Specification (TS) Table 3.3.1.1 Function 6, Main Steam Isolation Valve-Closure, and Function 9, Turbine Stop Valve Closure (Trip Oil Pressure -Low), as defined in the TS bases. The TS bases state a scram will occur on isolation of at least one main steam isolation valve (MSIV) [EIIS: SB][ISV] in three of four main steam lines (MSLs), and on· closure of three of four turbine stop valves (TSV) [El IS: TA][ISV]. A review determined that iso_lation of three of four MSLs, or closure of three of four TSVs, would not necessarily have resulted in a full Scram while the test fixture was in use. The test box was designed to reduce unnecessary RPS actuations. The test box consists of a S ohm resistor in parallel with a 5 VAC lamp terminated with banana jacks. The RPS test box establishes a low resistance path in parallel with the trip logic relay contacts. The RPS has two independent trip systems (A and B) with two trip logics (i.e., trip divisions) in each trip system: A and C trip logics for Trip System A, and Band D trip logics for Trip System B. For Function 6 (MSIV Closure), which uses pressure transmitters and trip units to detect changes in hydraulic pressure, there are sixteen total instrument channels. (two per MSIV) with each logic division having four instrument channels and each trip system having eight. The logic used ensures a full reactor scram occurs for the condition where at least one MSIV in three or more MSLs are less than 90% open. This occurs as the logic uses vaives in A and C MSLs for Division A trip logic, A and B MSLs for the Division B trip logic, Band D MSLs for the Division C trip logic, and C and D MSLs for the Division D trip logic. By varying the order in which the auxiliary relay contacts are paralleled within each RPS trip logic it can be assured that a half Scram will occur in each trip system even if all the MSL switches on any one MSL fail. ·similarly, the TSV logic has eight instrument channels with -the same alternating logic for the four TSVs. The use of the RPS test box, as implemented in the procedures, would bypass MSL valve position signal inputs for two MSLs (i.e., bypass four instrument channels) and prevent the associated trip logic from being in a tripped condition (i.e., half-scram). This prevents the associated trip system · from generating a half-scram when two of three isolated MSLs are !n the bypassed division and, while a valid Group 1 isolation (closure of all four MSLs) would still result in a full scram, a scram would not occur in two of four possible MSL isolation scenarios involving just three MSLs, as required by the TS bases. For Function 9 (TSV Closure), the logic used ensures a full reactor scram occurs for the condition where three or more TSVs are less than full open. Each trips stem monitors trip fluid ressure Page 2 of 5 | ML18117A482
Quad Cities Nuclear Power Station | Unit 1 | Tornado Missile Protection Non-Conformance in Association with EGM 15-002 | 04-30-2018 | On March 1, 2018, Quad Cities Nuclear Power Station (QCNPS) conservatively identified a non-conforming condition with the three Emergency Diesel Generators (EOG) intake stacks, exhaust stacks, and related fuel oil tank vents, with respect to tornado missile protection. Compensatory measures were implemented and verified in accordance with the NRG Enforcement Guidance Memorandum (EGM) 15-002, "Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance," and DSS-ISG-2016-01, Revision 1, "Enforcement Discretion for Tornado- Generated Missile Protection Noncompliance." All three EDGs were returned to operable but non-conforming status in accordance with EGM 15-002 and DSS-ISG-2016-01 guidance, and an eight-hour Event Notification was made to the NRC. This condition is reportable under multiple reporting criteria in accordance with 10CFR50.73 requirements indicated above. This condition is a legacy issue that has existed since the original licensing of the plant. Due to the historic nature of this issue, a specific cause of the identified vulnerabilities was not determined. No actual consequences resulted from the nonconforming condition. NRC FORM 366 (02-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the lnfonmation Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the ;. (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the infonmation ·c-"http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3!) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR Quad Cities Nuclear Station Unit 1 05000254 NUMBER NO. 2018 - 002 00 | PLANT AND SYSTEM IDENTIFICATION General Electric -Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Emergency Onsite Power Supply System [EK], Emergency Diesel Generators [DG], and Fuel Oil Storage and Transfer System [DE] Energy Industry Identification System (EllS) codes are identified in the text as [XX]. EVENT IDENTIFICATION During a systematic review of the plant protection for tornado generated missiles the Unit 1, 2, and Common Emergency Diesel Generators [DG](EDG) were identified as non-conforming to the station Licensing Basis. A. CONDITION PRIOR TO EVENT Unit: 1 Event Date: March 1, 2018 Event Time: 1210 hours Reactor Mode: 1 Mode Name: Power Operation Power Level: 100% There were no structures, systems, or components (SSCs) out of service or inoperable that contributed to the event. B. DESCRIPTION OF EVENT In response to Regulatory Issue Summary (RIS) 2015-06 Quad Cities Nuclear Power Station (QCNPS) reevaluated tornado missile protection under the Enforcement Guidance Memorandum (EGM) 15-002 to insure compliance with the Current Licensing Basis (CLB). The QCNPS CLB requires protection against the effects of single bounding tornado generated missile impacts. Protection against multiple missiles outside the Power Block is not part of the QCNPS CLB. The EDGs [DG] have intake and exhaust piping, and fuel storage [DE] tank vents that are located outside the protection of concrete structures. The potential crimping of these lines from missile impact could prevent the associated Diesel Generator from performing its safety function. Although not described in the CLB, a multiple missile event could prevent redundant EDGs from performing their required safety functions. Therefore, it was conservatively decided to report the EDGs as non-conforming. On March 1, 2018, at 121 O hours, the Unit 1, 2 and Common Emergency Diesel Generators [DG] were declared inoperable. Compensatory actions in accordance with EGM 15-002 guidance were implemented to return the equipment to operable but non-conforming status. On March 1, 2018, at 1243 hours, ENS #53235 was made to the NRG. This event is reportable as a licensee event report (LER) in accordance with the following: 1O CFR 50.73(a)(2)(i)(B) for operation or condition prohibited by TS, since the design deficiency (i.e., non-conforming condition) existed for a time longer than permitted by TS, 10 CFR 50.73(a)(2)(ii)(B) for a condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety, 10 CFR 50.73(a)(2)(v)(D) for a condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident, and 10 CFR 50.73(a)(2)(vii) for an event where a single cause or condition causes two independent trains or channels to become ino erable in a sin le s stem desi ned to miti ate the conse uences of an accident. NRG FORM 366A (04-2017) Page _2_ of _4_ | ML18120A157
Susquehanna Steam Electric Station | Unit 1 | Secondary Containment Declared Inoperable Due to the Opening of a Plenum | 00-04-2018 | On November 30, 2017 at approximately 1030 hours, Susquehanna control room received indication of a loss of Secondary Containment Zone 2 differential pressure, noting differential pressure less than 0.25 inches water gauge 0NG) for several seconds. As a result, Technical Specification (TS) 3.6.4.1 Surveillance Requirement 3.6.4.1.1 was not met and TS 3.6.4.1 action statement 'A' was entered. The alarm came during an entry into the Unit 2 Zone 3 Exhaust Plenum for fan maintenance. This event is similar to an event that occurred on February 11,2018 (LER 50-388(387)/2018-001-00). The condition is being reported in accordance with 10 CFR 50. 73(a)(2)(v)(C) as an event or condition that could have prevented fulfillment of a safety function. The condition was previously reported on November 30, 2017 in accordance with 10 CFR 50.72(b)(3)(v)(C) in EN #53098. This event was unable to be replicated under various scenarios and no obvious equipment issues were identified. A sign was installed on the Unit 2 Zone 3 exhaust plenum door that states: "Entry into the plenum may impact secondary containment, notify control room prior to entry to evaluate LCO requirements." There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366 (02-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-1 0202, (3150-01 04), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1 022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http://vmw. nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1 022/r3D NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LERNUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station Unit 1 05000-387 NUMBER NO. 2017 007 01 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, approximately 100 percent Rated Thermal Power Unit 2 - Mode 1, approximately 100 percent Rated Thermal Power There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. EVENT DESCRIPTION On November 30, 2017 at approximately 1030 hours, Susquehanna control room received indication of a loss of Secondary Containment Zone 2 differential pressure, noting differential pressure less than 0.25 inches water gauge (WG) for several seconds. As a result, Technical Specification (TS) 3.6.4.1 Surveillance Requirement 3.6.4.1.1 was not met and TS 3.6.4.1 action statement 'A' was entered. The alarm came during an entry into the Unit 2 Zone 3 Exhaust Plenum for fan maintenance. This event is similar to an event that occurred on February 11, 2018 (LER 50-388(387)/2018-001-00). As a result of the November 2017 event, the Zone 2 filtered exhaust flow controller [EllS System/Component Code: VA!TC] gain and ratio settings were adjusted to have the filtered exhaust fans respond more quickly during a transient. Traces before settings adjustments and after adjustments were reviewed and indicate the adjustment did result in the Zone 2 filtered exhaust fans responding more quickly, but the adjustments did not prevent recurrence of the February 11, 2018 event. Additional troubleshooting was initiated on February 28, 2018 and March 6, 2018 but was unsuccessful in identifying the cause. Zone 2 differential pressure remained above 0.25 inches WG during the troubleshooting and no obvious component issues were identified. The condition is being reported in accordance with 10 CFR 50. 73(a)(2)(v)(C) as an event or condition that could have prevented fulfillment of a safety function. The condition was previously reported on November 30, 2017 in accordance with 10 CFR 50.72(b)(3)(v)(C) in EN #53098. CAUSE OF EVENT This event was unable to be replicated and no obvious equipment issues were identified during troubleshooting. ANALYSIS/SAFETY SIGNIFICANCE Based on engineering analysis of the event, secondary containment could have performed its safety function of isolating as assumed in the accident analysis and of re-establishing 0.25 inches of vacuum WG (drawdown) within the assumed accident-analysis time (10 minutes). This event will not be counted as a safety system functional failure (SSFF) for the NRC performance indicator based on the engineering analysis supporting the system's ability to fulfill the safety function. NRC FORM 3668 (04-2017) Page 2 of 3 | ML18124A012
Duane Arnold Energy Center 05000-331 1 OF 4 | Unknown Unit | Loss of RPS Function During MSIV and TSV Channel Functional Testing due to Use of a Test Box | 04-04-2018 | On February 6, 2018, at 1312 CST, while operating at 100% power, a Maintenance Supervisor determined that the use of the Reactor Protection System (RPS) test box described in site procedures would result in the loss of two RPS reactor scram functions. Technical Specifications (TS) 3.3.1.1 requires that RPS instrumentation for Table 3.3.1.1-1, Function 5, for Main Steam isolation Valves (MSIVs) and Table 3.3.1.1-. 1, Function 8, for Turbine Stop Valves (TSVs) remain OPERABLE. Surveillance Test Procedure (STP) 3.3.1.1-17, Main Steam Isolation Valve Functional Test, used the RPS test box from June 2015 through July 2016. STP 3.3.1.1-19, Functional test of TSV Closure Input to RPS and RPT, had used the RPS test box from May 2006 through December 2017. The cause of this event was determined to be inadequate plant effect evaluations for revising the STPs to incorporate use of the RPS test box. This event was of low safety significance and had no impact on public health or safety. This event is reportable pursuant to 10CFR50.73(a)(2)(v) as an Event or Condition that Could Have Prevented Fulfillment of a Safety Function. STP 3.3.1.1-19 was revised on February 28, 2018 to eliminate the use of the RPS test box. NRG FORM 366 (06-2016) NRG FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. ~,pfltAtcJ,'-f~ Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by \~) LICENSEE EVENT REPORT (LER) internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, CONTINUATION SHEET Washington, DC 20503. If a means used to impose an information collection does not display a currently valid 0MB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 6. LER NUMBER 3. PAGE I YEAR I SE N Q U U M E B N E T R IA L R N E O V . Duane Arnold Energy Center 05000-331 2 OF 4 2018 001 00 | I. Description of Event: On February 6, 2018,·at 1312 CST, while operating at 100% power, a Maintenance Supervisor determined that the use of the Reactor Protection System (RPS) test box described in site procedures would result in the loss of two RPS reactor scram functions. Technical Specifications (TS) 3.3.1.1 requires that RPS instrumentation for Table 3.3.1.1- 1, Function 5, for Main Steam isolation Valves (MSIVs) and Table 3.3.1.1-1, Function ff, for Turbine Stop Valves (TSVs) remain OPERABLE. SurvemanceTest Procedure (STP) 3.3.1.1-17, Main Steam Isolation Valve Functional Test, used the RPS test box from June 2015 through July 2016. STP 3.3.1.1-19, Functional test of TSV Closure Input to RPS and RPT, had used the RPS test box from May 2006 through December 2017. Both STP 3.3.1.1-17 and 3.3.1.1-19 were revised to incorporate the use of a test box to reduce unnecessary RPS actuations by eliminating the half scram created during previous STP performances. Between June 2015 and July 2016, STP 3.3.1.1-17 was performed 6 times. Between February 2014 and December 2017, STP 3.3.1.1-19 was performed 18 times. The performance of these STPs using the test box caused a loss of the RPS trip functions by bypassing more than the TS minimum allowed inputs per trip channel to maintain trip function operability. The unintended loss of RPS trip functions during these tests resulted in a NRC reportable condition under 1O CFR50. 73(a)(2)(v) as "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: (A) Shutdown the reactor and maintain it in a safe shutdown condition," and (D) "Mitigate the consequences of an accident." II. Assessment of Safety Consequences: The RPS initiates a reactor scram when at least one MSIV in 3 of the 4 Main Steam Lines close or when 3 of 4 TSVs close. The· automatic MSIV and TSV closure reactor scrams preserve the integrity of the fuel cladding and the Reactor Coolant System in anticipation of the transients caused by closure of these valves. With the use of the RPS test box a half scram for the trip system under test would still have occurred for an MSIV or TSV isolation as designed (all 4 steam lines isolated) because each trip logic channel individually produces a half scram. NRC FORM 366 (06-2016) | ML18128A197
Peach Bottom Atomic Power Station | Unit 2 | Fire Safe Shutdown Requirements Not Met for Spurious Operation of Valves at a High-Low Pressure Interface | 05-11-2018 | On 3/14/18, during a review of the Fire Protection Program Safe Shutdown Analyses, station personnel identified two valves that establish the boundary between a high pressure system and a low pressure system did not meet requirements contained in 1O CFR 50, Appendix R, Section 111.G for protection against spurious operation during a fire. A flow path exists through the Reactor Water Cleanup (RWCU) System into the Reactor Core Isolation Cooling (RCIC) pump discharge line into the 'B' feedwater line and into the low-pressure piping for the feedwater recirculation line back to the main condenser. During a fire, the cables could be damaged in such a way that the power cable to the outermost valve could be reenergized and the valve could open. The second valve is also normally closed but could spuriously open. If the fire also caused three other isolation valves in the RWCU system to not close, a flow path to the main condenser could exist, resulting in a loss of reactor vessel water inventory. This condition was not identified during the original analysis in the 1980's. There were no actual safety consequences as a result of this condition. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03131/2020 (04-2018} Estimated burden per response to comply v.ilh this mandatoiy collection request: BO hours. Reported lessons learned are incorporated into the licensing process and fed back lo industiy. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Aegulatoiy CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Aesource@nrc.gov, and to the Desk Officer, Office of Information and Aegulatoiy Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB control number, the NAG may not conduct or sponsor, and a person is not required to respond to, the inlormation collection. http://www.nrc.gov/reading-rm/doc-coffections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR Peach Bottom Atomic Power Station Unit 2 05000277 NUMBER NO. 2018 - 001 0 | Unit Conditions Prior to the Event Unit 2 and Unit 3 were both operating in Mode 1 at approximately 100% rated thermal power. There were no structures, systems or components out of service that contributed to this event. Description of Event On 3/14/18, station personnel were reviewing and updating the Fire Protection Program Safe Shutdown Analyses. The update including classifying two motor operated valves in the feedwater system as "high/low pressure interface" valves. An analysis originally performed in the 1980's did not identify the valves as high/low pressure interface valves. It was determined that a flow path existed from the reactor vessel through the Reactor Water Cleanup (RWCU) System into the Reactor Core Isolation Cooling (RCIC) pump discharge line into the '8' feedwater line and into the low-pressure piping for the feedwater recirculation line back to the main condenser. The two valves (in each unit) are: Unit 2 Unit 3 M0-2-06-0388 M0-3-06-0388 FW Long Path Recirculation Isolation Valve M0-2-06-2663 M0-3-06-3663 Long Path Recirculation Common Return Line As high/low pressure interface valves, both valves must be assumed to have the potential to spuriously open due to fire damage to electrical cables for the valves. A review performed in 2015 determined the two valves are a potential path for diversion of flow from the RCIC pump discharge if they should spuriously open during a fire, which could affect post-fire safe shutdown scenarios that rely on RCIC. Due to the potential for diversion of flow during a fire, power to the normally closed 2663/3663 valves was removed by opening the breaker during normal operations. During the 2015 review, it was assumed that removing power from the closed valves during normal operations would prevent the valve from opening during a fire and would eliminate the risk of loss of reactor vessel inventory during a fire. It was determined that the only action needed was to update fire protection documentation and calculations to classify the valves as high/low interface valves. During the March 2018 updating process, it was determined that the possibility of a 3-phase hot short during a fire also needed to be considered. The power cable between the breaker and the motor operator for the valve is in a cable tray with other energized cables. A 3-phase hot short could re-energize the valve operator and open the 2663/3663 valve. For this to create an actual flow path to the main condenser, fire damage to four additional valves would need to occur that would result in the valves spuriously opening or not closing if already open. The valves are the M0-2/3-06-0388 valve and three normally open primary containment isolation valves in the RWCU system: | ML18131A272
Cooper Nuclear Station 05000298 1 OF 3 | Unknown Unit | Inadequate Packing on Motor Operated Valve Results in Unplanned High Pressure Coolant Injection lnoperability and a Loss of Safety Function | 05-08-2018 | On March 10, 2018, while returning High Pressure Coolant Injection (HPCI) and Augmented Off-Gas to service following planned maintenance, Cooper Nuclear Station (CNS) Operations personnel observed rising pressure in the drywell. During the HPCI restoration, HPCI-MOV-M015 was cycled and left open as part of the return to service process. Shortly thereafter, drywell temperature and pressure started to slowly rise. It was determined the most likely cause of the change in drywell parameters was due to the stroking of HPCI-MOV-M015. A decision was made to close the valve to stop the leak, resulting in an unplanned entry into Technical Specification Limiting Condition for Operation 3.5.1, due to HPCI inoperability. Following valve closure, drywell temperature and pressure, along with the unidentified leakage rate, decreased. A decision was made to perform a normal plant shutdown to make repairs. CNS entered Mode 3, Hot Shutdown, on March 11, 2018. New packing was installed on HPCI-MOV-M015 and CNS returned to Mode 1, Power Operation, on March 17, 2018. The cause of the packing leak was determined to be that in effort to preserve and maximize the margin for the stroking function, packing consolidation and torquing methods were altered which impacted packing sealing performance. No safety consequences were associated with this condition. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid 0MB control number, the http://www.nrc.gov/reading-rrn/doc-collections/nureqs/staff/sr1022/r3D NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITYNAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Cooper Nuclear Station 05000-298 NUMBER NO. 2018 -001 -00 | PLANT STATUS Cooper Nuclear Station (CNS) was in Mode 1, Power Operations, 100 percent power, at the time of discovery. BACKGROUND The High Pressure Coolant Injection (HPCI) System [EIIS:BJ] provides protection to the core for the case of a small break in the reactor coolant pressure boundary which does not result in a rapid depressurization of the reactor vessel. The HPCI System permits the nuclear plant to be shutdown while maintaining sufficient reactor vessel water inventory until the reactor vessel is depressurized. The HPCI System continues to operate until reactor vessel pressure is below the pressure at which Low Pressure Coolant Injection [EIIS:BO] operation or Core Spray System [EIIS:BM] operation can be used to maintain core cooling. HPCI consists of a steam turbine assembly [EIIS:TRB] driving a multi-stage booster and main pump assembly [EIIS:P] and system piping, valves, controls and instrumentation. The HPCI turbine is driven by steam from the reactor which is generated by decay and residual heat. There are two normally open containment isolation valves in the main steam supply line to the turbine. One of these valves, HPCI-MOV-M015 is located in the drywell. These containment isolation valves [EIIS:ISV] automatically close upon receipt of a HPCI turbine steam line high flow signal, or a HPCI turbine steam supply low pressure signal, or high steam line space temperature. EVENT DESCRIPTION On March 10, 2018, while returning HPCI and Augmented Off-Gas to service following planned maintenance to repair a steam leak on an associated drain line, CNS entered abnormal procedure 2.4PC, "Primary Containment Control" due to rising pressure in the drywell. During the HPCI restoration, HPCI-MOV-M015 steam supply inboard isolation valve was cycled and left open as part of the return to service process. Shortly thereafter, drywell temperature and pressure started to slowly rise, causing entry into the abnormal procedure. Operations and Engineering personnel determined the most likely cause of the change in drywell parameters was due to the stroking of HPCI-MOV-M015. A decision was made to close the valve to stop the leak, causing HPCI to be inoperable resulting in an unplanned entry into Technical Specification Limiting Condition for Operation 3.5.1 due to isolating the steam supply to HPCI. Following valve closure, drywell area temperatures and pressure, along with the unidentified leakage rate, decreased. A decision was made to perform a normal plant shutdown to make repairs. CNS entered Mode 3, Hot Shutdown, on March 11, 2018. New packing was installed on HPCI-MOV-M015 on March 15, 2018, and CNS returned to Mode 1, Power Operation, on March 17, 2018. NRC FORM 366 (04-2018) Page 2 of 3 | ML18136A539
LaSalle County Station | Unit 1 | Technical Specification Required Shutdown due to Reactor Pressure Boundary Leakage | 03-31-2020 | On March 22, 2018, a through-wall pipe leak was identified on a three-fourths inch vent line coming off the bonnet on a reactor recirculation pump discharge valve. This condition was reactor coolant system (RCS) pressure boundary leakage, which required entry into technical specifications (TS) actions for required shutdown. The leakage was significantly less than the 10 gallons per minute emergency action threshold. At the time of discovery, Unit 1 was in Mode 1. A controlled shutdown of Unit 1 was performed, having all necessary shutdown equipment available; and, there was no impact to Unit 2. This condition was reported on March 22, 2018 (ENS 53276) in accordance with 10 CFR 50.72(b)(2)(i) for plant shutdown required by Technical Specifications and 10 CFR 50.72(b)(3)(ii)A for the pressure boundary leakage as a principal safety barrier being in a degraded condition. The cause for the steam leak on the vent line was determined to be fatigue cracking that initiated on the external surface of the pipe at the toe of the socket fillet weld. Crack propagation occurred under low cycle fatigue conditions. In addition, the fracture surface contained deformation features which were indicative of a potential high nominal stress. Actions were taken to repair the vent line after plant shutdown and perform failure analysis on the degraded component. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)A as a condition that required a plant shutdown in accordance with TS and 10 CFR 50.73(a)(2)(ii)A as a principal safety barrier being in a degraded condition. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fad back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch [T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollecls.Resource@nn;.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB control number, the NRC may not conduct or http./lwww.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person Is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR LaSalle County Station, Unit 1 05000373 NUMBER NO. 2018 004 00 | PLANT AND SYSTEM IDENTIFICATION LaSalle County Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected component was a three-fourths inch vent line (1 RR32AB-3/4") coming off the bonnet on the 1 B reactor recirculation pump discharge valve (1833-F0678). CONDITION PRIOR TO EVENT Unit(s): 1 Date: March 22, 2018 Time: 0300 CDT Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 24 percent DESCRIPTION On March 22, 2018, at 0300 CDT, a through-wall pipe leak was identified on a three-fourths inch vent line coming off the bonnet on the 1 B reactor recirculation pump discharge valve (1833-F0678). Personnel observed a plume of steam was coming from a partial circumferential crack at the toe of the weld connecting the small-bore vent pipe 1 RR32AB-3/4" and the valve bonnet. This condition was determined as a reactor coolant system (RCS) pressure boundary leakage, which required entry into technical specifications (TS) actions for required shutdown. Specifically, TS 3.4.5, Reactor Coolant System Operational Leakage, Required Actions C.1 and C.2 were entered, which require the unit to be in Mode 3, Hot Shutdown within 12 hours, and Mode 4, Cold Shutdown in 36 hours, respectively. The leakage was significantly Jess than the 10 gallons per minute emergency action threshold. At the time of discovery, Unit 1 was in Mode 1. A controlled shutdown of Unit 1 was performed, having all necessary shutdown equipment available. Unit 1 was placed into Mode 4 on March 22, 2018, at 1652 CDT. There was no impact to Unit 2. This condition was reported to the NRC via Event Notification System (ENS) 53276 on March 22, 2018 as a degraded condition that involved a required plant shutdown. CAUSE The failure occurred after approximately seven days of service following the vent line installation during the Unit 1 refueling outage (L 1R17). A component failure analysis was completed which determined that the failure was attributed to fatigue cracking that initiated on the external surface of the pipe at the toe of the socket fillet weld. Based on the relatively large spacing of the fracture surface fatigues striations, crack propagation occurred under low cycle fatigue conditions. In addition, the fracture surface contained deformation features which were indicative of a potential high nominal stress. For the failed "B" vent line assembly, the likely cause for the high nominal stress was contact with the clamshell support clamp. Based on the clamshell clamp and pipe wear marks, the support appeared to have applied a downward force to the failed line during service. Lab inspections did not detect fatigue cracking at the socket weld location in the similar intact "A" vent line, which suggests that failure was not imminent. The station initiated a root cause investigation to determine additional causal factors for this failure. REPORTABILITY AND SAFETY ANALYSIS This condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)A as a condition that required a plant shutdown in accordance with TS and 10 CFR 50.73(a)(2)(ii)A as a principal safety barrier being in a degraded condition. This condition was reported to the NRC via ENS report number 53276 on March 22, 2018. There were no safety consequences resulting from the event. Makeup capability was adequate to compensate for the leak. All emergency core cooling systems (ECCS) were operable and capable of fulfilling their intended safety functions during the period of leakage. The leak was within the capability of the leak detection system and was within the capability of the leak collection system. | ML18141A637
Watts Bar Nuclear Plant | Unit 1 | Control Room Emergency Ventilation System Inoperable due to Main Control Room Door Being Left Open | 05-24-2018 | At 1058 Eastern Daylight Time (EDT) on March 26, 2018, a Main Control Room (MCR) alarm was received for low control room positive pressure. At 1100 EDT, a Control Room Envelope (CRE) door was found ajar and immediately closed. Technical Specification Limiting Condition for Operation (LCO) 3.7.10, Control Room Emergency Ventilation System (CREVS), was declared not met for both trains and Condition B entered. At 1100 EDT on March 26, 2018, the alarm cleared, CREVS was declared operable and LCO 3.7.10, Condition B was exited. Later that day at 1839 EDT, a MCR alarm was received for low control room positive pressure. At 1840 EDT, a CRE door was found ajar and immediately closed. Technical Specification LCO 3.7.10 for CREVS, was declared not met for both trains and Condition B entered. At 1840 EDT on March 26, 2018, the alarm cleared, CREVS was declared operable and LCO 3.7.10, Condition B was exited. These events were caused by human performance errors when individuals traversing the control building complex failed to confirm the MCR envelope boundary door was properly latched. A worn latching component of the MCR envelope door contributed to this event, and was replaced. A site stand-down was conducted to brief and reaffirm to site personnel on the requirements for door closure throughout the plant. An engineering change is in development to magnetically lock the MCR door and to provide indication when the door is not fully shut and latched. NRC FORM 366 (02-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION • ~--BY ulVIB: NU. 3150-0104 i:;Ar-'"'""': ... ··--- (04-2017)) Estimaled burden per rasponse ID comply with this mandatory collection request: 80 hours. Reported lessons 9amed are incorporated into the Dcensing process and led back ID indusby. Send comments ragarding burden ostimale ID the Information Soivices Branch (T- 2 F43), U.S. Nuc8ar Regulatory Commission, Washington, QC 20~1.or by e-mail ID LICENSEE EVENT REPORT (LER) lnfocol-. Rosoun:e@nrc.gov, and ID tho Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, CONTINUATION SHEET Washington, DC 20503. If a means used ID impose an inlonmalion collaction does not display a cunanll'( vain 0MB conlml number, tho NRC may not conduct or sponsor, and a person is not required ID raspond ID, tho information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Watts Bar Nuclear Plant, Unit 1 05000390 NUMBER NO. 2018 - 003 00 | I. Plant Operating Conditions Before the Event Watts Bar Nuclear Plant (WBN) Unit 1 and Unit 2 were at 100 percent rated thermal power (RTP) . 11. Description of Event A. Event Summary At 1058 Eastern Daylight Time (EDT) on March 26, 2018, a Main Control Room (MCR) alarm was received for low control room positive pressure. At 1100 EDT, a Control Room Envelope (CRE) door {EIIS:DR} was found ajar and immediately closed. Technical Specification Limiting Condition for Operation (LCO) 3. 7 .10, Control Room Emergency Ventilation System (CREVS){EIIS:VI}, was declared not met for both trains and Condition B entered. At 1100 EDT on March 26, 2018, the alarm cleared, CREVS was declared operable and LCO 3.7.10, Condition B, was exited. Later that day at 1839 EDT, a MCR alarm was received for low control room positive pressure. At 1840 EDT, a CRE door was found ajar and immediately closed. Technical Specification LCO 3.7.10 for CREVS, was declared not met for both trains and Condition B entered. At 1840 EDT on March 26, 2018, the alarm cleared, CREVS was declared operable and LCO 3.7.10, Condition B was exited. This event is being reported to the Nuclear Regulatory Commission (NRC) under 1 O CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event A worn latching component contributed to this condition. C. Dates and approximate times of occurrences Date Time (EDT) Event 3/26/18 1058 MCR alarm was received for low control room positive pressure. TS 3. 7 .1 Ow as declared not met for both trains and Condition B entered 3/26/18 1100 CRE door was found ajar and immediately closed. TS 3.7.10 Condition B exited with cleared alarm 3/26/18 1839 MCR alarm was received for low control room positive pressure. TS 3. 7 .10 was declared not met for both trains and Condition B entered 3/26/18 1840 CRE door was found ajar and immediately closed. TS 3.7.10 Condition B exited with cleared alarm. D. Manufacturer and model number of each component that failed during the event The door involved in this event was fabricated by TVA. E. Other systems or secondary functions affected No other systems or secondary functions were affected. NRG FORM 366A (04-2017) Page _2_ of _s_ | ML18144A998
grand gulf nuclear station | Unknown Unit | Secondary Containment Door Misaligned, Due to 1nadequate Criteria, Could Have Prevented Fulfillment of a Safety Function | 05-25-2018 | On March 31, 2018, at approximately 0200, Grand Gulf Nuclear Station (GGNS) Operations personnel performed Technical Specification Surveillance Requirement (SR) 3.6.4. 1.4, Secondary Containment Drawdown. During the surveillance, secondary containment pressure was unable to be maintained, as required by SR 3.6.4.1.4, and Operators -in the field-identified air-leakage from the Auxiliary Building Rail Bay Door. The door-had -been operated the previous day by supplemental personnel, who improperly seated the door, causing excessive air flow across the seals .. The cause of the door misalignment was a lack of criteria for determining proper door seating. The procedure has a step to inspect the door for misalignment; however, there are no match marks or quantitative metrics to compare the performance against a standard. Corrective actions include restoring door alignment and satisfactorily performing the previously failed surveillance. In addition, match marks or alignment aids will be added to the door, and referenced in t~e relevant procedures. Engineering analyzed the results of the failed Surveillance, and determined that the GGNS dose analysis would have been preserved and the Secondary Containment safety function would have still been met. In addition, no other component or system failures contributed to this event. NRC FORM 366 (02-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43}, U.S. Nuclear Regulatory Commission, Washington, DC · 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http://www.nrc.gov/reading.;.rm/doc-collections/nuregs/staff/sr1022/r3D NRG may not conduct or sponsor, and a person is not required to respond to, the information co~oo. · · · 1. FACILITYNAME 2. DOCKET NUMBER 3. LERNUMBER YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 05000-416 NUMBER NO. 2018 -005 -00 | A PLANT CONDITIONS PRIOR TO THE EVENT 100 percent reactor power with no inoperable structures, components, or safety systems contributing to the event. B. DESCRIPTION On March 30, 2018, at approximately 1500, after staging material in the Auxiliary Building Rail Bay, supplemental personnel closed the Auxiliary Building Rail Bay rollup door [DR] using the installed winches in accordance with the governing procedure. Peer checks, place keeping, and Refuel Services supervisor oversight at the work area were ·utilized. The ·door-seals -were vertfied ·to be ·in ·satisfactory ·condition and ·no ·obstructions -were ·present on the floor-sealing · surface. In addition, Security personnel verified that no light was coming under the door, as an additional precaution. On March 31, 2018, at approximately 0200, Operations personnel performed Technical Specification Surveillance Requirement 3.6.4.1.4, Secondary Containment [NG] Drawdown. During the surveillance, secondary containment 1 pressure was unable to be maintained, as required by SR 3.6.4.1.4, and Operators i,n the field identified air leakage from the Auxiliary Building Rail Bay Door. The test was secured, Secondary Containment was declared INOPERABLE, and Technical Specification Condition 3.6.1.4 A was entered at 0206. Secondary Containment was returned to an operable --status -by -returning the -system to a -previously ·known operable -configuration, with -the relevant ·floor -block-s and internal personnel doors as the Secondary Containment boundary. The Limiting Condition for Operation was declared met at 0344. After multiple attempts and the use of more experienced personnel, the door was properly seated. The experienced maintenance personnel had an understanding of how to seat the door that was not reflected in the procedure. The Secondary Containment Drawdown Surveillance was satisfactorily performed, at 1615, on April 1, 2018. -C. -REPORTABILITY This event is being reported under 10 CFR 50. 73(a)(2)(v)(C), as an event or condition that could have prevented fulfillment of a safety function of structures or systems that are needed to control the release of radioactive material. This event was initially reported under 10 CFR 50.72(b)(3)(v)(C) on March 31, 2018, via Event Report 53304. D. CAUSE The.cause .of .the .door misalignment was .a .lack .of .criteria for .determining .proper .door seating. Even though the procedure has a step to inspect the door for misalignment, there are no match marks or quantitative metrics to compare. the performance against a standard. E. CORRECTIVE ACTIONS The following actions are completed or planned. Completed: • Secondary Containment was returned to an operable status by returning the system to a previously known operable configuration. | ML18145A292
Browns Ferry Nuclear Plant (BFN) | Unit 1 | Unanalyzed Condition due to an Incorrectly Wired Breaker on Emergency Equipment Cooling Water Pump | 05-29-2018 | On March 8, 2018, at 0130 Central Standard Time (CST), during a relay functional test of the C3 Emergency Equipment Cooling Water (EECW) Pump trip circuit, incorrect wiring was discovered on the C3 EECW Pump breaker. This condition would have prevented the breaker closing springs from recharging while the transfer switch was in the emergency position. On March 10, 2018, at 2042 CST, Maintenance personnel completed work to correct the wiring for the pump breaker. On March 29, 2018, at 1344 Central Daylight Time (CDT), BFN Engineering determined that an unanalyzed condition, which significantly affected plant safety, had existed from October 28, 2015 to March 10, 2018. For postulated fire scenarios that could cause a Loss of Offsite Power and also result in Main Control Room Abandonment, the required EECW pumps utilized in the Fire Safe Shutdown procedure may not have been available. On March 29, 2018, at 2128 CDT, Event Notification# 53300 was made to the NRC. The cause of this condition was a legacy human performance (HU) error involving a failure to properly utilize HU tools. Corrective actions were to correctly rewire the circuitry for the C3 EECW Pump breaker, and to revise plant procedures in order to add HU tools which verify, during testing, that the breaker springs will recharge while the transfer switch is in the emergency position. NRG FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION ,. ·- 'CU tH UMts: NU. 31ou-ui04 CAt'1 ..c ;:,: --·-,, ___ _ (04-2018)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons le<W"ned <W"e incorpo.-ated into the licensing process and fed back to induslry. Send comments regarding burden estimate to the Information Se!vices Branch (T- 2 F43), U.S. Nucle<W" Regulatory Commission, Washington, DC 2055~001,or bye-ma~ to LICENSEE EVENT REPORT (LER) lnfocollects. Resource@nrc.gov, and to the Desk Office<, Office of lnfonnation and Regulatory Mairs, NEOB-10202, (315().0104), Office of Management and Budget CONTINUATION SHEET Washington, DC 20503. If a means used to ilT!JOse an information collection does not display a ctrrenlly valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 1 05000259 NUMBER NO. 2018 - 003 00 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Units 1 and 2, were in Mode 1 at approximately 100 percent rated thermal power, and BFN, Unit 3, was in Mode 5 for a refueling outage at zero percent power. II. Description of Event A. Event Summary On March 8, 2018, at 0130 Central Standard Time (CST), during a relay [RL Y] functional test of the C3 Emergency Equipment Cooling Water (EECW) [Bl] Pump [P] trip circuit, incorrect wiring was discovered on the C3 EECW Pump breaker [BKR]. This condition would have prevented the breaker closing springs from recharging while the transfer switch was in the emergency position. On March 10, 2018, at 2042 CST, Maintenance personnel completed work to correct the wiring for the pump breaker. On March 29, 2018, at 1344 CDT, BFN Engineering determined that even though the C3 EECW pump had been unavailable since August 23, 2012, an unanalyzed condition which significantly degraded plant safety actually existed from October 28, 2015 to March 10, 2018. This is based on the fact that the C3 EECW Pump was not credited in the backup control mode until 10CFR50.48(c) - National Fire Protection Association 805 became effective October 28, 2015. For postulated fire scenarios that could cause a Loss of Offsite Power (LOOP) and also result in Main Control Room (MCR) [NA] Abandonment, the required EECW pumps utilized in the Fire Safe Shutdown (FSS) procedure may not have been available. On March 29, 2018, at 2128 CDT this condition was reported to the NRC as Event Notification # 53300. The Tennessee Valley Authority (TVA) is submitting this report in accordance with 10 CFR 50.73(a)(2)(ii)(B), as any event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, components, or systems (SSCs) that were inoperable at the time of discovery, which contributed to this condition. | ML18149A495
clinton power station | Unknown Unit | Degraded Personnel Airlock Interlock Results in Loss of Primary Containment | 05-29-2018 | On March 30, 2018, at 1305 CDT, with the reactor at 98 percent thermal power a contractor identified that both doors of the Primary Containment personnel airlock at 828 ft elevation were open simultaneously. This individual was closing the interior door when he noticed that the exterior door was off its seat and started to open. The interior airlock door was shut immediately and the Main Control Room was contacted. Operations entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.1.1, "Primary Containment," Required Action A.1 at 1305 CDT. The LCO was exited approximately one minute later. Primary Containment was inoperable during the time both airlock doors were open but restored with the closing of the interior airlock door. Maintenance personnel performed equipment troubleshooting and subsequently repaired the interlock. The cause of the event is due to component wear over time of the exterior airlock door interlock parts that resulted in the containment airlock interlock not functioning properly. Cormctive action include creation of a preventative maintenance task to perform an in-depth inspection of the Primary Containment interlocks. This event is reportable under 10 CFR 50.73(a)(2)(ii)(A) as the condition of the nuclear power plant including its principal safety barriers, being seriously degraded, and 10 CFR 50.73(a)(2)(v)(C) as any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. This has been evaluated to not constitute a safety system functional failure. NRG FORM 366 (02-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LEA) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid 0MB control number, the (See NUREG-1 D22, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http1/WWlv.nrc.gov/reading-rmfdoc-colleclions/nuregs/staff/sr1022/r31) collection. 1. FACILITY NIAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Clinton Power Station, Unit 1 05000461 NUMBER NO. 2018 - 001 00 | PLANT AND SYSTEM IDENTIFICATION General Electric -- Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in text as [XX]. EVENT IDENTIFICATION Degraded Personnel Airlock Interlock Results in Loss of Primary Containment A. Plant Operating Conditions Before the Event Unit: 1 Event Date: 03/30/18 Event Time: 1305 Mode: 1 Mode Name: Power Operation Reactor Power: 98 percent B. Description of Event On March 30, 2018, at 1305 CDT, the 828 ft elevation Primary Containment airlock (1 MC03W) doors[DR] were discovered to be open simultaneously. An individual who was moving equipment made the discovery as he proceeded through the interior airlock door headed into Primary Containment. He noticed that the exterior airlock door was not securely shut and starting to open. Upon discovery of this condition, he immediately closed the interior door and proceeded to contact the Main Control Room. At 1305 CDT, Operations entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.1.1, "Primary Containment," Required Action A.1. The LCO was exited approximately one minute later at 1306 CDT. Maintenance personnel inspected airlock 1M C03W and discovered slight component wear on interlock parts of the exterior door. The interlock was repaired and both airlock doors were subsequently verified as functional. Based on recent maintenance records associated with the airlock doors, no issues had been identified. A non-emergency eight-hour notification was made in accordance with 1 O CFR 50.72. C. Cause of the Event Maintenance personnel performed equipment troubleshooting and determined the cause of the event as being due to component wear over time of the airlock door interlock parts that resulted in allowing both airlock doors to be able to be opened simultaneously. NRG FORM 366A (04-2017) Page _2_ of _3_ | ML18151A471
Limerick Generating Station | Unit 1 | Primary Containment Isolation Valve Failed to Fully Close Resulting in Condition Prohibited by Technical Specifications | 06-04-2018 | During the performance of reverse flushes of the Shutdown Cooling Piping for the refuel outage, the 1A Low Pressure Coolant Injection (LPCI) Outboard Injection Primary Containment Isolation Valve (PCIV) failed to fully close. The valve was manually closed and declared inoperable. Troubleshooting identified corrosion on the torque switch prevented the electrical and mechanical switches from closing on a demand signal. It was determined that the PCIV was inoperable after 9/8/17 when moisture from a nearby steam leak penetrated the motor operator limit switch compartment causing a ground in the motor operator. After the ground was received the valve was declared inoperable, actions were taken to clear the ground, and the valve was returned to an operable status. Though the PCIV was closed from 9/8/17 to 3/27/18, the valve was not deenergized per Technical Specification (TS) and the PCIV is required to close to support Suppression Pool Spray operation during a Loss of Coolant Accident (LOCA); therefore, this is a violation of TS and reportable per the requirements of 1O CFR 50.73(a)(2)(i)(B). NRC FORM 366 (02-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours Reported lessons learned are incorporated into the licensing process and led back to industry. Send comments regarding burden estimate to the Information Services Branch (T· 2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LEA) Regulatory Commission, Washington, DC 20555·0001. or by e·mai to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office ol Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office ol Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently va~d OMB control number, the (See NUREG-1 D22, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the Information http://www.nrc.gov/reading-rm/doc-collections/nuregs/stafflsr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR Limerick Generating Station, Unit 1 05000352 NUMBER NO. 2018 - 002 - 00 | I. Unit Conditions Prior to the Event Limerick Generating Station (LGS) Unit 1 was shut down for refueling outage 1R17 and in Operational Condition (OPCON) 4 at the time of identification. The condition was identified during reverse flushes of Shutdown Cooling piping. II. Description of the Event The A LPCI Outboard Injection Valve (HV-051-1 F017 A) is one of four Low Pressure Coolant Injection (LPCI) outboard injection valves on Unit 1. This valve is a Primary Containment Isolation Valve (PCIV) and a Pressure Isolation Valve (PIV). The A and B LPCI Outboard Isolation Valves have an additional function, in that during a Loss of Coolant Accident (LOCA) one of the two valves will need to be closed to supply water for Suppression Pool Spray. On 9/8/17, a ground occurred on the Low Pressure Coolant Injection (LPCI) Injection Valve HV-051- 1 F017A as a result of a steam leak from a nearby Reactor Water Cleanup (RWCU) valve. HV-051- 1 F017A was determined to be inoperable and was deenergized. The ground alarm cleared following drying of the compartment. The power was restored and the LPCI Injection Valve was returned to operable status. The valve was not stroked because the valve is a PIV. On 3/27/18, while in OPCON 4, Cold Shutdown, during the performance of reverse flushes of the Shutdown Cooling Piping for refuel outage 1 R17, the LPCI Injection Valve HV-051-1 F017A was opened. However, the valve failed to stroke fully closed when flushing was complete. The inoperable valve was deenergized and manually closed. On 4/3/18, a past functionality review concluded that the LPCI Injection Valve was inoperable as a result of the grounding condition. LGS concluded through evaluation that the A LPCI Outboard Isolation Valve was inoperable from 9/8/17 to 3/27/ 18 which resulted in the violation of two Technical Specifications (TS) and therefore is reportable per the requirements of 1O CFR 50.73(a)(2)(i)(B). TS 3.6.3.a.2 With an inoperable PCIV the penetration must be isolated with a de-energized PCIV within four hours or be in hot shutdown within the next 12 hours and in cold shutdown within the next 24 hours. TS 3.6.2.2 With an inoperable Suppression Pool Spray flow path on one of the AHR Loops, return the loop to the operable status within seven days or be in hot shutdown within the next 12 hours and in cold shutdown within the next 24 hours. NRG FORM 366A (04-2017) Page _2_ of _4_ | ML18155A193
Brunswick Steam Electric Plant (BSEP) | Unit 1 | Automatic Reactor Trip during Stator Coolant System Realignment | 03-31-2020 | On April 7, 2018, at 0836 Eastern Daylight Time (EDT), Unit 1 automatically tripped during realignment of the Stator Cooling System. The trip was uncomplicated with all systems responding normally. Reactor water level reached low level 1 (LL1) due to the reactor trip. Per design, the LL1 signal resulted in Group 2, Group 6, and Group 8 Primary Containment Isolation System (PCIS) actuations. The Reactor Protection System (RPS) and PCIS actuations are being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B). The direct cause of this event was a design deficiency which resulted in an unanticipated Turbine Protection System actuation that caused a main turbine trip and subsequent automatic reactor trip. The root cause of the design deficiency was determined to be human performance related. Corrective actions include training and procedure revisions. NRC FORM 366 (02-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant YEAR 05000325 NUMBER NO. (BSEP), Unit 1 2018 - 002 - 00 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. Background Initial Conditions At the time of the event, Unit 1 was in Mode 1 (i.e., Power Operation), at approximately 100 percent of rated thermal power (RTP). No safety-related equipment was inoperable at the time of the event. Reportability Criteria The Reactor Protection System (RPS) [JC] and Primary Containment Isolation System (PCIS) [JM] actuations are being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B). The event was initially reported to the NRC on April 7, 2018 (i.e., Event Number 53319). Event Description On April 7, 2018, realignment of the Unit 1 Stator Cooling System [TJ] was being performed in accordance with plant procedure 0PT-36.1, Stator Cooling System. On a monthly basis, the operating Stator Cooling pump is alternated. This is accomplished by starting the reserve pump, followed by shutting down the operating pump. When the reserve pump (i.e., the 1B pump) was started, a Loss of Stator Cooling and a Stator Coolant Low Flow alarm were received in the control room. Both Stator Cooling pumps were in service and reports from the field indicated normal Stator Cooling System pressure. Computer data indicated the expected increase in Stator Cooling System flow when the second pump was started. The Control Room staff evaluated indications for the Stator Cooling System and found no evidence that there were any problems with the system or impact on Stator temperature. The staff continued with restoration steps for 0PT-36.1. However, coincident with the alarms, a 120 second timer started; at the completion of which an automatic main turbine trip occurred. This resulted in an automatic reactor trip at 0836 Eastern Daylight Time (EDT). The scram was uncomplicated with all systems responding normally. Reactor water level reached low level 1 (LL1) due to the reactor trip. Per design, the LL1 signal resulted in Group 2 (i.e., floor and equipment drain isolation valves), Group 6 (i.e., monitoring and sampling isolation valves) and Group 8 (i.e., shutdown cooling isolation valves) isolations. The LL1 isolations occurred as designed; the Group 8 valves were closed at the time of the event. Event Cause The direct cause of this event was a design deficiency which resulted in an unanticipated Turbine Protection System [JJ] actuation that caused a main turbine trip and subsequent automatic reactor trip. This was the first performance of 0PT-36.1 after the recently completed Unit 1 refueling outage during which a new Turbine Control System (TCS) [JJ] was installed. | ML18156A565
Calvert Cliffs Nuclear Power Plant | Unit 1 | Items Non-Conforming to Design for Tornado Missile Protection | 06-07-2018 | On May 14, 2018, Calvert Cliffs Nuclear Power Plant determined that the Saltwater subsystems on both Units 1 and 2 do not conform with the licensing basis for protection against a tornado generated missile. The Saltwater system header is vulnerable to a tornado missile that enters the Intake Structure through the watertight door, IS-2. An extent of condition review did not identify any additional items that are non- conforming to the design basis for a tornado missile. Upon determination of the initial non-conformance for the Saltwater system subsystems, both Saltwater subsystems were declared inoperable for both Units. Compensatory measures were put in place and verified. Therefore, in accordance with the NRC Enforcement Guidance Memorandum EGM 15-002, both Saltwater system subsystems were returned to operable but non- conforming status and an 8-hour ENS Notification was made to the NRC. This condition has been in existence since original licensing of the plant. It is not known if it was overlooked or considered acceptable at the time of the original licensing process. There are no actual consequences as a result of the non- conforming condition. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported § + ~ ' ,;,' ' -V l ,'R Rl:cc,,1_ 0 . ; ~ LICENSEE EVENT REPORT (LER) l r e e s g s a o rd n i s n g le a b r u n r e d d e n a re e s in tim co a rp te o r t a o t e t d he in t I o n fo th r e m a lic ti e o n n s i S ng e rv p i r c o e c s e s B s r a a n n c d h f e ( d T - b 2 a c F k 4 3 to ), in U d . u S s . tr N y. u c S le e a n r d R co e m gu m la e to n r t y s ~ 0~ ., ~ , ,,., . , ' , , ' r . .. ..... ' ~ ~ Q CONTINUATION SHEET C th o e m D m e is sk s io O n f , f ic W er a , sh O in ff g ic t e o n o , f D In C f o 2 rm 05 a 5 ti 5 o - n 0 0 a 0 n 1 d , R or e g b u y l a e to -m ry a A il ff t a o i rs ln , fo N c E o O lle B c - t 1 s 0 .R 20 e 2 s , o u (3 rc 1 e 5 @ 0-0 n 1 rc 0 . 4 g ) o , v O , f a fi n c d e t o o f Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid 0MB control number, the NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, the information collection. ht!Q://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR Calvert Cliffs Nuclear Power Plant Unit 1 05000317 NUMBER NO. 2018 - 002 - 00 | PLANT AND SYSTEM IDENTIFICATION Calvert Cliffs Nuclear Power Plant, Units 1 and 2, are Combustion Engineering Pressurized Water Reactors with a licensed maximum power level of 2737 megawatts thermal. The Energy Industry Identification System codes used in the text are identified as [XX]. A. CONDITION PRIOR TO EVENT Units 1/2 Date: May 14, 2018 Power level: 100 percent/100 percent Mode: 1/1 There were no structures, systems, or components (SSCs) out-of-service that contributed to this event. B. DESCRIPTION OF EVENT On May 14, 2018 during evaluation of protection for Technical Specification equipment from the damaging effects of a tornado generated missile, it was determined that a non-conforming condition exists with the Saltwater [BS] System subsystem piping [PSP] with respect to tornado missile protection. Specifically, since a tornado generated missile could strike Saltwater system subsystem piping on either Unit, the design does not meet the licensing basis and a non conforming condition exists. This condition was entered into the corrective action program (separate entries for each Unit) and the NRG was notified via Event Notification 53401 on May 14, 2018. This event is reportable in accordance with 1O CFR 50. 73(a)(2)(i)(B) as a condition prohibited by Technical Specification; 1O CFR 50. 73(a)(2)(ii)(B) as an event or condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety; 1O CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfilment of the safety function of SSCs that are needed to mitigate the consequences of an accident, and 10 CFR 50.73(a)(2)(vii) as an event where a single cause or condition caused two independent trains to become inoperable in a single system. C. CAUSE OF EVENT This condition was part of the original plant design and has existed since the initial construction and licensing of the plant. Calvert Cliffs Unit 1 received its initial operating license on July 31, 1974 and Calvert Cliffs Unit 2 received its initial operating license on August 13, 1976, based in part on the design as described in the Final Safety Analysis Report (FSAR). The cause of the non conforming condition is a legacy design issue that was identified as part of the response to Regulatory Information Summary 2015-06, "Tornado Missile Protection." NRG FORM 366A (04-2018) Page _2_ of ...±.... | ML18164A028
Fermi 2 05000 341 1 OF 5 | Unknown Unit | Loss of Division 1 Offsite Power Causes Partial Loss of Feedwater Leading to ECCS Injection and Reactor Scram | 06-12-2018 | On April 14, 2018 at approximately 1040 EDT, a reactor scram on low reactor water level occurred due to a partial loss of feedwater accompanied by a reactor recirculation system scoop tube lock. The High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems automatically started in order to restore reactor water level as designed. Reactor water level was subsequently maintained using RCIC. No Safety Relief Valves actuated and the Primary Containment Isolation System responded as expected. The partial loss of feedwater and scoop tube lock were caused by a loss of Division 1 electrical power which occurred following a trip of the normal feed to Transformer 64, the 13.8 kV Bus 11 Position D breaker. Division 1 Emergency Diesel Generators (EDGs), EDG-11 and EDG-12, automatically started and energized Division 1 buses. In addition, both Low Pressure Coolant Injection (LPCI) subsystems were declared inoperable while aligned to their alternate power source following loss of their normal power source. The LPCI subsystems were declared operable following realignment to their normal source after EDG-11 and EDG-12 were started. Investigation has determined the direct cause of this event to be moisture intrusion into the A6 cubicle of the Bus 1-2B enclosure, which caused a ground fault that tripped the Bus 11 Position D breaker. Immediate corrective actions were completed to eliminate moisture intrusion into the Bus 1-2B enclosure. The root cause evaluation determined that the organization failed to recognize the degradation of the Bus 1-2B enclosure as a failure mechanism of the A6 switchgear. Corrective actions to prevent recurrence include developing and implementing a Preventive Maintenance strategy for outdoor metal clad switchgear. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10131/2018 (06-2016) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 CONTINUATION SHEET F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to - Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, * ""NEOB-10202, (3150-0104), Office of Managemanedn Btu dget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to Impose an Information collection does not display a currently valid OMB control number, the http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/srl022/r3/) NRC may not conduct or sponsor, and a person is not required to respond to, the Information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000- NUMBER NO. Fermi 2 341 2018 002 - 00 | NARRATIVE INITIAL PLANT CONDITIONS: Mode 1 Reactor Power: 100 percent There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT On April 14, 2018 at approximately 1040 EDT, an automatic reactor scram on low reactor water level (Level 3) occurred due to a partial loss of feedwater [SJ] accompanied by a reactor recirculation system [AD] scoop tube lock. All control rods [AC] fully inserted, and the lowest reactor water level reached was approximately 102 inches above top of active fuel. Division 1 Emergency Diesel Generators (EDGs) [EK], EDG-11 and EDG-12, automatically- started and energized Division 1 buses. The High Pressure Coolant Injection (HPCI) [BJ] and Reactor Core Isolation Cooling (RCIC) [BN] systems automatically started as designed on low-low reactor water level (Level 2) and restored reactor water level. Reactor water level increased until it reached high water level (Level 8), resulting in the HPCI, RCIC, and north reactor feed pump automatically tripping as designed at approximately 1043 EDT on April 14, 2018. Reactor operators subsequently maintained reactor water level in the normal level band by restarting and using RCIC. Reactor pressure was controlled using the main turbine bypass system [JI] to the main condenser [SJ]. The maximum pressure measured was approximately 1030 psig and no Safety Relief Valves [RV] actuated. Primary Containment Isolation System (PCIS) [JM] Groups 2, 4, 10, 11, 12, 13, 14, 15, 16, 17, and 18 associated with reactor water Levels 3 and 2 isolated as expected. Reactor cool down was controlled within Technical Specification and administrative limits. The partial loss of feedwater and scoop tube lock were caused by a loss of Division 1 electrical power which occurred following a trip of the normal feed to Transformer 64, the 13.8 kV Bus 11 Position D breaker [FK]. The result of the bus trip was a loss of power to Transformer 64, which then caused a loss of power to Division 1 emergency safety system Buses 64B and 64C [EB] and balance of plant (BOP) Bus 64A [EA]. The Division 1 Offsite Circuit was declared inoperable, requiring entry into Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1 under Condition D. The loss of BOP Bus 64A led to a trip of the center condenser pump, center heater feed pump, and both north and center heater drains pumps. As a result, the operating south reactor feed pump [SJ] tripped. The north reactor feed pump continued to operate. As designed, Division 1 power loss also caused reactor recirculation scoop tube locks and an automatic start of EDG-11 and EDG-12. The plant is designed with an automatic runback of the recirculation system to allow continued operation following the loss of a single feed pump. However, the loss of Division 1 power also resulted in the locking of the reactor recirculation pump speeds (scoop tube lock), disabling the runback feature. The south reactor feed pump trip and the reactor recirculation scoop tube locks led to a reactor scram on reactor water Level 3 since a single feed pump is not able to maintain reactor water level at 100% power operation. In addition, the loss of Division 1 power caused a trip of the North Reactor Building Closed Cooling Water (RBCCW) pump, resulting in initiation of Divisions 1 and 2 of Emergency Equipment Cooling Water (EECW) and Emergency Equipment Service Water (EESW). During this event, at approximately 1050 EDT on April 14, 2018 it was discovered that the Division 2 EECW Temperature Control Valve (TCV) controller was found in Emergency Bypass instead of staying in Auto mode as expected. In the Emergency Bypass configuration, the TCV operates in the Full Open position, which provides the maximum level of | ML18164A077
River Bend Station | Unit 1 | Potential Loss of Safety Function of Control Building HVAC due to Legacy Design Flaw | 06-07-2018 | On April 10, 2018, at 05:38 p,m. COT, with the plant operating at 100 percent power, a design vulnerability in the Control Building Chill Water (HVK) logic was identified during a review of HVK Chiller and Chill Water Pump control logic. This design vulnerability could prevent the auto start of the HVK Chillers upon restoration of safety related power by emergency diesel generators following a Loss of Offsite Power. This HVK control logic vulnerability was introduced in error by a system modification in 1987. A compensatory measure was put in place to restore operability of the system until a modification can be installed to permanently remove the design vulnerability. Operators are prepared to take action in the event of a loss of Control Building Ventilation to restore the safety function in accordance with existing procedures. Therefore this condition was of minimal significance with respect to the health and safety of the public. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons leamed are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T·2 F43), U. S. Nuclear Regulatory CONTINUATION SHEET Commissioo, Washington, DC 20555~OO1, or by e-mail to Infocolects.Resource@nrc.gov, and to the Desk Officer, Office of Informatiioo and Regulatory Affairs. NEOB·10202, (3150~104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form coIection does not display a currenUy valid OMB control number, the NRC may not conduct or http"l/www,nrc.goy/reading-rm/doc-coliections/Duregs/stafflsr1 022/r3/) sponsor, and a person is not required to respond to. the information collection. 1. FACILITY NAME 2. DOCKET NUMBER o 3. LER NUMBER YEAR SEQUENTIAL REV River Bend Station - Unit 1 05000- 1 458 NUMBER NO. 1-0 ~-I I 001 | BACKGROUND !fwo 1O O-percent capacity Chillers provide cooling to each ventilation system sub-loop, each of which provides cooling, heating, ventilation, pressurization, and smoke removal for several areas within the building. The ventilation system comprises two independent, redundant trains of components and subsystems either of which supports the safety function of providing a controlled environment in the main control room and the environmental requirements of the safety-related electrical equipment in the building. Each control building ventilation subsystem is supported by the respective safety-related emergency diesel generator. !fhe HVK System provides chilled water to the cooling coils in three separate air handlers within each division. The air handling system (HVC) removes the heat generated within the main control room and electrical equipment rooms. Air handlers serve the main control room, standby switchgear rooms, battery / charger rooms, inverter rooms, and chiller rooms. Each air handler serves both trains of their assigned areas (e.g., both the Division 1 and 2 standby switchgear rooms cooling may be fully served by the air handler in either train). REPORTED CONDITION On April 10, 2018 at 05:38 p.m. CDT, with the plant operating at 100 percent power, Engineering determined that time delay relays fURL Y**] in the Division" Control Building Chilled Water System (HVK) (VI) could fail in a manner that challenges he design safety function of the HVK System during a Loss of Offsite Power (LOP) event. Additionally, because there is no ime delay function in the Division I start logic, if a lOP occurs with Division I HVK Chillers [**CHU**] running both the Division I and Division" HVK Chilled Water Pumps [**P**] would start immediately after the lOP with no auto-start of either Division I or Division" Chillers. IThe start logic of the Division" Chillers is configured such that if there is a lOP, when power is restored to the emergency buses by the diesel generators, the Division" Chilled Water Pump will restart immediately, while the Division I Chilled Water Pump is prevented from starting for 30 seconds by Division" time delay relays. This allows the Division" logic to complete, starting the Division" Chiller. Completion of the Division" Chiller start logic requires a low flow signal from the opposite Division, which would be present because the time delay relays are inhibiting start of the Division I Chilled Water Pump. IThe HVK System conforms to the single failure criterion. Failure of either Division" time delay relay to provide the delay !function could allow both the Division I and Division" Chilled Water Pumps to immediately restart after a lOP when power is restored to the emergency buses. With both Chilled Water Pumps running, there would be no low flow signal from either Division, and neither the Division I nor Division II Chiller would receive a start signal. ~dditionally, if a lOP occurs with Division I HVK Chillers running and Division" Chillers in standby, neither Division I nor Division II chiller would auto start when power is restored to the emergency buses because the time delay function does not exist in the Division I control logic. tThis event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), 10 CFR 50.73(a)(2)(ii)(B) and 10 CFR 50.73(a)(2) (v)(D). | ML18164A214
Limerick Generating Station | Unit 1 | High Pressure Coolant Injection (HPCI) lnoperability due to Main Pump Inboard Seal Leak | 06-18-2018 | On April 17, 2018, the Unit 1 High Pressure Coolant Injection (HPCI) system was secured during surveillance testing due to a leak from the main pump inboard seal. Unit 1 HPCI System was isolated and declared inoperable at 1030. A retaining collar setscrew was not properly secured during reassembly of the HPCI inboard pump seal. The retaining collar captures a split ring that secures the mechanical seal sleeve in position. During surveillance testing, the seal sleeve moved out of position resulting in the inboard seal leak. Technicians performed a less than adequate inspection and did not ensure that the split ring was secured by the retaining collar. The individuals were coached and the procedure for a HPCI full pump rebuild was revised to include additional technical detail with technical hold points for pump seal reinstallation. NRG FORM 366 (02-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: ea hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43). U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Aesource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Ottice of Managemenl and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently vahd OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NAG may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collectionslnuregs/staff/srl022/r31) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV VEAR Limerick Generating Station, Unit 1 05000352 NUMBER NO. 2018 - 003 - 00 | I. Unit Conditions Prior to the Event Limerick Generating Station (LGS) Unit 1 was operating in Operational Condition (OPCON) 1 at 12 percent power at the time of the event. There were no other structures, systems, or components inoperable that contributed to the event. 11. Description of the Event On March 26, 2018 Unit 1 was shutdown for the refuel outage. During the refuel outage work was performed to repair a small leak on the HPCI Main Pump Seal. On April 15, 2018 the Unit 1 entered OPCON 2, Startup. At 051 O on April 16, 2018 with reactor pressure at 200 psig, Unit 1 HPCI was declared operable following the HPCI Operability Verification Surveillance Testing when no seal leakage was evident. At 0804 on April 17, 2018, the Unit 1 entered OPCON 1, Run. On April 17, 2018, with reactor pressure at 960 psig, the Unit 1 High Pressure Coolant Injection (HPCI) system was secured during surveillance testing due to a leak from the main pump inboard seal. Unit 1 HPCI System was isolated and declared inoperable at 1030. Troubleshooting identified that a retaining collar was not properly secured with its setscrew during reassembly of Unit 1 High Pressure Coolant Injection (HPCI) Main Pump inboard seal. The retaining collar captures a split ring that secures the mechanical seal sleeve in position. During surveillance testing, the seal sleeve moved out of position resulting in the pump inboard seal leak. This condition is reportable under 1O CFR 50.73(a)(2)(v)(D) as an event that could have prevented fulfillment of a safety function of a system that is needed to mitigate the consequences of an accident. An eight (8) hour Emergency Notification System (ENS) notification (#53341) was completed at 1629 hours on April 17, 2018. Following repair of the pump inboard seal, satisfactory post-maintenance testing, and surveillance testing, the Unit 1 HPCI system was declared operable at 1938 hours on April 17, 2018. Ill. Analysis of the Event Technicians performed a less than adequate inspection and did not ensure that the split ring was secured by the retaining collar. The individuals were coached and the procedure for a HPCI full pump rebuild was revised to include additional technical detail with technical hold points on pump seal reinstallation. NRG FORM 366A (04-2017) Page _2_ of _3_ | ML18169A237
River Bend Station | Unit 1 | Condition Prohibited by Technical Specifications due to Untimely Recognition of Failed Laboratory Analysis of Ventilation Charcoal Sample | 06-19-2018 | On April 30, 2018 with the Reactor operating in Mode 1 at 100% power, the results of a periodic surveillance test on Division II Control Room Fresh Air charcoal filter were received. The sample results indicated that the activated charcoal methyl iodide penetration test was above the allowable level. The test failure was determined to be due to the age of the charcoal. The condition was not immediately recognized because the sample results were received from the vendor thirteen days after the sample was obtained. This condition existed for a time longer than permitted by Technical Specifications. The activated charcoal was replaced and the filter has since been declared Operable. This event was of minimal significance to the health and safety of the public because the redundant Division I filter was Operable and available for use for the duration of the event. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150·0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reponed LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U. S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 2055:HJ001, or by e-mail to Infocolects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-l0202, (315()'()104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022. R,3 for instruction and guidance for completing this form collection does not display a currenHy valid OMB control number, the NRC may not conduct or http'//www, nrc,gov/reading-rm/doc-collections/nu regs/staff/sr10 22/r31l sponsor, and a person is not required to respond to, the informalion collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV River Bend Station - Unit 1 05000- 458 NUMBER 1- 0N O. I 003 | BACKGROUND IThe Control Room Fresh Air system (CRFA) [VI] is designed to filter radioactive nuclides in accordance with General Design Criteria 19 and Regulatory Guide 1.52. The design consists of two 100% independent/redundant carbon filter trains that are division ally separated. Control Room habitability includes maintaining Control Room operator dose within the limits of General Design Criteria 19, assuming an accident with onsite release. The dose calculations for Control Room habitability are based on the specified 1% penetration limit. REPORTED CONDITION On April 17, 2018 with the Reactor operating in Mode 1 at 100% power, a sample of activated charcoal from the Division II CRFA Filter (**FL T**) was obtained to be shipped to an offsite vendor for methyl iodide penetration analysis in accordance with a normally scheduled surveillance. On April 30,2018 the sample results were received. The test result indicated 1.4 7% penetration with an acceptance criterion of 1.0% or less. A confirmatory sample was acquired and tested with a similar result. The charcoal was replaced and the Division II CRFA Filter was declared Operable on May 3,2018. Firm evidence indicates that this condition began on April 17, 2018 when the sample was obtained and was not rectified until May 3, 2018. This condition existed for a time longer than permitted by the Technical Specification (TS) for having one CRFA subsystem inoperable. This condition is being reported in accordance with 10CFR50.73(a)(2)(i)(B), Operation or Condition Prohibited by Technical Specifications. CAUSAL ANALYSIS iThe charcoal failed the methyl iodide penetration analysis due to age related degradation. The untimely identification of the condition was a result of procedural guidance that allowed 31 days from sample time to receive analytical results. jAdditionally, only one charcoal analysis was being tracked and trended. There were other available analysis and parameters that could have been trended to better predict the life expectancy of the charcoal. CORRECTIVE ACTION TO PREVENT RECURRENCE fAn extent of condition found that the Standby Gas [VF] and Fuel Building Ventilation [VG] Charcoal Filter Trains are susceptible to this event. The Division I and Division II Standby Gas trains were sampled on May 9, 2018 and May 8, 2018 respectively. Both trains were found to be well within specification. The Division I and Division II Fuel Building Filters were sampled on July 14.2017 and December 12, 2016 respectively with both trains within specification. The Division I CRFA Filter was sampled on December 7,2016 with satisfactory results. The following actions are planned and documented in the station' s corrective action program. Procedure changes that would require sample time coordination with the lab vendor in order to receive sample results within three days of receipt of the sample for all systems susceptible to this condition. ~dditional charcoal analysis trending will be performed to improve life expectancy predictions. | ML18170A346
Peach Bottom Atomic Power Station | Unit 3 | Reactor Core Isolation Cooling System Pressure Switch Failure Results in Condition Prohibited by TS | 06-21-2018 | On 4/22/18, during a routine surveillance test of the Reactor Core Isolation Cooling (RCIC) system, the RCIC pump turbine tripped shortly after startup. The trip was the result of an indication of high pressure in the RCIC turbine discharge line. Troubleshooting determined that a pressure switch that monitors turbine exhaust pressure had failed. Actual exhaust pressure during the test was at the expected pressure of approximately 12 psig. The pressure switch was replaced and the RCIC system was restored to an operable status on 4/23/18. There were no actual safety consequences as a result of this condition. NRG FORM 366 (04·2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and led back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Comnission, Washington, DC 20555·0001, or by e-mail to lnfocoflects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. II a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. http://www.nrc.gov/reading-rmldoc-collections/nuregs/staff/sr1022/r3/l 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Peach Bottom Atomic Power Station Unit 3 05000278 NUMBER NO. 2018 - 001 0 | Unit Conditions Prior to the Event Unit 3 was operating in Mode 1 at approximately 100% rated thermal power. There were no structures, systems or components out of service that contributed to this event. Description of Event On 4/22/18, during a routine surveillance test of the Reactor Core Isolation Cooling (RCIC) system [EllS:BN], the RCIC pump turbine [EllS:TRB] tripped approximately 28 seconds after startup, prior to the system reaching rated flow and pressure. Concurrent with the RCIC trip, an alarm was received for RCIC turbine high exhaust pressure. Local indication for the exhaust line pressure was at the expected pressure of approximately 12 psig, below the trip setpoint of 50 psig, which is active after a 15-second time delay. Operators verified proper system response following the RCIC turbine trip. The RCIC system was declared inoperable at approximately 9: 12 am on 4/22/18. Technical Specification (TS) 3.5.3 Condition A was entered, which requires the RCIC system to be restored to operable within 14 days. Initial troubleshooting determined a RCIC turbine exhaust pressure switch [EllS:PS] had failed. At approximately 8:55 pm on 4/22/18, the pressure switch was electrically isolated, which made the RCIC system available to perform its function. After the switch was replaced, a surveillance test was successfully completed at 2:53 pm on 4/23/18, allowing the RCIC system to be returned to an operable status. The RCIC system was inoperable for approximately 29 hours and 19 minutes. Analysis of Event The RCIC system provides adequate core cooling and control of the Reactor Pressure Vessel (RPV) water level following an RPV isolation accompanied by a loss of coolant flow from the feedwater system. The High Pressure Coolant Injection (HPCI) system can also perform this function and was available during this event. The trip of the RCIC turbine on 4/22/18 was the result of an indication of high pressure in the RCIC turbine exhaust line. Two pressure switches monitor this pressure and are designed to shut down the turbine if discharge pressure reaches 50 psig. Actual exhaust pressure during the test was at the expected pressure of approximately 12 psig. Troubleshooting determined one of the two pressure switches had failed, which resulted in the trip of the RCIC pump turbine. The previous RCIC surveillance test was successfully completed on 1/16/18 which demonstrated operability. A degradation process, described in the Cause of the Event section of this report, had been occurring for a period of time. At some time between the successful test on 1/ 16/18 and the time at which the trip occurred during the surveillance test on 4/22/18, the degradation advanced to the point where an electrical short existed in the pressure switch. Although it is not known when this occurred, it is possible that NRG FORM 366A (04-2018) Page _2_ of _3_ | ML18172A260
River Bend Station | Unit 1 | Unanalyzed Condition due to Inadequate Protection from Tornado Generated Missiles | 07-03-2018 | On May 4, 2018 with the reactor operating in Mode 1 at 100% power, several licensing basis non-compliances associated with tornado-generated missile protection were identified in the Diesel Generator Building. Structures, Systems, or Components (SSC) affected by the non-compliances were declared inoperable. NRC Enforcement Guidance Memorandum (EGM) 5-002, Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance, was utilized to change the classification of the affected SSCs from Inoperable to Operable but Nonconforming. Several days later, additional non-conformances were identified in the Control Building and Standby Cooling Tower. EGM 15-002 was utilized once again to change the classification of the affected SSCs. The identified non-compliances were introduced during original plant construction. Initial and long-term compensatory actions were put in place to meet the enforcement discretion requirements of EGM 15-002. Plans are underway to resolve the non-compliances. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150·0104 EXPIRES: 03/31/2020 (04·20t8) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons leamed are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Informalion Services Branch (T·2 F43), U. S. Nudear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to Infocolects.Resource@nrc.gov, and 10 the Desk Officer. Office of Information and Regulatory Affairs, NEOB·10202, (3150~104), Office of Management and Budget, Washington. DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form colection does not display a currendy valid OMB control number, the NRC may not conduct or http://www,nrc,gov/reading-rmldoc-collectionslnuregs/staff/sr1 022/r3/) sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER River Bend Station - Unit 1 SEQUENTIAL REV 05000- 1 458 NUMBER 1-0NO. 004 | BACKGROUND Enforcement Guidance Memorandum (EGM) 15-002, Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance, provides guidance for exercising enforcement discretion when an operating power reactor licensee does not comply with a plant's current site-specific licensing basis for tornado-generated missile protection. Specifically, enforcement discretion would apply to the applicable Technical Specification (T8) Limiting Condition for Operation (LCO), which would require a reactor shutdown or mode change, if a licensee could not complete TS LCO Required Action within the stated TS Completion Time. Interim Staff Guidance DS8-18G-2016-01, Clarification of Licensee Actions in Receipt of Enforcement Discretion per Enforcement Guidance Memorandum EGM 15-002, includes additional information intended to facilitate an understanding of the expectations for consistent NRC oversight associated with implementing enforcement discretion for tornado missile protection non-compliance per EGM 15-002. Appendix A to DSS-ISG-2016-0 1 includes guidance for acceptable initial and follow-up comprehensive compensatory measures for licensee use in implementing the enforcement discretion outlined in EGM 15-002. The licensee is expected to document the utilization of EGM 15-002, inform the NRC resident inspector, and enter the issue into the corrective action program. With respect to initial compensatory measures, it is expected that the measures listed in Appendix A are already in place at sites that may be affected by severe weather, such as tornadoes and/or hurricane force winds. The measures provided should be verified as current and readily deployable within a very short timeframe (the shortest timeframe COUld, in some scenariOS, be dictated by a TS LCO 3.0.3 Completion Time of one hour). REPORTED CONDITION On May 4, 2018 with the reactor operating in Mode 1 at 100% power, several licensing basis non-compliances associated with tornado-generated missile protection were identified in the Diesel Generator Building [NB]. The Emergency Diesel Generators [EK] were declared inoperable. NRC Enforcement Guidance Memorandum (EGM) 15-002, Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance, was then utilized to change the classification of the affected System, Structure, or Component (SSC) from Inoperable to Operable but Nonconforming. The utilization of EGM 15-002 was declared in the Main Control Room Log, the resident NRC inspector was notified, and the non-compliances were entered into the corrective action program. On May 9, 2018 non-conformances were identified in the Control Building [NA]and Standby Cooling Tower [MK]. The following SSCs were affected: Division II DC [EJ] electrical power distribution subsystem. Division II and III Residual Heat Removal [BO] pumps. -Division I and II Standby Service Water [BI]. Once again the guidance of EGM 15-002 was followed to change the classification of the affected SSCs from Inoperable to Operable but Non-conforming. CAUSAL ANAL Y81S These vulnerabilities were introduced during the original design of the plant. Engineering judgement was exercised at the time of original construction to only protect certain openings from tornado missile transit with tornado-generated missile resistant barriers. Other small penetrations were deemed to be inconsequential. Typical engineering and licensing documentation practices at the time of construction did not include documenting such engineering judgements. Due to the historical nature of the issue, a specific cause for the non-compliances was not determined. CORRECTIVE ACTION !The initial compensatory actions of DSS-18G-2016-01 Appendix A were verified to be in place and readily deployable. Long | ML18184A439
Nine Mile Point | Unit 2 | Auto Start of Division II Emergency Diesel Generator Due to Loss of Line 6 | 07-09-2018 | At approximately 0248 on May 10, 2018, while at 0% power and in Cold Shutdown (mode 4) in support of the Nine Mile Point Unit 2 (NMP2) refueling outage, NMP2 experienced a partial loss of off-site power (Line 6) during relay testing that resulted in an automatic start of the Division 2 Emergency Diesel Generator (EOG). All systems responded per design during the event. The station responded in accordance with appropriate Special Operating Procedures and restored impacted systems. The condition was reported in Event Notification #53395 as an event or condition that results in a valid actuation of an emergency electrical power system, pursuant to 1O CFR.50.72(b)(3)(iv)(A). This·event is being reported as an event or condition that results in a valid actuation of an emergency electrical power system, pursuant to 50.73(a)(2)(iv)(A). NRG FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the lnlormation Services Branch (T-2 F43), U.S. f:,luclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnlocollects.Resource@nrc.gov, and to the Desk Officer, Office of lnlormation and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid 0MB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r30 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Nine Mile Point Unit 2 05000410 NUMBER NO. 2018 • 001 00 | I. DESCRIPTION OF EVENT A. PRE-EVENT PLANT CONDITIONS: Prior to the event NMP2 was at 0% power in cold shutdown, mode 4, in support of the refueling outage. B. EVENT: At approximately 0248 on May 10, 2018 with the plant in Cold Shutdown, Mode 4, in support of the refueling outage, Nine Mile Point Unit 2 experienced a partial loss of off-site power following the removal of the connection plug of Tripping Relay, 94BG-2/R925, during North American Electric Reliability Corporation (NERC) functional testing. This resulted in the loss of Line 6 and subsequently the automatic start of the Division 2 Emergency Diesel Generator. All systems responded as designed for the event. The station responded in accordance with appropriate Special Operating Procedures and restored impacted systems. C. INOPERABLE STRUCTURES, COMPONENTS, OR SYSTEMS THAT CONTRIBUTED TO THE EVENT: None D. DATES AND APPROXIMATE TIMES OF MAJOR OCCURRENCES AND OPERATOR ACTIONS: All Occurrences and Action took place on May 1O , 2018: 0248: Control Room Alarm for Loss of 115KV from Scriba - Loss of line 6 received 0248: Division II EOG Energized and picked up the Division 2 Bus. 0248: Entered SOPs: N2-SOP-3 Loss of AC. N2-SOP-31 Loss of Shutdown Cooling, 2RHS*P1 B Tripped. N2-SOP-38 Loss of Spent Fuel Pool Cooling, 2SFC*P1 B Tripped. N2-SOP-97 RPS System Failures, Loss of 'B' RPM MG Set 0254: Shutdown Cooling re-established with 2RHS*P1 B 0322: Spent Fuel Pool Cooling re-established with 2SFC*P1 Bin cooling only mode 0326: Exiting N2-SOP-38 Loss of Spent Fuel Pool Cooling 0332: Exiting N2-SOP-31 Loss of Shutdown Cooling 0344: Exited SOP-97 RPS Failures, RPS 'B' Half SCRAM Reset 1123: Line 6 restored per N2-0P-70 1130: Secured Division II EOG NRG FORM 366A (04-2018) Page _2_ of _4_ | ML18192B988
Browns Ferry Nuclear Plant | Unit 3 | Main Steam Relief Valves Lift Settings Outside of Technical Specifications Required Setpoints | 07-16-2018 | On May 17, 2018, the Tennessee Valley Authority was presented with as-found testing results indicating that three of the thirteen Main Steam Relief Valves (MSRVs) from Browns Ferry Nuclear Plant, Unit 3, were outside the +/- 3 percent setpoint band required for their operability. Troubleshooting determined that the three MSRV discs failed by corrosion bonding to their valve seats. The valve discs were previously platinum coated to prevent this, and this was the first Unit 3 MSRV service interval to implement an improved surface treatment to prevent coating delamination. These three MS RVs were found to have been inoperable for an indeterminate period of time between March 26, 2016, and February 17, 2018, which is longer than permitted by Technical Specifications (TS). The affected valves remained capable of maintaining reactor pressure within American Society of Mechanical Engineers code limits. Additionally, the valves' ability to open under remote-manual operation, activation through the Automatic Depressurization System, or MSRV Automatic Actuation Logics were not affected. The valves remained capable of performing their required safety function. The valves failed to open within their TS required limits due to the valve discs corrosion bonding to their seats, as a result of their platinum anti-corrosion coatings flaking off. The immediate corrective action was to replace all thirteen of the Unit 3 MSRV pilot valves with refurbished valves during the Unit 3 Refueling Outage 18. The corrective action was to ensure pilot discs are prepared for platinum coating in accordance with the revised procedure which requires nitrogen pressure testing to verify valve seal functionality prior to coating. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAh _...,ULATORY COMMISSION APP• DT vmc: l'fV• ., IDU-V IU4 Cl\r1rsc;;,: U,)I,) 11.<U.<U (04-2017)) Estimated burden per response to comply with this mandatory collection request 80 hours. Reported lessens lea-ned are iocorporated into the licensing process and fed back to indus1ry. Send comments regarding burden estimate to the Information Seriices Branch (T- 2 F43), U.S. Nuclea-Regulat<>')' Commission, Washington, DC 20555--0001,or by e-mail to LICENSEE EVENT REPORT (LER) lnfocollects. Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (31~104), Office of Management and Budget CONTINUATION SHEET Washington, DC 20503. If a means used to impose an information collection does not display a cunrently valid 0MB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 3 05000296 NUMBER NO. 2018 - 004 00 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Unit 3, was in Mode 1 at approximately 85 percent power. II. Description of Event A. Event Summary On May 17, 2018, NWS Technologies provided the Tennessee Valley Authority (TVA) with the as-found testing results of the thirteen Main Steam Relief Valves (MSRVs) [RV], which were removed during the Spring 2018 Unit 3 Refueling Outage 18 (U3R18). Three of the Main Steam Line A and B Relief Valves (BFN-3-PCV-001-0179, BFN-3-PCV-001-0004, and BFN-3-PCV-001-0023) had as-found lift settings which were outside of the +/- 3 percent band of their setpoints required for their operability. Technical Specification (TS) 3.4.3 requires twelve of the thirteen Safety/Relief Valves (S/RVs) to be operable for S/RV system operability. These three MSRVs were found to have been inoperable for an indeterminate period of time between March 26, 2016, and February 17, 2018, and longer than permitted by TS 3.4.3. MSRV operability was restored on April 10, 2018, upon completion of post-maintenance testing (PMT) following the biennial scheduled replacement of the MSRV pilot valves with refurbished valves which were certified to lift within +/- 1 percent of their setpoints. Throughout this event, the two-stage MSRV pilot valves remained capable of maintaining the reactor pressure below 1375 psig, which is the American Society of Mechanical Engineers (ASME) code limit of 110 percent of the vessel design pressure. The valves remained capable of performing their required safety function. The TVA is submitting this report in accordance with Title 10 of the Code of Federal Regulations 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant's TS. It was determined that the MSRV pilot valve inoperability resulted from their setpoints gradually drifting during the course of their operating cycle, which began when Unit 3 entered Mode 2 on March 26, 2016, and February 17, 2018, when Unit 3 entered Mode 4. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. NRG FORM 366A (04-2018) Page _2_ of _7_ | ML18197A300
Clinton Power Station | Unit 1 | Division 2 Diesel Generator lnoperability Due to Air Receiver Remaining Isolated Following Clearance Removal Resulting in Unplanned Shutdown Risk Change | 07-16-2018 | On May 17, 2018, at 1503 CDT, with the plant in Mode 4 during refueling outage C1R18, a plant equipment operator discovered that the Division (Div) 2 Emergency Diesel Generator (DG) air start receiver isolation valves 1DG160 and 1DG161 were shut. At the time of discovery, the Div. 1 DG was inoperable for a 4160V 1A 1 partial bus outage. With the Div. 2 air start receiver valves shut, the Div. 2 DG was declared inoperable. Operations entered Technical Specification (TS) Limiting Condition for Operation (LCO) Required Actions for TS 3.8.2, "AC Sources-Shutdown," and TS 3.5.2, "Reactor Pressure Vessel (RPV) Water Inventory Control" as a result of the inoperability of the onsite AC power sources to isolation valves being credited to limit RPV drain time. The Div. 2 DG air receivers were realigned at 1545 CDT and the auto start function was restored. At 2104 CDT, the Div. 2 DG was declared operable following completion of the return to service checklist procedure. The cause of the event is that Operations relied solely on log entries to track component configuration, contrary to Exelon governance. Corrective measures include eliminating procedures that allowed tracking equipment configuration with log entries and reinforcing approved tracking methods with Operators. This event is reportable under the provisions of 10 CFR 50.73(a)(2)(v)(D), as "any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident" and 10 CFR 50.73(a)(2)(i)(B) as "any operation or condition prohibited by Technical Specifications." NRC FORM 366 (04-2018) NRC FORM 366A, U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the lnfonnation Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid 0MB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the infonnation collection. http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Clinton Power Station, Unit 1 05000461 NUMBER NO. 2018 - 002 - 00 | PLANT AND SYSTEM IDENTIFICATION General Electric -- Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in text as [XX]. EVENT IDENTIFICATION Division 2 Diesel Generator lnoperability Due to Air Receiver Remaining Isolated Following Clearance Removal Resulting in Unplanned Shutdown Risk Change A. Plant Operating Conditions Before the Event Unit: 1 Event Date: May 17, 2018 Event Time: 1503 Mode: 4 Mode Name: Power Operation Reactor Power: 000 percent B. Description of Event On May 17, 2018 at 1503 CDT with the plant in Mode 4 in refueling outage C1R18, an Equipment Operator (EO) identified that both the Division 2 Emergency Diesel Generator (EOG) [DG] air receiver outlet valves were closed while pertorming rounds in the Division 2 EOG room. With the valves shut, the Division 2 EOG could not have automatically started if required and, therefore, was inoperable. At the time of the discovery, Division 1 EOG was inoperable as a result of a Division 1 4160V 1A 1 partial bus outage. Following notification by the EO, Operations entered Technical Specification (TS) Limiting Condition for Operations (LCO) 3.8.2, "AC Sources-Shutdown," Actions B.1, B.2, and 8.3 due to the inoperability of both Division 1 and Division 2 EDGs. In addition, LCO 3.5.2, "Reactor Pressure Vessel (RPV) Water Inventory Control," Required Actions A.1, C.1 and C.2 were entered as a result of the inoperability of onsite AC power sources to isolation valves being credited to limit RPV drain down time. At 1545 CDT, Operations completed placing the Division 2 EOG air start system in standby and restored the EDG's auto start function. At 2104 CDT, following the completion of a return to service checklist procedure and field and panel walkdowns, the Division 2 EOG was declared operable and associated LCO Actions were exited. A non-emergency eight-hour notification was submitted in accordance with 1O CFR 50.72(b){3)(v), as a condition that alone could have prevent fulfilment of the onsite AC power function. NRG FORM 366A (04-2018) Page _2_ of _4_ | ML18199A106
Clinton Power Station 05000461 1 OF 4 | Unknown Unit | Failure of the Division 1 Diesel Generator Ventilation Fan Load Sequence Relay Circuit During Concurrent Maintenance of RHR Division 2 Results in an Unanalyzed Condition | 07-16-2018 | On Tuesday, March 7, 2017 at 2258 CDT, an Equipment Operator detected a relay cycling every 1O seconds from the Division (Div.) 1 480V Unit Substation (Sub) 1A . Agastat Time Delay Relay (TOR) 427X2-41 A (X2 relay) was determined to be the source of the clicking sound. The X2 relay supports the undervoltage load shed and restoration of the Div. 1 Emergency Diesel Generator (EOG) ventilation room fan 1V D01 CA. The logic is designed to shed 1V D01 CA on undervoltage, prevent it from restarting, then allow it to be restored 1O seconds after voltage is restored either by the EOG or return of the safety bus. An investigation of the relay cycling condition determined that 1V D01 CA was unable to respond to a demand signal and the cycling was the effect of interaction between the X2 and 427X3-41 A (X3) relays. As a result, Div. 1 EOG was declared inoperable on March 9. With the Div. 2 Residual Heat Removal (RHR) System already inoperable due to scheduled maintenance, the plant was determined to be in an unanalyzed condition. A causal analysis determined that the original design of the EOG ventilation fan relay logic relied on executing parallel sequencing logic to perform the control function, which was vulnerable to differences in relay model drop out voltages. Corrective actions included the replacement of the X3 relay with the original design relay and subsequent circuit modifications to eliminate the vulnerability to lower drop out voltage settings. Div. 2 RHR was returned to service on March 8. Subsequently, Div. 1 EOG was restored to OPERABLE on March 11. This is reportable as an unanalyzed condition, operation prohibited by the Technical Specifications and a loss of safety function. NRG FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150·0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LEA) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to ..... CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, ./' NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid 0MB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR Clinton Power Station 05000461 NUMBER NO. 2017 • 002 • 02 | PLANT AND SYSTEM IDENTIFICATION General Electric-Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in the text as [XX] EVENT IDENTIFICATION Failure of the Division 1 Diesel Generator Ventilation Fan Load Sequence Relay Circuit During Concurrent Maintenance of RHR Division 2 Results in an Unanalyzed Condition A. Plant Operating Conditions before the Event Unit: 1 Event Date: March 9, 2017 Event Time: 0319 Mode: 1 Mode Name: Power Operation Reactor Power: 99 percent 8. DESCRIPTION OF EVENT On March 7 at 2258, an area operator detected a "clicking sound" coming from safety related Unit Substation 1A (1AP11 E). The sound was determined to be emanating from relay 427X2-41A (X2 relay) which was cycling every ten (1 O) seconds. The model of this component is an Agastat Time Delay Relay (TOR) that provides the signal to reset the Load Shed and Resequencing circuit for Div. 1 Emergency Diesel Generator (EOG) Room Vent fan 1V D01 CA. Div. 1 EOG was declared inoperable on March 9 when it was determined that 1V D01 CA was unable to respond to a demand signal. An event investigation determined that relay 427X3-41 A (X3 relay) in the undervoltage circuitry for 1AP11 E was not operating as expected, causing the cycling of the X2 relay. The effect of this condition was that (1) the associated Fan 1VD01CA would be unable to start automatically or manually when required, and (2) the ability of the Div. 1 fan to properly sequence following restoration from a bus undervoltage condition was impacted. During an assessment of relay replacement history, it was established that the X3 relay which was originally an ITE Gould J13 relay had been replaced with a General Electric CR120B relay in 2008. The replacement X3 relay combined with the installed X2 relay satisfactorily passed post maintenance testing in 2008 (including undervoltage functional testing) and also passed integrated surveillance testing in 2009. A "like-for-like" replacement of the X2 relay was performed in 2011 and passed integrated surveillance testing in 2011 and 2013. The investigation determined, however, that the combined operating characteristics of the X3 and X2 relays was adversely impacted by a second "like-for-like" replacement of the X2 relay in May 2016. Through an error in work order planning, no testing was specified for this "like-for-like" replacement. However, the impact on the operating characteristics of the electrical circuit for this X2 replacement would not have been detected by the procedurally required post maintenance testing. Due to the successful integrated testing since 2008, variations in the dropout voltage and associated impacts of the relays used in this circuit had not been previously recognized. | ML18199A107
Salem Generating Station | Unit 1 | Inadequate Protection from Tornado Missiles Due to Nonconforming Design Conditions | 03-31-2020 | On June 1, 2018, Unit 2 identified a nonconformance associated with tornado missile protection during during development of a design change to minimize rainwater entry. Equipment required to be operable by Unit 2 technical specifications (TS) was affected and declared inoperable. Enforcement Guidance Memorandum (EGM) 15-002, "Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance" was used to reclassify the affected equipment as operable but nonconforming. On June 18, 2018, Unit 1 identified a nonconformance associated with tornado missile protection during response to NRC Regulatory Issue Summary (RIS) 2015-06, "Tornado Missile Protection". Equipment required to be operable by Unit 1 TS was affected and declared inoperable. EGM 15-002 was again used to reclassify the affected equipment as operable but nonconforming. These were reported to the NRC wihin 8 hours. Additional nonconformances on both units have been identified and entered into the station corrective action process (CAP). The nonconformances will be resolved by license amendment or plant modification per EGM 15-002. !.>~_...,.,114l•~~~~~.~rHl...,~~~~......,.1':~..,_.....,...,~u- *llliiWII<8,...,...~P.P~~....,.~-~·•~·~~·•••''Q•M••:-~VOIIMfi~;J;I!Y~J~N""~~~~'~.,._~r.....,""""•l-'l~';~. . _.....• NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to ~l .... industry. Send comments regarding burden estimate to the FOIA, Privacy and Information :~ ,. Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555- .. LICENSEE EVENT REPORT (LER) 0001, or by internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-1 0202, (3150-01 04), Office of Management and CONTINUATION SHEET Budget, Washington, DC 20503. If a means used to impose an information collection does not (See NUREG-1 022, R.3 for instruction and guidance for completing this form display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person http://www. nrc.gov/readinq-rm/doc-collections/nu regs/staff/sr1 022/r3{) is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 3. LERNUMBER I I YEAR SEQUENTIAL REVISION NUMBER NUMBER Salem Generating Station - Unit 1 05000272 2018-001-00 | PLANT AND SYSTEM IDENTIFICATION Westinghouse-Pressurized Water Reactor {PWR/4} IDENTIFICATION OF OCCURRENCE Event Date: 06/01/2018 Discovery Date: 06/01/2018 CONDITIONS PRIOR TO OCCURRENCE Unit 1 and Unit 2 were both operating in Mode 1 at approximately 10 0°/o rated thermal power. There were no structures, systems or components out of service that contributed to this event. DESCRIPTION OF OCCURRRENCE On June 1, 2018, station personnel determined that a steel cover plate was missing from an opening into the underground service water (SW) pipe tunnel. Consequently, Unit 2 equipment required to be operable by technical specifications (TS) was vulnerable to tornado missile impact. The affected equipment was declared inoperable. INITIAL compensatory measures following the guidance of DSS-ISG-2016-01, "Clarification of Licensee Actions in Receipt of Enforcement Discretion per Enforcement Guidance Memorandum EGM 15-002, 'Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance', Revision 1" were verified. Event number (EN) 53438 was reported to the NRC within 8 hours. Enforcement discretion per EGM 15-002 was then invoked, the affected equipment was declared operable but nonconforming and the associated technical specification action statements (TSAS) were exited. On June 18, 2018, station personnel identified that Unit 1 equipment required to be operable by TS was vulnerable to tornado missile impact. Enforcement discretion per EGM 15-002 was invoked after verification of INITIAL compensatory measures. EN 53438 was updated to include Unit 1. Additional nonconforming or potentially nonconforming conditions on both units have been entered into the corrective action program since initial identification. CAUSE OF EVENT The cause of the missing SW pipe tunnel cover plate is failure to recognize the cover plate as a tornado missile hazard barrier. Why the cover plate was removed is not known. The plate has been removed for many years and was not recognized as nonconforming until close review coincident with developing a design change to minimize rainwater entry. Implementation of hurricane season preparations per OP-AA-1 08-111-1001, "Severe Weather and Natural Disaster Guidelines" also prompted closer scrutiny of the configuration. | ML18207A191
i | Unknown Unit | EMRV Pressure Sensor As-Found Setting Exc::eeded Limiting Safety System Settings . ' _5._Elient Date 6. LER Number 7. Report Date , 8. Olher FaclUties Involved . I Month Day ·. . Year · . Year I Se N q .i u lm en b t e i r ll l .. R N e o v . Mon111 Dlly Year F N a I c A lr lty · Name .. , ' , · ,·' 05 D 0 o 0 c 0 kG INwnbor 06 05 2018 .2018 - 001 ·, - 00 07 31 2018 N Fa IA cl f~Name · -05 D 0 o 0 o 0 ko l Num ·, bor 9. Operating Mode 11. This Report is Submitted Pursuantto the Requirements of 10 CFR §: (Checkall thst apply} D D · 0 D 20.2201<b> 20.220aca1<a>ci> 50.73(a)(2)(ii)(A) 5().73(a><2>C~iiil(Al D D D · D 20,2201<d) 20:2203(a)<3>(ii} . · 5!).73(a)(2)(ii1(B) , so.1acai<21(vru}(B> N D D 0 0 20.22oa<aic1i - 20.2203(a)<4> 50;73(a)(2)(iii) 50.73(a)(2)(ix)(A) 0 0 ,0 D 20.2203(a)(2)(i) 50.36(c)(1}(i)(A) 50.73(a)(2)(iv)(A) 50.73(a)(2)(x) r 10. Power.Level D 20.22oa<a112>(ii> 18J. 50.36(c)(1)(ii)(A). 0 50.73(a)(2)(v)(A) D 1a.11ca><4> 0 D O· 0 20.2203(a)(2)(iii) so.as<c1c21 50.73(a)(2)(v)(B) 73.71(a)(5) . 0 D · 0 0 .· 20.22Q3(a)(2)(iv) so_4sca><a1<ii) . 50.7a(a)(2)(v)(C) 7a,i7(a)(1) --- 100 0 20.ffll3(a)(2iM . 0 50,7'J(s)(2}(i)<A) .. D S0.73(n)(2)(v){D) D n.n,a)la)ti} - D D . 20.22oa(a1c2><vi> ~ 50.73(a)(2)(i)(B) . . ·[ ] 50.73(a)~)(vii) ia'.n(a)(2)(iil D 0 50.73(a)(2)(i)(C) Other (Specify in Abstract below or in NRC Form 366A) 12. Licensee Contact forthis·LER Licen_see Contact . . ITelephone _Number (Include Area Code) Gary Flesher, Regulatory Assurance Manager (609) 971-4232 -. · in 13. Complete One Une for each Component Failure Descrlbei:1 this Report -· · ir Caw,e System ._ Componont · Manufacturer Reportl!lble to ICES Ciluse Syatam Co,mponent · -Mllitulacturer Reportabla lo ICES . ·- X SB PS · 8070 ..· N [t'.i • C .14, SUpplemental Report Expected Month". Day '. Year · 15. Expected Submission Date D Ves.(lfyes, complete 15. Expected Submission Date) ~ No .. . Abstract (Umit to 1400 spaces, i.e., approximately 14 single-spaced typewritten lines) ; '' While at full power steady state conditions, during calibration surveillance testing on 06/05/18; the 'A' Electromatlc Relief Valve . (EMAV) Pressure Switch (PS-IAOOBSA) as-found setpoint was _at 1095 pounds per square inch, gauge (pslg), which Is above the Technical Specification (TS).Limiting.SafetySystem Settings (LSSS} requirementof 1085 psig.The setpointwas immediately adjusted within an acceptable as~Jeft band (within 38 minutes} using guidance in the suJVeillance test procedure. The cause of the .. condition was setpoint drift. . . · . · . · _· . . . . . _ -. · ._ . _· · · .. -_ ·. . · · The TS Section 2.3.0 LSSS values for Relief Valve Initiation are set to stagger relief valve ()penlng for protection of the primary · containment. The 'A' and 'C' EMRVLSSS are set at <I= 1085 psig and 'B', 'D' and 'E' EMRV LSSS are set at <I= 1105 psig. · sat This occurrence is considered to have minimal ety significance as the primary containment structural integrity is bounded by Mark 1 Containment Long Term f>rogram analyses a.nd modifications which assume that all relief valves actuate simultaneously at 1105 · psig. The Automatic Depressurization System (ADS) function of the EMRV Is not affected by this pressure switch. Nona.of the pressure switches for the remaining 4 EMRVs were affected, and manual operation. of the EMRV was· not affected, This issue is reportable under 10 CFR so;aa(c)(1l(ii)(A) for' Limiting Safety System Se~ngs where anautomatic,safety~tem does not function as required (setting out ofrange) and .10 CFR 50. 73(a}(2)(i)(B) as an operation or condition which was prohibited by the plant's TS. · · · · · ·. · · · · · · ·. · · . . . . NAC FOAM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150.0104 · . EXPIRES: 03/31i2020 (04'2018) Estimated bunlan per respoilse 10 comply with Oils marulalory collection request 80 hows. Repmll!d lessons learned m incoiporated inlo the ricensing process and le_d back lo indmlly. Send commanls LICENSEE EVENT REPORT (LER) reganlin!i bunlen esfmale lo Iha lnfomtaliuil Ser.rices Branch (T·2 F43), U.S. Nuclear 'Regulalory CONTINUATION SHEET · Commlssicn, Washinglon, DC 20555-0001, or by e-mail 10 lnfocollects.Resourca@nrc.gov, mm 10 the Desk Olficer, Ollite ol lnlonnation and Regulatory Affairs, NEOB-10202, (3150-0104), Office ol Management and Budget, Washington. oC 20503. II a means used lo impose ari inlonnafion (See NUREG-1022, R.3 for Instruction and guidance for completing this form colleelion_does 11111 display a~enlly valid OMB.con!rol number, the NRC may.not conduct or pttp:/lwww.nrc,oov/raadiitg-rm/doc,.colfeclionwnuregs/staff/srt022/r3/) gponsor, and a, parson Is not required lo ,espond to, lha_inlormation collootion, 1. FACILITY NAME. 2. DOCKET NUMBER 3. LER NUMBER Oyster. CreekNuclear Generating 05000,;,219 YEAR SE N Q U U M E B N E T R IA L R N E O V . Station · · · · · 2018 ,001 ·-· 00 NARRATIVE . Plant Conditions PriorTo Event ·· | 07-31-2018 | ; '' While at full power steady state conditions, during calibration surveillance testing on 06/05/18; the 'A' Electromatlc Relief Valve . (EMAV) Pressure Switch (PS-IAOOBSA) as-found setpoint was _at 1095 pounds per square inch, gauge (pslg), which Is above the Technical Specification (TS).Limiting.SafetySystem Settings (LSSS} requirementof 1085 psig.The setpointwas immediately adjusted within an acceptable as~Jeft band (within 38 minutes} using guidance in the suJVeillance test procedure. The cause of the .. condition was setpoint drift. . . · . · . · _· . . . . . _ -. · ._ . _· · · .. -_ ·. . · · The TS Section 2.3.0 LSSS values for Relief Valve Initiation are set to stagger relief valve ()penlng for protection of the primary · containment. The 'A' and 'C' EMRVLSSS are set at <I= 1085 psig and 'B', 'D' and 'E' EMRV LSSS are set at <I= 1105 psig. · sat This occurrence is considered to have minimal ety significance as the primary containment structural integrity is bounded by Mark 1 Containment Long Term f>rogram analyses a.nd modifications which assume that all relief valves actuate simultaneously at 1105 · psig. The Automatic Depressurization System (ADS) function of the EMRV Is not affected by this pressure switch. Nona.of the pressure switches for the remaining 4 EMRVs were affected, and manual operation. of the EMRV was· not affected, This issue is reportable under 10 CFR so;aa(c)(1l(ii)(A) for' Limiting Safety System Se~ngs where anautomatic,safety~tem does not function as required (setting out ofrange) and .10 CFR 50. 73(a}(2)(i)(B) as an operation or condition which was prohibited by the plant's TS. · · · · · ·. · · · · · · ·. · · . . . . NAC FOAM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150.0104 · . EXPIRES: 03/31i2020 (04'2018) Estimated bunlan per respoilse 10 comply with Oils marulalory collection request 80 hows. Repmll!d lessons learned m incoiporated inlo the ricensing process and le_d back lo indmlly. Send commanls LICENSEE EVENT REPORT (LER) reganlin!i bunlen esfmale lo Iha lnfomtaliuil Ser.rices Branch (T·2 F43), U.S. Nuclear 'Regulalory CONTINUATION SHEET · Commlssicn, Washinglon, DC 20555-0001, or by e-mail 10 lnfocollects.Resourca@nrc.gov, mm 10 the Desk Olficer, Ollite ol lnlonnation and Regulatory Affairs, NEOB-10202, (3150-0104), Office ol Management and Budget, Washington. oC 20503. II a means used lo impose ari inlonnafion (See NUREG-1022, R.3 for Instruction and guidance for completing this form colleelion_does 11111 display a~enlly valid OMB.con!rol number, the NRC may.not conduct or pttp:/lwww.nrc,oov/raadiitg-rm/doc,.colfeclionwnuregs/staff/srt022/r3/) gponsor, and a, parson Is not required lo ,espond to, lha_inlormation collootion, 1. FACILITY NAME. 2. DOCKET NUMBER 3. LER NUMBER Oyster. CreekNuclear Generating 05000,;,219 YEAR SE N Q U U M E B N E T R IA L R N E O V . Station · · · · · 2018 ,001 ·-· 00 | . Plant Conditions PriorTo Event ·· Event Date: · June OS, 2018 Event.Time: 0900 .EDT Unit 1 Mode: Run . . . Power Level: 100% There were no SSCs that were inoperable at .the start of the event atjd contributed to the event.· of . . . . . Description Event . · . ·. . ·. .. . . . . . . ·· · · • . .· . . .. . . · . · . •-·. ·· . .. ·. . . . .· During the quarterly performance ofthe EMRVPressure SensorTestand Calibration SuiveUiance Test(ST) the 'A'. EMRVas-found setpoint value exceeded the TS LSSSHmit of 1085 psig •. . . . ' . . . During. performance of the SJ for the EMR\/s, each pressure switch is isolated by turning off the ADS/EM RV control . switch and isolating the loop by closing an isolation valve,· A test pump is then connected to a test port to pressurize the switch ·until the high switch trips. The test pressure is then decreased until the low switch resets. Switches are. · adjusted if found out of range and re-pressurized to validate setpoints. The process is repeated as needed untn all .. setpoints .are within as~left tolerances. The switch is then· unisolated and returned to· service prior to isolating and testing the next switch. The total out of service time is recorded by technicians for each switch tested. . · 'N ·D uring the.performance of the ST on 06/05118, the EMRV ~igh Pressur~ Switch (PS·lA~Oa63A), did not m~et As·.··. u fotmd Unadjusted Setpoint"requirements of 1064 psig to 1084psig. The actual reading was 1095 psig.Technicians ·. . adjusted the setpointwithin Te(::llnlcal Specification tolerances per the instructions in the surveillance procedure. The . EMRVout of service tim~ recorde~ during the ST for. the calibration check and adjustment was 38 minutes. · All of the remaining EMRV Pressure switches were tested with no out of tolerance conditions detected. An issue report was•.· . submitted to document the as-found out of tolerance·condition of the EMRV pres$Ure switch_ .•. Equipment Description · Bourdon Tube type pressure switch manufactured by Barksdale, Model numbtlr B2S-M12SS-TC: Analysis of ·Event One of the functions of theEMRVs. is to provide pressure control for the re~ctor pressure vessel. Together with the . high pressure scram function and the· isolation Condenser System (IEEE BL), the EMRVs limit pressure in the · Reactor Coolant System during. high pressure transients.·· · , ' . . . : . . The TS Section 2.3.D LSSS values for EMRV initiaiion are set to stagger relief valv~ (EMRV) opening for protection of the primary containment.. The 'A' and 'C' EMRV LSSS are set at <I= 1085 psig and 'B', 'D' and 'E' EMRV LSS are set at <I= 1105 psig. The as found high pressure trip value was) 095 .psig which exceeds the TS. LSSS Limits. This .•. occurrence is considered to have minimal safety significance as the primary containment structural integrity is . bounded by Mark 1_ C ontainment long Term Program analyses and modifications which· assume thatall. relief Vtilves . actuate simultaneously at 1105 psig. Hence, the LSSS of 1Q 85 psig is conservative; actuation of the 'A' EMRV at . 1095 psig.would not result in a challenge to containmen_t design limits. · . . . . ·. . . . . . ·. . . . . . . . . - The EMRVs are part of the Automatic Depressurization System (ADS) {IEEE BM). This system is designed tri depressurize the Reactor C:oolant System (IEEE AB) during small break. Loss-of~oolant Accident conditions so that· the.low pressure Core $pray System {IEEE EM) can lnjectwater into the reactor:. The ADS function oUhe EMRVs is not affected by th~se pressure switches. The ADS signal is initiated by the simultaneous occurrence of RPV triple low . water level, high drywell pressure arid core spray booster pump, differential pressure. ·A ll EMRVs would actuate at the same time upon receipt of an ADS signal. AOS,initiation logic is independent of the EMRV Pressure switch logi9/ . . . . . .. NRC FORM 386A (04-2018) Page _2_ of _i_ | ML18220A877
Limerick Generating Station | Unit 2 | Degraded Condition due to RPV Instrument Nozzle Leakage | 08-09-2018 | On May 8, 2017, while Unit 2 was shut down for refueling outage 2R14, leakage was identified from a 2-inch Reactor Pressure Vessel (RPV) instrumentation nozzle (N-160) during a RPV pressure test. The leakage amount was approximately one pint per minute. The leakage originated from the area where the nozzle penetrates the vessel wall. Prior to de-pressurizing, an extent of condition bare metal examination was conducted. No leakage was identified from any other instrument nozzles. A half nozzle repair was completed, consisting of replacing the outer portion of the existing nozzle with a new nozzle that was welded to the outside of the RPV. The safety significance of this event was minimal given the leakage was small, was found while the reactor was shut down, and would not have exceeded Technical Specification (TS) leakage limits for unidentified drywell leakage if it occurred during plant operation. Given the impact on the RPV boundary, this report is submitted in accordance with the requirements of 1O CFR 50.73 (a)(2)(ii)(A), which requires the reporting of any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded. NRG FORM 366 (02-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04·2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send t.'-'"~• N:ov,,.> comments regarding burden estimate to the Information Services Branch (T·2 F43). U.S. Nuclear {~'.~{) LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555·0001, or by e-mail to ~:;: . .~ .. ~ . v . / CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/read1ng-rmldoc-collectionslnuregslslaff/sr1022/r30 collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR Limerick Generating Station, Unit 2 05000353 NUMBER NO. 2017 - 004 - 01 | I. Unit Conditions Prior to the Event Limerick Generating Station (LGS) Unit 2 was shut down for refueling outage 2R14 and in Operational Condition (OPCON) 4 at the time of the event. The condition was identified during the Reactor Pressure Vessel [RPV] pressure test. 11. Description of the Event On May 8, 2017 at 0925, while LGS, Unit 2 was in cold shutdown for refueling, during the performance of the American Society of Mechanical Engineers (ASME) Leakage Testing of the RPV and associate piping, a through-wall leak was identified on an instrument nozzle [NZL], N-16D. The N-16D RPV penetration is an instrument nozzle located just below the Top-of-Active Fuel (TAF) at 280 degree azimuth on the vessel. The leak was approximately one pint per minute. A visual examination detected active leakage at the nozzle interface (annular gap) with the RPV Outer Diameter (OD). The leak was discovered during the RPV Class 1 pressure boundary system leakage test that is performed each refueling outage in accordance with ASME Section XI, IWB- 2500, and station procedures. Based on the design, any leakage into the annulus region between the nozzle body and the RPV wall would likely be associated with a through-wall failure of the nozzle assembly, either at the nozzle body or at the RPV attachment weld. Prior to de-pressurizing, an extent of condition bare metal, VT-2, examination of the N-11, N-12, and N-16 nozzles (9 total, not including the N-16D) was conducted on 5/8/17 to determine if any similarly constructed RPV nozzles exhibited leakage. No leakage was identified from any other instrument nozzles. With the leakage confirmed to be originating from the N-16D nozzle assembly, a repair team was mobilized, consisting of station, corporate, and industry experts. The repair method was a half nozzle repair which consisted of replacing the outer portion of the existing nozzle with a new lnconel alloy 690 nozzle that was welded to the outside of the RPV versus the inside. The original RPV attachment weld and a remnant section of the original nozzle in which the through-wall failure occurred were effectively abandoned in place. The repair was completed on May 23, 2017 and the post-repair leakage test immediately followed, which validated the integrity of the repair and the RPV Class 1 pressure boundary. On May 8, 2017, Emergency Notification System (ENS)# 52738 was made in accordance with 10 CFR 50.72 (b)(3)(ii)(A), for a degraded condition. Given the impact on the RPV boundary, this report is submitted in accordance with the requirements of 1O CFR 50.73 (a)(2)(ii)(A), which requires the reporting of any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded. Ill. Analysis of the Event There was no actual safety consequence associated with this event. The potential safety consequence of this event was minimal, given the leakage was small and was found while the reactor | ML18221A256
Brunswick Steam Electric Plant (BSEP) | Unit 1 | Setpoint Drift in Main Steam Line Safety/Relief Valves Results in Two Valves Inoperable | 08-09-2018 | On June 11, 2018, BSEP received the results of testing of eleven main steam line safety relief valves (SRVs) removed from Unit 1 during the spring 2018 refueling outage. Two of the eleven valves were found to have as-found lift setpoints of their pilot valves outside the +/-3 percent tolerance required by Technical Specification (TS) 3.4.3. TS 3.4.3 requires ten of the eleven installed SRVs to be operable. Since less than ten SRVs were operable, this event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operation prohibited by the plant’s TS. All 11 of the SRV pilot valves were replaced with certified spares before the startup of Unit 1. The direct cause of the out of tolerance as-found lift setpoints was corrosion bonding of the SRV pilot discs-to-the pilot seats. The root cause of the corrosion bonding was an inadequate procedure and work order instructions. Corrective actions include revising associated procedures to include sufficient detail to ensure consistent surface preparation and proper quality checks of surface condition are performed prior to platinum coating. NRC FORM 366 (02-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant YEAR 05000325 NUMBER NO. (BSEP), Unit 1 2018 - 003 - 00 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. Background Initial Conditions At the time of the event, Unit 1 was in Mode 1 (i.e., Power Operation), at approximately 100 percent of rated thermal power (RTP). Reportability Criteria Unit 1 Technical Specification (TS) 3.4.3 requires at least 10 of 11 main steam [SB] line safety/relief valves (SRVs) to be operable. Per Surveillance Requirement (SR) 3.4.3.1, each valve is required to open within +/- 3 percent of its opening setpoint. As-found testing of the valves indicated that two of the valves had lift setpoints outside this tolerance. Consequently, the plant operated in a condition which is prohibited by the TS, that is, with fewer than the required number of SRVs having lift setpoints within the +/-3 percent tolerance. Therefore, the condition is being reported per 10 CFR 50.73(a)(2)(i)(B) as operation in a condition prohibited by the plant TSs. Event Description During the spring 2018 Unit 1 refueling outage, all 11 Model 7567F Target Rock Two-Stage pilot valve assemblies in the SRVs were replaced with certified spares. The removed SRV pilot valves were sent to National Technical Systems (NTS) to determine the as-found set pressure. On June 11, 2018, test results were reported to BSEP. The test results showed that two of the 11 valves actuated at pressures outside of the +/-3 percent tolerance allowed by TS 3.4.3. The test data for the valves found out of tolerance are shown below. As-Found Lift TS Setpoint Percent Valve ID Pressure (psig) Difference (psig) 1-B21-F013B 1,150 1,218 5.91 S/N 1082 1-B21-F013G 1,130 1,225 8.41 S/N 1081 Event Cause The change in SRV lift setpoints resulted from corrosion bonding of the SRV pilot discs-to-the pilot seats. Corrosion bonding between the pilot disc and seat is an inherent problem with the two-stage SRV design used at BSEP. BSEP mitigates corrosion bonding of SRVs by coating each pilot disc surface with platinum. The integrity of the platinum coating is critical to mitigating corrosion bonding. The platinum coating of these SRVs was found to be degraded in large areas of the pilot disc, including the seating surface; which was | ML18221A552
Edwin I. Hatch | Unit 1 | Safety Relief Valves' As Found Settings Resulted in Not Meeting Tech Spec Surveillance Criteria 5. Evant Date 6. LER Number 7. Report Date 1. Other Facilities Involved I lllontll Dal( Year v- I le N qu _ en . l _ la l R N e o v . IIDnlh Day v- aclllllfName Do 0 c 5 ll 0 el 0 N 0 la nbar - 06 20 2018 2018 - 003 00 08 15 2018 F~Name Docbl Nuadlar 05000 9. Operating Mode 11. This Report Is Submitted Pursuant to the Requirements of 10 CFR §: (Check til that •ply) D D D D 2o.2201(b) 20.2203(a)(3)(i) 50.73(a)(2)(ii)(A) 50 73(a)(2)(viii)(A) D D D D 202201(11) 20.2203(a)(3)(ii) 50.73(a)(2)(ill(B) 50 73(a)(2)(vUi)(B) 1 D D 0 0 202203(a)(1) 20.2203(a)(4) 50 73(a)(2)(ii) 50 73(a)(2)(ix){A) D D D D 202203(a)(2){1) 50.36(c)(1)(i)(A) 50 73(a)(2)frv)(A) 50.73(a)(2)(x) 1 o. Power Level D 20.2203(a)(2)(ii) D 50.36(c)(1)(ii)(A) 0 50 73(a)(2)(v)(A) D 73 71<•><4> 0 D D 0 20 2203(a)(2)(i6) 50.38(c)(2) 50 73(a)(2)(v)(B) 7371(a)(5) 0 D 0 D 20 2203(a)(2)(1v) 50.46(a)(3)(11) 50.73(a)(2)(v)(C) 7377(a)(1) 100 D 20 2203(a)(2)(v) D 5D.73(a)(2)(1)(A) D 50 73(a)(2)(v)(0) 0 73 77(a)(2)(i) 0 0 D D 20 2203(a)(2)(11i) 50.73(11)(2)(1)(8) 50 73(a)(2)(11ii) 73 77(a)(2)(D) 0 D 50.73(a)(2)(l)(C) Other (Specify in Abstrad below or In NRC Fonn 366A) 12. Licensee Contact for this LER Licensee Contact Telephone Number (Include Area Code) Edwin I. Hatch I Jimmy Collins-Licensing Manager 912-537-2342 13. Complete One Line for each Component Failure Described In thisI R eport I I· I B Cau .. SB Slfllem RV Co mponent T0 M 2 a 0 n ufacturar y R eportable to ICES Jl Cause I System Component Manufacturer Reportable to ICES 14. Supplemental Report Expected Monltt Day Yur 0 0 15. Expected Submission Data v .. (If yes, complete 15 Expected Submluion Dale) No Abstract (Limit to 1400 spaces. i.e. • approximately 14 single-spaced typeWJltten lines) On June 20, 2018, Unit 1 was at 100 percent rated thermal power (RTP) when "as-found" testing results of the 3-stage main steam safety relief valves (SRVs) indicated two of the eleven Unit 1 SRVs had experienced a setpoint drift during the previous operating cycle which resulted in their failure to meet the Technical Specification (TS) opening setpoint pressure of 1150 +/- 34.5 psig as required by TS Surveillance Requirement (SR) 3.4.3.1. The test results showed that the two SRVs were slightly out of spec tow due to setpoint drift. The SRV pilots were disassembled and inspected to investigate the reason for the setpoint drift. Based on inspection results, the drift in setpoint was due to low abutment gap and low abutment pressure. Due to their location, drywall ventilation blowing on these two safety relief valves caused them to undergo a cyclic heating and cooling every 12 hours during the Unit's 2-year operating cycle. These temperature gradients across the valve internals caused a relaxation of the setpoint spring and bellows assembly. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U. S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc gov, and to the Desk Officer, OffiCe of Information and Regulatory Affairs, NEOB-10202, (3150-0104). OffiCe of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currenUy valid OMB control number, the NRC may not conduct or http //www. n_rc_,_go.Ylre.<~.ding:rf!llil~!)Qnslnuregststaffls.r1 022tr3J) sponsor. and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER I 3. LER NUMBER SEQUENT~L REV Y~R IEdwin I. Hatch Unit 1 I 05000-1 321 NUMBER 1- NO 0 . 120181-1 003 NARRATIVE Event Description On June 20, 2018 at 0852 EST with Unit 1 at approximately 100 percent rated thermal power, "as-found" testing of the 3- stage main steam safety relief valves (SRVs) (EllS Code RV) showed that two of the eleven main steam SRVs that were tested had experienced a drift in pressure lift setpoint during the previous operating cycle such that the allowable technical specification (TS) surveillance requirement (SR) 3.4.3.11imit of 1150 +/-34.5 (+/- 3%) psig had been exceeded. Below is a table illustrating the Unit 1 SRVs that failed as found testing results after being removed from service during the Spring 2018 refueling outage. MPL Lift Pressure Percent Drift 1B21-F013D 1095 psig -4.78% 1B21-F013E 1107 psig -3.74% Event Cause Analysis The cause of this event is due to low abutment gap and low abutment pressure. Due to their location, drywell ventilation blowing on these two safety relief valves caused them to undergo a cyclic heating and cooling of approximately 3 degrees every 12 hours during the Unit's 2-year operating cycle. These temperature gradients across the valve internals caused a relaxation of the setpoint spring and bellows assembly. This relaxation then caused the pilot disc to seat with less pressure, allowing the valve to open prematurely during as-found testing. Safety Assessment This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) because a condition occurred that is prohibited by TS 3.4.3. Specifically, an example of multiple test failures is given in NUREG-1 022, Revision 3, "Event Reporting Guidelines 10 CFR 50.72 and 50.7 3" which describes the sequential testing of safety valves. This example notes that "Sometimes multiple valves are found to lift with set points outside of technical specification limits." NUREG-1 022 further states in the example that "discrepancies found in TS surveillance tests should be assumed to occur at the time of the test unless there is firm evidence, based on a review of relevant information (e.g., the equipment history and the cause of failure), to indicate that the discrepancy occurred earlier. However, the existence of similar discrepancies in multiple valves is an indication that the discrepancies may well have arisen over a period of time and the failure mode should be evaluated to make this determination." Based on this guidance, the determination was made that this "as found" condition is reportable under the reporting requirements of 10 CFR 50.73(a)(2)(i)(B). There are eleven SRVs located on the four main steam lines within the drywell in between the reactor pressure vessel (RPV) (EllS Code RPV) and the inboard main steam isolation valves (MSIVs) (EllS Code ISV). These SRVs are required to be operable during Modes 1, 2, and 3 to limit the peak pressure in the nuclear system such that it will not exceed the applicable ASME Boiler and Pressure Vessel Code Limits for the reactor coolant pressure boundary. The SRVs are tested in accordance with TS Surveillance Requirement 3.4.3.1 as directed by the In-Service Testing Program to verify lift set points are within their specified limits to confirm they would perform their required safety function of overpressure protection. The SRVs must accommodate the most severe pressurization transient which, for the purposes of demonstrating compliance with the ASME Code Limit of 1375 psig peak vessel pressure, has been defined by an event involving the closure of all MSIVs with a failure of the direct reactor protection system trip from the MSIV position switches with the reactor ultimately shutting down as the result of a high neutron flux trip (a scenario designated as MSIVF). NRC FORM 366A (04-2018) Page 2 of 3 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U. S Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Offtcer, Off1ce of Information and Regulatory Mairs, NEOB-10202, (315().0104), Offtce of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currenUy valid OMB control number, the NRC may not conduct or bttp:f/W'If!!'l.,fJJJ;.govlre.adjog:(fllldoc-cQIJect!Qo.wvL~g§i§!i!fflsr1 0221r31) sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER I DYEA R SEQUENTIAL REV Un~ NUMBER NO. !Edwin I. Hatch 1 05000-1 321 L:J -I 1- 0 I 003 NARRATIVE The two SRVs which failed to meet their Tech Spec required actuation pressure setpoint lifted early (4.78% low and 3.74% low). None of the eleven SRVs tested this cycle had as-found test results out of range high. Therefore, since the two identified SRVs lifted earlier than expected, the ASME Code Limit of 1375 psig peak vessel pressure would be maintained under normal and accident conditions. The opening of one or more SRVs at lower pressures would result in a less severe transient with reduced peak vessel pressure. Also, the slightly lower actuating pressure does not pose a significant LOCA initiator threat due to as-found lift pressures being higher than normal operating pressures. Based on the observed setpoint drift slightly low, the overpressure protection system would have continued to perform its required safety function if called upon in its "as found" condition. Therefore, this event had no adverse impact on nuclear safety and was of very low safety significance. Corrective Actions The identified SRV pilots have been replaced with pilots who as-left testing is within valve specifications. Drywell ventilation ductwork will also be rerouted to move the flow path away from the "D" and "E" SRVs at the next available opportunity. Previous Similar Events LER 2-2017-004 identified SRV low setpoint drift for 2 of the 11 three-stage SRVs. Corrective actions included revising vendor specification to tighten as-left tolerances of abutment and pre-load gap, increase the minimum set for abutment pressure at the high end of specification, and tighten diametrical and face run-out tolerances for bellows assembly on the pre-load spacer mounting end. LER 1-2016-004 identified SRV low setpoint drift for 2 of the 11 three-stage SRVs. Corrective actions included revising vendor specifications to tighten as-left tolerances of abutment and pre-load gap, increase the minimum set for abutment pressure at the high end of specification, and tighten diametrical and face run-out tolerances for bellows assembly on the pre-load spacer mounting end. NRC FORM 366A (04-2018) Page 3 of 3 | 08-15-2018 | On June 20, 2018, Unit 1 was at 100 percent rated thermal power (RTP) when "as-found" testing results of the 3-stage main steam safety relief valves (SRVs) indicated two of the eleven Unit 1 SRVs had experienced a setpoint drift during the previous operating cycle which resulted in their failure to meet the Technical Specification (TS) opening setpoint pressure of 1150 +/- 34.5 psig as required by TS Surveillance Requirement (SR) 3.4.3.1. The test results showed that the two SRVs were slightly out of spec tow due to setpoint drift. The SRV pilots were disassembled and inspected to investigate the reason for the setpoint drift. Based on inspection results, the drift in setpoint was due to low abutment gap and low abutment pressure. Due to their location, drywall ventilation blowing on these two safety relief valves caused them to undergo a cyclic heating and cooling every 12 hours during the Unit's 2-year operating cycle. These temperature gradients across the valve internals caused a relaxation of the setpoint spring and bellows assembly. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U. S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc gov, and to the Desk Officer, OffiCe of Information and Regulatory Affairs, NEOB-10202, (3150-0104). OffiCe of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currenUy valid OMB control number, the NRC may not conduct or http //www. n_rc_,_go.Ylre.<~.ding:rf!llil~!)Qnslnuregststaffls.r1 022tr3J) sponsor. and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER I 3. LER NUMBER SEQUENT~L REV Y~R IEdwin I. Hatch Unit 1 I 05000-1 321 NUMBER 1- NO 0 . 120181-1 003 | Event Description On June 20, 2018 at 0852 EST with Unit 1 at approximately 100 percent rated thermal power, "as-found" testing of the 3- stage main steam safety relief valves (SRVs) (EllS Code RV) showed that two of the eleven main steam SRVs that were tested had experienced a drift in pressure lift setpoint during the previous operating cycle such that the allowable technical specification (TS) surveillance requirement (SR) 3.4.3.11imit of 1150 +/-34.5 (+/- 3%) psig had been exceeded. Below is a table illustrating the Unit 1 SRVs that failed as found testing results after being removed from service during the Spring 2018 refueling outage. MPL Lift Pressure Percent Drift 1B21-F013D 1095 psig -4.78% 1B21-F013E 1107 psig -3.74% Event Cause Analysis The cause of this event is due to low abutment gap and low abutment pressure. Due to their location, drywell ventilation blowing on these two safety relief valves caused them to undergo a cyclic heating and cooling of approximately 3 degrees every 12 hours during the Unit's 2-year operating cycle. These temperature gradients across the valve internals caused a relaxation of the setpoint spring and bellows assembly. This relaxation then caused the pilot disc to seat with less pressure, allowing the valve to open prematurely during as-found testing. Safety Assessment This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) because a condition occurred that is prohibited by TS 3.4.3. Specifically, an example of multiple test failures is given in NUREG-1 022, Revision 3, "Event Reporting Guidelines 10 CFR 50.72 and 50.7 3" which describes the sequential testing of safety valves. This example notes that "Sometimes multiple valves are found to lift with set points outside of technical specification limits." NUREG-1 022 further states in the example that "discrepancies found in TS surveillance tests should be assumed to occur at the time of the test unless there is firm evidence, based on a review of relevant information (e.g., the equipment history and the cause of failure), to indicate that the discrepancy occurred earlier. However, the existence of similar discrepancies in multiple valves is an indication that the discrepancies may well have arisen over a period of time and the failure mode should be evaluated to make this determination." Based on this guidance, the determination was made that this "as found" condition is reportable under the reporting requirements of 10 CFR 50.73(a)(2)(i)(B). There are eleven SRVs located on the four main steam lines within the drywell in between the reactor pressure vessel (RPV) (EllS Code RPV) and the inboard main steam isolation valves (MSIVs) (EllS Code ISV). These SRVs are required to be operable during Modes 1, 2, and 3 to limit the peak pressure in the nuclear system such that it will not exceed the applicable ASME Boiler and Pressure Vessel Code Limits for the reactor coolant pressure boundary. The SRVs are tested in accordance with TS Surveillance Requirement 3.4.3.1 as directed by the In-Service Testing Program to verify lift set points are within their specified limits to confirm they would perform their required safety function of overpressure protection. The SRVs must accommodate the most severe pressurization transient which, for the purposes of demonstrating compliance with the ASME Code Limit of 1375 psig peak vessel pressure, has been defined by an event involving the closure of all MSIVs with a failure of the direct reactor protection system trip from the MSIV position switches with the reactor ultimately shutting down as the result of a high neutron flux trip (a scenario designated as MSIVF). | ML18227A880
Duane Arnold Energy Center 05000-331 1 OF 4 | Unknown Unit | Both Doors in Secondary Containment Airlock Opened Concurrently | 08-16-2018 | On July 9, 2018, at 1334, while operating at 100% power, workers opened doors concurrently when entering a secondary containment access airlock. The individuals involved each closed their respective doors upon encountering this unexpected condition; however, the result was a brief inoperability of secondary containment integrity. This resulted in an 8 hour reportable event. The Resident Inspector was notified, and an Event Notification was made pursuant to 10 CFR 50. 72(b )(3)(v)(C) due to a condition at the time of discovery that prevented the fulfillment of the Secondary Containment safety function (Reference EN#53496). Following the event, the doors were verified to be functioning properly via Surveillance Test Procedure. A Root Cause Evaluation was previously conducted and determined the root cause of this event is that the airlock door interlock is not designed to prevent more than one airlock door from opening under all possible conditions. This event did not result in a safety system functional failure. There were no radiological releases associated with this event. NRG FORM 366 (06-2016) NRG FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016) #AAtout., Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. (..rJ Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by LICENSEE EVENT REPORT (LER) internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, CONTINUATION SHEET Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 6. LER NUMBER 3. PAGE I YEAR I SE N Q U U M E B N E T R IA L R N E O V . Duane Arnold Energy Center 05000-331 2 OF 4 2018 002 00 | I. Description of Event: On July 9, 2018, at 1334, while operating at 100% power, workers opened doors concurrently when entering a secondary containment access airlock. The doors being open at the same time caused a failure to meet Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.2 to verify that either the outer door(s) or the inner door(s) in each Secondary Containment access opening are closed. The identified condition caused Secondary Containment to be considered inoperable per TS LCO 3.6.4.1. The individuals involved immediately closed their respective doors upon encountering this unexpected condition. This action allowed SR 3.6.4.1.2 to be met, and restored Secondary Containment to an operable status. The failure to meet SR 3.6.4.1.2 resulted in an 8 hour reportable event. The Resident Inspector was notified, and an Event Notification was made pursuant to 10 CFR 50.72(b)(3)(v)(C) due to a condition at the time of discovery that prevented the fulfillment of the Secondary Containment safety function (Reference EN#53496). Secondary containment leak tightness is required to ensure that the release of radioactive materials from the primary containment is restricted to those leakage paths and associated leakage rates assumed in the accident analysis and that fission products entrapped within the secondary containment structure will be treated by the Standby Gas Treatment System prior to discharge to the environment. The Secondary Containment airlock utilizes an interlock device with an adjustable permanent magnet (mounted on the door), and an electromagnet (on the door frame) arranged in an electrical circuit so that door(s) are held closed and/or are allowed to open. Immediately following the event, on July 9, 2018 at 1342 hours, surveillance testing was performed satisfactorily per Surveillance Test Procedure (STP) 3.6.4.1- 02, Secondary Containment Airlock Verification. There were no radiological releases associated with this event. There were no other structures, systems or components inoperable at the start of this event that contributed to the event. II. Assessment of Safety Consequences: There were no actual safety consequences associated with this event; the potential safety consequences were minimal. Both doors on the airlock were open simultaneously for less than 10 seconds, and were able to close immediately upon discovery of the condition. NRG FORM 366 (06-2016) | ML18228A752
Perry Nuclear Power Plant 05000-440 1 OF 4 | Unknown Unit | : | 08-23-2018 | On July 1, 2018, at 0100 hours, while the plant was at 100 percent rated thermal power, a portion of the Division 1 Emergency Core Cooling System (ECCS) Loss Of Coolant Accident (LOCA) initiation logic was declared inoperable due to the discovery of a failed fuse. The fuse was replaced and the Division 1 ECCS LOCA initiation logic was declared operable at 0230 hours on July 1, 2018. The failed fuse caused the loss of a portion of the Division 1 ECCS LOCA initiation logic, which would have prevented the initiation of the Emergency Closed Cooling (ECG) A system. This resulted in ECG A and its supported systems to be declared inoperable. Low Pressure Core Spray (LPCS) is one of those supported systems and is considered a single train safety system. lnoperability of LPCS is considered an event or condition that could have prevented the fulfillment of a safety function. The failed fuse also caused the loss of a portion of the initiation logic, which would have prevented the automatic isolation of the Nuclear Closed Cooling system and Instrument Air to containment. The loss of containment isolation capability is also considered an event or condition that could have prevented the fulfillment of a safety function. The cause of the Gould Shawmut TR30R fuse failure is due to a manufacturing defect. Immediate corrective actions replaced the failed fuse. The spare fuse inventory was inspected, and suspect fuses were removed. Inspections are planned for circuits that were identified that could have the suspect fuses. If a suspect fuse is found, it will be replaced. The safety significance is very small. This issue is being reported in accordance with 10 CFR 50. 73(a)(2)(v)(D) as a condition that could have prevented the fulfillment of a safety function. This LER satisfies the evaluation, notification, and reporting obligation to report defects under 10 CFR 21.2(c). NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid 0MB control number, the NRC may not conduct or http://www. n re.gov/reading-rm/doc-collections/nu regs/staff/ sr1 022/r3/ sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Perry Nuclear Power Plant 05000-440 NUMBER NO. 2018 002 00 | Energy Industry Identification System (El IS) codes are identified in the text as [XX]. INTRODUCTION On July 1, 2018, at 0100 hours, while the plant was at 100 percent rated thermal power, a portion of the Division 1 Emergency Core Cooling System (ECCS) Loss Of Coolant Accident (LOCA) initiation logic was declared inoperable due to the discovery of a failed fuse [FU]. The fuse was replaced and the Division 1 ECCS LOCA initiation logic was declared operable at 0230 on July 1, 2018. The failed fuse caused the loss of a portion of the Division 1 ECCS LOCA initiation logic, which would have prevented the initiation of the Emergency Closed Cooling (ECC) A [CC] system. This resulted in ECC A and its supported systems to be declared inoperable. Low Pressure Core Spray (LPCS) [BM] is one of those supported systems and is considered a single train safety system. lnoperability of LPCS is considered an event or condition that could have prevented the fulfillment of a safety function. The failed fuse also caused the loss of a portion of the initiation logic which would have prevented the automatic isolation of Nuclear Closed Cooling [CC] and Instrument Air [LO] to containment. The loss of containment isolation capability is considered an event or condition that could have prevented the fulfillment of a safety function. EVENT DESCRIPTION On June 30, 2018, at 1613 hours the control room received an unexpected out of service alarm for the Residual Heat Removal (RHR) "A" system [BO] and the LPCS system. Initial walkdowns of the control room panels did not indicate any abnormalities associated with these systems. A troubleshooting plan was developed to further identify the cause of the concurrent alarms received in the control room. On July 1, 2018, at 0100 hours, while implementing the troubleshooting plan, the positive main line fuse was found to be failed in disconnect ED1A06-08. This disconnect serves multiple components associated with the ECCS LOCA initiation logic. The unit supervisor declared the affected portion of the ECCS LOCA logic inoperable and entered the following Technical Specification (TS) action statements: • TS 3.3.5.1 "ECCS Instrumentation", conditions A and B for the inability to automatically initiate the Division 1 Diesel Generator and Annulus Exhaust Gas Treatment train A • TS 3.7.1 "Emergency Service Water (ESW) System-Divisions 1 and 2", condition A for ESW A inoperability. • TS 3.8.1 "AC Sources-Operating", condition B for Division 1 Diesel Generator inoperability. • TS 3.3.6.3 "Suppression Pool Makeup (SPMU) System Instrumentation", conditions A and B for the inability to automatically initiate the SPMU A train. • TS 3.3.6.1 "Primary Containment and Drywell Isolation Instrumentation" conditions A and 8 for preventing the automatic isolation of Nuclear Closed Cooling system and Instrument Air to containment. | ML18236A294
River Bend Station | Unit 1 | Loss of Reactor Protection System Scram Function During Main Steam Isolation Valve Channel Functional Tests due to Use of a Test Fixture | 08-27-2018 | On June 26, 2018 during a review of industry operating experience, it was determined that use of the Reactor Protection System (RPS) test fixture described in station procedures would potentially result in the loss of one RPS reactor scram safety function. Technical Specification (TS) 3.3.1.1 requires that RPS instrumentation for Table 3.3.1.1-1 Function 6 for Main Steam Isolation Valve-Closure (MSIV) remain OPERABLE. It was concluded that the required number of Main Steam Line inputs for each RPS trip system was not maintained during the use of the RPS test fixture. Surveillance procedures were revised to incorporate the use of the test box in November 2014. Between November 2014 and May 2018, the MSIV Closure procedure was performed 15 times using the test fixture. While it did not meet the TS bases, RPS remained functional at all times. The failure to recognize the impact of the modification and procedure revisions is considered a human performance error by engineering personnel. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons leamed are incorporated into the licensing process and fed back 10 induslry. Send comments regarding burden estimate to the Information SelVices Branch (T·2 F43), U. S. Nuclear Regulatory CONTINUATION SHEET Commission, Washinglon, DC 2055~001, or by e-mail to InfocoUects.ReSOlJrce@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs. NEOB·l0202, (3150-<1104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form colection does nol display a currendy valid OMB controt number, the NRC may not conduct or http ·llwww.nrc.goY/reading-rm/doc-coliections/nu regs/staff/sr1 022/r31l sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER River Bend Station - Unit 1 SEQUENTIAL REV 05000-1 458 NUMBER 1-0N O. 1 " .. 2018 1 1_ 1 005 | ~. PLANT CONDITIONS PRIOR TO THE EVENT On June 26, 2018, River Bend Station (RBS) was operating in Mode 1 at 100% Power. There were no structures, systems, or components that were inoperable at the start of this event that contributed to this event. B. DESCRIPTION On June 26, 2018, engineering personnel identified that the use of the Reactor Protection System (RPS) [JC) test fixture, as implemented in a surveillance test procedure, unintentionally resulted in the loss of Technical Specification (TS) Table 3.3.1.1 Function 6, Main Steam Isolation Valve-Closure, as defined in the TS bases at the time of the event. TS bases required signals from 3 of 4 Main Steam Line (MSL) inputs for each RPS trip system for the Main Steam Isolation Valve (MSIV) [SB][(**ISV**) closure function. A review determined that use of the test fixture did not maintain the required number of MSL inputs for each RPS trip system. IThe test fixture was designed to reduce unnecessary RPS actuations. Before the use of the test fixture was incorporated into procedure, half scrams would occur during the performance of the RPS Main Steam Isolation Valve Closure surveillance test. The test fixture consists of a 5-ohm resistor in parallel with a 5 VAC lamp terminated with banana jacks. The RPS test fixture establishes a low resistance path in parallel with the trip logic relay contacts. RPS has two independent trip systems (A and B) with two logic divisions in each trip system: A and C divisions for Trip System A, and Band D divisions for Trip System B. For Function 6 (MSIV Closure) there are sixteen total instrument channels (two per MSIV) with each logic division having four instrument channels and each trip system having eight. This logic ensures a full reactor scram when at least one MSIV in three or more MSLs are less than full open. The use of the RPS test fixture, as implemented by procedure, would bypass MSIV position signal inputs for two MSLs (i.e., bypass four instrument channels) and prevent the associated trip logic division from being in a tripped condition (i.e., half-scram). If two isolated MSLs are in a bypassed division, a scram would not occur if only three MSLs are isolated. The first use of the test fixture was performed on November 11, 2014. To date, the surveillance test procedure has been performed fifteen times using the test fixture. The longest time the test fixture was installed during the fifteen surveillances was 5 hours and 15 minutes with three exceptions. On two separate occasions issues were encountered during performance of the procedure and it was not clear if the RPS test fixture was installed during the full occurrence. On one occasion the test procedure was performed when the plant was in a mode where the TS was not applicable. With one trip division bypassed and Function 6 inoperable, Technical Specification 3.3.1.1 Required Action G requires restoring RPS trip capability or being in Mode 2 within 6 hours. TS 3.3.1.1 Condition G was not intentionally entered during he performance of the surveillance but was either met each time or no firm evidence could be found to show that Condition G Completion Time was not met. C. REPORTABILITY IThis event is being reported under 10CFR50.73(a)(2)(v)(A) and 50.73(a)(2)(v)(D) as an event that that could have prevented the fulfillment of the safety function of structures or systems that are needed to (A) shut down the reactor and maintain it in a safe shutdown condition and (D) mitigate the consequences of an accident. D.CAUSE The cause of this event was an incorrect procedure revision due to an inadequate 50.59 evaluation of the associated design change. While the requirement of having 3 valve position signals per trip system to maintain the RPS trip capability was recognized during preparation of the procedure change and the associated 10 CFR 50.59 evaluation, the understanding of | ML18239A382
Nine Mile Point | Unit 1 | Manual Reactor Scram Due to Pressure Oscillations | 08-18-2018 | On March 20, 2017 at 02:27, Nine Mile Point Unit 1 performed a manual scram of the reactor due to pressure oscillations. This event is reportable under 10 CFR 50.72 (b)(2)(iv)(B) and 10 CFR 50.73(a)(2)(iv)(A) as any event or condition that resulted in a manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B). The Unit was offline and reactor shutdown was in-progress at the time of the scram. The cause of the scram was manual scram. The scram was required at approximately 4% reactor power when pressure oscillations occurred exceeding the procedurally required limit. The apparent cause of this event was Mechanical Pressure Regulator (MPR) oscillations caused by a combination of the fouling of the MPR' s pressure sensing bellows line and a bypass relay linkage passing through a worn bushing which created a friction induced sticktion of the linkage. The event described in this LER is documented in the plant's corrective action program. NRG FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: BO ·hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid 0MB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a p_erson is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3l) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Nine Mile Point Unit 1 05000220 NUMBER NO. 2017 - 002 01 | I. DESCRIPTION OF EVENT A. PRE-EVENT PLANT CONDITIONS: Prior to the event, Nine Mile Point Unit 1 (NMPl) was offline and reactor shutdown was in-progress. Reactor power was approximately 4%. B. EVENT: On March 20, 2017 at 0227, during a scheduled reactor shutdown in support of the 2017 refueling outage, Operators at Nine Mile Point Unit 1 inserted a manual scram due to pressure oscillations exceeding procedural limits. NMPl was offline with the scheduled reactor shutdown in-progress at the time of the scram. At approximately 4% reactor power, Control Room Operators recognized mechanical pressure regulator (MPR) oscillations causing pressure changes and turbine bypass valve movement. When pressure oscillations exceeded the procedurally required limit the Reactor Operator at The Controls manually inserted the reactor scram. Nine Mile Point Unit 2 (NMP2) was and remained at 100% throughout the event. Operations performed the ENS notification (#52624) required by 10 CFR 50.72(b)(2)(iv)(B) for the manual reactor scram due to pressure oscillations. Tpis notification met the 4 hour reporting requirements. This LER is being submitted pursuant to the requirements of 10 CFR 50.73(a)(2)(iv)(A). C. INOPERABLE STRUCTURES, COMPONENTS, OR SYSTEMS THAT CONTRIBUTED TO THE EVENT: None NRG FORM 366A (04-2017) Page _2_ of _6_ | ML18242A071
Browns Ferry Nuclear Plant (BFN) | Unit 1 | Inoperability of Unit 1 and 2 Emergency Diesel Generators Results in Condition Prohibited by Technical Specifications | 08-31-2018 | On July 2, 2018, at 1122 Central Daylight Time, it was discovered that the last performed surveillance on the C Emergency Diesel Generator (DG) Battery had recorded the specific gravity of Battery Cell 20 at 1.204. This was 0.025 less than the average battery cell specific gravity of 1.229. The difference in specific gravity between the individual cell and the average cell was more than the BFN Unit 1 and Unit 2 Technical Specifications (TS) Limiting Conditions for Operation (LCO) 3.8.6, Table 3.8.6-1, Category C, limit of 0.020. On August 3, 2018, a past operability evaluation determined that, because of this condition, the C DG had been inoperable for longer than the LCO 3.8.1 Condition B, 14 day allowed outage time. Also, during this time, there were two periods where a second Unit 1 and 2 DG was inoperable for longer than the two hours allowed by TS LCO 3.8.1 Condition H for two or more concurrently inoperable Unit 1 and 2 DGs. This condition resulted in a violation of both Unit 1 and 2 TS. The cause of this event is that the TS 3.8.6 Surveillance Requirement (SR) is non-conservative in regard to checking Category C limits. No SR is specified in TS 3.8.6 to check Category C limits. Corrective actions are to replace the battery cell, to issue an Operations Standing Order ensuring TS 3.8.6 Category C limits are met when quarterly SRs are performed on DG batteries, to revise battery SR procedures, and to revise Unit 1, 2, and 3 TS 3.8 to address the discrepancy between the SR and the TS 3.8.6 LCO Condition B required action. N RC FORM 366 (04-2018) -1 I NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION I APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T- •. ::.<,,J>" Mo"t..i"'to 2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001,or by e-mail to - $ .. . . ~ . : LICENSEE EVENT REPORT (LER) I R n e fo g c u o la ll t e o c r t y s . A R ff e a s ir o s u , rc N e E @ O n B rc -1 .g 0 o 2 v 0 , 2, a n ( d 3 1 t 5 o 0 -0 th 1 e 0 4) D , es O k f fic O e f fic o e f r , M O a f n fic a e g em of e n I t n fo a r n m d a tio B n u dg an e d t, 'l.,.. .... ... n i'' CONTINUATION SHEET Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a ... t! """,,. person is not required to respond to, the information collection. - 1. FACILITY NAME I 2. DOCKET NUMBER I 3. LER NUMBER - I I SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 1 05000259 NUMBER NO. I I 2018 I - 005 I - 00 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Units 1 and 2, were in Mode 1 at approximately 100 percent rated thermal power. II. Description of Event A. Event Summary On July 2, 2018, at 1122 Central Daylight Time (CDT), it was discovered that the last performed surveillance on the C Emergency Diesel Generator (DG)[EK][DG] Battery[BTRY] had recorded the specific gravity of Battery Cell 20 at 1.204. This was 0.025 less than the average battery cell specific gravity of 1.229. The difference in specific gravity between the individual cell and the average cell was more than the BFN Unit 1 and Unit 2 Technical Specifications (TS) Limiting Conditions for Operation (LCO) 3.8.6, Table 3.8.6-1, Category C, limit of 0.020. On August 3, 2018, a Past Operability Evaluation (POE) determined that, because of this condition, the C DG had been inoperable for longer than the LCO 3.8.1 Condition B, 14 day allowed outage time. Also, during this time, there were two periods where a second Unit 1 and 2 DG was inoperable for longer than the two hours allowed by TS LCO 3.8.1 Condition H for two or more concurrently inoperable Unit 1/2 DGs. This condition resulted in a violation of both Unit 1 and 2 TS. The Tennessee Valley Authority (TVA) is submitting this report in accordance with 10 CFR 50.73(a)(2)(i)(B), as any event or condition which was prohibited by the plant TS. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, components, or systems (SSCs) that were inoperable at the time of discovery, which contributed to this condition. I , - I | ML18243A112
i | Unknown Unit | Potential Loss of Safety Function and Condition Prohibited by Technical Specifications due to Emergency Diesel Generator Lube Oil Chiller Leak Caused by Design Deficiency. | 09-04-2018 | On 7/4/18 River Bend Station declared the Division II Emergency Diesel Generator (EDG) operable after completing a planned maintenance outage. On 7/4/18 immediately following the outage, the Division I EDG was declared inoperable for planned testing for approximately 4 hours. On 7/5/18 operators noted a rise in the Division II EDG lube oil filter differential pressure. A grab sample was obtained that indicated the presence of water in the lube system which led operators to declare the Division II EDG inoperable. An engineering evaluation later determined that this condition started when the Division II EDG was restored to normal operating temperature following the maintenance outage. It was then recognized that the Division I and the Division II EDG were declared inoperable simultaneously and the Technical Specification required action completion times for one inoperable EDG were not met prior to discovery of the water intrusion. The cause of the water intrusion was determined to be a design deficiency in the EDG lube oil cooler which led to a leak in the floating tubesheet seals. The leak was repaired and the Division II EDG was returned to an operable status. Design changes have been developed to correct the design deficiency and are scheduled to be in place by the end of 2019. This event had minimal significance to the health and safety of the public. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/3112020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reponed LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U. S. Nuclear Regulatory CONTINUATION SHEET Commission, Washinglon, DC 2055!Hl001, or by e-mail 10 Infocollecls.Resource@nrc.gov, and 10 Ihe Desk Officer, Office of Informalion and Regulalory Affairs, NEOB-l02D2. (31SQ.Ol04), Office of Managemenl and Budget, Washinglon, DC 20503. If a means used 10 impose an information (See NUREG-l022, R.3 for instruction and guidance for completing this form coIection does not display a currentty valid OMB conlrol number, the NRC may not conduct or http://www.nrc.gov/reading-rmldoc-collections/nuregs/staff/sr1 022/r3D sponsor, and a person is not required to respond to, the informalion collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER River Bend Station - Unit 1 SEQUENTIAL REV 05000-1 458 NUMBER NO. I-~ 006 | A. PLANT CONDITIONS PRIOR TO THE EVENT On 7/6/18, River Bend Station (RBS) was operating in Mode 1 at 100% Power. Prior to the event there were no inoperable structures, systems, or components that contributed to the event. B. DESCRIPTION On 6/24/1814:15 the Division II Emergency Diesel Generator (EDG) (**DG**) [EK] was declared inoperable for a planned maintenance outage. The outage was completed and the Division II EDG was declared operable on 7/4/18 03:27. RBS then began a surveillance test of the Division I EDG. The Division I EDG was placed in maintenance mode as part of the surveillance test, rendering it inoperable on 7/4/18 04:27. The Division I EDG was later declared operable after the surveillance test on 7/4/18 07:53. On 7/5/18, Operators recognized that Division II Emergency Diesel Generator lube oil filter differential pressure increased rom 0.5 Pounds per Square Inch Differential (PSI D) to 13 PSID in less than one day. A lube oil sample was obtained and he cause was determined to be water intrusion. The Division II EDG was declared inoperable on 7/6/18 01 :43. The condition was verified not to exist on the Division I EDG. All Technical Specification (TS) required actions for one inoperable EDG were completed within the allowed completion times. n-he exact amount of water in the oil system could not be determined, but the fact that the lube oil filter was severely restricted indicates there was a significant amount of water contamination. The water intrusion was determined to be due to leakage past the floating tubesheet seals in the lube oil cooler (**CLR**) [LA]. System tagouts in which the components are allowed to go cold followed by rewarming are often associated with the initiation of new leakage past these seals. The Division II EDG had just undergone an extended maintenance window in which it was inoperable from 6/24/18 14: 15 to 7/4118 03:27 and the lube oil system was allowed to cool to ambient temperature. There is no concern that there was any water-to-oilleakage in Division II or that it was susceptible to this failure mechanism before this extended maintenance window. There is no technical basis to be able to determine that the Division II EDG would have been capable of meeting its mission, from 6/24/18 14: 15 when the maintenance outage started until it was repaired and restored on 7/9/18 22:09. n-herefore, the entirety of the Division II EDG was from 6/24/1814:15 to 7/9118 22:09. The Division I EDG was also inoperable during this window from 04:27 to 07:53 on 7/4/18. C. REPORTABILITY Because both EDGs were considered inoperable from 04:27 to 07:53 on 7/4/18, this event is being reported under 10CFR50.73(a)(2)(v)(A), 10CFR50.73(a)(2)(v)(B), 10CFR50.73(a)(2)(v)(C), and 50.73(a)(2)(v)(D) as an event that that could have prevented the fulfillment of the safety function of structures or systems that are needed to (A) shut down the reactor and maintain it in a safe shutdown condition, (B) remove residual heat, (C) control the release of radioactive material and (D) mitigate the consequences of an accident. This event is also being reported under 10CFR50.73(a)(2)(i)(B), any operation or condition which was prohibited by the plant' s Technical Specifications, due to the completion times of the TS required actions of one inoperable EDG from 6/24/18 14: 15 to 7/9/18 22:09 not being met. D.CAUSE The cause of the Lube Oil Cooler leakage is a design deficiency in which there is a mismatch between the lantern ring at he packed floating tube sheet and the tube sheet outside diameter. The clearance is too large between the lantern ring inside diameter and tube sheet outside diameter to fully cover the annulus between the tube sheet outside diameter and flange inside diameter. The lantern ring should fit tightly around the tube sheet (1/32" clearance). The RBS lube oil cooler has a non-standard floating tube sheet (14-15/16" ), machined smaller by the original vendor, but the size of the lantern ring appears to not have been changed to match the tube sheet. This causes improper retaining of the rubber packing, which over time deforms and extrudes into open spaces around the lantern ring. This deprives it of its normal resiliency, | ML18247A460
Fermi 2 05000 341 1 OF 4 | Unknown Unit | Non-Functional Mechanical Draft Cooling Tower Fan Brakes Leads to HPCI Being Declared Inoperable and Loss of Safety Function | 09-29-2018 | At 0940 EDT on August 3, 2018, the Division 2 Mechanical Draft Cooling Tower (MDCT) fans were declared inoperable due to loss of power to the over speed fan brake inverter. The MDCT fans are required to support operability of the Ultimate Heat Sink (UHS) and the Emergency Equipment Cooling Water (EECW) system. The Division 2 EECW system cools the High Pressure Coolant Injection (HPCI) system room cooler. As a result, the non-functionality of the fan brakes led to an unplanned HPCI inoperability. Since HPCI is a single train system designed to mitigate the consequences of a loss of coolant accident (LOCA), this event could have prevented the fulfillment of a safety function. The cause of the event was the failure of the Division 2 fan brake inverter. Corrective Actions were taken to replace the blown fuse and inverter returning the MDCT fans, the UHS, EECW and HPCI to service on August 4, 2018 at 2151 EDT. The fan brake system is only required for a design basis tornado and there was no credible tornado threat during this event. The inverter was fully tested by Fermi 2 with assistance and guidance from the vendor NOVA. All testing was satisfactory. The fuse has been sent for failure analysis. The HPCI system is not required to mitigate a design basis tornado. The safety significance of this event is very low and there were no radiological releases associated with this event. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3160-0104 EXPIRES: 03131/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons leamed are Incorporated Into the licensing process and fed back to Industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear 19 CONTINUATION SHEET Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See h t N tp U :/ R /w E w G w -1 .n 0 r 2 c 2 .g , o R v/ . r 3 e a fo d r i n In g s -r tr m u / c d ti o o c n - c a o n ll d e c g t u io id n a s n /n c u e r e fo q r s c /s o t m af p f/ l s e r t l i n 0 g 2 t 2 h / i r s 3 / f ) o rm u N s R e C d to m a Im y p n o o s t e c a o n nd I n u f c o t r m o a r t io s n p o c n o s l o le r c , ti a o n n d d a oe p s e n rs o o t n d is i p s la n y o t a r c e u q r u re ir n e t d ly t v o a l r i e d s O po M n B d c to o , n t t r h o e l n I u n m fo b r e m r a , ti t o h n e collectlon, 1. FACILITY NAME 2. DOCKET NUMBER YEAR 3 S . E L Q E U R E N N U T M IA B L E R REV NUMBER NO. Fermi2 05000- 05000-341 201Z - 005 - 0 | INITIAL PLANT CONDITIONS Mode-1 Reactor Power - 100 percent There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT At 0940 EDT on August 3, 2018, the Division 2 Mechanical Draft Cooling Tower (MDCT) [CTW] fans [FAN] were declared inoperable due to loss of power to the over speed fan brake [BRK] inverter [INVT]. The brakes prevent the fans from experiencing over speed from a design basis tornado as described in Updated Final Safety Analysis Report (UFSAR) Section 9.2.5.2.2. The MDCT fans are required to support operability of the Ultimate Heat Sink (UHS) [BS]. The UHS is required to support operability of the Division 2 Emergency Equipment Cooling Water (EECW) system. The EECW system cools various safety related components, including the High Pressure Coolant Injection (HPCI) [BJ] system room cooler [CLR]. As a result, the non-functionality of the fan brakes led to an unplanned HPCI inoperability based on the inoperability of the EECW to the HPCI room cooler. Following restoration of the brake inverter, HPCI was declared operable on August 4, at 2151 EDT. Therefore, the single train HPCI system was inoperable for approximately 36 hours and 11 minutes. This report is being made pursuant to 10CFR50.73(a)(2)(v)(D) as a condition that could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident. Technical Specification 3.7.2 requires the UHS reservoir to be operable in Modes 1, 2, and 3. The UHS operability requirements in Modes 4 and 5 are determined by the systems the UHS supports. The UHS reservoir is divided into two one-half capacity reservoirs, corresponding to Division 1 and Division 2. Each reservoir is the cooling source for that division's service water subsystems, including the service water for the Emergency Diesel Generators (EDGs) [[DG]]. A two-cell MDCT is located above each of the one-half capacity reservoirs. Each cell is equipped with a MDCT fan. Two MDCT fans above each one-half capacity reservoir are required for it to be considered operable. The "A" and "C" MDCT fans are in Division 1 and the "B" and "D" fans are in Division 2. The MDCT fans have a brake system to prevent overspeed from a design basis tornado as described in UFSAR Section 9.2.5.2.2. Thus the fan brakes are a design feature of the fans and their functionality impacts the operability of the MDCT fans and therefore the UHS. The brake mechanism senses the speed of the motor and blades and uses nitrogen pressure to activate a brake system to slow the fan speed. The control power for this braking control module is powered by the R1700SO11B (Division 2 Residual Heat Removal (RHR) MDCT Fans overspeed Brake Inverter). Without this inverter being energized, neither of the Division 2 MDCT fan brakes would perform their design function. Therefore, this inverter failure renders both of the Division 2 MDCT fans inoperable. A past operability review was performed and concluded that the MDCT Brake Inverter Panel R1700S011 B was discovered to be indicating no AC Volts or Amps during daily rounds on August 3, 2018 at 0940. An Operator records the output voltage daily and it was observed that the output voltage was within acceptable limits on August 2, 2018 at 1035 EDT. Thus, the inverter was observed to be functioning 23 hours 5 minutes before discovery and the maximum possible period of inverter failure prior to discovery and restored to service is approximately 59 hours and 16 minutes. A review verified that the Division 1 UHS and RCIC systems were operable during the possible period of inverter failure, as well as during the period when Division 2 UHS and HPCI were declared inoperable. Therefore, there was not a violation of Technical Specifications and Licensing Basis due to this condition. TS 3.7.2 Condition B allows for 72 hours | ML18272A002
Calvert Cliffs Nuclear Power Plant | Unit 1 | Control Room Loss of Ventilation Due to Smoke Detector Failure Causing Common Supply Damper to Shut | 10-08-2018 | On July 7, 2018, at 02:42 the main Control Room experienced a loss of ventilation due to the Control Room supply damper fully closing. This isolated ventilation flow to the Control Room which resulted in both trains of the Control Room Emergency Ventilation System and Control Room Emergency Temperature System being out of service, resulting in Technical Specification Limiting Condition for Operations 3.7.8 and 3.7.9 not being met, respec:;tively. Field troubleshooting isolated the cause of failure to Control Room ventilation smoke detector. The smoke detector functions to shut the Control Room supply damper. Manual action was taken to open the Control Room supply damper. The Units exited the associated Technical Specifications at time 02:49. This event is reportable in accordance with 1O CFR 50.73(a)(2)(v)(D) and 10 CFR 50.73(a)(2)(vii). The apparent cause of the smoke detector failure is that no preventive maintenance activity existed to inspect and clean the Control Room ventilation smoke detector to prevent dust and dirt accumulation settling on the smoke detector head. A preventative maintenance activity is being implemented. NRG FORM 366 (04-2018) ;\,, NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported .~, ,;f'..p,'flRla:Glft.,.,.o-, lessons learned are incorporated into the licensing process and fed back to industry. Send comments [ , ~ LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to ~,, . the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of q ,. ..... Management and Budget, Washington, DC 20503. If a means used to impose an information collection (See NUREG-1022, R.3 for instruction and guidance for completing this form does not display a currenfly valid 0MB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. htt12://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR Calvert Cliffs Nuclear Power Plant, Unit 1 05000317 NUMBER NO. - - 2018 003 01 | PLANT AND SYSTEM IDENTIFICATION Calvert Cliffs Nuclear Power Plant, Units 1 and 2, are Combustion Engineering Pressurized Water Reactors with a licensed maximum power level of 2737 megawatts thermal. The Energy Industry Identification System codes used in the text are identified as [XX]. A. CONDITION PRIOR TO EVENT Units 1/2 Date: July 7, 2018 Power level: 100 percent/100 percent Mode: 1/1 There were no structu'res, systems, or components out-of-service that contributed to this event. B. DESCRIPTION OF EVENT On July 7, 2018, at 02:42 the main Control Room experienced a loss of ventilation due to the Control Room [NA] supply damper [DMP] fully closing. This isolated ventilation flow to the Control Room which resulted in both trains of the Control Room Emergency Ventilation System [VI] (CREVS) and Cantrall Room Emergency Temperature System [VI] (CRETS) ~eing out-of-service and, therefore, inoperable. Both Units were affected. 1 With both trains of C~EVS inoperable, Technical Specification Condition 3.71D applies. This Condition has a 24-hour Completion Time to restore one train to Operable status. With both trains of CRETS inoperable, Technical Specification Condition 3.7.9.C applies. This Condition requires entry into LCO 3.0.3. Field troubleshooting isolated the cause of failure to Control Room ventilation smoke detector [DET] (OAE5347). The smoke detector functions to shut the Control Room supply damper by energizing the associated solenoid valve (O-SV-5342) [PSV]. The associated solenoid valve was observed in the energized state via thermography. The solenoid valve is normally de-energized to maintain the damper open. Air was manually isolated to the solenoid valve and air pressure removed to return the Control Room supply damper to an open state. Once the damper was opened, the trains of 9REVS and CRETS were restored to Operable status and the associated Technical Specificatidns for each Unit were exited at time 02:49. For a period of 7 minutes there was a loss of CREVS and CRETS function, therefore this event is reportable in accordance with 1O CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfilment of the safety function of SSCs that are needed to mitigate the consequences of ·an accident, and 1O CFR 50.73(a)(2)(vii) as an event where a single cause or condition caused two independent trairis to become inoperable in a single system. NRG FORM 366A (04-2018) Page_2_ of~ | ML18283A306
Pilgrim Nuclear Power Station 05000-293 1 OF3 | Unknown Unit | Supplement to Start-Up Transformer Degraded Voltage Relay Found Outside_ Technical Specification Limit | 10-25-2018 | On September 13, 2017 with the unit at 100 percent power, Pilgrim Nuclear Power Station discovered during calibration of four Start-Up Transformer Degraded Voltage Relays (ABB model number ITE- 27N) after the relays had been removed from the plant, relay 127A -604/1 had an as-found setpoint value outside the Technical Specifications Table 3.2.B limit of 110.6 plus or minus 0.56 Volts ac (Vac) (110.04 -111.16); the as-found value was 109.90 Vac. This relay was replaced with a spare relay that was calibrated prior to its installation. Pilgrim Nuclear Power Station is submitting this Licensee Event Report in accordance with 1O CFR 50.73(a)(2)(i)(B) -Any operation or condition that was prohibited by the plant's Technical Specifications. This event was not risk significant. There was no threat to public health and safety from this condition. NRG FORM 366 (04-2017) ) \ NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid 0MB control number, the http://www.nrc.gov/reading-rm/doc-collect1ons/nuregs/staff/sr1022/r3/) NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Pilgrim Nuclear Power Station 05000-293 NUMBER NO. 2017 -012 -01 | BACKGROUND The startup transformer supplies power to the station auxiliary power distribution system whenever the main generator is offline. After the main generator has been synchronized to the 345 kV system and has been partially loaded, the auxiliary power distribution system is manually transferred from the start-up transformer (SUT) to the unit AC power source (unit auxiliary transformer [UAT]). Automatic fast transfer capability is provided in the design to restore the auxiliary power distribution system lo its preferred offsite AC power source, the SUT, in the event that the unit AC power source (UAT) is lost or any reason. The diesel generator load shedding logic will also be actuated immediately upon the fast transfer of the safety related buses A5 and A6 to the SUT if a Loss-Of-Coolant-Accident signal is present When the SUT secondary voltage is below the degraded voltage alarm reset setpoint. The primary function of the 127A -604/1 degraded voltage relays and their settings for the SUT is to ensure a minimum voltage at which the emergency buses can be operated indefinitely to provide their intended safety functions. If voltage drops below that point for a specified time limit, the degraded voltage relays will initiate transfer of the emergency buses from offsite power to the onsite emergency diesel generators. 1 EVENT DESCRIPTION During calibration of four SUT Degraded Voltage Relays (ABB model number ITE-27N) after the relays had been removed from the plant, relay 127A-604/1 had an as-found setpoint value outside the Technical Specifications (TS) Table 3.2.B limit of 110.6 plus or minus 0.56 Volts ac (Vac) (110.04 - 111.16). The as found value was 109.90 Vac. This relay was replaced with a spare relay that was calibrated prior to its installation. CAUSE OF THE EVENT A preliminary failure analysis concluded that the relay was exhibiting drift. However, testing at a vendor facility concluded that the relay had repeatable good performance with no indication of unacceptable drift. Similarly, other identical relays purchased at the same time did not show signs of excessive drift. Therefore, the cause of the relay .failure remains inconclusive. However, the failure was .unique to the · affected relay, which was replaced. Based on a review of calculations, margins exist to compensate for the minor deviation, which indicates that the degraded voltage relay would operate within safety limits but outside the TS limits. CORRECTIVE ACTIONS • I The relay was replaced, restoring the safety function of the SUT degraded voltage relay to initiate transfer | ML18304A331
River Bend Station | Unit 1 | Manual Reactor Scram due to Reactor Recirculation Pump Trip Caused by Transformer Failure | 10-31-2018 | On February 01, 2018 River Bend Station was performing a plant startup. At approximately 27% power, an attempt was made to shift Reactor Recirculation Pump '8' from slow to fast speed. A failure in the pump motor transformer caused the pump to trip during the upshift, requiring entry into AOP-0024, Thermal Hydraulic Stability Controls and GOP-0004, Single Loop Operation. Both procedures require monitoring core flow using the Validated Core Flow Emergency Response and Information System computer data point (WTX). When operators observed the data point they noted that it was "Suspect" and magenta in color, persuading the control room team to question the validity of WTX. The control room team engaged Nuclear IT to help resolve the anomaly. The control room team attempted to use several alternate indications of core flow, but ultimately was unable to reconcile the anomaly with the quality and color of WTX. Although the reactor was in compliance with Technical SpeCifications, the decision was made to conservatively shutdown the reactor. Nuclear IT contacted the operating crew several minutes after the shutdown to inform them that the data provided by WTX was indeed valid. AOP-0024 and GOP-0004 were revised, the color of "Suspect" data points was changed, and an extent of condition review was performed to determine if other transformers with the same vulnerability exist. NRCF ORM3 66 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (Q4..2018) .." "'-.. Estimated burden per response to comply with this mandatory collection request 80 hours. Reported . :~. LICENSEE EVENT REPORT (LER) lessons leamed are incorporaled Into the licensing process and fed back to Industry. Send comments f¥~ regarding burden estimate to the Information Services Branch (T-2 F43), U. S. Nudear Regulatory \. ..... ./ CONTINUATION SHEET Commission. Washington, DC 20555'()OO1, or by &-mail to Infocolects.Resoorce@nrc.gov, and to the Desk OffIcer, OffIce of Information and Regulatory Affairs. NEOB-10202, (3150'()104), Office of Management and Budgel, Washington. DC 20503. ~ a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form coIection does not display a currenUy valid OMB control number, the NRC may not conduct 0( http'//www nrc goylreading-rm/doc-collections!nuregs/stafflsr1 022/r31) sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2, DOCKET NUMBER o 3. LER NUMBER YEAR SEQUENTIAL REV River Bend Station - Unit 1 05000-1 458 NUMBER NO. 1-0 ~- I I 007 | IA. PLANT CONDITIONS PRIOR TO THE EVENT On February 1, 2018, River Bend Station (RBS) was operating in Mode 1 at approximately 27% power, performing a plant startup following a mid-cycle outage. Reactor Recirculation [AD] Pump 'A' was operating in fast speed and Reactor Recirculating Pump 'B' was operating in slow speed. B. BACKGROUND Reactor Recirculation System IThe purpose of the Reactor Recirculation System (RCS) is to provide the driving flow to the jet pumps to circulate reactor coolant through the core. The RCS provides forced coolant water flow through the core to increase the core power density and to remove heat from the fuel. The RCS, in conjunction with the Recirculation Flow Control System, provides a means of controlling reactor power over a limited range by varying the coolant flow through the reactor core at a controlled rate. Forced circulation of coolant water through the core allows a higher power level than could be achieved with natural circulation. Normal power for the Recirculation Pump motor is from an oil filled step-down transformer (**XFMR**) which is designed to accelerate the motor to full speed in 10 seconds. With reactor power less than approximately 30%, the Recirculation Pump Motor is powered from the Low Frequency Motor Generator (LFMG) set which runs the motor at a slow speed of 450 rpm. Plant Computer Systems IThe Emergency Response and Information System (ERIS) provides on-line monitoring of approximately 1,200 plant process variables. The system monitors both digital and analog input signals at specified intervals, performs calculations !With selected input data, processes the data, and can produce meaningful displays, logs, and plots of plant performance representing safety related and transient response data. IThe Orbital Network Engineering ONE system is a server system consisting of a central processor, random access memory, hard drives, analog and digital input/output modules, time standard synchronization, and self-error checking. The Validated Core Flow ERIS point (WTX) is produced from input from ONE. C. DESCRIPTION On February 01, 2018 River Bend Station was performing a plant startup following a mid-cycle outage. At approximately 27% power, an attempt was made to shift Reactor Recirculation Pump 'B' from slow to fast speed. The pump tripped during he upshift at 09:46, requiring entry into AOP-0024, Thermal Hydraulic Stability Controls and GOP-0004, Single Loop Operation. Both procedures require the operating crew to monitor core flow to determine if the core is in a power to flow region where thermal hydraulic instabilities are more likely and to verify Technical Specification requirements are met. Both procedures instruct operators to use WTX to monitor core flow. Operators found that the quality of the core flow value provided by WTX was tagged as "Suspect". The color of the value on the visual display was also magenta in color. The control room team was concerned that WTX was not providing reliable data due to the magenta color and "Suspect" | ML18304A436
Nine Mile Point | Unit 2 | NMP2 Turbine Trip and Scram Due to Unit Differential Relay Trip | 10-25-2018 | At 0033 on August 27, 2018, Nine Mile Unit 2 (NMP2) experienced an automatic reactor scram on turbine control valve fast closure due to a turbine trip. All control rods inserted. There were no safety system actuations. In response to the turbine trip and reactor scram all systems responded per design. The station responded in accordance with appropriate procedures and restored impacted systems. The condition was reported in Event Notification #53565 as an event or condition that results in a valid RPS actuation (scram) pursuant to 1 OCFR.50.72(b)(2)(iv)(B). This event is being reported as an event or condition that results in a valid RPS actuation pursuant to 1O CFR50. 73(a)(2)(iv)(A). The direct cause of this event is an actuation of the 'A' phase Unit Differential Relay, 87-2SPUY02(1) due to a grid disturbance on the 'A' phase of the 2-15 Clay-Edie transmission line. The root cause of the event is a failure of Relay & Control technicians to hold themselves accountable for use of the HU tools in preventing errors while removing grounding screws from the Unit Differential Relaying Circuitry. Corrective actions included: removal of the identified shorting screws and qualifications for those involved with the event. NRC FORM 366 (04-2018) ..... NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: BO hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currenfly valid 0MB control number, the NRG may not conduct or http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR Nine Mile Point Unit 2 05000410 NUMBER NO. 2018. - 002 - 00 | I. DESCRIPTION OF EVENT A. PRE-EVENT PLANT CONDITIONS: Prior to the event NMP2 was at 100% power. B. EVENT: On August 27, 2018 at 0033 while operating at one hundred percent power, NMP2 experienced a turbine trip resulting in a SCRAM. In response to the turbine trip and reactor scram, Operations entered N2-EOP-RPV, Reactor Pressure Vessel (RPV) Control Flowchart and N2-SOP-101 C, Reactor Scram, due to reactor pressure vessel low water level and high reactor pressure. Two Safety Relief Valves (SRV's) opened and reclosed during the transient. Operators established a normal RPV level band of 160-200 inches using Condensate and Feedwater, and a pressure band of 800-1000 psi using Digital Electro Hydraulic Control (DEHC) and turbine bypass valves. C. INOPERABLE STRUCTURES, COMPONENTS, OR SYSTEMS THAT CONTRIBUTED TO THE EVENT: None D. DATES AND APPROXIMATE TIMES OF MAJOR OCCURRENCES AND OPERATOR ACTIONS: All Occurrences and Action took place on August 27, 2018: 0033 Grid Disturbance Occurs Due to a Phase 'A' Fault External to the Statioh 0033 'A' Phase Unit Differential Relay Actuates 0033 RPS A and B Control Valve Fast Closure Trip Received 0033 Two Safety Relief Valves Opened and Closed Per Design 0033 Entered EOPs and SOPs: N2-EOP-RPV, Control, for RPV Low Water Level and High Reactor Pressure N2-SOP-101 C, Reactor Scram. 0033 Established Normal RPV Level Band Using Condensate and Feedwater 0033 Pressure Band Established Using DEHC and Turbine Bypass Valves. 0039 Reset Level Setpoint Setdown Per N2-SOP-101 C 0226 Exited N2-EOP-RPV Control Exited N2-SOP-101 C Reactor Scram E. METHOD OF DISCOVERY: This event was self-revealina. NRG FORM 366A (04-2018) Page _2_ c,f _4_ _ | ML18306A486
Quad Cities Nuclear Power Station | Unit 1 | Two Reactor Protection System Channels Impacted by Single Main Stop Valve Limit Switch Failure | 11-06-2018 | On June 9, 2018, at 1240 hours, Quad Cities Nuclear Power Station (QCNPS) main turbine Main Stop Valve number 1 (MSV1) failed to provide the appropriate Reactor Protection System (RPS) relay actuations during periodic surveillance activities. The associated limit switch failed to properly actuate relays in subchannels of both the A and B RPS Trip System channels. Operations entered Technical Specification (TS) 3.3.1.1. Condition B due to one inoperable channel in each trip system. Fuses associated with the subchannels in both the A and B RPS channels were removed to meet the TS Action Statement. The limit switch was replaced on June 10, 2018, and associated RPS channels were tested satisfactory at 0538 hours. The cause of the switch failure was occasional binding due to inadequate lubrication during assembly by the manufacturer. The safety significance of this event was minimal. The associated RPS logic requires signals from 3 of 4 valves, and the other 3 valves were providing proper signals per surveillance results. All other RPS inputs were functional. This report is submitted in accordance with the requirements of 10 CFR 50.73(a)(2)(vii) for a single condition that caused two independent channels to become inoperable in a single system designed to shut down the reactor and maintain it in a safe shutdown condition. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid 0MB control number, the NRG may not conduct or http://www.nrc.gov/readinq-rm/doc-collections/nuregs/staff/sr1022/r3Q sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR Quad Cities Nuclear Power Station 05000254 NUMBER NO. 2018 - 003 01 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Emergency Diesel Generators [DG] Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Two Reactor Protection System Channels Impacted by Single Main Stop Valve Limit Switch Failure A. CONDITION PRIOR TO EVENT Unit: 1 Event Date: June 9, 2018 Event Time: 1240 hours Reactor Mode: 1 Mode Name: Power Operation Power Level: 100% There were no structures, systems, or components (SSCs) out of service or inoperable that contributed to the event. B. DESCRIPTION OF EVENT On June 9, 2018, at 1240 hours, Quad Cities Nuclear Power Station (QCNPS) Unit 1 was performing a Turbine Stop Valve Closure Scram Instrumentation Functional Test. Main Stop Valve (MSV)[V] number 1 (MSV1 ), also referred to as Turbine Stop Valve number 1, did not produce the appropriate alarm or relay actuations in the Reactor Protection System (RPS)[JD] channels A or B. Operations entered Technical Specification (TS) 3.3.1.1. Condition B due to one inoperable channel in each trip system. Operations subsequently removed fuses associated with the associated RPS sub-channels at 1838 on June 9, 2018 to satisfy the requirements of the TS Action Statement. A new limit switch [33] was installed on the MSV number 1. Post maintenance testing on this new switch was satisfactory and TS 3.3.1.1. Condition B was exited at 0346 on June 10, 2018. The RPS logic for all four MSVs was verified satisfactory at 0538 on June 10, 2018. This event is reportable as a licensee event report (LER) in accordance with 10 CFR 50.73(a)(2)(vii) for a single condition that caused two independent channels to become inoperable in a single system designed to shut down the reactor and maintain it in a safe shutdown condition. C. CAUSE OF EVENT An inspection of the degraded limit switch showed occasional binding attributed to insufficient or dried out lubricant, and a hardened a-ring on the operating shaft. Additional causal evaluation confirmed inadequate lubrication during assembly by the manufacturer. | ML18313A034
Watts Bar Nuclear Plant | Unit 1 | Control Room Emergency Ventilation System lnoperable due to Main Control Room Door Being Left Open | 11-13-2018 | At 01 13 Eastern Daylight Time (EDT) on September 11 , 2A18, a Main Control Room (MCR) alarm was received for low control room positive pressure. At 0114 EDT, a Control Room Envelope (CRE) door was found ajar and immediately closed. Technical Specification Limiting Condition for Operation (LCO) 3.7.10, Control Room Emergency Ventilation System (CREVS), was declared not met for both trains and Condition B entered. At 0114 EDT on September 11,2018, the alarm cleared, CREVS was declared operable and LCO 3.7.10, Condition B was exited. This event was caused by a human performance error when an individual traversing the control building complex failed to confirm the MCR envelope boundary door was properly latched. The open control room door was identified and promptly closed. Stand-downs were conducted to brief and reaffirm to site personnel with MCR a@ess on the requirements for door closure. A work order to install engineering features on MCR doors to ensure they are closed after opening is scheduled to be performed in January 2019. This condition is being reported as an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident in accordance with 10 CFR 50.73(a)(2XvXD). NRC FORM 366 (04-2018) NRC FORM 366A U.S, NUCLEAR REGULATORY GOMMISSION A'JP'<9VED tsY (JMt : NU. lr'tbo-o',t04 EXPtRtstii VStS1tZgZg {04-2018) Estimated burden per response to comply with this mandatory collection request B0 hours. Reported lessons learned are incorporated into the licensing process and fed back to o*n*'t* industry. Send comments regarding burden estimate to the lnformation Services Branch fl- *"o* 2 t43), U,S. Nuclear Regulatory Commission, Washingon, DC 20555-0001,0r by email to hEi f r., " -1.:{ r +y: e g ;,l : x . , j. . r. r;.:*.li . : : . yi & # o' i aE LICENSEE EVENT REPORT (LER} l R n e fo g c u o la lle to c r t y s , A R fi e a s ir o s u , r c N e E @ O n B rc -1 .g 0 o 2 v 0 , 2 a , n ( d 3 1 t 5 o $ 0 t 1 h 0 e 4 ) D , e O sk f t 0 ce ff c o e f r , M O a f n fic a e g e o m f e n ln t fo a rm nd a ti B on u d a g n e d t CONTINUATION SHEET Washin$on, DC 20503. lf a means used to impose an information collection does not display a cunenfly valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Watts Bar Nuclear Plant, Unit 05000390 NUMBER NO. 1 2018 r 004 r00 | L Plant Operating Conditions Before the Event Watts Bar Nuclear Plant (WBN) Unit 1 was at 97 percent rated thermal power (RTP) and Unit 2 was at 100 percent RTP. 11. Description of Event A. Event Summary At 01 13 Eastern Daylight Time (EDT) on September 1 1 ,2018, a Main Control Room (MCR) alarm was received for low control room positive pressure. At 0114 EDT, a Control Room Envelope (CRE) door {EllS:DR} was found ajar and immediately closed. Technical Specification Limiting Condition for Operation (LCO) 3.7.10, Control Room Emergency Ventilation System (CREVS) {EllS:Vl}, was declared not met for both trains and Condition B entered. At 01 14 EDT on September 11,2018, the alarm cleared, CREVS was declared operable and LCO 3.7.10, Condition B was exited. This event is being reported to the Nuclear Regulatory Commission (NRC) under 10 CFR 50.73(a)(2)(vXD) as an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event No inoperable structures, systems, or components contributed to this condition. C. Dates and approximate times of occurrences Date Time Event (EDT) 0113 9111118 MCR alarm was received for low control room positive pressure. Technical Specification (TS) 3.7.10 was declared not met for both trains and Gondition B entered 0114 9111118 CRE door was found ajar and lmmediately closed. TS 3.7.10 Condition B exited with cleared alarm D. Manufacturer and model number of each component that failed during the event No equipment failures occurred during the event. E. Other systems or secondary functions affected No other systems or secondary functions were affected. NRC FORM 3664 (A4AA18) Page 2 of q ,,,,, NRG FORM 366A U.S. NUCLEAR REGULATORY COMMISSION AITFR(JVtsU EY 9ME: N(). 3100-0104 EXF¦RESi 93t31t2020 (04-2018) Estimated burden per response to comply with this mandatory collection request 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to *n*'}* industry. Send comments regarding burden estimate to the lnformation Services Branch ([- g 3u { , l* t h ;f , i .;.;..,,,..i,if;if. i E LTCENSEE EVENT REPORT (LER) 2 l R n e f t o 4 g c 3 u o l ) a l , l e to U c r , t y S s " . A N R f u i e a c s i le r o s a u , r r c N R e E e @ g 0 u n B l r a - c 1 to . 0 g ry 2 o 0 v C 2 . , o a m n ( m d 3 1 is t 5 s o S io 0 n th 1 , 0 e W 4 D ) a , s e h O s in k f g f i t 0 c o f n e ii , c o e D f r C , M 0 2 a f 0 f n i 5 c a 5 e g S e 0 o n 0 e f 0 n 1 l t n , f 0 o a r r m n by d a e ti B - o m n u a d i a l g n e to d t TTffiIff CONTINUATION SHEET Washington, DC 20503. lf a means used h impose an information collection does not display a cunently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Watts Bar Nuclear Plant, Unit 0s000390 NUMBER NO. 1 2018 004 r00 NARRATIVE F. Method of discovery of each component or system failure or procedural error Plant alarms indicated a loss of MCR positive pressure. The response procedure for low MCR pressure requires that the MCR doors be checked for proper closure, at which time door C054 was found open. G. Failure mode, mechanism, and effect of each failed component No equipment failures occurred during the event. H. Operator actions Upon receipt of the alarms, operations personnel promptly closed the MCR boundary door. l. Automatically and manually initiated safety system responses fhe MCR low pressure alarm properly actuated when the MCR door was left open. lll. Cause of the Event A. Cause of each component or system failure or personnel error No equipment fallures occurred during the event. B. Cause(s) and circumstances for each human performance related root cause The event was the result of an individual operating the boundary door failing to properly close the door and confirm its closure (lack of attention to task). lV. Analysis of the Event The CRE is required to be operable in Modes 1 through 6. Operability requires integrity of the CRE such that it will have a low unfiltered in-leakage during accident conditions to maintain the dose to operators within the requirements of Criterion 19 of 10 CFR 50, Appendix A. The TS's allow the CRE boundary to be opened intermittently under administrative control, normally to allow routine personnel ingress and egress from the control room envelope. Administrative controls in the case of boundary doors are that an individual is in control of the door when it is opened. On September 1 1 ,2018, an individual traversing the control building complex left the MCR boundary door C054 ajar. This resulted in operations personnel entering TS LCO 3.7.10, CREVS, for one or more CREVS trains inoperable due to an inoperable CRE boundary. Low positive pressure (less than 0.125 inches of water gauge WG) in the control room for 90 seconds NRC FORM 3664 {44-2018) Page 3 of 5 | ML18317A031
Grand Gulf Nuclear Station | Unit 1 | \ | 11-16-2018 | On August 22, 2017 at 2321 hours central daylight time, Grand Gulf, Nuclear Station {GGNS) entered Technical \ Specification {TS) conditions for three Limiting Condition for Operations {LCOs) not met due to Residual Heat Removal 'A' system (RHR A) being declared inoperable. Entergy Operations Inc. (Entergy) made the decision to shut down the plant based on the results of troubleshooting performed on the RHR A pump. The A RHR pti'mp TS differential pressure was out of specification (low) and.,could not be returned to acceptable limits. GGNS initiated plant shutdown as required by Technical Specifications 3.5.1, 3.6.1.7, and 3.6.2.3 at 1200 hours CDT on August29, 2017, due to expected restoration of RHR Aexceeding the completion time of 7 days prior to restoring Operability. The shutdown was completed and·entry into MODE 3 occurre<:J at 2217 hours CDT on August 29, 2017. . ~ ~ The direct cause of the event was in.creased surface roughness from corrosion in the Division I Residual Heat Removal Pump due to suppression pool water quality and lack of pump passivation. Corrective actions include replacement and successful testing of the pump, reanalysis of calculation limits, procedural upgrades, and the enhancement of pump management controls. This condition is reportable as a completion of a plant shutdown required by the TS. NRC FORM 366 (02-2018) / NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OM~ control number, the http://www.nrc.gov/readinq-rm/doc-collections/nuregs/staff/sr1022/r3l) NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Grand Gulf Nuclear Station Unit 1 05000-416 NUMBER NO. 2017 -006 -01 | DESCRIPTION On August 22, 201T9-t 2321 hours central daylight time (CDT), Grand Gulf Nuclear Station entered Technical Specification (TS) conditions for three Limiting Condition for Operations (LCOs) not met due to Residual Heat Removal [BO] 'A' (RHR A) being declared inoperable. LCOs not met: 1) TS 3.5.1 for one low pressure Emergency Core Cooling System [BO] injection/spray subsystem. 2) TS 3.6.1.7 for one RHR containment spray subsystem, and 3) TS 3.6.2.3 for one RHR suppression pool cooling subsystem. Entergy Operations Inc. (Entergy) made the decision to shut down the plant based on the results of troubleshooting performed on the RHR A pump. Grand Gulf Nuclear Station initiated plant shutdown required by Technical Specifications 3.5.1, 3.6.1. 7, and 3.6.2.3 at 1200 hours CDT on August 29, 2017, due to expected restoration of RHR A exceeding the TS completion time of 7 days prior to restoring Operability. The shutdown was completed and entry into MODE 3 occurred at 2217 hours CDT on August 29, 2017. REPORT ABILITY Entergy completed Event Notification 52936 notifying the Nuclear Regulatory Commission of the commencement of a plant shutdown in accordance with 1O CFR50.72(b)(2)(i), due to the anticipated inability to complete the required A RHR Pump repairs prior to exceeding the TS LCO time limits. The completion of the shutdown reported in Event Notification 52936 is reportable in accordance with 1O CFR50.73(a)(2)(i)(A), the completion of any nuclear plant shutdown required by the plant's Technical Specifications. LCOs not met: 1) TS 3.5.1 for one low pressure ECCS injection/spray subsystem. 2) TS 3.6.1.7 for one RHR containment spray subsystem, and 3) TS 3.6.2.3 for one RHR suppression pool cooling subsystem. CAUSE The A RHR pump TS differential pressure was out of specification (low) and could not be returned to acceptable limits prior to exceeding the 7 day limiting condition for operatioh time. The direct cause of the event was increased corrosion in the Division I Residual Heat Removal Pump resulting in loss of total developed head due to increased surface roughness. NRG FORM 366A (04-2017) Page 2 of 3 | ML18320A190
Fermi 2 05000 341 1 OF 4 | Unknown Unit | Inoperability of Reactor Water Cleanup System Isolation Differential Flow-High Function | 03-31-2020 | On May 31, 2018 at 1420 EDT, the Reactor Water Cleanup (RWCU) System Isolation Differential Flow -High function was declared inoperable as a result of the RWCU Differential Flow Indicator reading downscale. This condition would have prevented the primary containment isolation valves for the RWCU system from automatically isolating on a high differential flow signal. The cause of the downscale reading was due to a capacitor failure within the square root converter. Corrective actions were taken to replace the capacitor within the square root converter and return the RWCU System Isolation Differential Flow -High function to operable on June 1, 2018 at 0947 EDT. Additional corrective actions included verification of the shelf life of the current inventory of capacitors and a 10-year preventative maintenance activity to replace the capacitor due to the 10-year service life. The safety related function of the RWCU System is to provide primary containment isolation upon receipt of a primary containment isolation signal, or upon indication of a high-energy line break (HELB) in the RWCU System piping in response to the following signals: low reactor water level 2; high RWCU equipment temperatures; high RWCU pump room differential temperature; or high RWCU System differential flow. Due to the availability of other automatic RWCU isolation functions as well as the ability to manually isolate RWCU, the safety significance of this event is very low. There were no radiological releases associated with this event. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 0313112020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are Incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U. S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to infocollects.Resource@nrc.gov, and to the Desk Officer, Office of information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an Information (See NUREG-1022, R.3 for Instructton and guidance for completing this form collection does not display a currently valid OMB control number, the NRC may not conduct or http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1 022/r3/) sponsor, and a person isn ot required to respond to, the Information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000- NUMIB ER 1 NO. Fermi2 208- 004E 00 341 | INITIAL PLANT CONDITIONS Mode -1 Reactor Power - 100 percent There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT On May 31, 2018 at 1420 EDT, the Reactor Water Cleanup (RWCU) [[CE]] System Isolation Differential Flow -High function was declared inoperable as a result of the RWCU Differential Flow Indicator [[Fl]] reading downscale; which would have prevented the primary containment isolation valves [[ISV]] for the RWCU system from automatically isolating on a high differential flow condition. At 1519, RWCU was shutdown and the affected penetration flow paths were isolated in accordance with station procedures as required by Fermi 2 Technical Specification 3.3.6.1. All other RWCU primary containment isolation instrumentation functions remained operable and the associated RWCU system primary containment isolation valves were capable of being remotely closed by the control room operators throughout the event. The high differential flow signal is initiated from transmitters that are connected to the RWCU pump outlet and RWCU system discharge to condenser and feedwater. The outputs of the transmitters are compared (in a common summer) and the resulting output is sent to two high flow trip systems. If the difference between the inlet and outlet flow is too large, each trip unit generates an isolation signal. Inoperability of the non-redundant circuitry causes the channels in both trip systems to be inoperable. The remainder of the circuit is redundant and can be considered on a per trip system basis. The square root converter [[CNV]] is within the non-redundant portion of this string. The RWCU system is non-safety; however, the isolation valves provide a safety function to provide primary containment isolation upon receipt of a primary containment isolation signal, or upon indication of a high-energy line break (HELB) in the RWCU system piping in response to the following signals; low reactor water level 2; high RWCU equipment temperatures; high RWCU pump room differential temperature; or high RWCU system differential flow. The differential flow isolation signal is designed to detect the leaks below the capacity of the reactor coolant makeup and within the cold leg portion (approx. 120F) of the system, which would not change ambient air conditions. A similar event had occurred previously on May 27, 2018 as described in LER 2018-003. Actions had been taken to replace a capacitor [[CAP]] within the square root converter. Troubleshooting during this event identified that the replacement capacitor had-failed. Following another replacement of the capacitor within the square root converter, the RWCU System Isolation Differential Flow -High function was declared operable on June 1, 2018 at 0947 EDT. Therefore, the non-redundant RWCU System Isolation Differential Flow -High function was inoperable for approximately 19.5 hours. Event Notification 53435 was made at 1620 on May 31, 2018 pursuant to 10CFR 50.72 (b)(3)(v)(C) and 10CFR 50.72 (b) (3)(v)(D). This report is being made pursuant to 10CFR50.73(a)(2)(v)(C) as a condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material and 10CFR50.73(a)(2)(v)(D) as a condition that could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident. The Updated Final Safety Analysis Report (UFSAR), the TS Bases, and NRC reporting requirements were reviewed as part of an evaluation regarding event reportability. Based on this review, it was determined that the RWCU Differential Flow leak detection function is credited to mitigate a break in the RWCU system piping accident as described in UFSAR Chapter 6. | ML18323A214
Hope Creek Generating Station 05000-354 1 OF3 | Unknown Unit | Hiah Pressure Coolant lniection Svstem lnooerable Due to Failed Fuse | 03-31-2020 | On September 26, 2018, at 1530 the High Pressure Coolant Injection (HPCI) system became inoperable due to a failed fuse in channel 'A' of the system initiating logic. At the time of the failure Hope Creek was in Operational Condition 1 at 100% power. The failed fuse also affected the 'A' channel of the Core Spray and Low Pressure Coolant Injection (LPCI) sub-systems. The HPCI system can be initiated by either of two channels, designated as 'A' channel and 'C' channel. The 'C' channel of the HPCI system remained functional. The fault was isolated to a single component associated with the HPCI system high water level trip (level 8). With the fault isolated, power was restored to the remaining effected portions of the 'A' channel EGGS systems at 2101 on September 26, 2018. With power restored to the other circuits, the 'A' Core Spray and 'A' LPCI subsystems were restored to operable. The HPCI system remained inoperable in accordance with plant Technical Specifications. HPCI was restored to operable status on September 27, 2018 at 1755, following replacement of the effected component, a trip unit, associated with the 'A' channel high water level switch. These conditions are being reported in accordance with 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented the fulfillment of a safety function. NRG FORM 366 (02-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http://www.nrc.gov/reading-rm/doc-collections/nureqs/staff/sr1022/r3{) NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Hope Creek Generating Station 05000-354 NUMBER NO. 2018 -004 -00 | PLANT AND SYSTEM IDENTIFICATION General Electric-Boiling Water Reactor (BWR/4)* High Pressure Coolant Injection (BJ ) - EllS Identifier {BJ} Core Spray (BM) - EllS Identifier {BM} Low Pressure Coolant Injection (BO) - EllS Identifier {BO} *Energy Industry Identification System {EllS} codes and component function identifier codes appear as {SS/CCC} IDENTIFICATION OF OCCURRENCE Event Dates: September 26, 2018 Discovery Dates: September 26, 2018 CONDITIONS PRIOR TO OCCURRENCE Hope Creek was in Operational Condition (OPCON) 1 - Power Operation, at 100% power. DESCRIPTION OF OCCURRENCE On September 26, 2018, at 1530 the High Pressure Coolant Injection (HPCI) {BJ} system became inoperable due to a failed fuse in channel 'A' of the system initiating logic. At the time of the failure Hope Creek was in Operational Condition 1 at 100% power. The failed fuse also affected the 'A' channel of the Core Spray and Low Pressure Coolant Injection (LPCI) sub-systems. The HPCI system can be initiated by either of two channels, designated as 'A' channel and 'C' channel. The 'C' channel of the HPCI system remained functional. The fault was isolated to a single component associated with the HPCI system high water level trip (level 8). With the fault isolated, power was restored to the remaining effected portions of the 'A' channel EGGS systems at 2101 on September 26, 2018. With power restored to the other circuits, the 'A' Core Spray and 'A' LPCI subsystems were restored to operable. The HPCI system remained inoperable in accordance with plant Technical Specifications. HPCI was restored to operable status on September 27, 2018 at 1755, following replacement of the effected component, a trip unit associated with the 'A' channel high water level switch. The HPCI system was inoperable for 26 hours and 25 minutes. These conditions are being reported in accordance with 1O CFR 50. 73(a)(2)(v)(D) as a condition that could have prevented the fulfillment of a safety function. CAUSE OF EVENT The failed fuse was removed and a short circuit to ground was identified on the load side of the fuse. The effected trip unit modules were then removed one at a time until the module containing the HPCI high water level trip, 1 BJLS N693A-B21, was removed and the resistance increased, indicating that the short circuit was removed. The fuse and trip unit module were replaced and the system functions were restored. Analysis of the failed module found it to be working correctly during subsequent testing. Review of operating experience found a Part 21 notice, 1999-31-0 containing information that capacitor C25, connected across the de input power to the trip unit, has a potential to short circuit. Measurements made on the C25 capacitor found it to be open and outside of tolerance, reading 0.13 nanofarads instead of 1 microfarad. The capacitor age was within the date range identified in the Part 21 notice. Based on this, the likely cause of failure is a short circuit of capacitor C25 on trip unit 1 BJLS-N693A B21, HPCI high water level trip. NRG FORM 3668 (02-2018) Page 2 of 3 | ML18324A614
River Bend Station | Unit 1 | Potential Loss of Safety Function and Unanalyzed Condition due to Legacy Design Deficiency in Control Building HVAC. | 11-20-2018 | On September 25,2018, with the plant operating at 90 percent power, a design vulnerability in the Control Building Ventilation (HVK) system control logic was identified during an extent of condition review of a previously reported condition. The review identified a vulnerability in the HVK Chiller start logic. The design vulnerability had been in place since original plant construction and could cause a loss of all Control Building Cooling for up to 20 minutes following a Loss of Offsite Power. Compensatory measures were put in place to restore operability of the system until a temporary modification could be installed to remove the design vulnerability. This condition was of minimal significance with respect to the health and safety of the public. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply v.ith this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are Incorporated Into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U. S. Nudear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555'{)OO1, or by e-mail to Infocolects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEDB-10202, (3150'{)104), Office of Management and Budget, Washington, DC 20503. ~ a means used to impose an information (See NUREG-l022, R.3 for instruction and guidance for completing this form colection does not display a currendy valid OMB control number, the NRC may not conduct or http·!twww,nrc,govlreading-rm/doc-collectionslnuregs/staff/sr1022/r31) sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER o 3. LER NUMBER River Bend Station - Unit 1 YEAR SEQUENTIAL REV 05000-1 458 NUMBER NO. 1-0 ~-I I 08 | BACKGROUND !The Control Building Ventilation (HVK) [VI] system consists of two 1O O-percent capacity Chillers (**CHU**) which provide cooling to each ventilation system sub-loop. Each of which provides cooling, heating, ventilation, pressurization, and smoke removal for several areas within the building. The ventilation system comprises two independent, redundant trains of components and subsystems either of which supports the safety function of providing a controlled environment in the main control room and the environmental requirements of the safety-related electrical equipment in the building. Each HVK subsystem is supported by the respective safety-related emergency diesel generator and conforms to the single failure criterion. Irhe HVK System provides chilled water to the cooling coils in three separate air handlers within each division. The air handling system (HVC) removes the heat generated within the main control room, electrical equipment rooms and chiller rooms. Each air handler serves both trains of their assigned areas (e.g., both the Division I and II standby switchgear rooms cooling may be fully served by the air handler in either train). Normally, one HVK Chiller is in operation, with one from the opposite division in standby. This provides for an immediate and automatic swap with no manual actions should a problem exist in the operating division. Division I HVK consist of HVK Chillers 'A' and 'C' and Division II HVK consist of HVK Chillers 'B' and '0'. REPORTED CONDITION On September 25,2018, with the plant operating at 90 percent power, Engineering identified that if either HVK Chiller 'A' or HVK Chiller 'B' was started up to 20 minutes prior to a Loss of Offsite Power (LOP) event then any single failure in the opposite division that causes that division not to run would cause a loss of all Control Building cooling until the HVK Chiller 20 minute quick restart timer times out. Additionally, if either the Division I or the Division II HVK start sequence is initiated (manually or automatically) before the 20 minute time out, then the associated chilled water pump would start and then trip as the Chiller would not start in the required time period. In this condition, HVK Chiller 'A' and HVK Chiller 'B' cannot be used as the running or standby Chiller. When this condition exists, if either of these Chillers is started then the Control Building cooling system does not meet single failure criteria until the 20 minute quick restart timer times out. HVK Chiller 'C' and HVK Chiller '0' have not been affected by this deficiency since 2016 when a digital control system upgrade was installed. The new control system changed the allowed number of starts in a 20 minute period from 1 to 2. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), 10 CFR 50.73(a)(2)(ii)(B) and 10 CFR 50.73(a)(2) (v)(D). CAUSAL ANALYSIS The HVK control logic design deficiency was introduced during original plant design and construction. The deficiency was previously identified several times over the life of the plant. However, the deficiency was not recognized as a violation of licensing basis requirements and corrective actions were not put in place to remediate the deficiency. | ML18324A744
Fermi 2 05000 341 1 OF 3 | Unknown Unit | Inoperability of Reactor Water Cleanup System Isolation Differential Flow-High Function | 05-27-2018 | On May 27, 2018 at 0630 EDT, the Reactor Water Cleanup (RWCU) System Isolation Differential Flow -High function was declared inoperable as a result of the RWCU Differential Flow Indicator reading downscale. This condition would have prevented the primary containment isolation valves for the RWCU system from automatically isolating on a high differential flow signal. The cause of the downscale reading was due to a capacitor failure within the square root converter. Corrective actions were taken to replace the capacitors within the square root converter and return the RWCU System Isolation Differential Flow - High function to operable on May 28, 2018 at 0046 EDT. The safety related function of the RWCU System is to provide primary containment isolation upon receipt of a primary containment isolation signal, or upon indication of a high-energy line break (HELB) in the RWCU System piping in response to the following signals: low reactor water level 2; high RWCU equipment temperatures; high RWCU pump room differential temperature; or high RWCU System differential flow. Due to the availability of other automatic RWCU isolation functions as well as the ability to manually isolate RWCU, the safety significance of this event is very low. There were no radiological releases associated with this event. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03r31w2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are Incorporated intoth e licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U. S. Nuclear Regulatory \ * CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrcgov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of (See NUREG-1022, R.3 for instruction and guidance for completing this form Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or http://www.nrc.gov/reading-rm/doc-collections/nureqs/staff/srl022/r3/) sponsor, and a person is not required tor espond to, the Information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. 05000- Fermi 2 341 2018 - 003] - 00I | INITIAL PLANT CONDITIONS Mode -1 Reactor Power - 100 percent There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT On May 27, 2018 at 0630 EDT, the Reactor Water Cleanup (RWCU) [[CE]] System Isolation Differential Flow -High function was declared inoperable as a result of the RWCU Differential Flow Indicator [[Fl]] reading downscale; which would have prevented the primary containment isolation valves [[ISV]] for the RWCU system from automatically isolating on a high differential flow condition. At 0753, RWCU was shutdown and the affected penetration flow paths were isolated in accordance with station procedures as required by Fermi 2 Technical Specification 3.3.6.1. All other RWCU primary containment isolation instrumentation functions remained operable and the associated RWCU system primary containment isolation valves were capable of being remotely closed by the control room operators throughout the event. The high differential flow signal is initiated from transmitters that are connected to the RWCU pump outlet and RWCU system discharge to condenser and feedwater. The outputs of the transmitters are compared (in a common summer) and the resulting output is sent to two high flow trip systems. If the difference between the inlet and outlet flow is too large, each trip unit generates an isolation signal. Inoperability of the non-redundant circuitry causes the channels in both trip systems to be inoperable. The remainder of the circuit is redundant and can be considered on a per trip system basis. The square root converter [[CNV]] is within the non-redundant portion of this string. The RWCU system is non-safety; however, the isolation valves provide a safety function to provide primary containment isolation upon receipt of a primary containment isolation signal, or upon indication of a high-energy line break (HELB) in the RWCU system piping in response to the following signals; low reactor water level 2; high RWCU equipment temperatures; high RWCU pump room differential temperature; or high RWCU system differential flow. The differential flow isolation signal is designed to detect the leaks below the capacity of the reactor coolant makeup and within the cold leg portion (approx. 120F) of the system, which would not change ambient air conditions. Troubleshooting identified that a capacitor [[CAP]] within the square root converter had failed, which caused the output signal to fail downscale thus removing the inlet flow signal from the summer. As described above, this failure in the non- redundant portion of the circuitry affected the channels in both trip systems. Following replacement of the capacitor within the square root converter, the RWCU System Isolation Differential Flow - High function was declared operable on May 28, 2018 at 0046 EDT. Therefore, the non-redundant RWCU System Isolation Differential Flow -High function was inoperable for approximately 18 hours. Event Notification 53429 was made at 1242 EDT on May 27, 2018 pursuant to 10CFR 50.72 (b)(3)(v)(C) and 10CFR 50.72 (b)(3)(v)(D). This report is being made pursuant to 10CFR50.73(a)(2)(v)(C) as a condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material and 10CFR50.73(a)(2)(v) (D) as a condition that could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident. The Updated Final Safety Analysis Report (UFSAR), the TS Bases, and NRC reporting requirements were reviewed as part of an evaluation regarding event reportability. Based on this review, it was determined that the RWCU Differential Flow leak detection function is credited to mitigate a break in the RWCU system piping accident as described in UFSAR Chapter 6. | ML18327A076
Clinton Power Station | Unit 1 | Undervoltage Condition Caused by an Offsite Ameren Transformer Bushing Failure Initiates an Automatic Start of an Emergency Diesel Generator - | 11-21-2018 | On September 26, 2018, at 0946 CDT, the Clinton Power Station (CPS) experienced a trip of the Emergency Reserve Auxiliary Transformer (ERAT) Static VAR Compensator (SVC). A fault on the 138 kV feed to the station created a voltage transient which the ERAT SVC could not compensate for causing it to trip. Approximately 15 seconds following the trip of the ERAT SVC, the Division (DIV) 1 Safety Related 4160 kV Bus 1A1 locked out the Reserve Auxiliary Transformer (RAT) feed breaker and the ERAT feed breaker causing the DIV 1 Diesel Generator to start and load to the 1A1 bus due to a sustained degraded (second level) undervoltage condition as designed. Operations entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1, "AC Sources~Operating" Required Actions A.1 and A.2 as a result of the voltage transient. Th.e cause of the event was a failure of the high side bushing on offsite Clinton Route 54 to Substation Transformer No. 2 which caused the south feed to the Tabor Substation to cycle. Cycling of the south feed of the Tabor Substation caused the transient on the station 138 kV feed, which resulted in the subsequent station equipment responses. Ameren bypassed the affected transformer and restored the station 138 kV feed. The ERAT was restored to normal configuration on September 26, 2018, at 1354 CDT. Operations subsequently exited TS LCO 3.8.1, Actions A.1 and A.2. Ameren has completed installation of a 138 kV ring bus to improve the reliability of the 138 kV feed to CPS and is in the process of upgrading the feeds to the new substation. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as any event or condition that resulted in manual or automatic actuation of emergency electrical power systems. NRG FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: BO hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid 0MB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Clinton Power Station, Unit 1 05000461 NUMBER NO. 2018 - 004 00 | PLANT AND SYSTEM IDENTIFICATION General Electric -- Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in text as [XX]. EVENT IDENTIFICATION Undervoltage Condition Caused by an Offsite Ameren Transformer Bushing Failure Initiates an Automatic Start of an Emergency Diesel Generator A. Plant Operating Conditions Before the Event Unit: 1 Event Date: September 26, 2018 Event Time: 0946 Mode: 1 Mode Name: Power Operation Reactor Power: 099 percent B. Description of Event On September 26, 2018, at 0946 CDT, the Clinton Power Station (CPS) experienced a trip of the Emergency Reserve Auxiliary Transformer (ERAT) Static VAR Compensator (SVC)[COMP]. A fault on the 138 kV feed created a voltage transient ERAT SVC causing it to trip. Approximately 15 seconds following the trip of the ERAT SVC, the Division (DIV) 1 Safety Related 4160 kV Bus 1A 1 locked out the Reserve Auxiliary Transformer (RAT) feed breaker and the ERAT feed breaker causing the DIV 1 Emergency Diesel Generator (EOG) to start and load to the 1A 1 bus due to a sustained degraded (second level) undervoltage condition. Operations entered Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.8.1, "AC Sources-Operating" Required Actions A.1 and A.2 as a result of the voltage transient. A review of the safety related equipment actuation, and the response of the RAT, ERAT, ERAT SVC, and EOG, determined that plant equipment responded as designed for the event. Only the DIV 1 safety related 4160 kV Bus 1A 1 was impacted since DIV 2 and 3 were being supplied by the RAT at the time of the event. On September 26, 2018 at 1354 CDT the ERAT SVC was returned to Operable status following restoration of the offsite 138 kV line by Ameren and TS 3.8.1 Actions were exited. | ML18331A164
Peach Bottom Atomic Power Station | Unit 3 | Automatic Reactor Scram Due to Loss of Two Condensate Pumps | 11-29-2018 | On 9/30/18, an automatic reactor scram of Unit 3 occurred due to low reactor vessel water level following the loss of two condensate pumps. Plant equipment responded properly. The High Pressure Coolant Injection and Reactor Core Isolation Cooling systems automatically initiated on reactor low water level and restored level, in addition to the '3C' condensate pump and feedwater system. Reactor cooldown commenced in accordance with plant procedures. The cause of the event was determined to be due to an electrical fault in the power cable for '38' condensate pump a.nd actuation of ground protective circuitry for the '3A' condensate pump. The electrical fault in power cables for the '38' pump caused a ground current transient that raised the ground potential of the '3A' condensate pump transformer, resulting in a trip of the '3A' pump. Subsequently, power cables for the '38' pump were replaced and ground circuitry for the '3A' pump was corrected to prevent such interaction. There were no actual safety consequences as a result of this event. The '3C' condensate pump and reactor feedwater remained available for post-scram recovery. NRG FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04·2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocotlects.Resource@nrc.gov, and to the Desk Officer, Oflice ol Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. http:l/www.nrc.gov/readinq-rmldoc-collectionslnuregs/staff/srl 022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR Peach Bottom Atomic Power Station Unit 3 05000278 NUMBER NO. 2018 - 003 0 | Unit Conditions Prior to the Event Unit 3 was operating in Mode 1 at approximately 100% rated thermal power. There were no structures, systems or components out of service that contributed to this event. Description of Event On 9/30/18, at approximately 1128 hours, Condensate [EllS:SO] Pumps '3A' and '38' both tripped. With the loss of two of the three condensate pumps, reactor water level lowered as expected from the normal 23 inches to the automatic reactor scram setpoint of 1 inch. Plant equipment responded as expected. The High Pressure Coolant Injection (HPCI) [EllS:BJ] and Reactor Core Isolation Cooling (RCIC) [EllS:BN] systems automatically initiated on reactor low water level. Group II and Ill containment isolation signals were received, resulting in valve closures for several systems, including portions of Residual Heat Removal (AHR) shutdown cooling, reactor water cleanup, drywell drains and drywell purge. HPCI and RCIC were secured and reactor level was maintained with the '3C' condensate pump and a reactor feed pump. Reactor cooldown commenced in accordance with plant procedures. Analysis of Event Initial investigation of the event revealed the '38' condensate pump trip occurred first and the '3A' condensate pump tripped immediately (approximately 0.009 seconds) afterwards. A visual inspection of the cables at the cubical identified a degraded section of insulation on the 8 phase cable. The insulation showed a scorch mark where an electrical arc occurred. When the cable was cut, water was observed in the area between the aluminum conductors. The cable had been replaced in October 2017 and was pulled through underground conduit. The end of the cable was not adequately sealed to prevent water from entering the cable during the cable pull. A ground overcurrent relay for the '3A' condensate pump was found to be tripped. Ground fault detection circuitry for the '3A' condensate pump uses a zero-sequence current transformer (CT), which requires the ground wire for the cable shield to pass through the CT. When ground wires were installed for the '3A' condensate pump power cables in October 2015, the ground wire was not properly routed through the CT. As a result, when the ground fault occurred at the '38' pump transformer, a ground potential rise occurred which actuated the '3A' ground detection circuitry. This event is being reported in accordance with the following: • 1O CFR 50. 73(a)(2)(iv)(A) - any event or condition that resulted in manual or automatic actuation of systems including HPCI, RCIC, the reactor protection system (reactor scram) or containment isolation. There were no safety consequences as a result of this event. All safety systems responded as expected. The '3C' condensate pump and reactor feedwater remained available for post-scram recovery. NRG FORM 366A (04-2018) Page_2_ of~ | ML18333A304
Peach Bottom Atomic Power Station | Unit 3 | Failure of a Main Steam Isolation Valve to Fully Close | 11-30-2018 | On 10/1/18 at approximately 12:32 pm, Main Steam Isolation Valves (MSIVs) were stroked closed in preparation for entering Mode 4. The Unit 3 'B' inboard MSIV, A0-3-01A-0808, gave a split indication and it was determined that the valve had stopped approximately 1 inch short of full closure. Turbulent steam flow had caused vibration of the MSlV poppet, causing the poppet cap guide to wear against the anti-rotation lug, resulting in a notch in the poppet cap guide. During valve closure, the poppet traveled its normal path, but the last 1 inch of stem travel did not occur because the stem anti-rotation lug was caught in the notch, which prevented the stem from reaching the pilot seating surface. The stem and the poppet cap guide were replaced, and a modification was performed to stabilize the poppet to prevent recurrence. There were no actual safety consequences as a result of this event. The Unit 3 outboard MSIV was operable for performing its containment isolation function. NRG FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and led back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the lnlormation Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. II a means used to impose an information (See NUREG-1D22, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the inlormation collection. http:f/www.nrc.gov/readinq-rm/doc-collections/nuregs/stall/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Peach Bottom Atomic Power Station Unit 3 05000278 NUMBER NO. 2018 - 004 0 | Unit Conditions Prior to the Event Unit 3 was in Mode 3, Hot Shutdown, following a reactor scram that occurred on 9/30/18 (ref. LER 3-18- 003). There were no structures, systems or components out of service that contributed to this event. Description of Event On 9/30/18, at 11 :28 am, Unit 3 experienced an automatic reactor scram following a loss of the '3A' and '38' condensate pumps. In the process of transitioning to Mode 4, Cold Shutdown, and in accordance with plant procedures, the Main Steam Isolation Valves (MSIVs)[EllS:ISV] were closed at approximately 12:32 pm on 10/1 /18 when reactor pressure reached 1O psig. Seven of the eight MS IV s indicated full closed. A0- 3-01 A-0808 ("MSIV 808"), the Unit 3 'B' inboard MSIV, gave a split indication (both open and closed lights lit) with its control switch in the close position. In-field inspection of MSIV 808 identified that the valve had stopped approximately 1 inch short of full closure. After disassembling the valve, an inspection found that an anti-rotation lug on the shaft had worn into a guide in the poppet cap. The stem and the poppet cap guide were replaced, and a modification was performed to stabilize the poppet to prevent recurrence. The valve was tested on 10/8/18 and met all performance criteria. An extent of condition review determined that the outboard MSIVs are not susceptible to this failure mechanism due to design differences. A visual inspection and diagnostic testing was performed on the three remaining inboard MSIVs (80A, 80C and 80D). During diagnostic testing, both the 80A and 80D valves showed normal operation, with test data closely aligned with their as-left test data from 2011. Based on these results, it was concluded that both 80A and 80D MSIVs are capable of performing their design function for the remainder of the cycle. During diagnostic testing of MSIV BOC, the test data showed a difference in the operating characteristics. Therefore, the valve was disassembled. In-body inspection identified wear of the poppet cap guide from the anti-rotation lugs. The valve stem was not prevented from reaching full travel and seating properly. The stem and the poppet cap guide were replaced, and a modification was performed to stabilize the poppet to prevent recurrence. Analysis of Event Each MSIV is a 'Y'-shaped, 26 inch globe valve manufactured by Atwood & Morrill (model 20851-H) and provides primary containment isolation for the four main steam lines during a design basis event. The bottom end of the valve stem closes a small hole in the main plug (the poppet). When open, it acts as a pilot valve to relieve differential pressure on the poppet. The valve stem travel is approximately 1O inches; the poppet travels 9 inches and the last 1 inch of stem travel closes the pilot hole. NRG FORM 366A (04·2018) Page _2_ of _!... | ML18334A035
Perry Nuclear Power Plant 05000-440 1 OF 3 | Unknown Unit | : | 11-30-2018 | During a recent NRC inspection, it was discovered that Perry Nuclear Pow~r Plant (PNPP) has an unfused circuit that crosses multiple safety-related fire zones. The· resulting extent of condition review found an additional two components with unfused circuits also crossing multiple safety-related fire zones. Without overcurrent protection for these circuits, the potential exists that an initial fire event affecting these circuits could cause short circuits that would cause excessive current through the circuits beyond the capacity rating of the conductors. This could lead to a secondary fire in another plant area where the circuits are routed, challenging the ability to achieve and maintain safe shutdown. Compensatory fire watches have been established for the areas affected. Planned . corrective actions include plant modifications to install ovei'current protection in the. affected circuits. These events are being reported under 10CFR50.73(a)(2)(ii)(B) as an unanalyzed condition. Notifications were made under 10CFR50.72(b)(3)(ii)(B), Unanalyzed Condition, on October 4, 2018 (EN 53644) and October 19, 2018 (EN 53675). The cause of the event was due to a legacy issue stemming from the design and installation of the systems, prior to initial plant startup in 1986, that led to the vulnerability to cause a secondary fire. ~ The postulated events are considered to be of very low safety significance. NRC FORM 366 (04-2018) ,-, NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-201,8.); --.., Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported ;C ..... ' ' I l . l LICEN C S O E N E T I E N V U E A N T T IO R N E P SH O E R E T T ( LER) 1 l r C e ,e o s g s m a o r m n d s i i n s l s g e i o arn b n u , I r e d W d e n a a s r e e h s in i t n i g m c t o o a r n t p e , o t Ir D o a C t t e h d 2 e 0 in I 5 n t 5 o fo 5- t r h m 0 e 0 a l 0 t i i c 1 o e n , n o s S r in e b g r y v p i Ir e c oc - e m s e a s i B s l r t a a o n n d c ln h fe f o ( d T c o - b 2 ll a e c F c k 4 ts 3 t . o R ), e in U s d . o S u u s . r t c r N y e u . @ c S l n e e r a n c r d . g R- c o e o v g m , u a m l n a e d to n ry t t o s ~ the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collectiIo n does not display a currently. valid 0MB control number, the NRG may not conduct or http://www.nrc.gov/1r,e-adinq-rm/doc-collections/nuIr egs/staff/sr1022/r3/ sponsor, and a person is not I r equired to 1r,e spond to, the information collection. 1. FACILITY NAME 2.DOCKET NUMBER 3.LER NUMBER ' SEQUENTIAL REV YEAR 1- Perry NuclearPower Plant 05000-440 NUMBER NO. - - 2018 003 00 NARRA! TIVE Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. I INTRODUCTION ~ r_ During a recent NRC inspection, it was discovered that Perry Nuclear Power Plant (PNPP) has an unfused I circuit that crosses multiple safety-related fire zones. The resulting extent of condition review found an I I additional two components with unfused circuits also crossing multiple safety-related fire zones. Without I I overcurrent protection for these circuits, the potential exists that an initial fire event affecting these circuits I I could cause short circuits that would cause excessive current through the circuits beyond the capacity rating I of the conductors. This could lead to a secondary fire in another plant area where the circuits are routed, I I I challenging the ability to achieve and maintain safe shutdown. Compensatory fire watches have been established for the areas affected. Planned corrective actions include plant modifications to install I overcurrent protection in the affected circuits. EVENT DESCRIPTION On October 4, 2018, with PNPP in MODE 1 at 100% rated thermal power and during the 2018 NRC Fire PrI otection Triennial Inspection, it was determined that the potential exists for a secondary firI e to occur due to an unfused alternating current (AC) circuit [IC] associated with the Division 1 Diesel Generator 1A Ventilation I Fan [VJ]. During a focused extent of condition investigation of safety-related Heating, Ventilation and Air I Conditioning (HVAC) drawings on October 19, 2018, two additional unfused circuits were identified; I I 0M23C0002A, Motor Control Center (MCC) Switchgear and Miscellaneous Area HVAC Recirculation Fan I [VI], and 0M24C0001A, Battery Room Exhaust Fan [VI]. Based on the additional findings, an expanded scope, that included a sample of non-HVAC safety-related 480V MCC fed circuits, was performed with no I additional unfused circuits found. I '{1/ithout overcurrent protection for these circuits, the potential exists that an initial fire event affecting these I circuits could cause short circuits that would cause excessive current through the circuits beyond the capacity rating of the conductors. This could lead to a secondary fire in another plant area where the circuits are I I I I routed, challenging the ability to achieve and maintain safe plant shutdown. Compensatory fire watches were implemented for the affected fire areas. These conditions are being reported under 10CFR50.73(a)(2)(ii)(B) as unanalyzed conditions. Notifications I J were made under 10CFR50.72(b)(3)(ii)(B), Unanalyzed Condition, on October 4, 2018 (EN 53644) and October 19, 2018 (EN 53675). CAUSE OF EVENT The cause of the event was due to a legacy issue stemming from the design and installation of the systems, prior to initial plant startup in 1986, that led to the vulnerability to cause a secondary fire. . NRC FORM 366A (04-2018) Page 2 of 3 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) ,,�..,..,.',. Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) . regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory .... CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to \""9°/ the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of �. · Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currenHy valid 0MB control number, the NRC may not conduct ot http:f/www.nrc.gov/readinq-rm/doc-collections/nuregs/staff/sr1022/r3/ sponsor, and a person is · not required to respond to, the information collection. ·1. FACILITY NAME 2.DOCKET NUMBER 3.LER.NUMBER SEQUENTIAL REV YEAR Perry Nuclear Power Plant 05000-440 NUMBER NO. 2018 003 00 | EVENT ANALYSIS Plant design .in regard to IEEE cable separation, divisional independence, fire detection and suppression capabilities, coupled with Appendix R circuitry/method protection and Fire Protection procedural guidance provides reasonable assurance that post-fire safe shutdown will be achieved and maintained for the identified conditions. Additionally, the suspect AC control cables are insulated in cross-linked thermosetting polyethylene. Thermoset insulation as opposed to thermoplastic insulation can withstand higher temperatures during longer periods of time and burns at lower rates. Based on the expectation that any secondary fire potential would be very localized and limited (low voltage and contained to the affected cable/raceway), in addition to the aspects of the plant design and operation, there is a reasonable assurance that post-fire safe shutdown will be achieved and maintained given the postulated failure mode and the events that would have to occur in order to achieve .the postulated condition. The overall risk of this condition is judged to be very small, based on the consequential impact relative to the aforementioned aspects of plant design and the expected response to a fire event. Correspondingly, as at least one method of safe shutdown would remain available for any potential fire, this condition would be expected to be of very low safety significance. CORRECTIVE ACTIONS: Compensatory fire watches have been implemented for the affected fire areas. Planned corrective actions include plant modifications to install over-currenfprotection in the respective equipment control circuitry. PREVIOUS SIMILAR EVENTS: On October 17, 2013, at 1300 hours with the plant in mode 1, a review of industry operating experience regarding the impact of 1.,mfused Direct Current ammeter circuits in. the Control Room determined the described.condition to be applicable to the Perry Nuclear Power Plant resulting in a potentially unanalyzed condition with respect to 10 CFR 50 Appendix R analysis requirements. The original plantwiring design and associated safe shutdown analysis for the Class 1 E batteries control room ampere indications did not include overcurrent protection features to limit the fault current. This event was reported under 50.7 3(a)(2)(ii)(B) as an ·· unanalyzed condition. On June 19, 2014, with the plant in mode 1, a review of industry operating experience regarding the impact of unfused. Direct Current (DC) circuits determined the described condition to be applicable to the Perry Nuclear Power Plant related to the Turbine Emergency Bearing Oil Pump, Reactor Feed Pump Turbine 'A' Emergency Lube Oil Pump, Turbine Emergency Seal Oil Pump, and the Reactor Feed Pump Turbine 'B' Emergency Lube Oil Pump circuits. The cause was determined to be latent design deficiency in the identified circuits dating back to original design and installation that was not identified during the design review for 1 O CFR 50 Appendix R Section 111.G. Thi� event was reported under 50.73(a)(2)(ii)(B) as an unanalyzed condition: COMMITMENTS None | ML18334A366
Browns Ferry Nuclear Plant | Unit 1 | Standby Gas Treatment System Train C Inoperable Longer Than Allowed by Technical Specifications | 12-06-2018 | On October 6, 2018, at approximately 0001 Central Standard Time (CST), Standby Gas Treatment (SGT) System train C failed to automatically start in response to a Primary Containment Isolation signal which was received after Unit 3 was manually scrammed in support of the Unit 3 Cycle 6 forced outage. SGT train C was manually started. SGT trains A and B started automatically as expected. On October 18, 2018, a Past Operability Evaluation determined that SGT Train C was inoperable for longer than the Unit 1, 2, and 3 Technical Specifications (TS) Limiting Condition of Operation (LCO) 3.6.4.3 seven day allowed outage time for a single inoperable SGT subsystem. The apparent cause of this event was the failure of a handswitch contact to close because of a loose cracked phenolic barrier plate inside the switch which impeded switch rotation. This crack was most likely the result of external forces on the switch and existed prior to the failure. Corrective actions for this condition are to replace the failed handswitch, to replace all other handswitches affected by this condition, and to add a log note to the switch’s catalog ID to inspect new switches for barrier plate damage prior to installation. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T- 2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001,or by e-mail to LICENSEE EVENT REPORT (LER) Infocollects. Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, CONTINUATION SHEET Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 1 05000259 NUMBER NO. 2018 - 006 - 00 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Unit 1, was in Mode 1 at approximately 80 percent power. BFN Unit 2 was in Mode 1 at 100 percent power and Unit 3 was in Mode 3 at approximately 0 percent power for the Unit 3 Cycle 6 forced outage. II. Description of Event A. Event Summary On October 6, 2018, at approximately 0001 Central Standard Time (CST), Standby Gas Treatment (SGT) System train C failed to automatically start in response to a Primary Containment Isolation signal which was received after Unit 3 was manually scrammed in support of the Unit 3 Cycle 6 forced outage. SGT train C was manually started. SGT trains A and B started automatically as expected. On October 18, 2018, a Past Operability Evaluation determined that SGT Train C was inoperable for longer than the Unit 1, 2, and 3 Technical Specifications (TS) Limiting Condition of Operation (LCO) 3.6.4.3 seven day allowed outage time for a single inoperable SGT subsystem. The Tennessee Valley Authority (TVA) is submitting this report in accordance with Title 10 of the Code of Federal Regulations 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant’s TS. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. C. Dates and approximate times of occurrences Dates & Approximate Times Occurrence September 27, 2018 Last known successful use of hand switch [HS] 2345 CDT HS-66-69A/2. October 06, 2018 SGT C started manually after failing to start 0002 CDT automatically. SGT C declared inoperable. October 8, 2018 SGT C declared operable. 0954 CDT | ML18340A152
Grand Gulf Nuclear Station | Unit 1 | .. | 12-12-2018 | ~t approximately 0918 hours on Tuesday, December 12, 2017, while operating in MODE 1 at approximately 18 percent power, the Grand Gulf Nuclear Station (GGNS) experienced a loss of the Engineered Safety Features (ESF) Transformer 11 which was powering the Division 1 ESF bus. Subsequently, the station experienced an automatic start of the Division 1 Emergency Diesel Generator and the partial isolation of the primary and secondary containment buildings. Both of these events were expected and as designed. The direct cause of ESF actuations was the loss of ESF Transformer 11. The cause of the transformer loss was due to a degraded cable with a zinc shield coming in contact with moisture. ~dditionally, GGNS experienced an unrelated isolation of the Reactor Core Isolation Cooling System upon restoration of power. The isolation of the Reactor Core Isolation Cooling System did not result in a safety system functional failure. !This event is reportable to the NRC in accordance with 10 CFR 50.72(b)(3)(iv) and 10 CFR 50.73(a)(2)(iv)(A) as an event or condition resulting in a valid actuation of a ESF system. \ NRC FORM 366 (02-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear CONTINUATIQN SHEET Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means .( See NUREG-1022, R.3 for instruction and guidance for completing this form ~sed to impose an information collection does not display a currently valid OMB control number, the bnQ;//www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3L) NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 05000-416 NUMBER NO. 2017 -007 -01 | DESCRIPTION At.approximately 0918 hours on Tuesday, December 12; 2017, while operating in MODE 1 at approximately 18 percent power, the Grand Gulf Nuclear Station (GGNS) experienced a loss of the Engineered Safety Features (ESF) Transformer 11 [EB] which was powering the Division 1 ESF bus [EA]. The transformer experienced an instantaneous ground resulting in a transformer lockout and loss of power to the ESF bus. Subsequently, the station experienced an automatic start of the Division 1 Emergency Diesel Generator [EK] and the partial isolation of the primary and secondary containment buildings. Both of the system actuations were expected responses to a loss of ESF bus and both systems responded as designed. The direct cause of ESF actuations was the loss of ESF Transformer 11 . Additionally, GGNS experienced an unrelated isolation of the Reactor Core Isolation Cooling System [BN] upon restoration of power. The isolation of the Reactor Core Isolation Cooling System did Mt result in a safety system functional failure. REPORT ABILITY This event is reportable to the NRC in accordance with 10 CFR 50.72(b)(3)(iv)(A) and 10 CFR 50.73(a)(2)(iv)(A) as an event or condition resulting in a valid actuation of a ESF system. · The 1O CFR 50 .. 72 reporting requirements were met with the completion of Emergency Notification System (ENS) Notification 53115, at 1740 hours eastern standard time on December 12, 2017. (CAUSE Direct Cause: The direct cause of the ESF actuation was the loss of ESF Transformer 11 and the opening of the transformer feeder breaker due to an instantaneous ground. The cause of the transformer loss was due to a degraded cable with a zinc shield coming in contact with moisture. NRG FORM 3668 (02-2018) Page 2 of 3 | ML18346A393
Fermi 2 05000 341 1 OF 5 | Unknown Unit | Emergency Diesel Generator Load Sequencer Inhibits Automatic Start of Residual Heat Removal Pumps Under Certain Scenarios Due to Unrecognized Original Design Defect | 12-14-2018 | On 10/19/2018, DTE Electric Company identified that the Engineered Safety Feature Bus degraded voltage relay scheme could inhibit all Residual Heat Removal (RHR) pumps from automatically starting and performing the Low-Pressure Coolant Injection (LPCI) function during a Loss of Offsite Power (LOP) with a non-simultaneous Loss of Coolant Accident (LOCA). At the time, Fermi 2 was in Mode 4 and automatic LPCI function was not required. However, since this condition was present from original plant design and construction, the result is past inoperability of the Emergency Diesel Generators and RHR pumps in certain non-simultaneous LOP/LOCA scenarios. This is a reportable, unanalyzed condition prohibited by Technical Specification, and additionally represents a loss of safety function, single cause inoperability of independent trains and single cause inoperability in multiple systems. The safety significance of this event is very low due to the capability of the RHR pumps to be manually started. There were no radiological releases associated with this event. L The root cause was an original plant design defect. A design modification to correct the design defect was implemented and successfully tested on all four degraded voltage circuits between 10/22/2018 and 10/24/2018. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03312020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons 'eared are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43),U . S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of (See NUREG-1022, R.3 for instruction and guidance for completing this form M co a ll n e a c g ti e o m n e d nt o e a s nd n ot B d u i d s g p e la t, y W a a s c h u i r n re g n to tl n y , va D li C d 2 0 0 M 5 B 03 . con I t f r o a l m nu e m an b s e r, u s th e e d N t o R C im p m o a s y e n a o n t i c n o fo n r d m u a c t t i o o n r http://www.nrc.gov/reading-rm/doc-collections/nureqs/staff/srl022/r3/) sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000- NUMBER NO. Ferm12 341 2018 - 006:: - 00I | INITIAL PLANT CONDITIONS Mode - 4 Reactor Power - 0 percent There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT. On 10/19/2018 at approximately 0400 EDT, during investigation into failed Emergency Diesel Generator (EDG) [[DG]] surveillance tests for Loss of Offsite Power (LOP) with a Loss of Coolant Accident (LOCA), DTE Electric Company identified that the Engineered Safety Feature (ESF) Bus [[BU]] degraded voltage relay [[RLY]] scheme could inhibit all Residual Heat Removal (RHR) [[BO]] pumps [[P]] from automatically starting during a LOP with a non-simultaneous LOCA (LOP/LOCA). The LOP/LOCA surveillance tests for EDGs 11 and 12 had been performed on 10/18/2018 and had resulted in the trip of RHR pumps A and C, respectively. The subsequent engineering review identified a design flaw in the degraded voltage load shed relay scheme that caused the RHR pumps used for the Low-Pressure Coolant Injection (LPCI) function to trip and not be automatically restarted. The review identified that under certain sequences of events, the timing of the loss of voltage relay trip string, load shed, and EDG breaker closure, and the parallel timing of the degraded voltage relay scheme resulted in a degraded voltage load shed signal occurring during the operation of the EDG load sequencer. Parallel timing of the degraded voltage relay scheme resulted in a trip of the RHR pump due to the degraded voltage relay load shed signal being present concurrently with the RHR pump start. Operation of the degraded voltage relay scheme during a loss of power event is nonconforming to UFSAR Section 8.2.2.5.3, which states degraded grid relaying does not operate during load sequencer operation. DTE determined that this design flaw was common to all four EDG degraded voltage load shed circuits and affected both divisions of RHR. However, there was no impact on other loads automatically started by the sequencer, such as Core Spray (CS) [[BM]], since the degraded grid load shed signal cleared prior to CS initiation. Previous performances of the EDG LOP/LOCA surveillance procedures had been successfully performed in a scenario where the LOP and LOCA signals were initiated at the same time. Engineering review confirmed that the degraded voltage load shed relay scheme worked appropriately and automatic start of the RHR pumps was not inhibited in this scenario. The EDG LOP/LOCA surveillance procedures had been revised since their last usage in the previous refueling outage in 2017. The procedure revisions resulted in a testing sequence where a simulated LOP signal was initiated, and several minutes later after validation of a successful LOP test, a simulated LOCA signal was initiated. Under the revised test sequence, the EDG is supplying the safety related 4KV bus at rated voltage and frequency when the simulated LOCA signal is initiated. Due to the timing of the degraded grid relay scheme, the degraded voltage load shed signal is still present when the EDG breaker closes and the RHR pump is being sequenced onto the bus. Since the RHR pump breaker closes when the degraded voltage load shed signal is present, the RHR breaker immediately trips, which is consistent with the October 18, 2018 failed surveillance test results. The RHR System is designed to provide removal of reactor core decay heat and sensible heat from the reactor and containment during normal and postulated plant accident conditions. During postulated LOCA conditions, LPCI, an operating mode of the RHR system and part of the Emergency Core Cooling System (ECCS), provides core cooling by flooding the reactor core with water drawn from the suppression pool. Control logic is provided to automatically initiate the LPCI mode upon receipt of a low reactor water level and/or high drywell pressure signal. The objective of the ECCS, in conjunction with the containment, is to limit the release of radioactive materials should a LOCA occur. The ECCS consists | ML18348B118
Surry Power Station | Unit 1 | Windblown Debris Caused Transformer Fault Resulting in Auto-Start of Emergency Diesel Generator | 01-00-2018 | On October 11, 2018, at 23:04 hours, with Units 1 and 2 at 100% power, 'A' Reserve Station Service Transformer pilot wire lockout signal caused an undervoltage condition of the 1J emergency bus and the subsequent automatic start of the #3 Emergency Diesel Generator (EDG). The #3 EDG energized the 1J emergency bus loads as designed. At the time of the event, the site was experiencing rain and strong winds associated with Tropical Storm Michael. On October 12, 2018, after the high winds had passed, inspections and functional tests determined that no repairs to the electrical service system were required. Normal alignment of the #3 EDG and the primary off-site power supply to the 1J emergency bus were reestablished within 24 hours. Both Units 1 and 2 remained at 100% power. All equipment operated as designed. - An eight-hour non-emergency event notification was made to the NRC pursuant to 1.0 CFR 50.72(b)(3)(iv)(A) due to a valid actuation of the #3 EDG. This report is being made pursuant to 10 CFR 50. 73(a)(2)(iv)(A) due to a valid actuation of the #3 EDG. NRG FORM 366 (04-2017) Page -- 1 - of 3 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to the Information Services Branch :(T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to ln/ocollects. CONTINUATION SHEET Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office .of Management and Budget, Washington, DC 20503. If a (See NUREG-1022, R.3 for instruction and guidance for completing this form means used to impose an information collection does not display a currently valid 0MB control number, the NRG may not conduct or sponsor, and a person is not required .to respond to, the http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR NUMBER NO. Surry Power Station, Unit 1 05000- 280 . 2018 ~ 002 00 | 1.0 DESCRIPTION OF THE EVENT On October 11, 2018, the site was experiencing rain and strong winds associated with Tropical Storm Michael. At 23:04 hours, with Units 1 and 2 operating at 100% power, a 'B'. phase to ground pilot wire lockout signal on the 'A' RSST [EIIS-EA-XFMR] resulted in electrical isolation of the 'A' RSST, the 'D' Transfer Bus, and the Unit 1 'J' Emergency Bus. Emergency bus 1J [EIIS-EK-BU] was de-energized due to the normal bus supply breaker [EIIS-EK BKR] opening on the UV signal. The UV signal initiated the automatic start sequence for the #3 Emergency Die~el Generator (EOG) [EIIS-EK-DG] and energized the 1J bus, as designed. All 1J emergency busloads were verified to be in proper alignment. All e.quipment performed as expected. · .A.t the time of the pilot wire lockout signal, an individual witnessed a flash in the area of the RSSTs. A piece of charred roofing insulation was found in the area, but no smoke or flames were observed. It was subsequently determined that roofing material ha,d become airborne during the storm and contacted the bus work associated with 'A' RSST initiating the lockout signal. '·', '; Post event testing.of the 'A' RSST was .completed satisfactorily; and no repairs were required .. On. October 12, 2018, at 22:05 hours,.after the 1J 4160, V emergency bus normal power supply was reestal:>lishecUhe #3 EOG was ~ecured and returned to normal. automatic standby alignment: · , , ., . _ .. - , . .., . , ·. ; ,. . ·,· .. . •:. ~ ' •, An eight-h9ur non-emergency event notification was made-to the ,,NRG pursuant to 10 CFR 50. 7'2(b)(3)(iv)(A) due to a validactuaUon_oUhe #3 EOG. This report is being-made pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to a valid actuation of the #3 EOG. 2.0 SIGNIFICANT SAFETY CONSEQUENCES AND IMPLICATIONS During the event, the redundant 1 H 4160 V emergency bus was supplied by normal off-site power. Also, the Unit 2 4160 Vemergency busses, 2H and 2J, were supplied by normal off-site power. The #1, #2, and #3 Emergency Diesel Generators remained available to supply power to emergency bus loads. All equipment performed as designed, and the normal eqlJipment alignment was _restored by the Operations team in .a timely manner. Therefore this event is of minimal safety significance. 3.0 CAUSE OF THE EVENT It was determined that the roofing material which had contacted the RSST had originated from a breach in the roofing system on the northwest end of the Unit 1 Turbine Building. The roof is constructed with a foam insulation layer covered by a Hypalon elastomeric liner, which is held in place at a parapet with adhesive_ and mechanical fasteners. During the storm, winds peeled back the roof parapet flashing cap, exposing the Hypalon liner edges. The wind induced air pressure lifted the liner and mechanical fasteners from the roof uncovering the insulation sheets. The insulation became airborne and contacted the 'A' RSST causing the lockout signal. The roof insulation material matched the charred material found near the RSST. | ML18351A089
Susquehanna Steam Electric Station | Unit 1 | Standby Liquid Control Valve Failed Surveillance Test | 01-09-2018 | During the performance of the quarterly flow verification, the 1A Standby Liquid Control (SBLC) Pump could not obtain the Technical Specification required flow of 40 gallons per minute due to the SBLC Injection Pump 'A' Discharge Pressure Relief Valve (PSV148F029A) lifting and being unable to reseat itself. This failed to meet the requirements of Technical Specification Surveillance Requirement 3.1.7.7 and consequently, the 1A SBLC pump was declared inoperable. This condition is being reported in accordance with 10 CFR 50. 73(a)(2)(i)(B) as a condition prohibited by technical specifications and 10 CFR 50. 73(a)(2)(v)(A) as a condition that could have prevented fulfillment of a safety function. The 'B' train of Standby Liquid Control had been unavailable during the time the 'A' was inoperable. The cause of the event was determined to be inadequate work instructions for installing the insulation on the associate.d relief valves. Corrective actions include additional guidance for installing insulation around the relief valves. There were no actual safety consequences associated with this event. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, CONTINUATION SHEET ~ ~ the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of (See NUREG-1 022, R.3 for instruction and guidance for completing this form Management and Budget, Washington, DC 20503. If a means used to impose an information http://www. nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1 022/r3{) collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station Unit 1 05000-387 NUMBER NO. 2018 006 01 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, approximately 95 percent Rated Thermal Power Unit 2 - Mode 1, approximately 98 percent Rated Thermal Power As part of the surveillance the 18 Standby Liquid Control Pump was taken out of service. While this did not impact the operability of the 1A Standby Liquid Control Pump it does affect the reporting criteria. EVENT DESCRIPTION During performance of quarterly Standby Liquid Control (S8LC) flow verification, on September 26, 2018 at approximately 1023, the 1A S8LC Injection Pump 'A' Discharge Pressure Relief Valve [EllS: RV] lifted after the 1A S8LC pump [EIIS:P] was started. The relief valve was unable to reseat itself, resulting in failure to meet Technical Specifications (TS) Surveillance Requirement (SR) 3.1.7.7 minimum required flow rate of 40 gallons per minute (gpm) and consequently, the 1A S8LC pump was declared inoperable. Maintenance technicians observed that the insulation [EllS: INS] surrounding the relief valve was in contact with its reset arm. Performance data indicates a rapid decrease in S8LC flow approximately 2 minutes after the initial pump start, and is believed to be the point of the relief valve lifting. The insulation had been re-installed during the Unit 1 Refuel outage on April 27, 2018. This event is being reported as a condition prohibited by technical specification since insulation interference had existed and in the event of relief valve actuation, the 'A' train would have been inoperable longer than the technical specification completion time. Even though both trains were taken out of service as part of a planned surveillance, the condition of the insulation was discovered during the surveillance which led the 'A' train to be considered inoperable. This is being reported as a condition that could have prevented the fulfillment of a safety function since the '8' S8LC pump was taken out of service during the time frame after the insulation had been re-installed. Specifically, on June 28th for a quarterly surveillance and on July 26 for maintenance. Maintenance replaced the S8LC Injection Pump 'A' Discharge Pressure Relief Valve and corrected the insulation configuration. As found bench testing was performed on the originally installed relief valve on 10/1/18 which satisfactorily passed lift checks. CAUSE OF EVENT The cause of the event was determined to be inadequate work instructions on installing the insulation. There was no information in the routine task instructions advising the insulators on the impact the insulation could have on the moving parts of the valve. | ML18353A430
Clinton Power Station,.Unit 1 05000461 1 OF 5 | Unit 1 | Division 3 Shutdown Service Water Pump Start Failure | 12-18-2018 | On June 15, 2017, Clinton Power Station (CPS) commenced procedure CPS 9069.01, Shutdown Service Water Operability Test. The purpose of this procedure is to verify operability of the Division 3 Shutdown Service Water (SX) System Pump 1S X01 PC and selected valves per the lnservice Testing program on a quarterly basis. At 0958, SX pump 1S X01 PC was started and after approximately 30 seconds, it tripped due to thermal overload. The pump was declared inoperable and Operations entered Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.7.2, Condition A which requires the High Pressure Core Spray (HPCS) system to be declared inoperable and enter TS LCO 3.5.1 Condition B which requires verification by administrative means that the Reactor Core Isolation Cooling (RCIC) system is operable and within 14 days restore the HPCS system to operable status. The cause of the event was an incremental increase in internal pump resistance that could not be overcome by the developed torque of the motor starting from standby conditions. This increased pump resistance was due to unidentified impacts during a design modification (i.e., dry packing at pump start, unidentified corrosion effects on packing shaft sleeve, and inadequate hard-face material). Another root cause was the untimely implementation of a corrective action that resulted from a 2014 causal evaluation due to inadequate procedure guidance. Corrective actions have been completed to restore operability of 1S X01 PC and ensure failure mechanisms introduced by design changes have been assessed. This event is reportable under 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented the fulfilment of a safety function and 10 CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: BO hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Seivices Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid 0MB control number, the NRG may not conduct or http://www.nrc.gov/readinq-rm/doc-collections/nuregs/staff/sr1022/r3Q sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Clinton Power Station, Unit 1 05000461 NUMBER NO. I 2017 - 008 01 | PLANT AND SYSTEM IDENTIFICATION General Electric -- Boiling Water Reactor, 3473 Megawatts Thermal Hated Core Power Energy Industry Identification System (EIIS) codes are identified in text as [XX]. EVENT IDENTIFICATION Division 3 Shutdown Service Water Pump Start Failure A. Plant Operating Conditions Before the Event Unit: 1 Event Date: 6/15/17 Event Time: 0958 Mode: 1 Mode Name: Power Operation Reactor Power: 97 percent B. Description of Event On June 15, 2017, Clinton Power Station (CPS) attempted to perform the quarterly surveillance test of the Division 3 shutdown service water (SX) [Bl] pump [P] (1 SX01 PC). The pump ran for approximately 30 seconds before thermal overloads tripped the pump motor [M]. At 0958, Operators declared the Division 3 SX, Division 3 Emergency Diesel Generator (EOG) [EK], Division 3 Inverter [EF], Division 3 Direct Current Distribution [EJ], Division 3 Alternating Current Distribution [ED], and the High Pressure Core Spray (HPCS) [BG] system inoperable due to the pump trip. Operators entered the Technical Specification Actions Requirements for Limiting Condition for Operation (LCO) 3.7.2 and LCO 3.5.1, ECCS - Operating. Operators verified within one hour that the Reactor Core Isolation Cooling (RCIC) system was operable and entered the action to restore HPCS to operable status within 14 days. A second pump run was attempted with video recording that showed the motor spinning the shaft more quickly for the first rotation, then immediately slowing down to approximately 70 RPM. The run lasted approximately 8 seconds before the pump was manually secured. At 2220 hours, Operators completed an 8-hour non-emergency notificatio·n to the NRC (Event Notification Number 52806) under 10 CFR 50.72(b)(3)(v)(D) due to the loss of a single train safety system, that is, inoperability of the HPCS system function. This event is reported under 1O CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications and under 1O c·FR 50.73(a)(2)(v)(D) as a condition that could have prevented the fulfillment of a safety function. This is because the Division 3 SX pump was potentially inoperable greater than the 14 days allowed for an inoperable HPCS system by TS 3.5.1 Condition B, (last successful run of the Division 3 SX ·pump was on March 15, 2017, prior to pump failure on June 15, 2017, and return to service on June 23, 2017). This condition could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. | ML18354A733
River Bend Station | Unit 1 | Inadvertent Initiation of Reactor Core Isolation Cooling due to Personnel Error | 12-31-2018 | On November 2, 2018 at 03:53 technicians were performing a Surveillance Test Procedure on the Reactor Core Isolation Cooling (RCIC) system with the reactor operating at 94% power. Improper completion of a procedure step caused an inadvertent initiation of the RCIC system. The initiation was recognized as inadvertent and was secured. The RCIC system was restored to a normal standby lineup. RCIC injected into the Reactor Pressure Vessel (RPV) for approximately 30 seconds. A two inch RPV level increase was observed. No change in feedwater temperature or reactor power was noted. The cause of the initiation was attributed to human error. This event was of minimal significance to the health and safety of the public. NRC FORM 366 (04-2018) NRC FORM 36~A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to oomply with this mandatory oollection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are inoorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U. S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of (See NUREG-1022, R.3 for instruction and guidance for completing this form Management and Budget, Washington, DC 20503. If a means used to impose an information http"//www nrc goy/reading-rm/doc-coUecUons/nuregs/staff/sr1022/r3/) collection does not display· a currently vaud 0MB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 05000-1 " CYEAJR SEQUENTIAL REV ~-I NUMBER 1-NO0. River Bend Station - Unit 1 458 I 009 | BACKGROUND The Reactor Core Isolation Cooling (RCIC) [BN] system is designed to operate either automatically or manually following Reactor Pressure Vessel (RPV) (**RCT**) isolation accompanied by a loss of coolant flow from the Feedwater [SJ] system to provide adequate core cooling and control of RPV water level. Under these conditions, the High Pressure Core Spray (HPCS) [BG] and RCIC systems perfom1 similar functions. The RCIC system consists of a steam driven turbine (**TRB**) pump unit, piping, and valves to provide steam to the turbine, as well as piping and valves to transfer water from the suction source to the core via the Feedwater system piping. The steam supply to the turbine is piped from main steam line A, upstream of the inboard main steam line isolation valve. The RCIC system is designed to provide core cooling for a wide range of reactor pressures, 150 psig to 1231 psig. Upon receipt of an initiation signal, the RCIC turbine accelerates to a specified speed. As the RCIC flow increases, the turbine control valve is automatically adjusted to maintain design flow. REPORTED CONDITION ' On November 2, 2018 at 03:53, with the reactor operating at 94% power, RCIC was inadvertently initiated and injected water into the RPV. At the time of initiation, plant technicians were performing a Surveillance Test which inserts a half initiation signal for RCIC by installing a test fixture in the start logic circuitry. The Surveillance Test Procedure (STP) was not correctly followed and the wrong test fixture was installed by the technicians. Installation of the incorrect test fixture inserted a half initiation from a channel of the start logic that was not part of the test procedure. The technicians then manually inserted a half initiation signal in accordance with the STP. The combination of the manual initiation signal and the signal created-from the installation of the incorrect test fixture met the start logic requisite and the RCIC start sequence began. The Main Control Room staff recognized the initiation, validated the initiation to be inadvertent, and took actions per the appropriate abnormal operating procedure. RCIC was secured and restored to a normal standby lineup. RCIC injected into the RPV for approximately 30 seconds at a maximum rate of approximately 600 gallons per minute (gpm). A two inch RPV level increase was observed. No change in feedwater temperature or reactor power was noted. CAUSAL ANALYSIS This event was caused by incorrect performance of an STP. The technicians performing the test procedure failed to use proper verification practices in accordance with site procedures. The STP clearly states to install the "Red A/B" test fixture. The "Green B/C" test fixture was installed instead despite distinct labeling attached to both test fixtures. Installation of the test fixture was identified as a critical step in the STP. Site Human Performance procedures require that a verification from a second person is performed on critical steps to ensure the action is completed correctly. Although the STP did not indicate the need for a verification, the Human Performance procedure requirement to perform the verification was still active. CORRECTIVE ACTION TO PREVENT RECURRENCE The following actions have been completed to prevent recurrence. • An extent of condition was performed to identify any other STPs that do not require a verification before installing a test | ML19003A143
River Bend Station | Unit 1 | Reactor Scram due to Turbine Control Valve Failure | 01-09-2019 | On November 10, 2018 at 00:46, with the reactor operating at 100% power, Turbine Control Valve number 3 (CV3) unexpectedly closed. Turbine Control Valve number 4 (CV4) did not respond as designed and the reactor automatically scrammed on a reactor vessel high pressure signal. Following the scram, all major systems responded as designed. The CV3 closure was due to failure of the valve's push rod spring housing coupling bolts. The CV4 failure to correctly respond to the CV3 closure transient was due to incorrect operating procedure guidance. This event was of minimal significance to the health and safety of the public. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the lnfonnation Services Branch (T-2 F43), U. S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555--0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150--0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currenUy valid OMB control number, the NRG may not conduct or http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required lo respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER DYEA R SEQUENTIAL REV River Bend Station - Unit 1 458 05000-1 o-1 NUMBER 1- N G O. °10 I | BACKGROUND Steam is delivered to the High Pressure (HP) turbine (**TRB**) through the Main Stop Valves (MSVs) (**SHV**) and the Turbine Control Valves (CVs) (**SCV**). There are four MSVs that shut off steam to the turbine under trip conditions. The four CVs are used to control the load on the turbine. The exhaust from the HP turbine is sent to the Moisture Separator/Reheaters (MSRs) (**MSR**) to improve the quality of the steam prior to being delivered to the Low Pressure (LP) turbines. Steam leaving the MSRs flows into the LP turbines through the four Combined Intermediate Valves (CIVs). Each CIV is made up of two valves, an Intermediate Stop Valve (ISV) and an Intercept Valve (IV). The Electro-Hydraulic Control (EHC) [JI] System controls the position of large steam valves by means of electrical signals that change the hydraulic fluid flows of the positioning components of the valves. The EHC System is controlled by inputs from Ovation software using a valve positioner module. The modulating valves controlled by the EHC System are MSV2, IV1, IV2 and the four CVs. The EHC load limit function bounds the steady state open position of the CVs to limit the flow of steam to the turbine. Operators manually enter the desired load limit value from an EHC system graphic display interface. During no~mal plant operation at 100% power, three CVs are full open and one is approximately 30% open. If one of the full open CVs should unexpectedly close, the Turbine Bypass Valves and partially closed CV will open to control reactor vessel pressure. h"he CV operating mechanism utilizes a spring assembly which acts directly on the valve stem to hold the valve closed. The valve is then mechanically opened by a hydraulic cylinder which lifts the end of a lever with a push rod. Spring force opposes the hydraulic force on the push rod. The springs are compressed as the hydraulic pressure pushes the push rod up to open the valve, thus increasing the compressive force exerted by the springs. h"he push rod spring housing coupling joint consists of two rigid members held together by 20 bolts. One of the rigid members in the push rod spring housing coupling is the switch arm. REPORTED CONDITION On November 10, 2018, the reactor was operating at 100% power with CV1, CV2, and CV3 full open and CV4 27% open. ~t 00:46 CV3 unexpectedly closed. Both Main Turbine Bypass Valves fully opened as designed. CV4 did not open as designed which resulted in an automatic reactor scram on high reactor vessel pressure. There were no maintenance activities being performed on the EHC System or CVs prior to or during the event. PREVIOUS OCCURRENCE EVALUATION On April 23, 2012, CV3 unexpectedly closed. The other three CVs and Turbine Bypass Valves responded as designed. Operators stabilized the plant and a planned outage was later executed to repair CV3. The cause of the CV closure was determined to be failure of the push rod spring housing coupling bolts. One of the root cause evaluation failure analysis recommendations was to ensure that the bearing surface is flat with a slope of less than 1 :20 as recommended by the | ML19009A412
Peach Bottom Atomic Power Station | Unit 3 | Reactor Coolant System Pressure Boundary Leakage Resulting in Technical Specification Required Shutdown | 12-21-2018 | On 9/21/18, the High Pressure Coolant Injection (HPCI) system was declared inoperable due to two inoperable differential. pressure indicating switches that are used for isolating HPCI in the event of a break in the HPCI turbine steam line. A containment entry was made and it was determined that the instruments were incapable of performing their design function due to a leak on a one-inch diameter pressure sensing line. The line is a reactor coolant system pressure boundary, resulting in a Technical Specification required shutdown in order to repair. - The cause was determined to be vibration-induced fretting of the instrument line by a support bracket. The section of the pipe with the leak was replaced. There were no actual safety consequences as a resultr'oftbis event. NRC FORM 366 (04-2018) NRC FORM .366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid 0MB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r30 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Peach'Bottom Atomic Power Station Unit 3 05000278 NUMBER NO. 2018 - 002 1 | Unit Conditions Prior to the Event Unit 3 was operating in Mode 1 at approximately 100% rated thermal power. There were no structures, systems or components out of service that contributed to this event. Description of Event On 9/20/18 at approximately 1930 hours, an Equipment Operator, during normal rounds, identified that differential pressure switches DPIS-3-23-076 and DPIS-3-23-077 [EIIS:PDS] for the High Pressure Coolant lrijectio_n (HPCI) system [EIIS:BJ] were reading lower than expected. Upon further review and investigation, it was determined that the switches would-not have been able to perform their Technical Specification (TS) 3.3.6.1 required function of isolating the HPCI steani line in the event of a break. The two switches were declared inoperable on 9/21 /18 at approximately 1755 hours and were inoperable for approximately 22-1/2 hours as a result of this event. Required actions of TS 3.3.6.1 were performed, including isolation of HPC.1 steam line. As a result of the isolation, TS 3.5.1 Condition C was entered for HPCI being inoperable, which requires the system to be restored within 14 days. Further analysis of the low differential pressure indicated on the DPISs suggested a possible leak of the instrument line upstream of the DPISs. This was supported by a small increase in measured drywell leakage that was identified on 9/20/18. A reactor power reduction to 35% was initiated on 9/22/18 at 0200 hours to support an entry into the drywell. The drywell inspection verified leakage of the 1-inch diamet.er instrument line (Schedule 80, Type 304 stainless steel), which is a reactor coolant system pressure boundary. TS 3.4.4 Condition C was entered at 0955 hours on 9/22/18, which requires the unit to be in Mode 3 in 12 hours and Mode 4 in 36 hours. A controlled shutdown was initiated and the unit entered Mode 3 at 2029 hours on 9/22/18 and Mode 4 at 0701 hours on 9/23/18. The lea!< was located at a point where the instrument line was supported by a rectangular shaped bracket. Vibration had caused the bracket to wear the instrument line, eventually resulting in a through-wall steam leak. The section of pipe that contained the leak was replaced. Similar small-bore piping was inspected and repairs performed as necessary. Following repairs, a normal startup was commenced and Unit 3 entered Mode 1 at 1638 hours on 9/25/18. Analysis of Event This event is being reported in accordance with the following: • 1O CFR 50.73(a)(2)(i)(A) - the completion of any nuclear plant shutdown required by the plant's Technical Specifications. TS 3.4.4 Condition C;reqb.lires the unit to be in Mode 3 within 12 hours for any reactor coolant-system pressure boundary leakage. This TS action was entered on 9/22/18 at | ML19010A037
Peach Bottom Atomic Power Station | Unit 2 | Emergency Diesel Generator Exhaust Stacks Nonconforming Design for Tornado Missile Protection | 12-21-2018 | On 1/9/17, it was determined that the site's Emergency Diesel Generators do not conform with the licensing basis for protection against tornado generated missiles. The exhaust stacks for the four on-site diesel generators extend approximately seven feet above the roof of the diesel generator building. In the event of a tornado, debris generated from the tornado could strike the exhaust stacks and, if at a sufficient mass and velocity, could crimp the exhaust stacks in a manner that would affect diesel generator operation. An extent of condition review identified unprotected cables that could be impacted by a tornado and affect the ability to maintain safe shutdown. As a result of the non-conforming conditions, on 1/ 9/17 at 1530, all four emergency diesel generators were declared inoperable and on 11/1/18, the Reactor Core Isolation Cooling system and the RHR Suppression Pool Cooling system were declared inoperable. Compensatory measures were put in place and, in accordance with NRC guidance contained in EGM 15-002, the equipment was returned to an operable but non-conforming status. Long-term corrective actions are being evaluated in accordance with EGM 15-002 and the plant's licensing basis. There are no actual consequences as a result of the non-conforming condition. NRG FORM 366 (06-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 10/31/2018 (06-2016)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 LICENSEE EVENT REPORT (LER) F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and·to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid 0MB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http://www. n re. gov/ reading-rm/doc-collections/nuregs/staff/s r1 022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Peach Bottom Atomic Power Station Unit 2 05000-277 YEAR NUMBER NO. 2017 - 001 - 01 | Unit Conditions Prior to the Event Unit 2 and Unit 3 were both operating in Mode 1 at approximately 100% r9,ted thermal power. There were no structures, systems or components out of service that contributed to this event. Description of Event On 1/9/17, based on an engineering analysis, it was determined that the site's four Emergency Diesel Generators [EIIS: DG] do not conform with the licensing basis for protection against tornado generated missiles. As a result, one or more of the diesel generators may not have been able to perform their safety design function if a tornado were to impact the site and if debris of sufficient mass and velocity were to strike the diesel engine exhaust stacks. As a result of the non-conforming condition, on 1/9/17, at 1530, all four emergency diesel generators were declared inoperable in accordance with Technical Specification (TS) 3.8.1. With two or more diesel generators inoperable, TS 3.8.1 Condition F requires all but one to be restored to an operable status within two hours, or per Condition G, be in Mode 3 in 12 hours. Compensatory measures were verified as being in place in accordance with NRC guidance contained in EGM 15-002, "Enforcement Discretion for Tornado-Generated Missile Protection Noncompliance" (ML 15111 A269). As allowed by the EGM, the Emergency Diesel Generators were immediately returned to an operable but non-conforming status. Following identification of the EOG stack vulnerability, a walkdown of the site was performed to identify any other non-conforming conditions. Three rooms that contain safety-related cables associated with equipment needed for safe shutdown following a tornado were identified as non-conforming. Two of the rooms ("MG-Set rooms"), adjacent to each unit's reactor building, have an exterior wall that is steel panel on I-beam construction, which does not conform with the site's licensing basis. The third room, a fan room in the Radwaste Building; between the two MG-Set rooms, has an exterior wall that consists of louvers that do not provide adequate protection from tornado generated missiles. As a result of the non-conforming conditions that affect equipment required for safe shutdown following a tornado, on 11/1/2018, the Reactor Core Isolation Cooling (RCIC) [EIIS:BN] system and the RHR Suppression Pool Cooling [EIIS:BT] system were declared inoperable for both units. Technical Specification (TS) 3.5.3, Condition A was entered for an inoperable RCIC system and TS 3.6.2.3, Condition C was entered for two inoperable RHR Suppression Pool Cooling subsystems. Compensatory measures described in EGM 15-002 were verified as being in place and, as allowed b·y the EGM, the systems were immediately returned to an operable but non-conforming status. EGM 15-002, along with Interim Staff Guidance DSS-ISG-2016-01, "Clarification of Licensee Actions in Receipt of Enforcement Discretion Per Enforcement Guidance Memorandum EGM 15-002" (ML 15348A.202), provide guidance from the NRC for acceptable compensatory measures that licensees· can put in place if equipment is determined to be inoperable as a result of tornado generated missiles. | ML19010A038
Calvert Cliffs Nuclear Power Plant | Unit 2 | Both Unit 2 Emergency Diesel Generators Inoperable Due to Depressurization in Common Air Start Headers | 01-09-2019 | On October 11, 2018, during a post maintenance start of Unit 1 Emergency Diesel Generator (EOG) 18, its air start control valves failed to shut as designed. This caused air pressure in the common air start headers, shared with both Unit 2 EOGs, to depressurize to. a point that rendered both Unit 2 EOGs inoperable. Operations isolated EOG 18 air start control valves which resulted in air start pressure returning to normal on both Unit 2 EOGs. This event resulted in a loss of safety system function for Unit 2 EOGs to exist for 30 minutes. The cause was due to a diode shorting in EOG 18 air start control circuitry which caused two fuses in the circuitry to fail, thus preventing relays to shut the air start control valves. The diode was installed in the air start circuitry during this EOG 18 maintenance period to suppress induced voltage observed with newly installed control relays. The apparent cause of the diode failure was due to an undetected manufacturing defect. This event revealed a previously unknown design vulnerability in the circuitry where failure of a single fuse, at a specific time in the EOG start interval, could cause loss of air start pressure to the other EOGs that share the common air start headers. Corrective actions taken included removal of the new diodes and relays from the control circuitry and installation of isolation valves in the common air start headers. · NRG FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported ,:P..,,.'R.REGc,4>'0 lessons learned are incorporated into the licensing process and fed back to industry. Send comments t:t ""' LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory f- ~ ....... CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to Ii, the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of ') Management and Budget, Washington, DC 20503. If a means used to impose an information collection (See NUREG-1022, R.3 for instruction and guidance for completing this form does not display a currently vaiid 0MB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. httQ://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3!'.) 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR NUMBER NO. Calvert Cliffs Nuclear Power Plant, Unit 2 05000318 - - 2018 001 01 | PLANT AND SYSTEM IDENTIFICATION Calvert Cliffs Nuclear Power Plant, Units 1 and 2, are Combustion Engineering Pressurized Water Reactors with a licensed maximum power level of 2737 megawatts thermal. The Energy Industry Identification System codes used in the text are identified as [XX]. A. CONDITION PRIOR TO EVENT Units 1/2 Date: October 11, 2018 Power level: 100 percent/100 percent Mode: 1/1 There were no structures, systems, or components out-of-service that contributed to this event. 8. DESCRIPTION OF EVENT Calvert Cliffs has four Emergency Diesel Generators [DG] (EOG) and one Station Blackout diesel generator. Three of the EDGs (EDGs 1B , 2A, and 28) are Fairbanks Morse (FM) diesels. Emergency Diesel Generator 1A and the Station Blackout diesel (DG OC) are Societe Alsacienne De Const~uctions Mecaniques De Mulhouse CM diesels. Each u~1 it has two EDGs that automati,lly provide backup electrical power to a Safety Relate (SR) 4 KV bus [BU] on an under voltage si nal or on a Safety Injection Actuation Signal. Diesel Generator .OC can be manually aligned t any of the SR 4 KV busses as needed. . . Each of the three FM EDGs has two ·independent and redundant air receivers [RCV] which s·upply starting air to each EOG through two parallel air start control valves [CV]. The air start headers for all three FM EDGs are connected together. Emergency Diesel Generator 1A and DG OC have their own separate air start systems and were not impacted by this event. On October 11, 2018, Operations was performing a post maintenance slow speed start of EOG 1B , when EOG 1 B's air start control valves did not go shut after EOG 1B was started. At 2303, this resulted in air pressure in the common FM air start headers to depressurize to a point where there was insufficient pressure to start either Unit 2 EDGs and thus Operations declared EDGs 2A and 28 inoperable. Operations was able to manually isolate EOG 1B air start control valves which allowed pressure in the common air start headers to recover. At 2333 pressure was sufficiently restored and EDGs 2A and 28 were declared operable. During the maintenance period preceding this post maintenance test on EOG 1B , Calvert Cliffs replaced the existing Agastat relays [RL Y] in EOG 1 B air start control circuit with Allen Bradley electronic relays. Additionally, diodes [EB] were installed in EOG 1B air start control circuitry to help dampen induced voltage spikes that had occurred after the electronic relays were previously installed on EOG 28. The air start CVs are normally closed and open on receipt of a diesel start signal when their associated solenoid valves [SV] are energized-by relays in the air start control | ML19015A019
LaSalle County Station | Unit 2 | Manual Reactor Scram due to Main Condenser Vacuum Degradation | 01-15-2019 | On August 31, 2018, while operating at approximately 29 percent power, a reactor manual scram signal was inserted on Unit 2 due to main condenser vacuum degrading. The turbine was tripped following the scram. During the scram, one control rod did not fully insert but was manually fully inserted. The plant was in a stable condition, with reactor pressure being maintained by the turbine bypass valves, and reactor water level was controlled using feedwater. Except for the single control rod insertion, required safety systems and shutdown equipment performed as expected, and there was no impact to Unit 1. This condition was reported on August 31, 2018 (ENS 53576) in accordance with 10 CFR 50.72(b)(2)(iv)(B) for a reactor protection system (RPS) actuation. This condition is reportable in accordance with 10 CFR 50. 73(a)(2)(iv)(A) as a condition that resulted in a valid actuation of the RPS. The condition was attributed to localized impingement degradation of a turbine building miscellaneous equipment drain header resulting in through-wall failure. Corrective actions were taken to install a robust welded temporary patch on the drain header, with a header replacement scheduled for the upcoming Unit 2 refueling outage L2R17 (2019), and revise procedures to incorporate lessons learned. A root cause investigation identified additional corrective actions necessary to address weaknesses in the original design of the header susceptibility to localized impingement (on both units}, revisions to training materials and procedures, and training and communications to engineering staff regarding piping failure mechanisms. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply v.ith this mandatory collection request: 80 hours. Reported lessons teamed are incorporated into the licensing process and fed back to industry. Send convnents LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocotlects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. http://www.nrc.gov/readinq-rm/doc-collections/nureqs/staff/sr1022/r3D 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR NUMBER NO. LaSalle County Station, Unit 2 05000374 2018 - 001 01 | PLANT AND SYSTEM IDENTIFICATION LaSalle County Station Unit 2 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the main condenser and turbine building equipment drains (TE) system. Specifically affected was the miscellaneous drain header (2TEC5A) from the A and B turbine-driven reactor feed pump (TDRFP) steam supply drain lines. CONDITION PRIOR TO EVENT Unit(s): 2 Date: August31,2018 Time: 2105 CDT Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 29 percent DESCRIPTION On August 31, 2018, at approximately 29 percent power and during a controlled unit shutdown to support a planned maintenance outage L2M20, a reactor manual scram signal was inserted due to main condenser vacuum degrading. The turbine was tripped following the scram. Main condenser vacuum was at approximately six inches mercury (Hg) of back-pressure and slowly improving following the scram and turbine trip. During the scram, one control rod (30-31) did not fully insert. This control rod was manually inserted to notch position 00 (fully inserted), with the first position identified as notch position 24 of 48 (fully withdrawn). The plant was in a stable condition, with reactor pressure being maintained by the turbine bypass valves, and reactor water level was controlled using feedwater. Four weeks prior to the event, on August 3, 2018, Unit 2 off-gas flow suddenly increased to an abnormal level. A leak (approximately 3-inch diameter hole) was identified on a miscellaneous drain header 2TEC5A, in the heater bay. A temporary repair consisting of an 8-inch pipe that was cut in half to form a patch for the bottom of the header was installed. The fabricated patch included a clamping mechanism and a vent valve to divert the steam during its installation. The patch brought off-gas flow back down to normal. As steam inputs into the header were removed during the unit shut down four weeks later, the dynamics at the patch changed which allowed air in-leakage to increase. When water was added via the TDRFP gland steam loop seal, air in-leakage was again significantly reduced at the patch. However, as more inputs changed to a vacuum, there was increased air in-leakage. This, combined with other air in-leakage sources, such as the steam packing exhauster (SPE) loop seal not being full, eventually led to the degradation of main condenser vacuum requiring an unplanned manual scram. CAUSE The causal investigation determined the root cause was the original design of the miscellaneous drain header 2TEC5A is susceptible to localized impingement degradation, which resulted in through-wall failure. The 2TEC5A header has inputs from two, one-inch orifices that provide continuous superheated steam into the 2TEC5A header from the 2A and 28 TDRFP low-pressure steam supply drain lines. One of the inputs discharges directly over the hole that developed in the bottom of the 2TEC5A header, and the other is within a few inches. These inputs create high velocity localized impingement that structurally weakened the header to the point of failure. Contributing causes included weaknesses with the vendor following purchase order requirements, SPE loop seals that have been a historical source of air in-leakage to the condenser, ineffective communication between site Engineering and the affected organizations during L2R16 which resulted in inaccurate recommendations, and inadequate technical review of the temporary leak repair evaluation that did not anticipate or account for changing conditions in the header during the Unit 2 shutdown process. A separate causal investigation evaluated the control rod 30-31 failure to fully insert during the manual reactor scram. The cause was determined to be a lack of explicit guidance and test data available for decision-making based on the aggregate impact of insert stall flows above 5.0 gpm and channel distortion on scram times. | ML19015A070
Browns Ferry Nuclear Plant | Unit 1 | Hiqh Pressure Coolant Injection Declared Inoperable due to Steam Supply Valve Isolation | 01-15-2019 | On July 9, 2018, during performance of surveillance procedure 1-SR-3.3.6.1.2(38), High Pressure Coolant Injection System Steam Supply Low Pressure Functional Test, an unexpected High Pressure Coolant Injection (HPCI) isolation occurred. The isolation was discovered at 1111 Central Daylight Time (CDT) during a walkdown of the Unit 1 Control Room when the Unit Operator identified that the inboard and outboard HPCI steam supply valves were closed. It was determined that the valves had closed at approximately 0958 CDT during performance of 1-SR-3.3.6.1.2(38). Unit 1 entered Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.5.1, ECCS -Operating, Condition C, at approximately 1111 CDT, which required restoring HPCI to operable status within 14 days and verification that Reactor Core Isolation Cooling (RCIC) is operable by administrative means. Following successful completion of the functional test, HPCI was placed in standby readiness lineup. The HPCI system was declared operable on July 10, 2018, at 1342 CDT. During the period of Primary Containment Isolation, the HPCI system was unable to perform its safety function. However, in an emergency, sufficient systems were available to provide the required safety functions. The most likely cause of the unexpected HPCI isolation during performance of the HPCI test was determined to be past operation of the HPCI steam supply low pressure switches at an electrical current level near the manufacturer's rating, which resulted in degradation of the switch electrical contacts. The degradation eventually resulted in momentary arcing during functional testing of an adjacent switch, which energized the downstream logic relays causing Unit 1 HPCI to isolate. The corrective action for this event is to revise procedures 1/2/3-SR-3.3.6.1.2(3B) to lift a wire for the pressure switch under test and then re-land the wire prior to moving to the next pressure switch. NRG FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION .. ·- --CH vml:I: l'IV. 31;,u-u IU4 Cl\rl"c;:,: U.01.01/.<U.<U (04-2018)) Estimated burden per response to comply with this mandatory collection request 80 oours. Reported lessons le11'Tled are incorporated into the licensing process and fed ba,k to industry. Send comments regarding burden estimate to the lnfoonation Services Branch (T- 2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 2055!>0001,or by e-mail to LICENSEE EVENT REPORT (LER) lnfocollects. Resource@nrc.gov, and to the Desk Officer, Office of lnfolTTlation and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budge~ CONTINUATION SHEET Washington, DC 20503. If a means used to ilf!)()Se an infoonation collection does not display a cLJTen11y valid OMS control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 1 05000259 NUMBER NO. 2018 - 004 01 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Unit 1, was in Mode 1 at approximately 100 percent rated thermal power. II. Description of Event A. Event Summary On July 9, 2018, at approximately 0920 Central Daylight Time (CDT), BFN Instrumentation and Control Maintenance personnel (MIG) commenced a scheduled High Pressure Coolant Injection (HPCl)[BJ] System Steam Line Supply Low Pressure Functional Test [WO 118568097/1-SR-3.3.6.1.2(3B)]. This Surveillance Requirement (SR) involves closing Pressure Switches (PS)[PS] 1-PS-073-0001A and 1-PS-073-0001C, which are in the logic circuit for automatic low-pressure induced closure of HPCI isolation valves [ISV]. At approximately 1111 CDT during a walkdown of the Unit 1 Control Room, the HPCI Steam Line inboard and outboard isolation valves (1-FCV-73-0002 and 1-FCV-73-0003)[FCV] were found closed. Operations personnel entered Abnormal Operating Instruction 1-AOl-64-2B, Group 4 HPCI Isolation. After investigation, it was found that the valves closed at 0958 CDT during performance of Surveillance Functional Test; therefore, HPCI was declared inoperable retroactive to 0958 CDT. The Primary Containment Isolation System (PCIS) Group 4 Isolation was subsequently determined to be caused by a deficiency on the PS which allowed the circuit to complete while another PS was taken closed for testing. In response to HPCI system inoperability, BFN, Unit 1, entered Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.5.1, Emergency Core Cooling Systems (ECCS) - Operating, which requires each ECCS injection/spray subsystem and the Automatic Depressurization System (ADS) function of six safety/relief valves to be operable in reactor Modes 1, 2, and 3. Condition C was entered due to HPCI inoperability, with required actions to immediately verify Reactor Core Isolation Cooling (RCIC)[BN] operable by administrative means and restore HPCI to operable status within 14 days. RCIC was verified operable by Operations personnel. On July 9, 2018, at 1310 CDT, MIG completed the HPCI System Steam Supply Low Pressure Functional Test satisfactorily. At 1342 CDT on July 10, 2018, Operations personnel declared HPCI operable and exited TS LCO 3.5.1 Condition C. The Tennessee Valley Authority (TVA) is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(v)(A), (B), and (D), as any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to shut down the reactor and maintain it in a safe shutdown condition, remove residual heat, or mitigate the consequences of an accident. NRG FORM 366A (04-2018) Page _2_ of _8_ | ML19015A071
LaSalle County Station | Unit 1 | Turbine Stop Valve Limit Switch Failure due to Lubricant Degradation | 01-15-2019 | During quarterly surveillances of turbine stop valve (TSV) limit switch number 3 (1 C71-N006C), the component exhibited degraded performance on May 20, 2018 and a failure on September 9, 2018. The component was replaced and sent offsite for component testing and failure analysis. The component failure analysis completed on November 16, 2018 determined the cause was attributed to degradation of the switch lubricant due to exposure from a high temperature environment, which established firm evidence that the sluggish performance exhibited in May 2018 was related to the failure in September 2018 and that a past inoperability condition existed. The component 1C 71-N006C is the TSV-3 Closure RPS channel A2 scram limit switch. This device is required by technical specifications to support LCO 3.3.1.1 function 8 (RPS) and LCO 3.3.4.1 (EOC-RPT). Each TSV position is monitored by two limit switches (for TSV-3, A2 and B1 channels). This condition results in the TSV-3 input to RPS A2 as well as one channel of the EOG- RPT trip being INOPERABLE. The appropriate LCO Conditions and Required Actions were entered and tracked. The RPS and EOC-RPT functions were maintained due to the redundant channels remaining OPERABLE. There were no reportability thresholds applicable to this issue at the time of the event, and there was no loss of safety function. The condition is reportable in accordance with 10 CFR 50.73{a){2)(i)(B) for operation or condition prohibited by Technical Specifications. Immediate corrective actions were taken to replace the component and restore the associated channel to OPERABLE. Additional actions included performance of a causal investigation, identification of a new limit switch model that has greater heat tolerance, with a component replacement schedule starting in 2019. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and led back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocotlects.Resource@nrc.gov, and to the Desk Officer, Office al Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office at Managemenl and Budget, Washington, DC 20503. If a means used to impose an inlormation (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. http://www.nrc.gov/reading-nn/doc-collections/nuregs/staff/sr1022/r30 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR NUMBER NO. LaSalle County Station, Unit 1 05000373 2019 - 001 00 | PLANT AND SYSTEM IDENTIFICATION LaSalle County Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the main turbine system. The affected component was the turbine stop valve (TSV) limit switch 1C 71- N006C. This is the limit switch for the TSV number 3 Closure Reactor Protection System (RPS) A2 channel. CONDITION PRIOR TO EVENT Unit(s): 1 Date: November 16, 2018 Time: 0000 CDT Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 100 percent DESCRIPTION On May 20, 2018, the limit switch on Unit 1 TSV-3 was found to be sluggish during surveillance testing. Troubleshooting performed witnessed the limit switch actuating arm failing to return to the relaxed position following movement of the TSV actuating rod assembly and the associated collar which interacts with the 1C 71-N006C limit switch. After the limit switch was re-lubricated with the lubricant utilized by the manufacturer during assembly and exercised, the switch performed as required. The limit switch is normally held in the actuated position during unit operation and is only allowed to return to the relaxed, shelf state position, once per quarter. A causal investigation was performed at the time of the May 2018 component performance issue, which recognized that historical performance issues for sluggish limit switches was due to heat-related degradation of the lubricant in the pivot area of the limit switch. Previous site experience with relubrication of sluggish limit switches had been successful in fully restoring limit switch function. It was also noted that the 1C 71-N006C component had been recently replaced in February 2018. Due to the limit switch having a short in-service period (i.e., less than three months), a new infant mortality failure mechanism was suspected. During surveillance testing performed on September 9, 2018, the switch failed to reposition or return to its shelf state. The component was replaced and sent offsite for component testing and failure analysis. The component failure analysis (documented in report dated November 16, 2018) verified the limit switch malfunction and determined the cause was attributed to degradation of the switch lubricant due to exposure from a high temperature environment, as was evidenced by dried lubrication. The testing facility also confirmed that the correct lubrication was used by the manufacturer for the component. This information established firm evidence that the sluggish limit switch operation during the May 2018 event and the September 2018 malfunction were related. CAUSE The failure analysis functionality testing verified the limit switch malfunction. The limit switch was sluggish and failed to return to shelf state. Based on the internal component inspections, the failure mode was attributed to: • Degradation of the limit switch lubricant due to exposure from a high temperature environment, as evidenced by dried lubrication. • Fretting of the cam shaft I bushing likely caused by vibration experienced in the operating environment exacerbated by the lack of lubrication. • 20 inch-pounds CCW torque was required for switch and contact activation, which is less than the expected 27 inch-pounds of torque from Namco Operational Data. REPORTABILITY AND SAFETY ANALYSIS The component 1C 71-N006C is the TSV-3 Closure RPS channel A2 scram limit switch. This device is required to be OPERABLE per LCO 3.3.1.1 function 8 (RPS) and LCO 3.3.4.1 (EOC-RPT). TSV-3 was fully closed during the surveillance, which should have resulted in the 1 C71-N006C switch being open. Each TSV position is monitored by two limit switches (for TSV-3, A2 and B1 channels). This condition results in the TSV-3 input to RPS A2 as well as one channel of the EOC-RPT trip being INOPERABLE. The appropriate LCO Conditions and Required Actions were entered and tracked. The RPS and EOC-RPT functions were NAC FOAM 366A (04-2018) Page _2_ of _3_ | ML19015A101
Surry Power Station | Unit 1 | Auto-Start of Emergency Diesel Generators due to Pilot Wire Lockout on 'C' Reserve Station Service Transformer | 03-31-2020 | On November 12, 2018, at 16:36 hours, with Unit 1 at 100% power and Unit 2 defueled, 'C' Reserve Station Service Transformer (RSST) pilot wire lockout actuated while energizing the underground feeder cables to the 'C' RSST following transformer replacement. While 'C' RSST replacement activities were ongoing, the Surry 1 'H' and 2'J' emergency busses were supplied from the dependable alternate power supply, Unit 2 station service back-feed. The 'C' RSST lockout signal resulted in a partial loss of off-site power to the Unit 1 'H' emergency bus and to the Unit 2 'J' emergency bus. The #1 and #3 Emergency Diesel Generators (EOG) automatically started and loaded the 1 'H' and 2'J' emergency buses, respectively, as designed. The Unit 1 Main Steam Power Operated Relief Valves (PORV) momentarily opened, however the Unit 1 power level was maintained at full power. No operational issues were experienced by Unit 2. Deficient workmanship in the surface preparation of the splice connection of an underground feeder cable caused the cable fault and lockout condition. Affected cable splices were replaced prior to returning the 'C' RSST to service. An eight-hour non-emergency event notification was made to the NRC pursuant to 10 CFR 50. 72(b )(3)(iv)(A) due to a valid actuation of the #1 EDG and the #3 EDG. This report is being made pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to a valid actuation of the #1 EDG and the #3 EDG. NRC FORM 366 (04-2017) Page , 1 of 3 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects. CONTINUATION SHEET Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a (See NUREG-1022, R.3 for instruction and guidance for completing this form means used to Impose an Information collection does not display a currently valid 0MB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the http://www.nrc.gov/reading-rm/doc-coUections/nuregs/staff/sr1022/r3Q information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTiAL REV YEAR NUMBER NO. Surry Power Station, Unit 1 05000- 280 2018 • 003 00 | 1.0 DESCRIPTION OF THE EVENT During the Unit 2 fall 2018 refueling outage, the Surry electrical distribution system was in an off-normal alignment to support 'C' RSST [EIIS-EA-XFMR] replacement. 'C' RSST is the primary source which normally supplies power from the off-site transmission network to the 'F' transfer bus and the 1' H' and 2'J' emergency busses [EIIS-EK-BU]. During the 'C' RSST replacement activities, the 'F' transfer bus and the 1' H' and 2'J' emergency busses were supplied from the off-site transmission network by the dependable alternate power source, back-fel;!d via the Unit 2 'C' Station Service Transformer. On November 12, 2018, at 16:36 hours, 'C' RSST pilot wire lockout actuated while energizing the underground feeder cables to perform a phasing activity following 'C' RSST replacement. The lockout signal isolated both the primary and dependable alternate power sources to the 'F' transfer bus and to the 1 'H' and 2'J' emergency busses. #1 and #3 Emergency Diesel Generators (EOG) [El IS-EK-DG] received automatic start signals and loaded onto the 1' H' and 2'J' emergency buses, respectively, as designed. At the time of the event, Unit 1 was operating at 100% power, and a brief, minor thermal power transient was experienced due to actuation of the three Unit 1 Main Steam (MS) line Power Operated Relief Valves (PORV) [EIIS SB-RV]. The PORVs actuated for approximately 10 seconds due a to momentary loss of normal power supply to the Unit 1 semi-vital bus [EIIS-EC-BU]. During that time, the MS line pressures reduced by approximately 7 psig before the PORVs re-closed, and pressures stabilized at pre-event.levels. Thermal power level also stabilized at pre-event conditions. This effluent pathway was evaluated, and it was determined that no radionuclides were released to the environment as a result of the PORVs 'actuating. At the time of the event, Unit 2 was defueled in Refueling Shutdown mode. No operational impacts were experienced on Unit 2. On November 12, 2018, at 18:23 hours, the dependable alternate off-site power circuitry to the 'F' transfer bus was reestablished by Unit 2 back-feed. At 18:45 hours and 19:06 hours, the Unit 2 back-feed circuitry was re-established to 1' H' and 2'J' emergency busses, respectively. At 19:37 hours and 21 :39 hours, #1 EOG and #3 EOG, respectively, were returned to normal automatic standby alignment. All Unit 1 and Unit 2 Technical Specification action statements associated with emergency electrical systems were exited when the #1 and #3 EDGs were returned to normal alignment. · Post event testing determined that the pilot wire lockout signal was caused by a cable fault due to poor workmanship in the surface preparation of the underground cable splice connection which reduced the cable's ability to withstand transient surges. All electrical cables supplying 'C' RSST were tested, and all deficient cable splices were replaced. An eight-hour non-emergency event notification was made to the NRC pursuant to 10 CFR 50.72(b)(3)(iv)(A) due to a valid actuation of the #1 and #3 EDGs. This report is being made pursuant to 1O CFR 50. 73(a)(2)(iv)(A) due to a valid actuation of the #1 and #3 EDGs. 2.0 SIGNIFICANT SAFETY CONSEQUENCES AND IMPLICATIONS During the event, the redundant 1'J' 4160 V emergency bus and redundant 2'H' 4160 Vemergency bus were supplied by the primary sources of off-site power, 'A' RSST and 'B' RSST, respectively. The #1, #2, and #3 Emergency Diesel Generators rem?ined available to supply power to emergency bus loads. The actuation of Unit 1 MS PORVs resulted in a momentary minor thermal power transient, and the plant remained within safety analysis limits. Normal equipment alignment was restored by the Operations team in a timely manner. There were no radiological effluents. Therefore this event is of minimal safety significance. | ML19016A133
Clinton Power Station | Unit 1 | Division 1 Transformer Failure Leads to Instrument Air Isolation to Containment Requiring a Manual Reactor Scram | 08-03-2018 | On December 9, 2017 at 1347 CDT the Main Control Room received annunciators that indicated a trip of a 4160V 1A 1 Breaker (1AP07EJ), 480V transformer 1A and A1 feed breaker. The loss of Division 1 480V power caused the Instrument Air (IA) containment isolation valves to fail close as designed. The loss of IA affected various containment loads, including the scram pilot air header and . containment isolation valves. Another consequence of this event was that secondary containment (SC) vacuum was not maintained within Technical Specification (TS) limits due to Fuel Building ventilation dampers failing closed by design due to the loss of power. In addition, this event resulted in the inoperability of the Low Pressure Core Spray System (a single train safety system) and inoperability of primary containment due to primary to secondary containment differential pressure being outside TS limits. Operations entered Emergency Operating Procedure (EOP) -08, Secondary Containment Control. Division 2 Standl:)y Gas Treatment System was activated at 1350 and restored SC vacuum within allowable TS values at 1351 and the EOP was exited. Due to the loss of IA, a manual reactor scram was inserted at 1353 when two control rods began drifting in as expected. A phase to ground fault was identified on 480V transformer 1A (1AP11 E). On December 14, 2017, the 480V transformer was replaced and the plant returned to Mode 1 operations on December 15, 2017. The condition described in this report was determined to be reportable under 10 CFR50.73(a)(2)(iv)(A), 10 CFR 50.73(a)(2)(v)(C), 10 CFR 50.73 (a)(2)(ii)(B) and 10 CFR 50.73 (a)(2)(v)(D). Based on analyses performed at vendor test facilities following the event, the cause of the transformer failure was determined to be excessive layer to layer design stress within the 4160V winding. The identification of a pre-existing design defect during the cause analysis also resulted in the issuance a 10 CFR Part 21 notification to the NRG. This event is classified as an unplanned scram with complications due to the loss of Div. 1 480 power. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid 0MB control number, the NRG may not conduct or http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/l sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR Clinton Power Station, Unit 1 05000461 NUMBER NO. 2017 • 010 02 | PLANT AND SYSTEM IDENTIFICATION General Electric -- Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in text as [XX]. EVENT IDENTIFICATION Division 1 Transformer Failure Leads to Instrument Air Isolation to Containment Requiring a Manual Reactor Scram A. Plant Operating Conditions Before the Event Unit: 1 Event Date: 12/09/17 Event Time: 1347 Mode: 1 Mode Name: Power Operation Reactor Power: 97 percent B. Description of Event At 1347 CDT on December 9, 2017, the Main Control Room received annunciators that indicated a trip of the 4160V [EB] 1A 1 breaker [BKR] 1A P07EJ and the loss of 480V unit substations 1A and A 1. Numerous Division 1 components lost 480V power (powered from unit substations 1A and A 1) including the scram pilot air header isolation valves and the reactor water cleanup system. The Division 1 containment Instrument Air isolation valves had failed closed by design due to the loss of power. Due to the loss of containment instrument air, several control rods began to drift into the core as expected and, by procedure, a manual reactor scram was performed at 1353. Due to the loss of power, the Fuel Building ventilation dampers failed closed by design. With the normal ventilation system secured, secondary containment vacuum rose t~ slightly greater O inches water gauge which exceeded the Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.1 limit of greater than or equal to 0.25 inches vacuum water gauge at 1348. The Control Room entered Emergency Operating Procedure-a, Secondary Containment Control. Another consequence of this event was that primary containment to secondary containment differential pressure exceeded the limits of TS 3.6.1.4, "Primary Containment Pressure." In addition, the Low Pressure Core Spray System (a single train safety system) was declared inoperable due to the loss of power and TS Limiting Condition for Operation (LCO) 3.5.1, "EGGS-Operating," Action A.1 was entered. Secondary Containment vacuum was restored within TS requirements at 1351 by starting the Division 2 Standby Gas Treatment System (SGTS). Inspection of 480V transformer 1A (1AP11 E) found an area on the upper end of the B phase coil that was consistent with a phase to ground fault. On December 14, 2017, the transformer was replaced and the plant returned to Mode 1 operations on December 15, 2017. NRG FORM 366A (04-2018) Page _2_ of _4_ | ML19022A264
River Bend Station | Unit 1 | Condition Prohibited by Technical Specifications due to Inadequate Design Change of Under Voltage Relay Trip Set Point Range | 01-23-2019 | On October 24, 2018, three under voltage relay as found trip set points were found outside of the Technical Specification (TS) allowed range. The condition was discovered during the performance of a planned Surveillance Requirement test. The relays were replaced or calibrated to within the TS allowed range and returned to service. On November 29, 2018, a past operability report was completed on the condition. The report concluded that there was no reasonable assurance that the under voltage relay trip values would remain within the TS allowed range for the entirety of the 2 year calibration Preventive Maintenance (PM) interval. The calibration PM interval was changed from 2 years to 60 days. The cause of the out-of-tolerance relay trip values was an inadequate design change. This event was of minimal significance to the health and safety of the public. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (~2018) Estimated burden per response to comply with this mandatory collection request 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T·2 F43), U. S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB control number, the NRC may not conduct or http://www. nr c.gov/readi ng-rm/doc-collections/nu regs/staff/ sr1 022/r3/) sponsor, and a.person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER River Bend Station - Unit 1 458 05000-1 | BACKGROUND Under voltage relays (**RL Y**) E22-S004-27S1 (27S1 ), E22-S004-27S2 (2782), E22-S004-27S3 (27S3), and E22-S004-27S4 (2784) monitor the Division 111 4160 Volt Alternating Current (VAC) Switchgear (**SWGR**) [EK] (E22-S004) bus voltage. These relays perform the following safety functions on a bus under voltage condition: .... Trip High Pressure Core Spray [BG] Diesel Generator Service Water [Bl] Pump (SWP-P2C) . .. Start the load sequence timer for SWP-P2C . ... Provide a start signal to the Division Ill Emergency Diesel Generator. .. Provide a closure permissive for the Emergency Diesel Generator output breaker. ... Provide a closure permissive for the High Pressure Core Spray Pump Motor Breaker. IThe 27S relays are arranged in a one-out-of-two-twice arrangement as seen below. The contacts are normally open. When the relay actuates the associated contact closes. In order for the safety function to occur the 2781 or 27S3 and the 2782 or 27S4 must actuate. ... TSE 7 a-"l- 21s2 ~:;~2.7S4 "'----------------- Under voltage relays E22-S004-27N 1 (27N 1) and E22-S004-27N2 (27N2) monitor the voltage of the normal offsite supply Ito E22-S004. The safety function of these relays is to actuate on an E22-S004 under voltage condition to isolate E22-S004 ~rom the normal offsite supply by providing a trip signal to the offsite power supply circuit breaker. Actuation of either relay !will perform the safety function. IAII six of these relays are made by the same manufacturer and have the same model number. These relays are not used on the Division I or Division II safety related switchgears. The Technical Specification (TS) allowable trip value range for lthese relays is 86.23 VAC to 95.00 VAC as measured downstream from the 120/4200 VAC potential transformers which equates to 3019 VAC to 3325 VAC at E22-S004. REPORTED CONDITION On October 23, 2018, three E22-S004 under voltage relay as found trip set points were outside of the TS allowed range. The condition was discovered during the performance of a planned Surveillance Requirement (SR) test. The 2782 relay | ML19023A542
YEAR SEQUENTIAL REV | Unknown Unit | Automatic Reactor Scram Due to Main Transformer Trip | 01-29-2019 | On May 18, 2018, at 0651 PDT, Columbia Generating Station experienced a Main Transformer lockout relay trip. Coincident with the unplanned trip, an external line to ground fault occurred. A Reactor scram was automatically initiated by the plant in response to the transient. All rods fully inserted as expected; no Emergency Core Cooling Systems actuated or injected. Plant Operators effectively maintained Reactor power, pressure and level. This event did not pose a threat to the health and safety of the public. This event was reported via Event Notification #53410 under 10 CFR 50.72(b)(2)(iv)(B) as an event that resulted in actuation of the Reactor Protection System when the Reactor was critical. The root cause of the Main Transformer lockout and Reactor scram was that the vendor-supplied Buchholz relay did not meet the standard performance requirements to be insensitive to external faults. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U. S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB control number, the NRC may not conduct or http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000- NUMBER NO. Columbia Generating Station 397 2018 - 001 - 01 | Plant Conditions At the time of the event, the plant was operating in Mode 1 at 100% power. There were no safety related structures, systems, or components that were inoperable at the start of the event that contributed to the event. Event Description On May 18, 2018, at 0651 PDT, an offsite line to ground fault occurred on the 500kV network, which supplied a peak current of approximately 7kA to the Main Transformer [XFMR]. The Buchholz relay [RLY] actuated causing the Main Transformer to trip and lock out. This resulted in an automatic Reactor [RCT] scram and subsequent trip of both Reactor Recirculation [AD] pumps [P]. Reactor power, pressure, and level were maintained as expected for this condition. Safety Relief [SB] Valves [V], MS- RV-1A and MS-RV-1B, opened on Reactor high pressure, as expected for this condition. After pressure lowered below the reset point, MS-RV-1B indicated open, therefore Operations removed power supply fuses for MS-RV-1B. Safety Relief Valve tailpipe temperatures confirmed that all valves were closed. Further investigation determined that there was faulty indication for MS-RV-1B, and that the valve had closed as expected when the reset point was reached. Suppression Pool level and temperature remained steady within normal operating limits. Reactor Pressure Vessel water level was maintained with the Condensate [SD] and Reactor Feedwater [SJ] Systems with startup flow control valves [FCV] in automatic. Reactor pressure was maintained with the Turbine Bypass [JI] Valves controlling in automatic. No Emergency Core Cooling Systems actuated or injected. The transformer lockout initiated the fast transfer to the startup transformer, which supplied offsite power to the plant electrical loads. This event is reportable as an event that resulted in actuation of the Reactor Protection System when the Reactor was critical per 10 CFR 50.73(a)(2)(iv)(A). This event was reported under 10 CFR 50.72(b)(2)(iv)(B) via Event Notification #53410. Immediate Corrective Actions Per plant procedures, Operations personnel restarted a Reactor Recirculation pump to maintain core recirculation, and commenced plant cooldown. Bonneville Power Administration performed electrical diagnostic testing of the transformer and concluded that the overall health of the transformer was acceptable. Energy Northwest replaced the Buchholz relay and implemented a temporary modification to transfer the trip function of the Buchholz relay to the sudden pressure relay. The temporary modification increases the reliability of the trip function with a two out of three trip logic, and has no effect on any safety-related design functions. The Main Transformer was then placed back in service. | ML19030B268
Cooper Nuclear Station 05000298 1 of 4 | Unknown Unit | Torus to Drywall Vacuum Breaker Failure to Indicate Full Closed Causes Loss of Safety Function | 01-24-2019 | On June 19, 2017, during performance of surveillance 6.PC.207, the control switch for vacuum breaker PC-AOV- NRV21 was cycled open then closed. When the control switch was taken to close, the vacuum breaker failed to indicate closed. Operations declared Primary Containment (PC) and PC-AOV-NRV21 inoperable and entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.1.1 Condition A and LCO 3.6.1.8 Condition Bat 21 :15 hours. In addition, TS LCO 3.6.1.1 Condition B was entered at 22:15 hours due to PC-AOV-NRV21 still indicating intermediate. The control switch for PC-AOV-NRV21 was cycled open, and then closed a second time. At this time, PC-AOV-NRV21 indicated closed. Operations declared PC and PC-AOV-NRV21 operable at 23:11 hours and exited TS LCO 3.6.1.1, Condition A and Condition B, and TS LCO 3.6.1.8, Condition B. Two potential causes were identified during troubleshooting activities. The first is increased internal friction in the valve air operator of the vacuum breaker could cause the operator to close too slowly,and limit the ability to fully close. The second is the solenoid operated valve (SOV) could bleed vented air off slowly causing the vacuum breaker to not fully close. Both the valve air operator and the SOV were replaced during troubleshooting activities. ' There were no· safety consequences associated with this condition. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. ............I \. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send f~i LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. \ ..... "/ Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a (See NUREG-1022, R 3 for instruction and guidance for completing this form means used to impose an information collection does not display a currently valid 0MB control http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Cooper Nuclear Station 05000- 298 NUMBER NO. 2017 -004 -01 | PLANT STATUS Cooper Nuclear Station (CNS) was in Mode 1, Power Operations, 100 percent power, at the time of discovery; i.e., June 19, 2017. BACKGROUND The function of the Torus to Drywall Vacuum Breaker [EIIS:VACB] is to relieve vacuum in the drywall. There are 12 internal vacuum breakers which allow air and steam flow from the suppression chamber (torus) to the drywall when the drywall is at a negative pressure. Torus to Drywall Vacuum breakers prevent an excessive negative differential pressure across the drywall boundary. Each vacuum breaker is a self-actuating valve [EIIS:V], similar to a check valve, which can be remotely operated for testing purposes. A negative differential pressure across the drywall wall is caused by rapid depressurization of the drywall. Design Bases Accident (OBA) analyses assume the vacuum breakers to be closed initially and to remain closed and leak tight, until the suppression pool is at a positive pressure relative to the drywall. The requirement that the vacuum breakers be closed ensures that there is no excessive bypass leakage should a Loss of Coolant Accident (LOCA) occur. The function of the primary containment [EIIS:NH] is to isolate and contain fission products released from the Reactor Primary System following a design basis LOCA and to confine the postulated release of radioactive material. The safety design basis for the primary containment is that it must withstand the pressures and temperatures of the limiting OBA without exceeding the design leakage rate. The leakage from the drywall to the suppression chamber must be limited to ensure the pressure suppression function is accomplished and the suppression chamber pressure does not exceed design limits. The vacuum breaker has a safety function in the closed position to limit the amount of bypass flow to ensure proper containment response on a postulated LOCA event and an open safety function post LOCA to limit negative differential pressure between the drywall and the suppression chamber. With the valve partially open, the LOCA containment response cannot be assured. EVENT DESCRIPTION On June 19, 2017, during performance of surveillance 6.PC.207, "Torus to Drywall Vacuum Breaker Operation," the control switch for vacuum breaker PC-AOV-NRV21 was cycled open, then closed. When the control switch was taken to close, the vacuum breaker failed to indicate closed. As such, Operations declared Primary Containment and PC-AOV-NRV21 inoperable and entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.1.1 Condition A and Leo 3.6.1.8 Condition Bat 21: 15 hours. In addition, TS LCO 3.6.1.1 Condition B was entered at 22: 15 hours due to PC-AOV-NRV21 still indicating intermediate. | ML19031B333
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Secondary Containment Differential Pressure Exceeded the Technical Specification Surveillance Requirement | 02-01-2019 | At 1010 on December 5, 2018, Secondary Containment differential pressure exceeded the Technical Specification Surveillance Requirement of greater than or equal to 0.25 inches of vacuum water column. The highest Secondary Containment differential pressure was measured at a positive value of 0.06 inches water column. This condition existed for approximately 3 minutes before the differential pressure was restored to normal when the Standby Gas Treatment system was manually initiated. This event was caused by a trip of the service air compressor 39AC-2A. The loss of instrument air pressure caused Reactor Building ventilation to isolate and raise Secondary Containment differential pressure. The instrument air pressure was restored when 39AC-2A was isolated and the two backup air compressors started. This condition did not impact the ability of the Standby Gas Treatment system to establish and maintain the required negative pressure in the containment structure. When Secondary Containment did not meet the Technical Specification Surveillance Requirement 3.6.4.1.1 for differential pressure, the Limiting Condition of Operation (LCO) was not met. Therefore, Secondary Containment was inoperable. This event was being reported under 10 CFR 50.72(b)(3)(v)(C). NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments CONTINUATION SHEET regarding burden estimate to the Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a (S ee NUREG-1022, R.3 for instruction and guidance for completing this form person is not required to respond to, the information collection. http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 – 333 NUMBER N0. 2018 – 001 – 00 | Background The Secondary Containment [EIIS identifier: NG] is a structure comprised of the Reactor Building that surrounds the primary containment and refuel equipment. Its safety function is designed to provide containment for postulated accident scenarios: loss-of-coolant accident and refueling accident. This structure forms a control volume that serves to hold up and dilute fission products in the event of an accident. Since pressure may increase in Secondary Containment relative to the environmental pressure, the system was designed to include a differential pressure vacuum such that external atmosphere would leak into containment rather than fission products leak out. The systems which maintain a differential pressure vacuum inside Secondary Containment are the normal Reactor Building Ventilation (RBV) system [VA] and the safety-related Standby Gas Treatment (SBGT) system [BH]. During a postulated accident scenario, the normal RBV isolates and the SBGT initiates in order to filter gas from Secondary Containment to the environment. SBGT has the capacity to maintain the differential pressure vacuum. Event Description At 1010 on December 5, 2018, Secondary Containment differential pressure exceeded the Technical Specification Surveillance Requirement of greater than or equal to 0.25 inches of vacuum water gauge. The highest Secondary Containment differential pressure was measured at a positive value of 0.06 inches water column. This condition existed for approximately 3 minutes before the differential pressure was restored to normal when the Standby Gas Treatment system was manually initiated. This event was caused by a trip of the service air compressor 39AC-2A. The loss of instrument air pressure caused Reactor Building ventilation to isolate and raise Secondary Containment differential pressure. The instrument air pressure was restored when 39AC-2A was isolated and the two backup air compressors started. Event Analysis Loss of instrument air pressure to the Reactor Building Ventilation system’s air operated dampers caused the dampers to move to the closed position. Once air pressure is removed, spring pressure will force the air operator in the closed direction and thus close the damper. The result is the system not maintaining a negative pressure in the Reactor Building as compared to the outside environment. Cause The cause of this event was a loss of instrument air pressure when the 39AC-2A Service Air Compressor tripping off-line due to high inter-stage pressure and failure of the discharge check valve to close, allowing system pressure to be lost. External Events Hatch, Unit 1, Condition Prohibited by Tech Specs due to Secondary Containment Inoperability, caused by in- leakage through degraded secondary containment door seals. (ML18080A054) Fermi, Unit 2, Secondary Containment Pressure Exceeded Technical Specification due to Reactor Building HVAC System Manipulation – This event was cause by a degraded bolt and pivot linkage on a modulating damper. (ML18054A752) Page 2 of 3 | ML19032A633
Fermi 2 05000 341 1 OF 3 | Unknown Unit | Reactor Building to Suppression Chamber Vacuum Breaker Condition Prohibited by Technical Specifications | 02-04-2019 | On 12/8/2018, an inconsistency was identified between the Updated Final Safety Analysis Report (UFSAR) and the original station design of the Reactor Building to Suppression Chamber vacuum breakers. The Reactor Building to Suppression Chamber vacuum breaker design includes two vacuum breakers, a check valve and a butterfly valve, in series in each of two lines from the Reactor Building to the Suppression Chamber. The UFSAR states that power is applied to automatically keep the butterfly valve vacuum breakers closed except when air is required to relieve a vacuum inside the primary containment and that a loss of power will cause the butterfly valve to open to prevent a negative differential pressure condition. Contrary to the UFSAR requirement, after losing power the original control circuit design prevented the butterfly valve vacuum breakers from re-closing once power was restored without manual Operator action. This original station design issue rendered the butterfly valve vacuum breakers inoperable and resulted in a condition prohibited by Technical Specifications. The butterfly valve vacuum breaker control circuits have been modified so that the valve operation meets the UFSAR requirements to open when power is lost and to automatically close when power is restored. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 033112020 (04-2018) t burden per response to comply with this mandatory collection request: 80 hours. Reported , RA Estimated LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regardinbugr den estimate to the Information Services Branch (T-2 F43), U. S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Managemeanntd Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB control number, the NRC may not conduct or http://www.nrc.gov/readinq-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, anda person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER LINOZ. ] 05000- Fermi 2 341 2018 - - 0070 7 - - 0 | INITIAL PLANT CONDITIONS Mode -4 Reactor Power - 0 percent There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT On 12/8/2018, an inconsistency was identified between the Fermi 2 Updated Final Safety Analysis Report (UFSAR) (Section 6.2.4.2.2.3 and Table 6.2-2) and the station design of the Reactor Building to Suppression Chamber Vacuum Breakers [[VACB]]. Each of the two associated containment penetrations [[PEN]] for the Reactor Building to Suppression Chamber Vacuum Breakers contain a check valve [[V]] in series with a butterfly valve . UFSAR section 6.2.4.2.2.3.1 states, "Power from divisional electrical buses [[BU]] is applied to the butterfly valves at all times to keep the valves closed, except when air is required to relieve a vacuum inside the primary containment." UFSAR Table 6.2-2 states that the butterfly valves fail open on a loss of power but the valves' post Loss of Coolant Accident (LOCA) position is closed. The UFSAR table further states (in Note 24 to UFSAR Table 6.2-2) that, "This butterfly valve is normally closed and opens automatically to prevent formation of a negative pressure in the torus. This butterfly valve closes automatically upon increasing torus pressure and remains closed during all containment high-pressure conditions." The terms Torus and Suppression Chamber are synonymous as are Reactor Building and Secondary Containment. On a loss of power (including a loss of offsite power) the butterfly valves open consistent with UFSAR Table 6.2-2. However, after a loss of power the seal in relays [[RLY]] associated with the butterfly valve control circuit would open and require manual operator action to reset the circuit and close the butterfly valves. The required manual operator action to reset the circuit is contrary to UFSAR section 6.2.4.2.2.3.1 and Note 24 to UFSAR in that: 1) once power is restored to the valves, including during a Loss of Offsite Power - Loss of Coolant Accident (LOP/LOCA), the butterfly valves will not be automatically closed and 2) a postulated LOP/LOCA will create a containment high-pressure condition, and the butterfly valves will not automatically remain closed. The identified condition does not impact the ability of the check valve vacuum breaker to perform its required functions. The function of the Reactor Building to Suppression Chamber vacuum breakers is to limit the differential pressure between Reactor Building and the Suppression Chamber and to relieve vacuum when the Suppression Chamber pressure drops below Reactor Building pressure. In addition, the two vacuum breakers (check valve and butterfly valve) in each of the two lines from the Reactor Building to the Suppression Chamber airspace are to remain closed (except during testing or when performing their intended function to relieve vacuum) to maintain a leak tight primary containment boundary. The opening of the butterfly valves on a loss of power ensures the vacuum relief safety function is met during a loss of power event where the check valve will function as required to prevent a negative differential pressure condition. However, once power is restored, the original station design prevented the butterfly valve from closing, as required post LOCA by the UFSAR, without manual Operator action. This original design issue rendered the butterfly valve vacuum breakers inoperable, which fails to meet the Limiting Condition for Operation (LCO) requirement of TS 3.6.1.7 for each Reactor Building to Suppression Chamber vacuum breaker to be operable. Specifically, since original plant design and operation the butterfly valves did not meet the requirement TS 3.6.1.7 to remain closed, except during testing or performing their intended function. This issue is reported under 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. | ML19036A741
Clinton Power Station | Unit 1 | Load Driver Card Failure Resulting in High Pressure Core Spray lnoperability | 02-05-2019 | On June 20, 2018, at 1145 CDT, during panel walkdown, a reactor operator identified that High Pressure Core Spray (HPCS) injection valve 1 E22-F004 was in the open position. Valve 1 E22-F004 is normally closed and receives an open signal upon HPCS initiation. Operations personnel verified that the valve was open locally and that the plant computer indicated the valve was in the 'not closed' position. No alarms or status lamps indicated why the valve would be open and there was no valid demand signal. Reactor power, pressure, level, and feedwater parameters remained steady and unchanged, with no indication of HPCS injection having occurred or required. With valve 1 E22-F004 in the open position without a demand signal, closure on a high reactor water level condition was not assured. HPCS was, therefore, declared inoperable. Technical Specifications (TS) 3.5.1, "Emergency Core Cooling Systems (ECCS)-Operating," and 3.6.1.3, "Primary Containment Isolation Valves (PCIVs)," were entered. The HPCS injection valve 1 E22-F004 was subsequently observed cycling without operator action. To assure the containment isolation function and closure on a high reactor water level condition, 1 E22-F004 was deactivated in the closed position. The apparent cause of the event was the load driver transient voltage suppressors failing causing the. open and close circuits to be energized. As a corrective measure, the original load driver circuit cards were replaced. This event was reported as an 8-hour non-emergency notification per 10 CFR 50.73(a)(2)(v)(D) as any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1 D22, R.3 for instruction and guidance for completing this form collection does not display a currently valid 0MB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. http://www. n re.gov/reading-rm/doc-collections/nu regs/staff/ sr1 022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Clinton Power Station, Unit 1 05000461 NUMBER NO. Ii - - 2018 003 01 | PLANT AND SYSTEM IDENTIFICATION General Electric -- Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in text as [XX]. EVENT IDENTIFICATION Load Driver Card Failure Resulting in High Pressure Core Spray lnoperability A. Plant Operating Conditions Before the Event Unit: 1 Event Date: June 20, 2018 Event Time: 1145 Mode: 1 Mode Name: Power Operation Reactor Power: 099 percent B. Description of Event On June 20, 2018, at 1145 CDT, the High Pressure Core Spray (HPCS) injection valve 1 E22-F004 was observed in the "OPEN" instead of the required "CLOSED" position. A review of computer point HP BC801, "HPCS Pump Discharge 1 E22-F004," and Transient Test (TT) Channel 50, "HPCS Injection Valve Position," showed the valve opened at approximately 0847 CDT. Operations entered Technical Specification (TS) 3.5.1, "EGGS-Operating," and TS 3.6.1.3, "Primary Containment Isolation Valves (PCIVs)," Required Actions in response to the event. The HPCS injection valve remained in the OPEN position as additional assessment and troubleshooting activities were conducted. At approximately 1324 CDT, the HPCS injection valve began cycling "OPEN" and "CLOSED." This condition occurred for approximately 13 minutes and 45 seconds at which time the 1 E22-F004 valve was de-energized and the valve manually isolated. C. Cause of the Event Troubleshooting was initiated to determine the cause for the HPCS injection valve OPEN/CLOSE circuit operations. The initiating event for the as-found position of valve 1 E22-F004 was that the 1 H 13-P663-B- . A 16-A1 23 (A 123) load driver circuit card [RLY ] failed in a manner that caused it to send a spurious signal which opened the valve. Troubleshooting also identified unexpected voltages at the output of the 1H13-P663-B-A1 6-A1 21 (A 121) load driver circuit card. This load driver provided the signal to close the valve. When both the A123 and A121 load driver cards were replaced, the voltages in the circuit returned to expected values. The apparent cause of the event was the load driver transient voltage suppressors suffered a random failure causing the circuits to be energized. NRG FORM 366A (04-2018) Page _2_ of _3_ | ML19042A077
Browns Ferrv Nuclear Plant | Unit 1 | Main Steam Relief Valves Lift Settings Outside of Technical Specifications Required Setpoints | 02-11-2019 | On December 12, 2018, the Tennessee Valley Authority was presented with as-found testing results indicating that two of the thirteen Main Steam Relief Valves (MSRVs) from Browns Ferry Nuclear Plant, Unit 1, were outside the +/- 3 percent setpoint band required for their operability. MSRV Line B failed 4.37 percent above its setpoint band and MSRV Line C failed 3.96 percent below its setpoint band. Troubleshooting determined that MSRV Line B disc failed above its setpoint band due to corrosion bonding to the valve seat as a result of its platinum anti corrosion coating flaking off. The valve discs were previously platinum coated to prevent this, and this was the first Unit 1 MSRV service interval to implement an improved surface treatment to prevent coating delamination. MSRV Line C failed below its setpoint band due to relaxation of the setpoint spring over time. These two MSRVs were found to have been inoperable for an indeterminate period of time between November 2, 2016, and October 14, 2018, and longer than permitted by Technical Specifications. The affected valves remained capable of maintaining reactor pressure within American Society of Mechanical Engineers code limits. Additionally, the valves' ability to open under remote-manual operation, activation through the Automatic Depressurization System, or MSRV Automatic Actuation Logics was not affected. The valves remained capable of performing their required safety function. ~II thirteen of the Unit 1 MSRV pilot valves were replaced with refurbished valves during the Unit 1 Refueling Outage 12. The corrective actions to preclude recurrence were to prepare the pilot discs for platinum coating in accordance with the revised procedure which required nitrogen pressure testing to verify valve seal functionality prior to coating. Additionally, the discs will be platinum coated, the setpoint spring for Pilot 1069 will be replaced, and the remaining springs will be tested and replaced, if necessary. NRG FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION Mr ·"vv'l:U t>T UMt>: NU. 310U-Ui04 l:Al'"'ll<t:"': vv,v ,._v_v (04-2017)) Estimated burden per response to comply wi1h this mandalllly collection request 80 hours. Reported lessons lea-ned a-e inoo,porated inlll the licensing process and fed back to industry. Send commenls regarding burden estimate to the Information Se!vices B<anch (T- 2 F43), U.S. Nuclea-Regulatofy Commission, Washington, DC 20555-0001,o,-by e-mai Ill LICENSEE EVENT REPORT (LER) lnfooollecls. Resource@nrc.gov, and to the Desk Officer, Office of lnfonnation and Regulalllly Affairs, NEOB-10202, (3150-0104), Office of Management and Budget CONTINUATION SHEET Washinglon, DC 20503. If a means used Ill i"1J()Se an information collection does not display a cooen11y valid 0MB control number, the NRG may not conduct o,-sponso,-, and a peraon is not required to respond Ill, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 1 05000259 NUMBER NO. 2018 - 007 00 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Unit 1, was in Mode 1 at approximately 86 percent power. II. Description of Event A. Event Summary On December 12, 2018, NWS Technologies provided the Tennessee Valley Authority (TVA) with the as-found testing results of the thirteen Main Steam Relief Valves (MSRVs) [RV], which were removed during the Fall 2018 Unit 1 Refueling Outage 12 (1R12). Two Main Steam Relief Valves on lines Band C (BFN-1-PCV-001-0018 and BFN-1-PCV-001-0034) had as-found lift settings which were outside of the +/- 3 percent band of their setpoints required for their operability. Technical Specification (TS) 3.4.3, Safety/Relief Valves (S/RVs), requires twelve of the thirteen S/RVs to be operable for S/RV system operability. These two MSRVs were found to have been inoperable for an indeterminate period of time between November 2, 2016, and October 14, 2018, and longer than permitted by TS 3.4.3. Throughout this event, the two-stage MSRV pilot valves remained capable of maintaining the reactor pressure below 1375 psig, which is the American Society of Mechanical Engineers (ASME) code limit of 110 percent of the vessel design pressure. The valves remained capable of performing their required safety function. The TVA is submitting this report in accordance with Title 10 of the Code of Federal Regulations 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant's TS. It was determined that the MSRV pilot valve inoperability resulted from their setpoints gradually drifting during the course of their operating cycle, which began when Unit 1 entered Mode 2 on November 2, 2016, and ended October 14, 2018, when Unit 1 entered Mode 4. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. NRG FORM 366A (04-201 B) Page _2_ of _7_ | ML19042A158
Quad Cities Nuclear Power Station | Unit 1 | Reactor Scram Due to Turbine-Generator Load Reject | 02-28-2019 | On September 26, 2018 at 19:08, Quad Cities Unit 1 received an automatic Reactor SCRAM from 100% power. The SCRAM was the result of a Turbine-Generator Load Reject Trip that occurred when the status of the load reject contacts on one Unit Output Breaker was being tested while the other Unit Output Breaker was open. The cause of the Turbine-Generator load reject trip was ineffective procedural controls tor ensuring both unit output breakers were closed prior to performing contacts status verifications. The immediate corrective actions include procedure revisions to provide enhanced guidance for performing contact checks. The issue is reportable under 10 CFR 50. 73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B). NRG FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T·2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV I Quad Cities Nuclear Power Station Unit 1 05000254 YEAR NUMBER NO. 2018 - 004 01 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Reactor Scram Due to Turbine-Generator Load Reject A. CONDITIONS PRIOR TO EVENT Unit: 1 Event Date: September 26, 2018 Event Time: 19:08 hours Reactor Mode: 1 Mode Name: Power Operation Power Level: 100% One Switchyard Ring Bus Unit Output Breaker 6-7 was open at the time of the event as a result of local grid activities. B. DESCRIPTION OF EVENT On September 26, 2018 at 19:08, Quad Cities Unit 1 received an automatic Reactor SCRAM from 100% power. The SCRAM was the result of a Turbine [TRB]-Generator [GEN] Load Reject Trip that occurred when the status of the load reject contacts on one ring bus unit output breaker [BRK] (7-8) was being tested while the other ring bus unit output breaker (6-7) was open. The switchyard is configured in a ring bus [BU] to ensure that during full power operation, when one of the 345 KV breakers is removed from service, at least one of the two ring bus unit output breakers remains closed. The contact status tests are performed after a ring bus unit output breaker has been manipulated with the unit online. Once the ring bus unit output breaker has been re-closed, the load reject contacts for each output breaker are checked to confirm the contacts are in the open position. While performing breaker manipulations on September 26, 2018, the Operating Crew misinterpreted a step in their governing procedure and the Unit Supervisor incorrectly directed maintenance electricians to perform the contact checks prior to Output Breaker 6-7 being closed. While checking the status of the load reject contacts for Output Breaker 7-8, the electricians were unable to obtain accurate voltage readings and identified there was no voltage present at the contacts. Believing no voltage was present, the Unit Supervisor directed the electricians to verify continuity across the same contacts using an ohm meter. The continuity.verification jumpered across the only set of open contacts in the Turbine-Generator Load Reject circuitry and initiated the Load Reject Trip and corresponding SCRAM of Unit 1. Following the reactor scram, the station received automatic Group II and Group Ill containment isolations due to momentary low reactor water level during the transient. The isolations were reset. The reactor SCRAM and the Group II and Ill containment isolations are reportable under 10 CFR 50. 73(a)(2)(iv)(A), as events or conditions that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B). | ML19059A037
YEAR SEQUENTIAL REV | Unknown Unit | Unplanned Loss of Safety Function of Gland Seal Exhauster Trip During Planned Maintenance Due to Inadequate Procedure | 03-01-2019 | On 1/1/2019, while performing planned maintenance on the Feedwater Distributed Control System (FW DCS) at 5 percent power, it was discovered that the automatic trip instrumentation of the Gland Seal Exhauster (GSE) was inoperable. The automatic GSE trip function is a documented assumption in the safety analysis for the Control Rod Drop Accident and is required by Technical Specification (TS) 3.3.7.3 when reactor thermal power is less than or equal to 10 percent. The automatic trip function of the GSE was inoperable for 1 minute 19 seconds. The impact on the GSE trip function during implementation of the site procedures and the applicable work order was inadequately documented prior to starting the planned maintenance on the FW DCS. The unplanned inoperability of the GSE trip function is reportable under 10 CFR 50.73(a)(2)(v)(C) and (D). There was no adverse impact to public health and safety or to plant employees and there were no radiological releases. The cause of the GSE trip inoperability resulted from inadequate procedural guidance during planned maintenance on the FW DCS. GSE trip operability was restored automatically by FW DCS without any required actions. Site procedures were revised on or before January 11, 2019 to describe the impact of the FW DCS on the GSE trip and reference the applicable TS. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U. S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB control number, the NRC may not conduct or http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000- NUMBER NO. Fermi 2 341 2019 - 001 - 00 | INITIAL PLANT CONDITIONS Mode – 2 Reactor Power – 5 percent DESCRIPTION OF THE EVENT On January 1, 2019 at approximately 0454 EST, while the Feedwater Distributed Control System (FW DCS) [[SJ, JK]] was being rebooted under a planned maintenance work order (WO), it was discovered that the required automatic trip instrumentation of the Gland Seal Exhauster (GSE) [[FAN]] [[TC]] was inoperable. The automatic GSE trip is assumed in the safety analysis for the Control Rod Drop Accident (CRDA) and is required by Technical Specification (TS) 3.3.7.3, “Gland Seal Exhauster (GSE) Trip Instrumentation,” when reactor thermal power is less than or equal to 10 percent rated thermal power (RTP). The automatic trip function of the GSE was inoperable for 1 minute, 19 seconds. No control rod movement occurred while the automatic trip of the GSE was inoperable. Per TS 3.3.7.3, the GSE trip instrumentation is required to be operable in Modes 1 and 2 when any GSE is in service, any main steam line is not isolated, and reactor thermal power is less than or equal to 10 percent RTP. The GSE trip instrumentation initiates a trip of the GSE breakers following events in which radiation in the main steam lines exceeds a predetermined value. Tripping the GSEs limits the offsite and control room doses in the event of a postulated CRDA. If a postulated CRDA were to occur in Modes 1 or 2 with a GSE in service, the main steam lines not isolated, and with reactor thermal power less than or equal to 10 percent RTP, radiological dose consequences from the CRDA could exceed those considered in the Updated Final Safety Analysis Report (UFSAR). Therefore, the GSE trip is credited to ensure conformance with the radiological evaluation of the CRDA in the UFSAR. Above 10 percent RTP, the postulated effects of a CRDA are not sufficient to cause fuel damage such that the GSE trip is not required. The TS Limiting Condition for Operation (LCO) 3.3.7.3 Condition B requires GSE trip capability to be restored within 1 hour if lost. During the FW DCS maintenance activity on January 1, 2019, the automatic trip function of the GSE was inoperable for 1 minute, 19 seconds, which met the TS LCO requirement. The GSE trip capability was restored automatically when the FW DCS finished rebooting; no operator action was required. The reboot of the FW DCS on January 1, 2019 was a planned maintenance activity to restore failed steam line flow signals. The Rod Worth Minimizer (RWM) and GSE control logic both receive feedwater and steam flow digital input from the FW DCS. Site procedures at the time of event explicitly discussed the impact of the FW DCS input on the RWM, but failed to describe the impact on the GSE trip instrumentation. The impact on the RWM was therefore planned before the start of the maintenance activity on the FW DCS and the applicable RWM TS LCO was entered in advance of the FW DCS reset. Since impact on the GSE was not identified in advance, entry into the GSE TS LCO 3.3.7.3 was not performed before beginning the FW DCS maintenance activity. The inoperability of the GSE trip function was immediately recognized when the FW DCS was rebooted based on panel indications in the Main Control Room, and GSE TS LCO 3.3.7.3 was then entered promptly. The unplanned inoperability of the GSE trip function is reportable under 10 CFR 50.73(a)(2)(v)(C) and (D) as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material, and mitigate the consequences of an accident, respectively. An 8-hour non-emergency Event Notification (EN 53811) was previously made under the corresponding requirement in 10 CFR 50.72(b)(3)(v)(C) and (D). | ML19060A290
i | Unknown Unit | Reactor Core Isolation Cooling System Declared Inoperable During Surveillance Testing | 02-28-2019 | On January 8, 2019, the Reactor Core Isolation Cooling (RCIC) system was declared inoperable. This action was taken because the RCIC system turbine-pump did not achieve the acceptance criteria of flow rate, discharge pressure, and speed during the performance of a surveillance test. Due to the unexpected response a Failure Modes Analysis was initiated to determine the cause. No deficient conditions were identified during troubleshooting. However, based on the investigation, the team determined that the direct cause was output signal loss from the RCIC flow controller. A spare calibrated controller was installed, the system was tested, and successfully returned to service. The High Pressure Coolant Injection system was operable and capable of providing high pressure core cooling similar to the RCIC system. This event had no impact on the health and/or safety of the public. This report is submitted in accordance with Title 1O Code of Federal Regulations 50.73(a)(2)(v)(D). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 3/31/2020 {04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear CONTINUATION SHEET Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and· to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid 0MB control number, the http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITYNAME 2. DOCKET NUMBER 3. LEA NUMBER YEAR SEQUENTIAL REV Pilgrim Nuclear Power Station 05000- 293 NUMBER NO. 2019 -001 -00 | BACKGROUND The Pilgrim Station Updated Final Safety Analysis Report (UFSAR) states that the Reactor Core Isolation Cooling (RCIC) system is designed to provide makeup water to the reactor vessel following reactor isolation in order to prevent the release of radioactive materials to the environment as a result of inadequate reactor core cooling. The system consists of a steam driven turbine-pump and associated valves and piping capable of delivering makeup water to the reactor vessel over a range of reactor pressures. The system can be operated automatically or manually, and is one of the systems credited in the UFSAR for a design basis Control Rod Drop Accident (CRDA). The RCIC system is sufficient to maintain reactor vessel water level at an acceptable limit during this event. EVENT DESCRIPTION On January 8, 2019, the RCIC turbine was started in automatic from the main control room per a quarterly ~urveillance. During the test run, the turbine did not reach rated conditions. Operators identified that flow controller, FIC-1340-01, output meter was indicating zero, which was unexpected. Operators attempted to change demand by varying the flow controller setpoint from 375 gallons per minute (gpm) to 425 gpm, but no change in output or flow occurred. Operators then manually stopped the RCIC turbine from the main control room and declared the RCIC system inoperable. rrhe NRG Operations Center was notified of the event in accordance with Title 1O Code of Federal Regulations (CFR) 50. 72 at 1545 hours on January 8, 2019. The event occurred during power operation while at 100 percent reactor power. The reactor mode selector switch was in the RUN position. CAUSE OF THE EVENT Due to the unexpected response a Failure Modes Analysis was initiated to investigate the cause. No deficient conditions were identified during troubleshooting. However, based on the investigation, the team determined that the direct cause was output signal loss from RCIC flow controller FIC-1340-01. CORRECTIVE ACTIONS rrhe installed flow controller was removed and replaced with a spare calibrated controller. An operability test run was completed and the system was successfully returned to service. ~ny further corrective actions will be documented in the corrective action program. Page 2 of 3 | ML19064A593
Peach Bottom Atomic Power Station | Unit 2 | Emergency Diesel Generator Air Inlet Check Valve Failure Results in a Condition Prohibited by Technical Specifications | 03-04-2019 | On 6/13/18, during a surveillance test of the E-3 Emergency Diesel Generator, higher than normal engine temperatures were noted and abnormal noises were heard while running the engine at full load. The engine was shut down and troubleshooting initiated. Inspection of the turbocharger air inlet check valve discovered a pin used to hold the check valve disc in place was missing. The pin had become dislodged and had traveled to the turbocharger, where it caused damage to the rotating blades of the turbocharger. Repairs were performed and the diesel generator was placed back in service on 6/23/18. Investigation of the failure determined that inadequate repairs during maintenance in April 2017 resulted in the pin loosening at certain engine loads. This event is being reported as required by 1O CFR 50.73(a)(2)(i}(B}. There were no actual safety consequences as a result of this event NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Eslimaled burden per response lo comply wilh !his mandatory collection request 80 hours. Reported lessons learned are incorporaled inlo !he licensing process and led back lo induslry. Send comments LICENSEE EVENT REPORT (LER) regarding burden eslimale lo !he lnlonnalion Services Branch (T-2 F43), U.S. Nuclear Regulalory CONTINUATION SHEET Commission, Washinglon, DC 20555·0001, or by e-mail lo lnfocollecls.Resource@nrc.gov, and lo !he Desk Officer, Office ol lnformalion and Regulatory Affairs, NEOB-10202, (3150·0104), Office al Managemenl and Budge!, Washinglon, DC 20503. If a means used lo impose an infonnalion (See NUREG-1022, R.3 for instruction and guidance for completing this form colleclion does nol display a currenlly valid OMB conlrol number, !he NRC may no! conducl or sponsor, and a person is nol required lo respond lo, !he infonnalion colleclion. http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1 D22/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Peach Bottom Atomic Power Station Unit 2 05000277 NUMBER NO. 2018 - 002 - 01 | Unit Conditions Prior to the Event Unit 2 and Unit 3 were both operating in Mode 1 at approximately 100% rated thermal power. There were no structures, systems or components out of service that contributed to this event. Description of Event On 6/13/18, a periodic surveillance test was being performed on the E-3 Emergency Diesel Generator (EOG). The test is performed to verify the EOG can slow start and run at full load for at least one hour. The EDG was started and after approximately 40 minutes, brought up to full load (2700 - 2800 kW). After approximately 30 minutes of operating at full load, temperature readings indicated higher than normal exhaust temperatures at several locations. After further observation and indications of higher than normal operating temperatures, the decision was made to shut down the engine. As the EDG was being shutdown, a rattling noise was heard in the area of the turbocharger. The EDG operated at full load for approximately 55 minutes. Troubleshooting centered around the turbocharger air inlet check valve, which allows for an increased flow of air to the turbocharger air inlet as the load on the engine increases. Inspection identified a pin used to hold the check valve disk to the pivot shaft was missing and had entered the air inlet piping. Air intake for the engine's two turbochargers is initially through a common pipe, which splits to direct air to each turbocharger. The dislodged pin bounced between the two turbochargers, causing damage to the aluminum turbocharger blades. The damage resulted in aluminum particles being distributed through the air intake, lube oil and exhaust systems. Aluminum particles were also found in the cylinders of the engine. Larger aluminum particles were caught in the intercooler fins. Repairs included replacing the air inlet check valve, replacing the turbochargers, removing larger particles of the impeller blades from the intercooler inlet, cleaning the cylinder liners, replacing piston rings and flushing the lubricating oil system. Post maintenance testing was performed, and the diesel generator was placed back in service on 6/23/18. Analysis of Event The onsite standby power source for the four 4 kV emergency buses in each unit consists of four EDGs. Each EOG can supply power to two 4 kV buses, one for each unit. Technical Specification (TS) 3.8.1, Condition B, provides required actions when one EDG is inoperable. These actions include determining that the remaining EDGs are not inoperable due to a common cause failure and restoring the EOG to an operable status within 14 days. The pin that had become dislodged from the E-3 EOG air inlet check valve had been replaced during preventive maintenance performed in April 2017. The pin was manufactured on site and was unique to the | ML19064B342
Pilgrim Nuclear Power Station 05000-293 1 OF4 | Unknown Unit | Failure of Main Steam Isolation Valve Limit Switch Results in a Condition Prohibited by Technical Specifications | 03-04-2019 | On January 5, 2019 during the performance of Main Steam Isolation Valve (MSIV) surveillance testing, control room alarm MSIV Not Full Open did not annunciate when MSIV A0-203-1 C was fully closed for stroke time testing. The MSIV Not Full Open alarm is expected when any MSIV position RPS limit switch opens. The cause was traced to failure of the MSIV position Reactor Protection System (RPS) limit switch LS6 to properly open and the associated logic system channel was placed in the tripped condition. On February 7, 2019, a detailed review of plant computer and annunciator system alarm data discovered that the MSIV position RPS limit switch LS6 did not open as expected when MSIV A0-203-1 C was closed on January 3; 2019 and the associated logic system channel was not placed in a tripped condition within the time constraints specified in Technical Specifications. The allowable action time to trip (de-energize) the RPS channel associated with failed limit switch LS6 on MSIV A0-203-1 C was exceeded because operations personnel did not correctly interpret the absence of the MSIV Not Full Open alarm upon closure of the MSIV on January 3, 2019. At the time of the event, the reactor mode selector switch was in the RUN position and the reactor was at 35 percent reactor thermal power. This event had no impact on the health and/or safety of the public. This report is submitted in accordance with Title 10 Code of Federal Regulations 50.73(a)(2)(i)(B); Operation or Condition Prohibited by Technical Specifications. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear CONTINUATION SHEET Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid 0MB control number, the http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Pilgrim Nuclear Power Station 05000- 293 NUMBER NO. 2019 -002 -00 | BACKGROUND rThe Reactor Protection System (RPS) provides timely protection against the onset and consequences of conditions that threaten the integrity of the fuel clad and reactor coolant pressure boundary. The Main Steam System conducts steam from the Reactor Pressure Vessel (RPV), via four steam lines, •hrough the Primary Containment to the Turbine. Each steam line has two, normally open, Main Steam Isolation Valves (MSIVs), one inside and one outside the Primary Containment. The MSIVs close automatically upon receipt of certain isolation signals. The RPS MSIV closure signals are initiated from limit switches (valve position) located on each of the eight MS IVs. Each MSIV has two limit switches; one inputs to RPS trip system A while the other inputs to RPS trip system B. Each RPS trip system receives an input from four MSIV-closure channels, each consisting of two limit switches (one for the inboard MSIV and one for the outboard MSIV in the same steam line) in series with a sensor relay. The design permits closure of any two lines without a full scram being initiated. There are four limit switch contacts on each MSIV that provide valve stem position input for control room indication and inputs into the RPS. Limit switches 5 and 6 are closed only when the MSIV is fully open (>90 percent open) and supply the RPS circuitry. It should be noted that prior to testing performed on January 5, 2019, there was an earlier failure of RPS limit switch LS5 on MSIV A0-203-1 C that was discovered on November 26, 2018 during testing. Upon discovery of the LS5 failure, the associated logic system channel was placed in a tripped condition. After discovering the failure of LS6 on MSIV A0-203-1 C on January 5, 2019, and placing the associated logic system channel in the tripped condition, both RPS MSIV closure channels associated with the "C" steamline MSIVs are in the tripped condition. EVENT DESCRIPTION On January 5, 2019 during the performance of MSIV surveillance testing, control room alarm MSIV Not Full Open did not annunciate when MSIV A0-203-1C was fully closed for stroke time testing. The MSIV Not Full Open alarm is expected when any MSIV position RPS limit switch opens. The cause was traced to failure of the MSIV position RPS limit switch LS6 to properly open and the associated logic system channel was placed in the tripped condition. On February 7, 2019, a detailed review of plant computer and annunciator ~ystem alarm data discovered that the MSIV position RPS limit switch LS6 did not open as expected when MSIV A0-203-1C was closed on January 3, 2019 at 0917 hours and the associated logic system channel was not placed in a tripped condition within the time constraints specified in Technical Specifications. he January 3, 2019 event occurred during power operation while at 35 percent reactor power. The reactor mode selector switch was in the RUN position. Page 2 of 4 | ML19065A050
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Secondary Containment Differential Pressure Exceeded the Technical Specification Surveillance Requirement | 03-15-2019 | On January 16, 2019, at 0137, with James A. FitzPatrick Nuclear Power Plant at 100% power, Secondary Containment differential pressure exceeded the Technical Specification Surveillance Requirement 3.6.3.1.1 of greater than or equal to 0.25 inches of vacuum water gauge while isolating Reactor Building Ventilation. This condition existed for approximately ten (10) seconds and returned to within limits when the isolation sequence was completed. The differential pressure did not exceed 0 so there was no unmonitored exfiltration and there were no actual radiological release events. When Secondary Containment did not meet the Technical Specification requirement for differential pressure, Secondary Containment was Inoperable. Therefore, this event is reportable under 10 CFR 50.73(a)(2)(v)(C). A differential pressure excursion during transition from normal to isolation mode of the Reactor Building Ventilation System is an expected condition, and attributable to the design of the system. The cause of exceeding the differential pressure requirement has been determined not to be associated with a component failure or equipment malfunction. Corrective actions include declaring Secondary Containment Inoperable when manually isolating Reactor Building Ventilation and increase the normal differential pressure in Secondary Containment. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments CONTINUATION SHEET regarding burden estimate to the Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a (S ee NUREG-1022, R.3 for instruction and guidance for completing this form person is not required to respond to, the information collection. http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 – 333 NUMBER N0. 2019 – 001 – 00 | Background The Secondary Containment (SC) [EIIS identifier: NG] is a structure comprised of the Reactor Building that surrounds the primary containment and refuel equipment. Its safety function is designed to provide containment for postulated accident scenarios: loss-of-coolant accident and refueling accident. This structure forms a control volume that serves to hold up and dilute fission products in the event of an accident. The system was designed to include a differential pressure vacuum (DP) such that external atmosphere would leak into containment rather than fission products leak out. The systems which maintain the DP is the normal Reactor Building Ventilation (RBV) system [VA] and the safety-related Standby Gas Treatment (SBGT) system [BH]. During a postulated accident scenario, the normal RBV isolates and the SBGT initiates to filter gas from SC to the environment. SBGT has the capacity to maintain DP. (Positive DP refers to a lower pressure inside SC in comparison to environmental air pressure) Event Description On January 16, 2019, at 0137, with James A. FitzPatrick Nuclear Power Plant (JAF) at 100% power, SC was manually placed into isolation mode using the operating procedure OP-51A to prepare for equipment maintenance. During this evolution, the DP exceeded the Technical Specification (TS) Surveillance Requirement SR 3.6.3.1.1 of greater than or equal to 0.25 inches of vacuum water gauge for approximately ten (10) seconds and returned to within limits by the SBGT system when the isolation sequence was completed. Operators identified this condition using the plant computer and recorded the lowest value at 0.14 inches of vacuum water gauge. An initial notification was submitted to the NRC by ENS 53828 per 10 CFR 50.72(b)(3)(v)(C). Event Analysis The SC DP tends to move towards zero, when the RBV is switched from normal to an isolation mode. The cause of the DP change during the transition phase is the difference in closure time for the RBV supply and exhaust isolation valves. The exhaust valves are designed to close within the first 5 seconds and the supply is designed to close within 15 seconds. Therefore, the supply fans keep bringing outside air in for up to 10 seconds after the exhaust valves have isolated, causing DP to lower. This may be observed from the readings obtained in the control room for the SC pressure during the transition phase. When RBV is operating, DP is controlled much higher than the 0.25 inches of vacuum water gauge; such that if an isolation is initiated the change due to the transition may not exceed the SR limit. On January 11, 2019, work to clean RBV cooling coils was performed due to an increasing trend in SC DP. This lowered the average normal DP from about 1.5 to 0.8. Therefore, during this event, the isolation transition change had a lower starting point and was able to exceed the TS requirement. The procedure used to isolate RBV during this event was OP-51A and it instructs starting SBGT to raise DP prior to isolating RBV. Operators did not expect that isolation transition to lower DP below the TS requirement because the normal and SBGT margin would normally be enough. Therefore, SC was not declared Inoperable in preparation for the planned maintenance. When SR 3.6.3.1.1 requirement of greater than or equal to 0.25 inches of vacuum water gauge was exceeded, TS 3.6.3.1 was not met, Secondary Containment was Inoperable, and this event is reportable per 10 CFR 50.73(a)(2)(v)(C). Page 2 of 3 | ML19074A293
Browns Ferry Nuclear Plant | Unit 1 | Automatic Reactor Scram Due to an Unanticipated Electro-Hydraulic Control Looic Condition | 03-28-2019 | On March 18, 2018, at 1158 CDT, the Unit 1 reactor automatically scrammed due to a Reactor Protection System (RPS) signal generated from High Reactor Steam Dome Pressure in response to the Electro-Hydraulic Control (EHC) system clamping the Turbine Control Valves. All control rods fully inserted into the core. Main Steam Isolation Valves (MSIV) remained open with Main Steam Relief Valves operating on the initial transient as expected. Main Turbine Bypass Valves controlled reactor pressure. Reactor Feedwater pumps remained in service to control reactor water level. Primary Containment Isolation System Groups 2, 3, 6, and 8 containment isolation and initiation signals were received. Upon receipt of these signals all required components actuated as required. All safety systems operated as expected. An investigation determined the event was caused by Operations and Engineering Management failing to track and review the aggregate impact of off-normal conditions. There was inadequate procedural guidance to assess operational impacts when equipment failures/faults occurred, prior to entering the work management process. The normal level of review would not have identified the condition leading to the scram. Both megawatt input transducers were replaced prior to Unit 1 restart from the scram. As an interim action, a Nuclear Operating Experience Report (NOER) was issued for communication to other TVA sites. This NOER stressed the importance of evaluating the full impact of failed digital equipment, which must include software logic inputs. As a corrective action to prevent future recurrence, operator responsibilities for performing operational impact reviews were clarified in procedures. This included developing a tool or checklist for operational impact reviews. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULAT ORY COMMISSION I Al n.vvCU '" UMt>: NU. 31:>U-UlU4 CAl'lr<c;:,: --·-··---- (04-2017)) Estimated burden per iesponse to comply with this mandatory collection request 80 houis. Reported lessons le..-ned ..-e incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Setvices B,anch (T- 2 F43), U.S. Nucle..-Regulatory Commission, Washington, DC 20555-0001,or by .,.n,aii to LICENSEE EVENT REPORT (LER) lnfocollects. Resouice@mc.gov, and to the Desk Officer, Office of lnfonnation and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget CONTINUATION SHEET Washington, DC 20503. If a means used ID ir1'!)0se an information coleclion does not display a cunientiy valid 0MB contro number, the NRC may not conduct or sponsor, and a person is not required to iespond ID, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 1 05000259 NUMBER NO. 2018 - 002 01 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Unit 1 was in Mode 1 at 100 percent power. II. Description of Event A. Event Summary At 1158 CDT on March 18, 2018, the Unit 1 reactor automatically scrammed due to a Reactor Protection System (RPS) [JC] signal generated from High Reactor Steam Dome Pressure in response to the Electro-Hydraulic Control (EHC) [JA] system clamping the Turbine Control Valves (TCVs) [PCV]. All control rods [AA] fully inserted into the core. Main Steam Isolation Valves (MSIV) [ISV] remained open with Main Steam Relief Valves (MSRVs) [RV] operating on the initial transient as expected. Main Turbine Bypass Valves [V] controlled reactor pressure. Reactor Feedwater pumps [P] remained in service to control reactor water level. Primary Containment Isolation System [JM] Groups 2, 3, 6, and 8 containment isolation and initiation signals were received. Upon receipt of these signals all required components actuated as required. All safety systems operated as expected. The Tennessee Valley Authority is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.7 3(a)(2)(iv)(A), as any event or condition that resulted in a manual or automatic actuation of the RPS and general containment isolation signals affecting containment isolation valves in more than one system or multiple MSIVs. 8. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event The EHC system had no megawatt input logic, because both megawatt input transducers [TD] (Nexus modules) were non-functional and had been out of service since January 22, 2018. | ML19087A244
Dresden Nuclear Power Station | Unit 2 | Secondary Containment Differential Pressure Exceeded Technical Specification due to Excess Ventilation Supply Flow | 03-29-2019 | On January 30, 2019, the operating heating boiler tripped during a period of extremely cold external air temperatures. To address the potential of freezing the heating steam coils and filters, procedures provided direction to open the ventilation inlet plenum doors. At 0910, the Reactor Building differential pressure degraded and was determined to be below 0.25 inches water column vacuum. Technical Specification (TS) 3.6.4.1, "Secondary Containment," was not met and Condition A, Secondary Containment inoperable, was required since differential pressure degraded below the 0.25 inches water column vacuum by local average gauge readings. Standby Gas Treatment was started to assist in differential pressure control. At 0928, differential pressure improved and was maintaining above 0.25 inches water column vacuum. TS 3.6.4.1 Condition A was exited. This event is reportable under 1O CFR 50.73(a)(2)(v)(C), "Any event or condition that could have prevented the fulfillment of the safety function of ... systems that are needed control the release of radioactive material." The cause of the event was determined to be inadequate procedural guidance for responding to loss of heating boilers during extreme cold external air conditions. Corrective actions include revising station procedure to prioritize actions to mitigate ventilation transients during a loss of heater boilers. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: BO hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, {3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid 0MB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. http://www. n re.gov/reading-rm/doc-collections/nu regs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Dresden Nuclear Power Station, Unit 2 05000237 NUMBER NO. 2019 - 001 00 | PLANT AND SYSTEM IDENTIFICATION Dresden Nuclear Power Station (DNPS), Unit 2, is a General Electric Company Boiling Water Reactor with a licensed maximum power level of -2957 megawatts thermal. The Energy Industry Identification System codes used in the text are identified as [XX]. A. Plant Conditions Prior to Event: Unit: 02 Event Date: 01/30/2019 Event Time: 091 O CST Reactor Mode: 1 Mode Name: Power Operation Power Level: 100 percent B. Description of Event: On January 30, 2019, the operating heating boiler [BLR] tripped during a period of extremely cold external air temperatures of approximately -25 degrees Fahrenheit (F). The heating boiler tripped with subsequent supply low air temperature alarm [TA] at 0850. The heating boiler tripped due to sluggish operation of its pressure regulator [RG]. Due to the loss of heating steam to the ventilation supply steam coils, the temperature of the supply air to the Reactor Building (RB) [NG] ventilation [VA] system rapidly decreased, which began to degrade the ability of RB ventilation to maintain Secondary Containment [NG] differential pressure (DP). To address the potential of freezing the heating steam coils [HCL] and filters [FLT], station procedures for loss of heating boilers provided direction to open the RB ventilation inlet plenum doors [DR]. Opening the plenum doors further degraded the ability to maintain RB DP due to additional air supply path to the plenum vent fan suctions. At 0900, there was an unexpected low RB differential pressure alarm [PDA]. At 0910, DP readings from the local gauges located on each wall of the refuel floor were obtained. The average of these RB DP readings was determined to be below 0.25 inches water column (we) vacuum showing Secondary Containment DP had degraded. This condition led to not meeting Technical Specification {TS) 3.6.4.1, "Secondary Containment," and required entering Condition A, "Secondary Containment inoperable in Mode 1, 2, or 3," Required Action A.1, "Restore Secondary Containment to OPERABLE status," with a Completion Time of four hours. At 0922, the Standby Gas Treatment (SBGT) [BH] system was started. At 0928, Unit 3 RB ventilation system was secured. RB DP improved and was maintaining above 0.25 inches we vacuum. TS 3.6.4.1 Condition A was exited. An 8-hour non-emergency notification was made via Emergency Notification System (ENS #53851) in accordance with 1O CFR 50.72(b){3){v)(C) for the loss of Secondary Containment. NRG FORM 366A (04-2018) Page _2_ of _3_ | ML19091A046
Quad Cities Nuclear Power Station | Unit 1 | HPCI System Inoperable Due to Blown Fuse in the Motor Speed Changer Circuit | 04-05-2019 | On February 5, 2019, at 1804 hours, a Motor Speed Changer (MSC) logic fuse blew during performance of Quad Cities Nuclear · Power Station (QCNPS) Unit 1 High Pressure Coolant Injection (HPCI) operability surveillance following planned maintenance activities. Had HPCI been demanded while the fuse was blown the HPCI turbine would have been unable to reach its required speed. During investigation of the blown fuse, the MSC motor and the MSC gearbox were discovered tG> be mechanically bound. Intermittent failure of the Low Speed Stop (LSS) Limit Switch (LS) due to age related degradation of internal electrical contacts allowed the MSC motor to remain energized when it should have been deenergized, leading to degradation. The limit switch contacts were found with high resistance attributed to observed deposits and pitting. None of these components were part of the work scope of this HPCI maintenance window. The immediate corrective action was replacement of the fuse, the LSS LS, the MSC motor and select MSC gearbox components. the safety impact was minimal based on the availability of other high pressure and low pressure Emergency Core Cooling Systems. This is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D) for an Event or Condition that Could Have Prevented Fulfillment of a Safety Function to Mitigate the Consequences of an Accident. NRG FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMS control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r31) 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR Quad Cities Nuclear Power Station Unit 1 05000254 NUMBER NO. 2019 - 001 - 00 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX]. EVENT IDENTIFICATION HPCI System Inoperable Due to Blown Fuse in the Motor Speed Changer Circuit A. CONDITION PRIOR TO EVENT Unit: 1 Event Date: February 5, 2019 Event Time: 1804 hours Reactor Mode: 1 Mode Name: Power Operation Power Level: 100% There were no other structures, systems or components (SSC) inoperable during this event time period that could have contributed to this event. 8. DESCRIPTION OF EVENT On February 5, 2019, at 1804 hours, during a Unit 1 High Pressure Coolant Injection (HPCl)[BJ] operability surveillance, a fuse [FU] blew in the logic for the Motor Speed Changer (MSC)[SM] for the HPCI Turbine [TRB]. The blown fuse disabled both the manual and automatic injection functions of HPCI. Had HPCI been demanded while the fuse was blown the HPCI turbine would have been unable to reach its required speed. The system had been out of service for planned maintenance, but no maintenance activities took place on equipment protected by this fuse. On February 6, 2019, at 0222 hours, ENS #53816 was made to the NRC under 10 CFR 50.72(b)(3)(v)(D), to report this event as an event or condition that could have prevented the fulfillment of a safety function. November 8, 2018 was the last successful test of Unit 1 HPCI. During troubleshooting, it was found that the MSC motor [MO] and the MSC gearbox were mechanically bound. The fuse .• the MSC motor, and select gearbox components were replaced. Subsequent troubleshooting determined that intermittent failure of the Low Speed Stop (LSS) Limit Switch (LS)[33], caused intermittent operation of the associated relay. The LS intermittent failure was due to high resistance contacts attributed to deposits and pitting caused by age related degradation. The LSS LS was replaced. After troubleshooting and repairs, a HPCI operability surveillance was performed successfully. HPCI was declared operable on February 8, 2019, at 1434 hours. Since HPCI is a single train safety system, this notification is being made in accordance with 10 CFR 50.73(a)(2)(v)(D) for an Event or Condition that Could Have Prevented Fulfillment of a Safety Function to Mitigate the Consequences of an Accident. C. CAUSE OF EVENT The cause of the event is the intermittent failure of the MSC LSS LS, which impacted both the MSC motor and gearbox. LS failure is attributed to age related degradation of internal LS electrical contacts. The LS had been installed for more than 9 years and was due for replacement at 10 years. NRG FORM 366A (04-2018) Page _2_ of _4_ | ML19095A380
Peach Bottom Atomic Power Station | Unit 2 | Emergency Bus Breaker Relay Failure Results in Loss of Safety Function | 04-11-2019 | On February 11, 2019, at 2232 hours, an off-site power source was Jost due to a malfunction of a lightning arrestor located at an off-site substation. As a result, six of the site's eight 4kV emergency buses transferred to their alternate offsite source. During this process, a breaker that supplies power to a 480 volt load center (E434) fed from the E43 emergency 4kV bus failed to automatically re-close due to a failed relay. This resulted in the E4 emergency die_sel .. generator being inoperable and Joss of safety function of the 'B' Core Spray loop. The 'A' Core Spray loop was . ,· inoperable at the time due to planned maintenance. This resulted in a loss of the Core Spray safety function for approximately 7 hours and 44 minutes. The 'A' Core Spray loop was restored and returned to an operable status at 0616, which restored the Core Spray safety function. The transfer to the alternate offsite power source also resulted in a Group JI and Ill primary containment isolation, as designed. This is considered an invalid actuation. There were no actual safety consequences as a result of this event. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to· the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid 0MB control number, the NRG may riot conduct or sponsor, and a person is not required to respond to, the information collection. http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FA~ILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR Peach Bottom Atomic Power Station Unit 2 05000277 NUMBER NO. 2019 - 001 - 00 | Unit Conditions Prior to the Event Unit 2 and Unit 3 were both operating in Mode 1 at approximately 100% rated thermal power. The Unit 3 'A' Core Spray [EIIS:BM] loop was out of service for planned maintenance. Description of Event On February 11, 2019, at 2232 hours, the Cooper-Nottingham (220-08 line) off-site power source was lost due to a malfunction of a lightning arrestor located at an off-site substation.· At the time of the transient, six of the site's eight 4kV emergency buses [EIIS:EB] were aligned to the #2 Emergency Auxiliary Transformer, which is normally fed by the 220-08 line. The loss of the 220-08 line caused the 4kV emergency buses to transfer to the #3 Emergency Auxiliary Transfor.mer, which is fed by the Ne-wlinville (220-34 line) offsit.e source. The transfer resulted in the loss of the running Control Rod Drive (CRD) [EIIS:AA] pumps and Group II and Ill primary containment isolations for both units. This is the designed response for this event and operators responded in accordance with plant procedures. The transfer also resulted in isolation of the Unit 3 main condenser off-gas recombiner, which caused a reduction in condenser vacuum and a reduction in Unit 3 power to 85%. Due to the loss of one offsite power source, Technical Specification (TS) 3.8.1 Condition A was entered, which has required actions to restore the offsite circuit within seven days. Following transfer of power for the E43 emergency 4kV bus to the alternate source, the E434 transformer breaker, which supplies power from the E43 bus to the Unit 3 E434 480 volt emergency load center [EIIS:ED], failed to automatically re-close. With the E434 breaker open, the Unit 3 E434 load center was de energized and inoperable. TS 3.8.7 Condition A was entered for Unit 2 and TS 3.8.7 Condition C was entered for Unit 3, which requires the E434 load center to be restored within 8 hours. At 2250 hours the E434 breaker was manually closed from the main control room to re-energize the emergency load center and TS 3.8.7 Condition A and Condition C was exited. The Unit 3 E434 load center was inoperable for 18 minutes. On February 12, 2019, at 0430 hours, the E4 diesel generator was declared inoperable due tc:> not meeting surveillance requirement conditions. TS Surveillance Requirement (SR) 3.8.1.11.c.2 and SR 3.8.1.19.c.2 require the E434 breaker to have the capability to automatically close in order for the E4 diesel generator to be considered operable. With one off-site source inoperable and one diesel generator inoperable, TS 3.8.1 Condition E was entered, which 'requires the off-site source or the diesel generator to be restored to - operable within 12 hours. The 'A' Core Spray loop was out of service at the beginning of this event for planned maintenance and was restored and returned to an operable status on February 12, 2019 at 0616 hours. NRG FORM 366A (04-2018) Page _2_ of _§_ | ML19109A097
Fermi 2 05000 341 1 OF 3 | Unknown Unit | Secondary Containment Airlock Doors Opened at the Same Time Resulting in a Condition Prohibited by Technical Specifications | 02-19-2019 | On February 19, 2019, at 1307 EST, with the reactor at 100 percent Core Thermal Power and steady state conditions, plant personnel notified the Main Control Room that both doors in the Secondary Containment Airlock on the Reactor Building Fifth Floor were opened and could not close. The Airlock Doors were opened simultaneously for a period of approximately five minutes (i.e., from 1253 to 1258 EST). A technician had opened both air lock doors simultaneously when he egressed through first door and grabbed the handle of the second airlock door and inadvertently pushed the door open before the opposing door had closed. The interlock device for the doors had failed. The interlock is designed to prevent both doors from being opened simultaneously. Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.3 was not met. The maximum Secondary Containment (SC) pressure observed during that time remained within TS limits. There were no radiological releases associated with this event. Declaring SC inoperable as a result of not meeting TS SR 3.6.4.1.3 is reportable under 10CFR50.72(b)(3)(v)(C) and this written report is required under 10CFR50.73(a)(2)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. The doors were closed in approximately 5 minutes and SC was restored. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03131/2020 (04-2018) Estimated burden perr esponstoe c omply with this mandatory collectiorenq ues8t0: hours, Reported LICENSEE EVENT REPORT (LER) lessonlesa rneadr ein corporated intoth el icensinpgro cesasn df edb ackto industry. Sendc omments y /- CONTINUATION SHEET regardinbgu rdene stimatteo theI nformatiSoenr viceBsr anch(T -2 F43),U . S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or bye -mail to Infocollects.Resource@nrc.gov, and to ". « the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of (See NUREG-1022, R.3 for instruction and guidance for completing this form Management andB udgeWta, shington, DC2 0503. If a meanuss edto imposaen i nformation http:/Ixnmww goo/reading-rm/doccollections/nuregs/staff/srl 022/r3/) s c p o on ll s e o c r, t a iod n no d a e p sn e o r t s d o is in p s l n ay o tr a e c q u u rre ir n et tl o y d r v e a s lid p o O n M tod B , t h co e n i t n ro f l o n rm um at b icoo e lnl rt e h, c e tio N n R . C may not conduct or 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Fermi 2 05000- 341 NUMBER NO. 312019 - 02 - 0 | INITIAL PLANT CONDITIONS Mode 1 Reactor Power 100% DESCRIPTION OF THE EVENT On February 19, 2019, at 1307 Eastern Standard Time (EST), with the reactor in steady state operations, the main control room was notified that both airlock doors [[DR]] for the Secondary Containment (SC) [[NH]] on the reactor building fifth floor were opened. The airlock doors were opened simultaneously for a period of approximately five minutes (i.e., from 1253 to 1258 EST). A technician had opened both air lock doors simultaneously when he egressed through first door and grabbed the handle of the second airlock door and inadvertently pushed the door open before the opposing door had closed. The airlock door locking pins became stuck once the doors were simultaneously opened preventing either door , from being closed. The interlock [[IEL]] device for the doors had failed. The interlock is designed to prevent both doors from being opened simultaneously. Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.3 was not met with both doors opened. The locking pins were released and airlock doors were closed after approximately 5 minutes. The airlock and secondary containment were restored. The maximum SC pressure observed during that time remained within TS limits for SC operability. There were no radiological releases associated with this event. Declaring SC inoperable was a result of not meeting TS SR 3.6.4.1.3. The condition was reported to the NRC Operations Center per event notification number 53888 under 10CFR50.72(b)(3)(v)(C) and this written report is required under 10CFR50.73(a)(2)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. SIGNIFICANT SAFETY CONSEQUENCES AND IMPLICATIONS There were no safety consequences or radiological releases associated with this event. At no time during this event was there a potential for endangering the public health and safety. The SC reactor and auxiliary building fifth floor airlock maintains one door closed when traversing into or out of the reactor building fifth floor. A negative pressure is maintained in the reactor building and portions of the auxiliary building. Radioactive materials remain in the auxiliary building and reactor building and any release of radioactive material is monitored for radiation before exhausting to the environment during normal operation. When both air lock doors were open for approximately 5 minutes on February 19, negative pressure was maintained in SC and the auxiliary building. The SC vacuum remained within the TS operability limit of greater than or equal to 0.125 inches of vacuum water gauge per TS Surveillance Requirement (SR) 3.6.4.1.1. Therefore, there was no unmonitored release during the event. CAUSE OF THE EVENT The technician turned the auxiliary building fifth floor door handle and inadvertently pushed on the auxiliary building door prior to the reactor building door being closed and latched. The technician didn't recognize the risk of turning the handle prior to verifying the opposing door being closed and latched and relied on the interlock to hold the reactor building door closed. The reactor building fifth floor airlock door did not latch and the airlock doors interlock failed, allowing the auxiliary building fifth floor door to open while the reactor building fifth floor door still was open. The interlock device failed. | ML19112A331
Perry Nuclear Power Plant 05000-440 1 OF 3 | Unknown Unit | : | 04-24-2019 | On February 25, 2019, at 0024 hours, the Reactor Protection System (RPS) automatically actuated due to turbine stop and control valve closure caused by a turbine trip. The turbine trip was caused by a loss of generator excitation, resulting in the loss of the main generator field. The cause was determined to be inadequate preventive maintenance (PM) acceptance criteria for generator exciter brush replacement. The criteria for brush inspection and replacement should have added margin to brush lifetime to ensure brushes could not wear to the point where brush spring tension could no longer be properly maintained. Corrective actions included modifying preventive maintenance criteria to add margin to replace brushes earlier in their lifetime, and ensuring all brushes are checked for vibration during the PM. The plant responded as expected, all control rods inserted and there were no Emergency Core Cooling System (ECCS) actuations. The risk of this event is considered very small in accordance with the Regulatory Guidance. This event is reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in an automatic actuation of the RPS. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid 0MB control number, the NRC may not conduct or http://www. nr e.gov/read i nq-rm/doc-collections/n u regs/staffl s r1 022/r3/ sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Perry Nuclear Power Plant 05000-440 NUMBER NO. 2019 001 00 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. INTRODUCTION On February 25, 2019, while coasting down to enter a refuel outage and with the plant in Mode 1 at approximately 7 4 percent rated thermal power, the Reactor Protection System (RPS) [JC] automatically actuated due to turbine stop and control valve closure caused by a turbine [TG] trip. The turbine trip was caused by a loss of generator [GEN] excitation [EXC]. The generator received a lockout signal from the loss of excitation relay [RLY] following its associated time delay relay [62] actuation. The plant responded as expected and all control rods inserted and there were no Emergency Core Cooling System (ECCS) actuations. At 0344 hours, notification was made to the NRC Operations Center (Event Notification ENS 53896) in accordance with 10 CFR 50.72(b)(2)(iv)(B) as an event or condition that results in an actuation of the RPS when the reactor is critical. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in an automatic actuation of the RPS. EVENT DESCRIPTION On February 25, 2019 at 0024 hours, an RPS actuation was automatically initiated due to turbine stop and control valve closure caused by a turbine trip. The main generator received a lockout signal from the loss of excitation relay following its associated time delay relay actuation. In the six seconds prior to the lockout signal, there was a decrease in grid voltage from approximately 346 Kilovolts (kV) to approximately 311 kV. Correspondingly, the main generator Mega Volts Ampere Reactiv~ (MVARs) increased significantly. This equipment response is expected for a valid loss of excitation event and once the field current stopped, the generator acted as an induction motor instead of a synchronous generator and drew MVARs from the grid to support its magnetic field. This flow of MVARs resulted in a decreased local grid voltage until the generator tripped. The event progression was that one or more of the exciter inboard brushes reached its wear limit. The brush spring(s) was(were) out of range to ensure positive, adequate downward pressure to the brush(es) to assure proper electrical connection was maintained. When the brush spring(s) pressure was limited, the brush(es) began to bounce/chatter. Each time a brush fails to make adequate connection, the current it is carrying is broken. As the radial distance between the brush and collector [COL] ring surface increases, the current is strong enough to cross over the minimal air gap creating an arc. An arc can impose physical damage and create surface defects in the form of pits (peaks and valleys) that act as increased friction to increase the wear rate of other brushes that may ride on the same ring surface. The longer this bouncing and subsequent arcing continues, conditions for impaired electrical connection degrade in an exponential manner. As high current discharges repeatedly occur, arcing also causes increased heating of the collector ring and brushes. Once the radial distance between the brush and collector ring surface increases enough, the air gap becomes great enough that the arc does not connect the brush and collector ring, but finds the path of least resistance, some external source to ground, which is referred to as a "flashover" event. | ML19114A443
Quad Cities Nuclear Power Station | Unit 1 | Four Main Steam Isolation Valves (MSIVs) Closure Times Exceeded | 04-25-2019 | On March 27, 2017, during refueling outage 01 R24 at 0840 hours, the Unit 1 Main Steam Isolation Valve (MSIV) as-found closure time test results indicated that four MSIVs failed to close within the required Technical Specification (TS) time of less than or equal to five seconds. The safety significance of this event was minimal. The cause of two of the four MSIV slow closure timing events was inadequate procedure on how to apply Super 0-Lube to valve stem bottom 0-ring of the airpack manifold solenoid, and the cause of the other two slow closure timing events was environmental conditions in the Unit 1 MSIV Room. Corrective actions included replacing the 1· 0203-1 B and 1· 0203-1 D MSIV airpack manifolds in 01 R25, revising the MSIV airpack manifold maintenance procedure regarding the amount of Super 0-Lube to be applied, and revising operating procedures to prevent MSIV closure time drift observed to occur at MSIV room temperatures below 90 degrees F. This condition is being reported in accordance with 10 CFR 50. 73(a)(2)(i)(B), which requires reporting of any operation or condition that was prohibited by the plant's TS. NRG FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory crnlection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the lnfonnation Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of lnfonnation and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an infonnation (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB contrrn number, the NRG may not conduct or sponsor, and a person is not required to respond to, the infonnation collection. http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Quad Cities Station Unit 1 05000254 NUMBER NO. 2017 - 002 01 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Four Main Steam Isolation Valves (MSIVs) Closure Times Exceed Technical Specifications Limit A. CONDITION PRIOR TO EVENT Unit: 1 Event Date: March 27, 2017 Event Time: 0840 hours Reactor Mode: 4 Mode Name: Cold Shutdown Power Level: 0% B. DESCRIPTION OF EVENT On March 27, 2017, while Unit 1 was in Mode 4 for refueling outage 01 R24, Operations was performing surveillance, "MSIV Closure Timing," when four of the eight Unit 1 Main Steam [SB] Isolation Valves [ISV] (MSIVs), 1-0203-1 B, 1-0203-1 D, 1-0203-2C, and 1-0203-20 failed to close within the required cold shutdown Technical Specification (TS) limit of greater than or equal to three seconds and less than or equal to five seconds. The closure times for those four MS IVs were 5. 7, 5.2, 5.1, and 5.6 seconds, respectively. The other four MS IVs all closed within the required TS time. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), which requires reporting of any operation br condition that was prohibited by the plant's Technical Specifications. C. CAUSE OF EVENT MS IVs 1-0203-2C and 1-0203-20 are located in the Unit 1 MSIV Room and MS IVs 1-0203-1 B and 1-0203-1 D are located in the Unit 1 Drywell. The cause of the slow closure timing events for the 1-0203-1 B and 1-0203-1 D MS IVs was due to an inadequate procedure on how to apply Super 0-Lube to valve stem bottom 0-ring of the airpack manifold. The slow closure times were due to excess Super 0-Lube on airpack manifold solenoids. The maintenance procedure for applying the Super 0-Lube was not specific on the amount of lubricant to be used on the bottom 0-ring. The cause of the slow closure timing events for the 1-0203-2C and 1-0203·.20 MSIVs was due to environmental conditions in the Unit 1 MSIV Room. Beginning in June 2009, the average temperature in the Unit 1 MSIV room was significantly reduced due to the replacement of the MSIV room coolers. An abnormal drift between the as-left closure time from the previous outage to the as-found closure time of the current outage has been observed to be correlated with cooler room temperatures. A similar temperature-correlated drift was not observed for the MSIVs located inside the drywell, where the temperature is consistently warmer than the MSIV Room._ NRG FORM 366A (04-2018) Page _2_ of _4_ | ML19115A136
Quad Cities Nuclear Power Station | Unit 2 | Two Main Steam Isolation Valves (MSIVs) Closure Times Exceeded | 04-25-2019 | On March 19, 2018, during refueling outage 02R24 at 07 45 hours, the Unit 2 Main Steam Isolation Valve (MSIV) as-found closure time test results indicated that the closure time for two MSIVs exceeded the Technical Specification (TS) upper limit of less than or equal to five seconds. These two MS IVs were the inboard valves on the A and C Main Steam Lines. The safety significance of this - event was minimal. The cause of the slow closure timing events was due to an inadequate procedure on how to apply Super 0-Lube to the valve stem bottom 0-ring of the airpack manifold. Corrective actions include replacement of the two air pack manifolds and revising the MSIV airpack manifold maintenance procedure regarding the amount of Super 0-Lube to be applied. This condition is being reported in accordance with 10 CFR 50. 73{a){2)(i)(B), which requires reporting of any operation or condition that was prohibited by the plant's TS. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04·2018)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send 'lr.,J.,._'ARrG(I(.., comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear { ~ LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, \ . • CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. II a means •*..-tc.• I} used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR Quad Cities Nuclear Power Station Unit 2 05000265 NUMBER NO. 2018 - 001 01 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Two Main Steam Isolation Valves (MSIVs) Closure Times Exceeded A. CONDITION PRIOR TO EVENT Unit: 2 Event Date: March 19, 2018 Event Time: 0745 hours Reactor Mode: 4 Mode Name: Cold Shutdown Power Level: 0% B. DESCRIPTION OF EVENT On March 19, 2018, while Unit 2 was in Mode 4 for refueling outage 02R24, Operations was performing surveillance, "MSIV Closure Timing," in accordance with Technical Specification (TS) Surveillance Requirement (SR) 3.6.1.3.6. During the surveillance, two of the eight Unit 2 Main Steam [SB] Isolation Valves [ISV] (MSIVs) failed to close within the required cold shutdown TS limit of greater than or equal to three seconds and less than or equal to five seconds. The two affected MSIVs were the inboard MS IVs on the A and C Main Steam lines. The closure times for those two MSIVs were 5.3 and 5.6 seconds, respectively. The other six MSIVs all closed within the required TS time. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), which requires reporting of any operation or condition that was prohibited by the plant's TS. C. CAUSE OF EVENT The cause of the slow closure timing for the MS IVs was due to an inadequate procedure on how to apply Super 0- Lube to valve stem bottom 0-ring of the airpack manifold. The slow closure times were due to excess Super 0-Lube on the airpack manifold solenoids. The maintenance procedure for applying the Super 0-Lube was not specific on the amount of lubricant to be used on the bottom 0-ring. D. SAFETY ANALYSIS System Design The MS IVs are 20-inch air/spring operated, balanced "Y"-type globe valves. The safety function of the MSIVs is to prevent reactor coolant [AD] inventory loss and protect plant personnel in the event of steam line breakage outside the isolation valves, and to complete the primary containment [NH] boundary after a Loss of Coolant Accident (LOCA). There are four main steam lines and each steam line has two isolation valves, one inside (inboard MSIV) and one outside (outboard MSIV) of primary containment. The valves are designed to close and to be leak-tight during the worst conditions of pressure, temperature, and steam flow following a break in the main steam line outside the containment. The MSIVs are leak tested in accordance with 10 CFR 50 Appendix J program. NRG FORM 366A (04-2018) Page _2_ of _4_ | ML19115A142
Clinton Power Station | Unit 1 | Unplanned Reactor Scram During Maintenance Outage Due to High Intermediate Range Monitor Flux | 04-24-2019 | On October 28, 2018, at 0445 CDT at approximately 0.5% power while performing a soft shutdown in support of a planned maintenance outage (C1 M23), the plant experienced an unplanned Reactor Protection System (RPS) actuation due to Intermediate Range Monitors (IRMs) High Flux. At the time of the event Main Steam Line (MSL) drains were being closed to control the reactor cooldown rate. When MSL drain isolation valve1 B21-F016 was full closed, pressure reduction (cooldown) stopped resulting in a small reactor water level change and the Feedwater system responded by injecting a small amount of cold water. This combination of conditions resulted in a positive reactivity change which resulted in the reactor scram. A review of the Feedwater system response determined that the system responded as designed and no equipment failure initiated the conditions leading to the scram. The cause of the event was pressure control guidance was not adequate to address the cooldown rate conditions during a soft shutdown. Corrective actions include implementing best practices for pressure control strategies, abort criteria based on reactor pressure, actions to minimize time in the region of vulnerability, and associated operator training. This event is reportable under the provisions of 1O CFR 50.73(a)(2)(iv)(A) as an "event or condition that resulted in the manual or automatic actuation of the Reactor Protection System." -J I NRG FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported ' lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means. used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid 0MB control number, the NRG may not conduct or http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR Clinton Power Station, Unit 1 05000461 NUMBER NO. 2018 - 005 - 02 | PLANT AND SYSTEM IDENTIFICATION General Electric -- Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in text as [XX]. EVENT IDENTIFICATION Unplanned Reactor Scram During Maintenance Outage Due to High Intermediate Range Monitor Flux A. Plant Operating Conditions Before the Event Unit: 1 Eve:nt Date: October 28, 2018 Event Time: 0445 Mode: 2 Mode Name: Startup Reactor Power: 0.5 percent B. Description of Event On October 28, 2018 at 0445 CDT at approximately 0.5% power while performing a soft shutdown in support of a planned maintenance outage (C1 M23), the plant experienced an unplanned Reactor Protection System (RPS) actuation due to Intermediate Range Monitors (IRMs) [IG] High Flux. At the time of the event Main Steam Line (MSL) drains were being closed to control the reactor cooldown rate. When MSL drain isolation valve1 B21-F016 was full closed, pressure reduction (cooldown) stopped resulting in a small reactor water level change and the Feedwater system [SJ] responded by injecting a small amount of cold water. A review of the motor driven reactor feedwater pump (MDRFP) injection valve 1 FW004 response during the event determined that the valve had responded as designed under the low feedwater demand conditions that the scram experienced. NRG FORM 366A (04-2018) Page_2_ of _3_ | ML19119A075
Comanche Peak Nuclear Power Plant 05000 445 1 OF 3 | Unknown Unit | LT OP Power Operated Relief Valve (PORV) Setpoint | 04-25-2019 | On February 2, 2019 at 1500, Westinghouse reported that while reviewing the Low Temperature Overpressure (L TOP) system analysis of record (CN-SCS-04-100, Rev. 3) for areas of margin that could offset the increase in differential pressure required to support the Mechanical Stress Improvement Project (MSIP), errors were discovered. On March 9, 2019 an evaluation was completed that determined the Unit 2 LT OP system had been inoperable in the past for longer than allowed by Technical Specifications. Corrective actions include changing the LT OP PORV lift settings, on both Units 1 and 2 to meet the protection requirements of 10 CFR 50 Appendix G, Fracture Toughness Requirements. All times listed in this report are Central Standard Time (CST). NRG FORM 366 (04-2018) NRG FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U. S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid 0MB control number, the NRG may not conduct or http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000-1 445 u~-1 NUMBER I-N~O. Comanche Peak Nuclear Power Plant I 001 | I. DESCRIPTION OF REPORTABLE EVENT A. REPORTABLE EVENT CLASSIFICATION This event is reportable in accordance with 1 OCFR50.73(a)(2)(i)(B); Any operation or condition which was prohibited by the plant's Technical Specifications except when: (1) The Technical Specification is administrative in nature; (2) The event consisted solely of a case of a late surveillance test where the oversight was corrected, the test was performed, and the equipment was found to be capable of performing its specified safety functions; or (3) The Technical Specification was revised prior to discovery of the event such that the operation or condition was no longer prohibited at the time of discovery of the event. B. PLANT CONDITION PRIOR TO THE EVENT Both Unit 1 and Unit 2 were operating at 100% Rated Thermal Power. C. STATUS OF STRUCTURES, SYSTEMS, OR COMPONENTS THAT WERE INOPERABLE AT THE START OF THE EVENT AND CONTRIBUTED TO THE EVENT Prior to the event, no Structures, Systems, or Components were inoperable that contributed to the event. D. NARRATIVE SUMMARY OF THE EVENT, INCLUDING DATES AND APPROXIMATE TIMES • · On February 4, 2019, Westinghouse informed Comanche Peak that calculation errors had caused the maximum allowable PORV LT OP lift settings to be higher than allowed to meet 10 CRR 50 Appendix G, Fracture Toughness Requirements. On March 13, 2019, an evaluation was completed that determined the Unit 2 LT OP system was inoperable for greater than the 7 day Completion Time while in MODE 4 on one occasion. The LT OP system was not operable because it did not comply with 10 CFR 50, Appendix G, Fracture Toughness Requirements. This single event would have required depressurizing the Reactor Coolant System (RCS) and establishing an RCS vent>/= 2.98 square inches within 8 hours. The evaluation also determined the Unit 2 LT OP system was inoperable for greater than the 24 hour Completion Time on three occasions while in MODE 5. The L TOP system was not operable because it did not comply with 10 CFR 50, Appendix G, Fracture Toughness Requirements. Each of the three events would have required depressurizing the Reactor Coolant System (RCS) and establishing an RCS vent>/= 2.98 square inches within 8 hours. In all four cases the failure to vent the RCS caused operation in a manner prohibited by Technical Specifications. The current PORV L TOP lift settings would not have resulted in a challenge to reactor vessel integrity and would have performed their safety function E. THE METHOD OF DISCOVERY OF EACH COMPONENT OR SYSTEM FAILURE, OR PROCEDURAL PERSONNEL ERROR A past operability evaluation was completed on March 13, 2019 that identified four times that Unit 2 was operating outside of Technical Specification requirements associated with completion times for L TOP inoperability in the three years prior to event discovery. Unit 1 was not operated outside of Technical Specifications in the three years prior to event discovery. NRG FORM 366A (04-2018) Page 2 of 3 | ML19127A079
Brunswick Steam Electric Plant (BSEP) | Unit 1 | Degraded Principal Safety Barrier, Technical Specification Shutdown, and Automatic System Actuation | 05-23-2019 | At 14:19 Eastern Daylight Time (EDT) on March 28, 2019, with Unit 1 in Mode 1 at approximately 100 percent power, drywell pressure and floor drain leakage began to increase. Operators proceeded with a controlled shutdown per procedures. The reactor was scrammed at 16:03 EDT to complete the shutdown. At 16:54 EDT, following the scram, Primary Containment Isolation System (PCIS) actuation occurred, closing the outboard Main Steam Isolation Valves (MSIVs) due to low condenser vacuum. Subsequently, Reactor Protection System (RPS) actuation occurred due to low reactor water level. The safety function of the MSIVs and RPS had already been completed. There was no impact on the health and safety of the public or plant personnel. This event was a result of a steam leak in the drywell caused by the failure of a 1-inch cryogenic pipe coupling. The failure was due to hydrogen embrittlement from long-term exposure to high temperature and elevated hydrogen levels. A Unit 1 and Unit 2 extent of condition evaluation was performed; susceptible cryogenic couplings were replaced with welded fittings. As a result of the Technical Specification-required shutdown, the valid actuations of PCIS and RPS, and the degradation of a principal safety barrier, this event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(A), 10 CFR 50.73(a)(2)(iv)(A), and 10 CFR 50.73(a)(2)(ii)(A) respectively. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB control number, the NRC may not conduct or http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant (BSEP), 05000325 YEAR NUMBER NO. Unit 1 2019 - 002 - 00 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. Background Initial Conditions At the time of the event, Unit 1 was in Mode 1 (i.e., Power Operation), at approximately 100 percent rated thermal power. Reportability Criteria This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(A) because a Technical Specification-required shutdown was completed. Technical Specification Action 3.4.4.A, Unidentified Reactor Coolant System (RCS) [AD] leakage increase not within limit, requires RCS leakage to be reduced to within limits within 8 hours. The shutdown was required because the leakage would not have been reduced to within limits within the required Technical Specification Completion Time. In addition, this event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) because, subsequent to the shutdown, with the Unit in Mode 3 at 0 percent power, it involved actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B). Specifically, the outboard MSIVs [JM] automatically closed, per design, in response to low condenser vacuum, and RPS [JC] actuation occurred, per design, in response to low reactor water level. This event is also being reported in accordance with 10 CFR 50.73(a)(2)(ii)(A) because it was the result of a degraded principal safety barrier (i.e., the RCS pressure boundary [AD]). The steam leak in the drywell was caused by the failure of a 1-inch cryogenic pipe coupling located on the steam side of the reference leg for the N004B reactor level instruments which is part of the RCS pressure boundary. During this event the Unit 1 unidentified RCS leakage was greater than 10 gallons per minute (gpm) for greater than or equal to 15 minutes and, as a result, an Unusual Event (UE) was declared. The NRC was notified of this per 10 CFR 50.72(a)(1)(i) via Event Notification number 53961 at 15:07 EDT on March 28, 2019. Event Description At 14:19 EDT on March 28, 2019, while operating at approximately 100 percent reactor power, the Brunswick Nuclear Plant Unit 1 N004B narrow range reactor water level instrument (1-C32-LI-R606B) failed high, and drywell pressure and drywell floor drain leakage began to increase. Operators vented the drywell and proceeded with a controlled shutdown in accordance with procedures. The reactor was scrammed at 16:03 EDT to complete the shutdown. At 16:54 EDT, during implementation of post scram actions, actuation of PCIS occurred, closing the outboard MSIVs due to low condenser vacuum. The MSIVs had been manually closed, per procedure, during the shutdown evolution to control reactor pressure and were in the process of being reopened when actuation occurred. The inboard MSIVs had not been reopened when the isolation occurred. Subsequently, at 16:58 EDT, a RPS actuation occurred due to reactor water level dropping below the actuation setpoint due to the increased steam demand associated with equalizing and opening MSIVs. All control rods were already inserted at the time of the actuation. The safety function of both the MSIVs and RPS had already been completed. During the shutdown, the unidentified RCS leakage was greater than 10 gpm for greater than or equal to 15 minutes and a UE was declared in accordance with Brunswick Emergency Action Level SU 5.1. The UE was terminated at 02:59 EDT on March 29, 2019, once RCS leakage was reduced to less than 10 gpm. Event Cause Investigation revealed that a 1-inch cryogenic (Cryofit) pipe coupling on the steam side of the reference leg for the N004B reactor level instruments experienced a 360 degree circumferential separation at the approximate center of the coupling. This opened a path for steam from the reactor to leak into the drywell. | ML19143A375
Brunswick Steam Electric Plant (BSEP) | Unit 1 | Unplanned Automatic Start of Emergency Diesel Generators | 05-23-2019 | At 04:02 Eastern Daylight Time (EDT) on March 25, 2019, an actuation of the four Emergency Diesel Generators (EDGs) occurred. Unit 1 was in Mode 1 at approximately 100 percent power and Unit 2 was in Mode 4 at 0 percent power. Unit 2 was in the process of aligning the electrical distribution system to power the emergency buses via the Unit Auxiliary Transformer (UAT) when a main generator differential lockout relay actuated; thereby starting the EDGs. The emergency buses remained energized from offsite power via the Startup Auxiliary Transformer (SAT) and, therefore, the EDGs did not tie to their respective buses. The EDGs responded per design to this event. The cause of event was a historical design change error. During replacement of the original Main Power Transformers (MPTs), the fact that the new transformers have lower second order harmonic in-rush current was not identified and, as a result, appropriate protective relay settings were not implemented. Corrective actions include revising operating procedures to preclude EDG automatic starts on Main Generator primary lockout when restoring the UAT backfeed. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB control number, the NRC may not conduct or http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant (BSEP), YEAR 05000325 NUMBER NO. Unit 1 2019 - 001 - 00 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. Background At the time of the event, Unit 1 was in Mode 1 (i.e., Power Operation), at approximately 100 percent rated thermal power (RTP). Unit 2 was in Mode 4 (i.e. Cold Shutdown), at 0 percent RTP. There was no inoperable equipment that contributed to the event. Reportability Criteria This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) because the plant experienced a valid start of its four Emergency Diesel Generators (EDGs) [EK]. The event was initially reported to the NRC on March 25, 2019 (i.e., Event Number 53955). Event Description At 04:02 Eastern Daylight Time (EDT) on March 25, 2019, an actuation of the EDGs occurred. Unit 2 was in the process of aligning the electrical distribution system to power the emergency buses via the Unit Auxiliary Transformer (UAT) [EA] when a main generator differential lockout relay actuated; thereby starting the EDGs. The emergency buses remained energized from offsite power via the Startup Auxiliary Transformer (SAT) and, therefore, the EDGs did not tie to their respective buses. The EDGs responded per design to this event. Troubleshooting and testing confirmed that the lockout was not a result of an actual fault condition or degraded equipment. Event Cause The direct cause of this event was a Main Generator primary lockout that occurred when generator breaker Power Circuit Breaker (PCB) 29A was closed during the alignment of the Unit 2 electrical distribution system to power the emergency buses via the UAT. The lockout occurred due to a trip of differential relay 2-GEN-87GT-2-A. The cause of event was a historical design change error. The function of the differential relay is to identify a fault inside the zone of protection by comparing the currents flowing into the zone with the currents flowing out of the zone. If the difference is greater than a set percentage, the relay will actuate. The 87GT-2 relay compares the sum of the currents through PCBs 29A and 29B with the sum of the currents through the main generator and UAT. It is primarily designed to detect a fault in the main power transformer but the zone of protection also includes portions of the isophase bus and 230kV system. A difference in these currents indicates a fault. In the event, PCB 29B and the no-load disconnect switch were open, so the relay was comparing the current flow through PCB 29A with the current flow into the UAT. When system voltage is applied to a transformer at a time when normal steady-state flux is at a different value from that existing in the transformer, a current transient occurs, known as magnetizing in-rush current. BSEP uses HU-1 relays for the differential protection. These relays have a differential unit, a harmonic restraint unit, and an indicating instantaneous trip unit. The differential unit and harmonic restraint unit contacts are in series. Per the vendor manual, the differential unit may or may not close its contact during | ML19143A378
Brunswick Steam Electric Plant (BSEP) | Unit 2 | Manual Reactor Protection System Actuation and Specified System Actuation | 05-28-2019 | At 17:47 Eastern Daylight Time (EDT) on March 30, 2019, with Unit 2 in Mode 1 at approximately 23 percent power and main turbine startup in progress, high temperature was sensed at main turbine bearing 9. A manual main turbine trip and manual actuation of the Reactor Protection System (RPS) were initiated in response to the high bearing temperature. All control rods inserted as expected during the scram. When the scram was inserted, reactor water level dropped below the Low Level 1 (LL1) actuation setpoint. Per design, the LL1 signal resulted in automatic actuation of the Primary Containment Isolation System (PCIS) with closure of Group 2, 6, and 8 isolation valves. Operators manually closed the Main Steam Isolation Valves (MSIVs), in anticipation of low condenser vacuum, prior to the Group 1 PCIS signal being received. All systems responded as designed. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in valid actuations of RPS and PCIS. The direct cause of this event was insufficient lubricating oil supply to the main turbine bearing 9 which caused the bearing to overheat; leading to the manual scram. The most probable cause for the insufficient oil flow was design differences which resulted in a misalignment between the lower half bearing flow channel and the oil supply port in the main turbine 9 bearing housing. Corrective actions include a procedure change to ensure that lubricating oil supply oil flow is not restricted as a result of bearing replacement. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB control number, the NRC may not conduct or http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant (BSEP), YEAR 05000324 NUMBER NO. Unit 2 2019 - 002 - 00 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. Background Initial Conditions At the time of the event, Unit 2 was in Mode 1 (i.e., Power Operation), at approximately 23 percent of rated thermal power (RTP). There was no inoperable equipment that contributed to the event. Reportability Criteria The Reactor Protection System (RPS) [JC] and Primary Containment Isolation System (PCIS) [JM] actuations are being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B). The event was initially reported to the NRC on March 30, 2019 (i.e., Event Number 53966). Event Description At 17:47 Eastern Daylight Time (EDT) on March 30, 2019, with Unit 2 in Mode 1 at approximately 23 percent power and main turbine startup in progress, high temperature was sensed at main turbine [TA] bearing 9. A manual actuation of the RPS was initiated in response to the high bearing temperature. The scram was uncomplicated with all systems responding normally. Reactor water level reached low level 1 (LL1) due to the reactor trip. Per design, the LL1 signal resulted in Group 2 (i.e., floor and equipment drain isolation valves), Group 6 (i.e., monitoring and sampling isolation valves), and Group 8 (i.e., shutdown cooling isolation valves) isolations. Operators manually closed the Main Steam Isolation Valves (MSIVs), in anticipation of low condenser vacuum, prior to the Group 1 PCIS signal being received. Event Cause The direct cause of this event was insufficient lubricating oil supply to main turbine bearing 9 which caused the bearing to overheat; leading to the manual scram. The most probable cause for the insufficient oil flow was design differences which resulted in a misalignment between the lower half bearing flow channel and the oil supply port in the main turbine 9 bearing housing. As a result of planned maintenance on the main turbine during the 2019 Unit 2 refueling outage, it was determined that main turbine bearing 9 required replacement. Main turbine bearings are provided cooling and are lubricated by way of the Main Turbine Lube Oil System [TD]. During preparations for Unit 2 startup, an Auxiliary Operator identified low oil flow in the drain pot of main turbine bearing 9. The low flow condition was evaluated by plant staff and discussed with a vendor representative. Additionally, borescope inspections of the lubricating oil supply and return lines for bearing 9 were completed. Based on these actions, it was incorrectly concluded that the oil flow was sufficient and would improve as turbine shaft speed increased. When startup resumed, during the process of starting the main turbine, bearing 9 failed due to insufficient lubricating oil supply. | ML19148A590
Pilgrim Nuclear Power Station 05000-293 1 OF 3 | Unknown Unit | Condition Prohibited by Technical Specifications Involving the Mechanical Vacuum Pump | 06-10-2019 | 12. LICENSEE CONTACT FOR THIS LER LICENSEE CONTACT r,LEPHONE NUMBER (Include Area Code) !Mr. Peter J. Miner -ReQulatory Assurance ManaQer ~08-830· 7127 13. COMPLETE ONE LINE FOR EACH COMPONENT FAILURE DESCRIBED IN THIS REPORT CAUSE SYSTEM COMPONENT MANU- REPORTABLE CAUSE SYSTEM COMPONENT MANU- REPORTABLE FACTURER TOEPIX FACTURER TO EPIX A JC RI GOBO y 14. SUPPLEMENTAL REPORT EXPECTED 15. EXPECTED MONTH DAY YEAR D SUBMISSION YES (If yes, complete 15. EXPECTED SUBMISSION DATE) ~ NO DATE !ABSTRACT (Limit to 1400 spaces, i.e., approximately 15 single-spaced typewritten lines) On April 13, 2019, the operating crew placed the key lock switch for Main Steam Process Radiation Monitor (PRM) 1705-20 to the INOP position and restored the Mechanical Vacuum (MV) pump to ready state. Subsequent research into the INOP position for the PRM 1705-20 switch revealed that this action does not introduce a channel trip signal. Not placing the PRM in a trip condition with the MV pump restored to ready state, is a violation of Technical Specification Action Statement 3.8.2.A.2 to place the channel or associated trip system in trip within 24 hours. There were no actual consequences to safety of the general public, nuclear safety, industrial safety, or radiological safety for this event. This report is submitted in accordance with Title 10 Code of Federal Regulations 50.73(a)(2)(i)(B). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43). U.S. Nuclear CONTINUATION SHEET Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Ottice of Management and Budget, Washington, DC 20503. If a means (See NUREG· 1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid 0MB control number, the http://www.nrc.gov/reading-rm/doc-collect1ons/nuregs/staff/sr1022/r3Q NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Pilgrim Nuclear Power Station 05000- 293 NUMBER NO. 2019 -003 -00 | BACKGROUND The Mechanical Vacuum (MV) pump is provided to remove gases from the main condenser during plant startup and shutdown when steam is not available for the steam jet air ejectors. !The MV pump isolation instrumentation initiates a trip of the MV pump and isolation of the associated isolation ~alve following events in which main steam line radiation exceeds predetermined values. Tripping and isolating ~he MV pump limits the offsite doses in the event of a control rod drop accident. The MV pump isolation instrumentation includes sensors, relays, and switches that are necessary to cause initiation of a pump isolation. The channels include electronic equipment that compares measured input signals With pre-established setpoints. When the setpoint is exceeded, the channel output relay actuates, which then outputs an isolation signal to the MV pump isolation logic. EVENT DESCRIPTION On April 13, 2019, the operating crew placed the key lock switch for Main Steam (MS) Process Radiation Monitor (PAM) 1705-20 to the !NOP position and restored the MV pump to ready state. Subsequent research into the INOP position for the PAM 1705-20 switch revealed that this action does not introduce a channel trip ~ignal. Not placing the PAM in a trip condition with the MV pump restored to ready state, is a violation of rTechnical Specification (TS) Action Statement 3.8.2.A.2 to place the channel or associated trip system in trip Within 24 hours. The event occurred during power operation while at 100 percent reactor power. The reactor mode selector switch was in the RUN position. CAUSE OF THE EVENT Not placing the affected MS PAM channel in a trip condition with the MV pump restored to ready state was a human performance error. CORRECTIVE ACTIONS After discovering that the IN OP position for the MS PAM 1705-2D switch does not introduce a channel trip signal as expected, the MV pump was removed from ready state in accordance with TS Action Statement 3.8.2.B.1. Any further corrective actions will be documented in the corrective action program. Page 2 of 3 | ML19161A283
Pilgrim Nuclear Power Station 05000-293 | Unknown Unit | Manual Reactor Scram Due to Degrading Condenser Vacuum | 06-11-2019 | On Friday, May 17, 2019 at 2303 [EDT], with the reactor at approximately 70% core thermal power, Pilgrim Nuclear Power Station initiated a manual reactor scram due to degrading condenser vacuum as a result of the trip of Seawater Pump 8. Investigation into the cause identified the Seawater Pump B breaker ground sensing relay in the tripped state. Following the Seawater Pump B trip and reactor scram, Main Condenser parameters responded as expected to a loss of seawater pump transient, no anomalies were noted. There were no radiological releases due to this event. All control rods inserted fully. All other plant systems responded as designed. This event had no impact on the health and/or safety of the public. This report is submitted in accordance with 1O CFR 50.73(a)(2)(iv)(A). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2017) Estimated burden per response lo comply with this mandatory collection request 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back lo industry. Send comments regarding burden estimate lo the Information Services Branch (T·2 F43), U.S. Nuclear CONTINUATION SHEET Regulatory Commission, Washington, DC 20555-0001, or by e-mail lo lnfocollecls.Resource@nrc.gov, and lo the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. II a means (See NUREG· 1022, R.3 for instruction and guidance for completing this form used lo impose an information collection does not display a currently valid 0MB control number, the hnp:J/www.nrc.gov/reading-rmldoc-collections/nuregs/stafflsr1022/r30 NRG may not conduct or sponsor, and a person is not required lo respond lo, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Pilgrim Nuclear Power Station 05000- 293 NUMBER NO. 2019 -004 • 00 | BACKGROUND During planned operation, steam from the low pressure turbine is exhausted directly downward into the condenser shells through exhaust openings in the bottom of the turbine casings. The objective of the main condenser is to provide a heat sink for the turbine exhaust steam, turbine bypass steam, and other flows. The heat dumped to the main condenser is removed by the Circulating Water System, also called the Seawater System. The water is pumped from and returned to Cape Cod Bay. Two vertical, removable element seawater pumps located in the intake structure provide a continuous supply of condenser cooling water. The pumps have a rated flow of 155,500 gal/min each and are powered by 1250 hp, 4160 V, 3 phase induction motors. The design seawater circulating water flow rate is 311,000 gal/min. EVENT DESCRIPTION On Friday, May 17, 2019 at 2303 [EDT], with the reactor at approximately 70% core thermal power, Pilgrim Nuclear Power Station initiated a manual reactor scram due to degrading condenser vacuum as a result of the trip of Seawater Pump B. Following the Seawater Pump B trip and reactor scram, Main Condenser parameters responded as expected to a loss of seawater pump condition. During the manual reactor scram, the plant experienced a Group 2 Isolation, Miscellaneous Containment Isolation Valves, and a Group 6 Isolation, Reactor Water Clean-Up Reactor Building Isolation Actuation, as designed. CAUSE OF THE EVENT Investigation into the cause identified the Seawater Pump B breaker ground sensing relay in the tripped state. The cause of the Seawater Pump B motor trip was a failed power supply cable. High resistance on the degraded 4160 volt motor lead connection caused overheating of the insulation, which eventually faulted to ground causing the pump to trip. CORRECTIVE ACTIONS The Seawater Pump B motor power supply cable was repaired. Any further corrective actions will be documented in the corrective action program. SAFETY CONSEQUENCES rrhere were no actual consequences to safety of the general public, nuclear safety, industrial safety, or radiological safety for this event. Page 2 of 3 | ML19162A032
Brunswick Steam Electric Plant (BSEP) | Unit 1 | False High Reactor Water Level Results in Automatic Specified System Actuations | 06-19-2019 | At 23:07 Eastern Daylight Time on April 21, 2019, with Unit 1 in Mode 1 at approximately 100 percent power, the Main Turbine and both Reactor Feed Pumps (RFPs) tripped resulting in a reactor scram and reactor water level dropping below Low Level (LL) 1 and 2. The LL1 resulted in Group 2 (i.e., floor and equipment drain isolation valves), Group 6 (i.e., monitoring and sampling isolation valves), and Group 8 (i.e., shutdown cooling isolation valves) isolations. The LL2 resulted in Group 3 (i.e., Reactor Water Cleanup) isolation, a secondary containment isolation signal, and High Pressure Coolant Injection and Reactor Core Isolation Cooling (RCIC) automatically starting and injecting into the vessel. All control rods inserted as expected during the scram and all systems responded as designed. The Main Turbine and both RFPs tripped due to two out of three level instruments sensing a false high reactor water level. The false signal was a result of hydrogen deflagration in the reactor level condensing chamber due to a flaw in the original design. There was no impact on the health and safety of the public or plant personnel. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) due to actuations of the Reactor Protection System, Primary Containment Isolation System, Emergency Core Cooling System, and RCIC. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB control number, the NRC may not conduct or http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant (BSEP), 05000325 YEAR NUMBER NO. Unit 1 2019 - 003 - 00 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. Background Initial Conditions At the time of the event, Unit 1 was in Mode 1 (i.e., Power Operation), at approximately 100 percent rated thermal power. Reportability Criteria This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) because it involved actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B). Specifically, the Reactor Protection System [JC], Primary Containment Isolation System [JM], Emergency Core Cooling System [BJ], and Reactor Core Isolation Cooling [BN] actuated during this event. The NRC was notified of this event per 10 CFR 50.72(b)(2)(iv)(A), 10 CFR 50.72(b)(2)(iv)(B), and 10 CFR 50.72(b)(3)(iv)(A) via Event Notification 54016 at 01:51 Eastern Daylight Time (EDT) on April 22, 2019. Event Description At 23:07 EDT on April 21, 2019, in Mode 1 at approximately 100 percent reactor power, Unit 1 automatically tripped due to a Main Turbine trip. The Main Turbine trip was a result of two out of three reactor level instruments sensing a false high reactor water level. All control rods inserted as expected during the scram. Safety Relief Valves G and K lifted per design. The same level instruments that failed also tripped both Reactor Feed Pumps. As a result, reactor water level dropped below the Low Level (LL) 1 and 2 actuation setpoints. Per design, the LL1 signal resulted in Group 2 (i.e., floor and equipment drain isolation valves), Group 6 (i.e., monitoring and sampling isolation valves) and Group 8 (i.e., shutdown cooling isolation valves) isolations. The LL2 signals resulted in Group 3 (i.e., Reactor Water Cleanup) isolation, a secondary containment isolation signal, and an automatic start of Standby Gas Treatment and Control Room Emergency Ventilation. Also, the LL2 resulted in High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) System automatically starting and injecting into the Reactor Pressure Vessel (RPV). Event Cause The direct cause of the false high reactor water level signal on two out of three level instruments was hydrogen deflagration in the associated condensing chambers. The root cause of this event was a flaw in the original design of the reactor level instrument condensing chambers that made them susceptible to accumulation of a flammable mixture of hydrogen and oxygen under certain conditions. A contributing cause to this event was that the Brunswick evaluation of General Electric (GE) Service Information Letter (SIL) 643, “Potential for radiolytic gas detonation,” did not fully address the vulnerability to hydrogen accumulation in the reactor level instrument condensing chambers. The two level instruments that sensed the false high reactor water level both have reference legs connected to the N12A RPV nozzle. These reactor level instruments indicated high level for a few seconds, then returned to normal. There was no actual high reactor level condition as verified by other indications. At the time of the event, Unit 1 had been on-line for approximately 10 days. The previous outage (i.e., approximately 10 days before the event) was the result of the failure of a cryogenic fitting on the steam line to the reactor level instrument condensing chambers on the N12B nozzle. During the outage, cryogenic fittings on the steam lines from the N12A and N12B nozzles were replaced. When the cryogenic couplings were replaced with welded fittings, the RPV level was reduced to below the N12A and N12B nozzles and air was introduced into the steam lines and condensing chambers for the level instruments. Air is rarely introduced into the condensing chambers; before this event the last maintenance that resulted in air introduction occurred in 1989. For deflagration to occur in the condensing chambers, hydrogen and oxygen must be present. The oxygen generated during normal operation does not support deflagration. During normal operation and refueling outages, there is effectively no opportunity for air to be introduced into the RPV level instrument reference leg condensing chambers. No air is present in the RPV during operation, and reactor water level | ML19170A398
LaSalle County Station | Unit 1 | Turbine Stop Valve Limit Switch Failure due to Insufficient Lubrication | 06-27-2019 | On March 23, 2019, during quarterly scram functional surveillances of turbine stop valves (TSV), the limit switch associated with TSV number 3 failed to return to shelf state when the lever arm was released. The failed component was replaced and sent offsite for component testing and failure analysis. The component failure analysis completed on May 3, 2019 determined the cause was attributed to insufficient lubrication in the shaft to bushing section of the limit switch. This established firm evidence that the failure mechanism and past inoperability condition may have existed since its last successful surveillance on December 15, 2018. The affected component 1C 71-N006C is the TSV-3 Closure RPS channel A2 scram limit switch. This device is required by Technical Specifications to support LCO 3.3.1.1 function 8 (RPS) and LCO 3.3.4.1 (EOC-RPT). Each TSV position is monitored by two limit switches (for TSV-3, A2 and B1 channels). This condition resulted in the TSV-3 input to RPS A2 as well as one channel of the EOC-RPT trip being INOPERABLE. The appropriate LCO Conditions and Required Actions were entered and tracked. The RPS and EOC-RPT functions were maintained due to the redundant channels remaining OPERABLE. There were no reportability thresholds applicable to this issue at the time of the event, and there was no loss of safety function. The condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) for operation or condition prohibited by Technical Specifications. Immediate corrective actions were taken to replace the component and restore the associated channel to OPERABLE. Additional actions included performance of a component failure analysis and to complete scheduled limit switch replacements of the current model with a new limit switch model that has greater heat tolerance. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04·2018) Estimated burden per response to comply with lhis mandatory collection request: 80 hours. Reported lessons learned are incorporated inlo the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nudear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555·0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB conlrol number, the NRC may not conduct or sponsor, and a person is not required lo respond to, lhe informalion collection. http://www.nrc.gov/readinq-rm/doc-collections/nuregs/staff/sr1022/r3D 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR NUMBER NO. LaSalle County Station, Unit 1 05000373 2019 - 002 00 | PLANT AND SYSTEM IDENTIFICATION LaSalle County Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the main turbine system. The affected component was the turbine stop valve (TSV) limit switch 1C 71- N006C [Namco model EA740]. This is the limit switch for the TSV number 3 Closure Reactor Protection System (RPS) A2 channel. CONDITION PRIOR TO EVENT Unit(s): 1 Date: May3, 2019 Time: 0000 CDT Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 100 percent DESCRIPTION On March 23, 2019, while performing surveillance testing for the Unit 1 turbine stop valve scram and EOC-RPT function relay 1 C71 A-K1 OC failed to de-energize as expected, indicating a potential issue with the associated limit switch for TSV-3 (1 C71- N006C). The valve otherwise functioned normally, closed and fast closed as expected. The test was performed a second time on stop valve number 3 to monitor its contacts more closely. The second time of testing, relay K1 OC did not actuate. The station entered applicable technical specification (TS) required action (RA) statements due to the failure of the K10C relay. • TS 3.3.1. 1 RA A.1, Place the channel in trip within 12 hours or RA A.2, Place associated trip system in trip within 12 hours. • TS 3.3.4.1 RA A.1, Restore channel to operable within 72 hours or TS 3.3.4.1 RA A.2, Place channel in trip within 72 hours. Troubleshooting performed identified that the limit switch actuating arm failing to return to the relaxed position following movement of the TSV actuating rod assembly and the associated collar which interacts with the 1C 71-N006C limit switch. On March 24, 2019, electrical maintenance technicians completed limit switch replacement on TSV-3. This TSV was re-tested satisfactorily, and instrumentation for TSV-3 was declared operable. The station exited applicable TS LCO 3.3.1.1 and TS LCO 3.3.4.1 time-clocks. The limit switch is normally held in the actuated position during unit operation and is only allowed to return to the relaxed, shelf state position, once per quarter. The limit switch had been tested satisfactorily on December 15, 2018 during its quarterly surveillance. This limit switch was previously replaced on September 9, 2018 due to similar performance behavior noted on this model of limit switch {Namco EA740], that was attributed to temperature-induced lubrication degradation. The limit switch that had been removed from service on March 23, 2019, was sent for off-site failure analysis. The failure analysis was completed on May 3, 2019, indicating the firm evidence of the failure mechanism. CAUSE The failure analysis functionality testing verified the limit switch malfunction. The limit switch was sluggish and failed to return to shelf state. Based on the internal component inspections, the failure was caused by binding between the shaft and the cam bushing due to a lack of lubrication. REPORT ABILITY AND SAFETY ANAL VSIS The 1C71-N006C is the TSV #3 Closure RPS A2 SCRAM limit switch which actuates 1C71A-K010C. This device is required to be OPERABLE per LCO 3.3.1.1 function 8 (RPS) and LCO 3.3.4.1 (EOC-RPT). TSV-3 was fully closed, which should have resulted in the 1C 71-N006C switch being open. Each TSV position is monitored by two limit switches (for TSV-3, A2 and B1 channels). This condition results in the TSV-3 input to RPS A2 as well as one channel of the EOC-RPT trip being INOPERABLE. The appropriate LCO Conditions and Required Actions were entered and tracked. The RPS and EOC-RPT Functions were maintained due to the redundant channels remaining OPERABLE. There was no loss of safety function. The event identification of the limit switch failure did not meet the reporting thresholds in accordance with 10 CFR 50.72. | ML19178A209
Palo Verde Nuclear Generating Station (PVNGS) | Unit 1 | Emergency Diesel Generator INOPERABLE due to Fuel Oil Transfer Pump Testing | 07-03-2019 | This LER addresses two events in which both emergency diesel generator (EDG) trains became INOPERABLE, once in Unit 1 on November 13, 2017, and once in Unit 3 on February 21, 2019. In each event, one EDG train became INOPERABLE due to a diesel fuel oil transfer pump (DFOTP) trip. A test was conducted on the opposite OPERABLE EDG train DFOTP to comply with the plant’s Technical Specification to determine the OPERABLE EDG was not INOPERABLE due to a common cause failure. The diesel fuel oil transfer system (DF) operating procedure used for the common cause failure validation contained a test sequence which inadvertently rendered the affected EDG INOPERABLE. This resulted in both EDG trains being INOPERABLE concurrently, which corresponds to an event that could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident (10 CFR 50.73(a)(2)(v)(D)). The preliminary cause was a failure to adhere to procedural guidance for the creation of a procedure change when the test sequence was added to the operating procedure. Specifically the procedure change did not address the impacts of all steps that affect operability. The procedure has been revised to eliminate the common cause testing method. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear CONTINUATION SHEET Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Palo Verde Nuclear Generating Station 05000-528 NUMBER NO. (PVNGS) Unit 1 2017 - 002 - 00 | All times are Mountain Standard Time and approximate unless otherwise indicated. 1. REPORTING REQUIREMENT(S): This Licensee Event Report (LER) is being submitted pursuant to 10 CFR 50.73(a)(2)(v)(D) corresponding to two events that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. The events were discovered on May 9, 2019, when an evaluation of the diesel fuel oil transfer pump (DFOTP) (EIIS Code: DC) common cause testing concluded that the test rendered the affected EDG INOPERABLE. The affected EDG is the OPERABLE EDG following the failure of the DFOTP on the opposite EDG. The evaluation was conducted to address questions on whether the affected EDG remained OPERABLE during the common cause test. In these events, both emergency diesel generator (EDG) (EIIS Code: EK) trains became INOPERABLE, once in Unit 1 on November 13, 2017, and once in Unit 3 on February 21, 2019. 2. DESCRIPTION OF STRUCTURE(S), SYSTEM(S) AND COMPONENT(S): Each of the station's units are provided with two seismically-qualified Class 1E EDGs rated at 5500 kW. Each EDG is able to supply power to a single 4.16 kV Class 1E bus. Each EDG is served by a seismically-qualified diesel fuel oil transfer system (DF), which consists of one diesel fuel oil storage tank (DFOST) and DFOTP, which provides fuel to the diesel fuel oil day tank. The DFOST capacity (84,000 gallons) is based on providing sufficient storage of diesel fuel oil for 7 days of continuous operation at 100% rated output power levels. The tanks are protected inside seismically-qualified concrete underground vaults. A DFOTP is submerged in, and takes suction from the DFOST. It discharges into the day tank and is automatically started and stopped by a signal from the day tank level instruments. The pump is started at the low level signal regardless of whether the diesel engine is running or not. If the pump fails to start, a low-pressure condition in the pump discharge is annunciated in the main control room. The DFOTP is powered and controlled by cables via underground duct banks to the DFOST. The day tank has a capacity of 1100 gallons. This capacity minimizes the fire protection requirements and is adequate to permit 2-1/2 hours of operation of the associated EDG at full load. The day tank is located in a separate enclosure, near and above the EDG, to provide a positive feed of fuel oil. Each day tank is equipped with a seismically-qualified level instrument, a normally isolated non-seismic level gauge, and an overflow and drain connection routed to the DFOST. The day tank level gauge is not seismically-qualified; consequently, opening the level gauge isolation valve results in the loss of the day tank seismic qualification. Additionally, the day tank drain valve is required to be closed to maintain EDG operability. Therefore, the opening of the day tank level gauge isolation and/or the day tank drain valves renders the affected EDG INOPERABLE. The Technical Specifications (TS) allow selected valves including the containment isolation valves and the emergency core cooling systems valves to be opened under administrative controls. However the TS do not allow the day tank valves to be opened in such a manner. The DF operating procedure contained a test to validate that a DFOTP common cause failure mechanism does not exist on a DFOTP after the redundant EDG DFOTP fails. The common cause test was added as a temporary procedure change to permit its use on November 13, 2017, the day after the Unit 1 ‘A’ DFOTP failed. The temporary procedure change was subsequently incorporated into the procedure on June 21, 2018. | ML19184A628
Dresden Nuclear Power Station | Unit 2 | Unit 2 Scram due to Main Turbine Low Oil Pressure Trip | 07-02-2019 | On May 9, 2019, at 0348 CDT, Unit 2 received an automatic reactor scram as the result of the main turbine tripping due to low oil pressure from the main shaft oil pump. Following the scram, all systems operated as expected, decay heat was being removed using the steam bypass valves to the condenser, and the safety relief valves did not lift. Inspection of the main turbine front standard and main oil pump revealed damage to the spline interface between the main gear quill shaft and the high-pressure control rotor. This damage led to a loss of power transfer between the main turbine and the main oil pump which supplies bearing header pressure. This event is reportable under 1 O CFR 50. 73(a)(2)(iv)(A), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section." The automatic actuation of the reactor protection system is listed in 1O CFR 50.73(a)(2)(iv)(B). The cause of the event was determined to be work order instructions contained an unrecognized critical activity that lacked the detail needed to prevent human error during installation of quill shaft oil gasket. Corrective actions include updating the model work orders for turbine front standard maintenance to include the proper level of detail and establishing new post-maintenance testing practices. NRG FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: BO hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection (See NUREG-1022, R.3 for instruction and guidance for completing this form does not display a currently valid 0MB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. http://www.nrc.gov/reading-rm/doc-collections/nuregs/stafl/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR NUMBER NO. Dresden Nuclear Power Station, Unit 2 05000237 2019 - 002 00 | PLANT AND SYSTEM IDENTIFICATION Dresden Nuclear Power Station (DNPS), Unit 2, is a General Electric Company Boiling Water Reactor with a licensed maximum power level of 2957 megawatts thermal. The Energy Industry Identification System codes used in the text are identified as [XX]. A. Plant Conditions Prior to Event: Unit 02 Event Date: 05/09/2019 Event Time: 0348 CDT Reactor Mode: 1 Mode Name: Power Operation Power Level: 100 percent B. Description of Event: On May 9, 2019, at 0348 CDT, with Unit 2 operating at 100 percent power, an automatic scram occurred due to the main turbine [TA] trip from low oil pressure. The Unit 2 main turbine tripped after receiving a turbine bearing oil [TD] low pressure alarm signal. The emergency bearing oil pump and the turning gear oil pump started as expected to support turbine coast down. Plant systems operated as expected in response to the automatic scram. All control rods inserted to their full-in position, Group 2 and Group 3 automatic isolations actuated as expected, decay heat was being removed using the steam bypass valves to the condenser, and the safety relief valves did not lift. Reactor vessel inventory and pressure were maintained in normal control bands. Operators performed required actions safely and in accordance with procedures and training. Inspection of the turbine front standard found metal particulate proximal to the spline joint where the quill shaft of the main shaft oil pump interfaces with the control rotor. The quill shaft is the mechanical drive between the high-pressure rotor and the shaft driven oil pump. The inspections of the spline joint found the splines had been completely consumed. Upon disassembly of the quill shaft, inspections found the oil supply manifold gasket to the quill shaft not cut properly. The splines of the quill are designed to be lubricated to minimize friction and allow for cooling. The gasket did not have the required hole to allow for oil flow to the quill splines. Due to lack of proper lubrication, the spline joint degraded slowly over time ultimately leading to complete material failure at the joint. The last work record associated with the oil supply manifold gasket was in 2013 during refuel outage D2R23. Additional review shows that the work order instructions lacked any reference to a gasket detail related to its configuration. | ML19189A087
browns ferry nuclear plant | Unknown Unit | Automatic Reactor Scram Due to a Turbine Load Reject | 07-08-2019 | On March 9, 2019, at approximately 2259 Central Standard Time (CST), Browns Ferry Unit 3 received an automatic Reactor SCRAM from 100 percent power as a result of a Turbine Load Reject. Browns Ferry Unit 3 declared a Notification of Unusual Event due to loss of the 500kV offsite source. The automatic SCRAM occurred as a Licensed Reactor Operator (LRO) made adjustments to lower incoming reactive power on Unit 3 at the request of the Balancing Authority. The LRO incorrectly operated a hand switch and changed the automatic voltage regulator (AVR) from auto to manual. In this mode of operation, the dynamic limiter is removed, which allows Operations personnel to adjust Mega Volt Amps Reactive (MVAR) beyond the Under Excitation Limiter (UEL) protection setting. As a result, the generator circuit breaker tripped causing a Turbine Load reject and an automatic SCRAM. All safety systems actuated as designed. The root cause for this event was determined to be that Operations department leaders have allowed continued negative human performance (HU) behaviors by inconsistently providing coaching or reinforcing the use of appropriate HU barriers. The corrective action to prevent recurrence is to revise the Operations Excellence Program, BFN-ODM-4.28, to require use of a dynamic learning environment to develop Operations Department Leaders' skills in coaching and reinforcing the use of appropriate HU barriers. Training will be required prior to assuming shift following initial qualification as Nuclear Unit Senior Operators (NUSO) and Shift Managers (SM). The currently qualified NUSOs and SMs have received training. A plastic cover was placed over the manual/auto select voltage regulator hand switch on all three Units to mitigate unintentional operation of the AVR from automatic to manual control. The Operating Instruction procedure for the Turbine Generator System was revised to prompt Operations personnel to validate the initial status of the AVR prior to adjusting MVAR. NRC FORM 366 (04-201B) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION .. ·-·--a, uma: ..... u. v (04-2017)) Estima1ed burden per response to comply wi1h this mandatory collection request 80 hours. Reported lessons lea-ne<l a-e incaporaled irm the licensing process and fed bai to indus1ry. Send commen1s regarding bu-den estimate to the lnbmation SeM:es Br.n:h [T- 2 F43), U.S. Nuclea-Regulatory Coomssion, Washingtm, 0C 20555-0001,or by e-mail m LICENSEE EVENT REPORT (LER) lnfocollecis. Resolll:e@rrc.gov, and to the Desk Officer, Office of Information and Reguaxy Affairs, NEOB-10202, (3150--0104), Office of Management and Budget. CONTINUATION SHEET WashingtJn, DC 20503. If a means used mi fll)()Se an inbmalion coleclion does not display a CIJTel1lly viiid 0MB control number, the NRC may not conduct or sponsor, and a person is not reqLired to respond m, the information colection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 3 05000296 NUMBER NO. 2019 - 001 01 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Unit 3, was in Mode 1 at approximately 100 percent power. II. Description of Event A. Event Summary On March 9, 2019, at approximately 2259 Central Standard Time (CST), Browns Ferry Unit 3 received an automatic Reactor SCRAM from 100 percent power as a result of a Turbine [TRB] Load Reject. The automatic SCRAM occurred as a Licensed Reactor Operator (LRO) made adjustments to lower incoming reactive power on Unit 3 at the request of the Balancing Authority (BA). The request was made by the BA to address a high voltage condition on the 500kV transmission system. During the adjustment, a LRO incorrectly operated a hand switch [HS], placing the Automatic Voltage Regulator [RG] (AVR) in manual control, and adjusted Mega Volt Amps Reactive (MVAR) beyond the Under Excitation [EXC] Limiter (UEL) protection setting. After two seconds, the generator excitation remained below the protection setting, which initiated a loss of excitation trip resulting in loss of the generator exciter field. Incoming MVAR and current increased on all three generator phases resulting in actuation of generator overcurrent protective relays [RLY ] and opening of the Unit 3 high-side breakers [BKR]. The generator circuit breaker tripped causing a Turbine Load Reject and automatic SCRAM. Systems that actuated as a result of the automatic SCRAM include those listed in Title 10 of the Code of Federal Regulations (CFR) 50.73(a)(2)(iv)(B). Primary Containment Isolation Systems [JE] (PCIS) Groups 1, 2, 3, 6, and 8 isolation signals were received. High Pressure Coolant Injection [BG] (HPCI) and Reactor Core Isolation Cooling [BN] (RCIC) initiated on low reactor water level. All four Unit 3 Diesel Generators [EK][DG] (DGs) started and loaded as expected and supplied AC power to their respective 4kV Shutdown Boards as designed. Browns Ferry Unit 3 declared a Notification of Unusual Event (NOUE) due to loss of the 500kV offsite source. The Tennessee Valley Authority (TVA) is submitting this report in accordance with Title 10 CFR 50.7 3(a)(2)(iv)(A), as any event or condition that resulted in a manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B). B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML19189A125
Grand Gulf Nuclear Station | Unit 1 | Manual Reactor Shutdown Due to Loss of Service Water | 07-09-2019 | On May 12, 2019, Grand Gulf Nuclear Station (GGNS) shutdown the reactor by moving the mode switch from RUN to SHUTDOWN due to a partial loss of Plant Service Water (PSW), in accordance with plant procedures. The partial loss of PSW was caused by a partial loss of power to PSW pumps, and degraded capacity in one PSW well. Loss of power to plant service water pumps was caused by animal intrusion onto electrical service lines. Drywell temperature briefly exceeded the technical specification limit but did not cause a loss of safety function, and Standby Service Water (SSW) was manually initiated to supply engineered safety function room and control room coolers. Completed corrective actions include restoration of electrical service, procedure revisions, and training. Planned corrective actions include improved plant and engineering focus on degraded systems, installation of more robust electrical service, and a revised maintenance strategy for plant service water components. This report is made pursuant to 10 CFR 50.73(a}(2)(iv)(A) for the actuation of the reactor protection system and initiation of SSW per 10 CFR 50.73(a)(2)(iv)(B); and 10 CFR 50.73(a}(2)(v)(D) for the potential loss of safety function. There were no consequences to the general safety of the public, nuclear safety, industrial safety and radiological safety for this event. NRC FORM 3668 (04-2018) Page 1 013 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150·0104 EXPIRES: 3/31/2020 (04-2018) Estimated burden per response to comply with this mandatoiy collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industiy. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear CONTINUATION SHEET Regulatoiy Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk OHicer, Office of Information and Regulatoiy Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3l) NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 05000-416 NUMBER NO. 2019 -002 -00 | Plant Conditions: Grand Gulf Nuclear Station (GGNS) Unit 1 was operating at approximately 100 percent power in MODE 1. There were no structures, systems, or components that were inoperable that contributed to the event. Description: On May 12, 2019, at 10:18 CST, the GGNS experienced an electrical Balance Of Plant 23 buss lockout (EA). This lockout was due to an electrical fault caused by a bird interacting with overhead transmission lines. All systems responded as designed. The electrical buss lockout de-energized enough Plant Service Water (PSW)(KG) pumps, combined with a degraded capacity on one well, to cause an unacceptable increase in component cooling water temperature and turbine building cooling water temperature. Based on the increase in these cooling system temperatures, and in accordance with plant procedures, operators moved the mode switch from RUN to SHUTDOWN on May 12, 2019 at 1039. During the event the partial loss of PSW induced a lockout of the drywall chillers and drywell temperature exceeded the technical specification limit of 135 degrees F. Due to reduced plant service water pressure, standby service water was manually initiated to provide cooling to the control room coolers (VI) and engineered safety function room coolers(VF). All other plant systems functioned as designed. Reportability: This event was reported under 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) for an event resulting in an actuation of the reactor protection system, and 10 CFR 50.72(b)(3)(v)(C) for a potential loss of safety function due to increased drywall temperature. The event notification is 54062. This report is made pursuant to 10 CFR 50. 73(a)(2)(iv)(A) for the actuation of the reactor protection system (manual shutdown via mode switch), and 10 CFR 50.73(a)(2)(iv)(A) for the manual initiation of standby service water, This report is also made pursuant to 10 CFR 50.73(a)(2)(v)(D) for the potential to prevent fulfillment of a safety function (drywell temperature greater than 135 degrees F, which exceeds the design basis accident assumptions for mitigation of a small break loss of coolant accident in the drywall.) Direct Cause: The direct cause(s) of the event were the ground fault on the BOP 23 feeder line caused by animal intrusion, and the degraded specific capacity of one radial well. Root Cause: The Root Cause of the event (inadequate plant service water flow resulting in manual reactor shutdown) is that engineering programs and processes for risk assessment lacks adequate guidance to identify and assess aggregate risk due to the combination of extended operation of 1) a temporary power modification for power plant service water NRG FORM 3668 (04-2018) Page 2 of 3 pumps via overhead feed, and 2) one degraded radial well specific capacity, resulting in the station not having bridging or mitigating actions in place to reduce reactor power after a partial loss of plant service water. Completed Corrective Actions: • Removed wire fencing on power poles which was related to direct cause of ground fault. • Adverse Condition Monitoring Plan for BOP 23 power lines and radial well #3 specific capacity. • Revised procedures to address a graded approach to loss of plant service water • Provided training to control room shift operators on lockout restoration demonstration. Planned Corrective Actions to Preclude Recurrence: The following corrective actions to preclude recurrence are planned, subject to changes per the appropriate corrective action process: • Add requirements for periodic aggregate reviews of the Risk Map items as well as recommended lower tier items (key system health items, ODMls, PDM Watch List, etc.) for the development and implementation of mitigation and bridging strategies for known vulnerabilities I risk issues. • Add requirements for review and update existing strategies for consideration of impacts from changes in plant conditions (i.e. changes in equipment conditions, new items identified, actions being extended, probability for reoccurrence or failure); and • Establish recommendations and guidelines for the performance of periodic reviews by a cross-discipline team including, but not limited to, Operations, System Engineering, and Maintenance. Planned Corrective Actions: The following actions are planned, subject to changes per the appropriate corrective action process: • Replace the appropriate power feed with a more robust design. • Develop and execute a maintenance strategy for the plant service water system major components Safety Significance: All safety systems responded as designed. There were no other actual consequences to safety of the general public, nuclear safety, industrial safety and radiological safety for this event. There were no abnormal radiological releases caused by this event. The drywell temperature transient was analyzed and determined to not constitute a condition which prevented fulfillment of a safety function because 1) the GGN operating license permits brief periods in which the temperature limits are exceeded, and 2) the experienced temperature is bounded by the GGN safety analysis. There was no challenge to protecting the health and safety of the general public because all Emergency Core Cooling Systems (ECCS) and Engineered Safety Features (ESF) equipment were operable and available prior to the shutdown. Operators followed the appropriate off-normal procedures and responded appropriately to the manual shutdown, temperature increases, and system realignments. Previous Similar Events: Entergy conducted a three year review, as described in NUREG-1022 guidance, and one similar event occurred. A similar event in December of 2017 had the same direct cause but did not result in a manual plant scram action by the control room. The causes and resulting corrective actions that have been completed to date have not prevented the direct cause from occurring again in this event on May 12, 2019. NRC FORM 3668 (04·2018) Page 3 of 3 | ML19190A218
Browns Ferrv Nuclear Plant | Unit 2 | Main Steam Relief Valves Lift Settings Outside of Technical Specifications Required Setpoints | 07-18-2019 | On May 29, 2019, the Tennessee Valley Authority was notified of as-found testing results that three Main Steam Relief Valves (MS RVs) from Unit 2 were outside the +/- 3 percent setpoint band required for operability. It was determined that these MSRVs failed due to corrosion bonding to the valve seat as a result of its platinum anti-corrosion coating flaking off. Previously, on April 27, 2018, MSRV BFN-2-PCV-001-0041 had been declared inoperable due to excessive leakage. Failure of this MSRV was caused by a delamination of a portion of the platinum anti-corrosion coating which lead to the leak. More than one MSRV was considered to be inoperable during the entire operating cycle and longer than permitted by Technical Specifications. The affected valves remained capable of maintaining reactor pressure within American Society of Mechanical Engineers code limits. All thirteen of the MSRV pilot valves have been replaced during the Unit 2 Spring 2019, refueling outage. The previous corrective action from LER 50-259/2018-007-00 to perform nitrogen leak testing prior to platinum coating had not yet been implemented for these valves. This continues to be the corrective action to prevent recurrence. In addition, an improved method of applying the platinum to the pilot discs will now be used which provides a more consistent and forgiving finish on the pilot valve seating surface. NRG FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION ~• ,~,cu l:H vmc: ,.v. ;s,,1u-v 1U4 t:Jo.t•u,c.:,: 03/31/LULU (04-2017)) Estimated burden per response to comply wi1h this mandatory collection request 80 hours. Reported lessons learned ..-e incorporated into the licensing process and fed ba:k to industry. Send comments regarding burden estimate to the lnfonnation Services Branch (f- 2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555--0001,or by e-mal to LICENSEE EVENT REPORT (LER) lnfocollects. Resource@nri:.gov, and to the Desk Officer, Office of lnfonnation and Regulatory Affairs, NEOE!-10202, (3150-0104), Office of Management and Budget CONTINUATION SHEET Washington, DC 20503. If a means used to impose an infonnation collection doos oot display a currently vaid 0MB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 2 05000260 NUMBER NO. 2019 - 002 00 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN) Unit 2 was in Mode 1 at approximately 91 percent power. II. Description of Event A. Event Summary On May 29, 2019, NWS Technologies notified the Tennessee Valley Authority (TVA) with the as-found testing results of the thirteen Main Steam Relief Valves (MSRVs) [EIIS:RV], which were removed during the Spring 2019 Unit 2 Refueling Outage 20 (U2R20). Three MSRVs (BFN-2-PCV-001-0004, BFN-2-PCV-001-0018, and BFN-2-PCV-001-0019) had as-found lift settings which were outside of the +/- 3 percent band of their setpoints required for operability. Technical Specification (TS) 3.4.3, Safety/Relief Valves (S/RVs), requires twelve of the thirteen S/RVs to be operable for S/RV system operability. The three MSRVs were found to have been inoperable for an indeterminate period of time during the entire operating cycle between March 29, 2017, and March 2, 2019, and longer than permitted by TS 3.4.3. Previously, on April 27, 2018, MSRV BFN-2-PCV-001-0041 had been declared inoperable due to excessive leakage. It was removed and replaced during a midcycle outage in May 2018. Subsequent testing by NWS Technologies identified the as-found lift setting was outside the required +/- 3 percent band. At the time, BFN-2-PCV-001-0041 was the only known inoperable MSRV and the requirement of TS 3.4.3 (twelve of the thirteen S/RVs operable) was considered to be met. Throughout this event, the two-stage MSRV pilot valves remained capable of maintaining the reactor pressure below 1375 pounds per square inch gauge (psig), which is the American Society of Mechanical Engineers (ASME) code limit of 110 percent of the vessel design pressure. The valves remained capable of performing their required safety function. The TVA is submitting this report in accordance with Title 10 of the Code of Federal Regulations 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant's TS. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML19199A333
Nine Mile Point | Unit 1 | Condition Prohibited by Technical Specifications due to Vacuum Breaker not Locked Closed | 06-24-2019 | On April 25, 2019, Nine Mile Point Unit t discovered that one vacuum breaker was not locked closed, as required by Technical Specification 3.3.6.f.(2). The mode of applicability was entered three times on previous startups. This event is reportable under 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. The cause of the event is Operations personnel have not consistently implemented the Degraded Equipment Log (DEL)/Equipment Status Log (ESL) to track operability concerns of systems and components. Action to prevent recurrence is reinforce implementation of the process to institutionalize use of the DEUESL into day to day operations. The event described in this LER is documented in the plant's corrective action program. NRG FORM 366 (04-2017) .. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) . Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LEA) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid 0MB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR Nine Mile Point Unit 1 05000220 NUMBER NO. 2019 - 002 • 00 | I. DESCRIPTION OF EVENT A. PRE-EVENT PLANT CONDITIONS: Prior to the event, Nine Mile Point Unit 1 (NMP1) was in cold shutdown. Reactor coolant system temperature was less than 212 degrees Fahrenheit (F) and pressure was atmospheric. B. EVENT: On April 2, 2019, during a planned refueling outage, a primary containment vacuum.breaker (IV- 68-08) failed post maintena·nce operability testing due to not indicating full open. The valve failure occurred while the station was in refuel with primary containment integrity not required; therefore, there was no Limiting Condition for Operability (LCO) entry made for TS 3.3.6.f.(2). The inoperable v_acuum breaker was not identified during the station's pre-startup reviews for primary containment operability. As a result, three plant startups were performed with the vacuum breaker closed, but not locked, as required by the applicable Technical Specification Action Statement. The condition was discovered on April 25, 2019, when the station identified the inoperable vacuum breaker while preparing for startup from the refuel outage. The inoperable primary containment vacuum breaker was locked closed prior to plant startup on April 26, 2019. The vacuum breaker was repaired and declared Operable on April 28, 2019. Nine Mile Point Unit 2 (NMP2) was unaffected by the event at NMP1. This event has been entered into the plant's corrective action program as IR 04243630. C. INOPERABLE STRUCTURES, COMPONENTS, OR SYSTEMS THAT CONTRIBUTED TO THE EVENT: No other systems, structures, or components contributed to this event. D. DATES AND APPRbXIMATE TIMES OF MAJOR OCCURRENCES AND OPERATOR ACTIONS: The dates, times, and major occurrences and operator actions for this event are as follows. April 2, 2019 - Vacuum breaker failed post maintenance testing, IR written, work assigned to Fix-it-Now (FIN) team. April 12, 2019 at 13:30 - Entered mode of applicability when Primary Containment Integrity is required. (Reactor Criticality established, Reactor Coolant Temp = 148 degrees F) NRG FORM 366A (04-2017) Page _2_ of _4_ , .. | ML19203A121
Fermi 2 05000 341 1 OF 3 | Unknown Unit | Secondary Containment Declared Inoperable Due to Opening Both Airlock Doors | 07-26-2019 | On May 29, 2019 at 2210 hours, during Security Force on Force Practice Drills both doors in the Secondary Containment (SC) air lock on the reactor building first floor were opened simultaneously for a period of approximately two seconds. During the drill exercise, the Controller failed to maintain the access control measures at the outer air lock door which resulted in additional drill personnel accessing through the door. The condition resulted in Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.3 not being met. The doors were secured immediately. SC pressure during that time remained unchanged and within TS limits. There were no radiological releases associated with this event. Declaring Secondary Containment inoperable for not meeting TS SR 3.6.4.1.3 is reportable under 10 CFR 50.72(b)(3)(v)(C). This written report is required under 10 CFR 50.73(a)(2)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03131/2020 (04-2018) ,%4 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported ' LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U. S. Nuclear Regulatory 3 CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to M f the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of (See NUREG-1022, R.3 for instruction and guidance for completing this form c M o a lle n c a t g io e n m e d n o t es a n no d t B d u isp d la g y eW a t,a c s u h r i r n e g n t t o ly n , va D l C id 2 O 0 M 50 B 3 . con I t f r o a l m num e b a e n r, us t s he e dt N o R C im p m o a s y e n a o n t i c n o f n or d m uc at t io o n r http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/srl022/r3/) sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000- NUMBER NO. Fermi 3412019 - .003 - 00 | INITIAL PLANT CONDITIONS Mode 1 Reactor Power 100% There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT On May 29, 2019 at 2210 hours, during Security Force on Force (FOF) Practice Drills, Secondary Containment (SC) [[NH]] doors [[DR]] at the Reactor Building (RBD08) first floor were opened at the same time. As part of the planned sequence of events, the "Drill Adversaries" entered and took position at the inner air lock door and propped the door open. The drill Controller stayed back behind the outer air lock door to stop personnel from accessing the door. During the drill exercise, the Controller failed to maintain the access control measures at the outer air lock door which resulted in additional drill personnel accessing through the door creating a loss of SC. On recognition of the condition, the inner air lock door was immediately secured. The Main Control Room was notified that both doors in the SC air lock on the Reactor Building first floor (RBD08) were opened simultaneously for a period of approximately two seconds. This resulted in Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.3 not being met. SC pressure remained unchanged and within TS limits. There were no radiological releases associated with this event. Declaring SC inoperable for not meeting TS SR 3.6.4.1.3 is reportable under 10 CFR 50.72(b)(3)(v)(C). This written report is required under 10CFR50.73(a)(2)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. The doors were closed in approximately 2 seconds and SC was restored. Event notification 54094 was submitted at 0010 hours on May 30, 2019. SIGNIFICANT SAFETY CONSEQUENCES AND IMPLICATIONS There were no safety consequences or radiological releases associated with this event. At no time during this event was there a potential for endangering the public health and safety. The SC air lock doors (RBD08) were opened for approximately two seconds. When both air lock doors were open for approximately 2 seconds on May 29, negative pressure was maintained in SC. The SC vacuum remained within the TS operability limit of greater than or equal to 0.125 inches of vacuum water gauge per TS Surveillance Requirement (SR) 3.6.4.1.1. The Standby Gas Treatment System did not start. There was no unmonitored release during the event. | ML19210B833
River Bend Station | Unit 1 | Manual Reactor Scram Initiated in Response to Loss of Feedwater due to Abnormal Plant Configuration | 07-30-2019 | On May 31, 2019, the Reactor was operating at 32% power with a planned shutdown in progress. The 'A' Low Pressure Feedwater Heater (LPFH) string was isolated due to level control issues in one of the heaters. The process of securing one of the Reactor Feedwater Pumps (FWP) resulted in higher than anticipated flow through the 'B' LPFH string. The high flow condition caused water level to rise in one of the '8' LPFHs which resulted in automatic isolation and bypass of the LPFHs. The LPFH string isolation restricted supply flow to the operating FWPs resulting in an automatic trip of the pumps and a loss of all feedwater. At 23:45 a manual Reactor Scram was inserted. Reactor Core Isolation Cooling (RCIC) was manually initiated for Reactor water level control. The 'C' FWP was restarted and Reactor water level control was transferred from RCIC to the 'C' FWP. The LPFH system configuration was not changed and approximately 43 minutes after the Scram, the 'C' FWP automatically tripped due to low suction pressure. Reactor water level lowered to level 3 causing a second Reactor Protection System actuation. Operators reestablished flow through the 'B' LPFH string and restarted the 'A' FWP restoring Reactor water level to the normal band. Corrective Actions are planned to revise procedures to accurately reflect the limitations of the configuration which lead to this event. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U. S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB control number, the NRG may not conduct or http://www. n re.gov/reading-rm/doc-collections/nu regs/staffi s r1 022/r3/l sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER DYEA R SEQUENTIAL REV I NUMBER NO. River Bend Station - Unit 1 05000- 458 ~-I 1-0 I 003 | REPORTED CONDITION On May 21, 2019, operators identified a water level control issue in one of the heaters (**HX**) in the 'A' Low Pressure Feedwater Heater (LPFH) string [SD] which required a plant shutdown to correct. However, a plant shutdown was not feasible at the time due to grid power demands. Continued operation with the 'A' LPFH water level control issue presented elevated risk. High LPFH water level initiates an automatic LPFH string isolation and bypass. Simulator scenarios were performed with a LPFH string isolated and bypassed and resulted in core power to flow ratios outside of the normal operating range and feedwater temperature reductions that would require an immediate Reactor Scram. Simulator scenarios performed with a LPFH string isolated and not bypassed resulted in plant parameters acceptable for continued operation. Trouble shooting activities determined that isolation of the LPFH string would restore the LPFH water level to normal and prevent an unplanned automatic response. An organizational decision was made to lower power and isolate the 'A' LPFH string with the bypass valve closed based on site and fleet engineering input, vendor input, and simulator scenario results. On May 29 the 'A' LPFH string was isolated with the bypass valve closed and water level in the 'A' LPFH returned to normal. On the night of May 31st, a plant shut down ensued to support maintenance on the 'A' LPFH. The process of securing one of the Reactor Feedwater Pumps (FWP) [SJ] resulted in higher than anticipated flow through the 'B' LPFH string. The high flow condition caused water level to rise in one of the 'B' LPFHs which resulted in automatic isolation of the LPFH 'B' string and bypass of all LPFHs. With the 'A' LPFH string already isolated, supply flow to the FWPs was restricted through the LPFH bypass line. The head loss in the LPFH bypass line was sufficient enough to lower FWP suction pressure below the FWP automatic trip set point. At 23:45 the operating FWPs automatically tripped due to low suction pressure and a manual Reactor Scram was inserted. Reactor Core Isolation Cooling (RCIC) [BN] was manually initiated for Reactor water level control. The 'C' FWP was restarted and Reactor water level control was transferred from RCIC to the 'C' FWP. LPFH system configuration was not changed and approximately 43 minutes after the Scram, the one operating FWP automatically tripped due to low suction pressure. Reactor water level lowered to level 3 initiating a second Reactor Protection System [JC] actuation. Operators reestablished flow through the 'B' LPFH string and restarted the 'A' FWP. Reactor water level was restored to the normal band. PREVIOUS OCCURRENCE EVALUATION CAUSAL ANALYSIS Plant dynamics with one LPFW string isolated were not fully understood. The station failed to effectively use the Critical Decision Making Process. Simulator scenario results were used as input in the decision to keep the LPFH bypass valve closed. The station utilizes a plant-reference simulator, meaning its response is modeled based on actual plant operation data. Since the plant had never operated at low power with one LPFH string in service with the LPFH bypass valve closed, there was no previous transient data available for simulator models. CORRECTIVE ACTION TO PREVENT RECURRENCE The following actions have been completed to prevent recurrence. | ML19211A854
Nine Mile Point | Unit 1 | Automatic Reactor Scram due to High Reactor Pressure | 07-26-2019 | On April 14, 2019 at 00:03, Nine Mile Point Unit 1 received an automatic scram of the reactor due to high reactor pressure. Due to the Turbine trip, the High Pressure Coolant Injection (HPCI) System automatically initiated, as designed. This event is reportable under 10 CFR 50.72(b)(2)(iv)(B) and 1O CFR 50.72(b)(3)(iv)(A) as any event or condition that resulted in a manual or automatic actuation of any of the systems listed in 1O CFR 50.72(b)(3)(iv)(B). The cause of the scram is that station personnel did not identify that the Restoring Arm Breakdown was incorrectly installed and therefore non-functional. This resulted in ineffective knowledge-based troubleshooting to correct a condition as opposed to corrections with controlled technical guidance and the right expertise. The event described in this LER is documented in the plant's corrective action program. NRG FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington,· DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid 0MB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Nine Mile Point Unit 1 05000220 NUMBER NO. 2019 • 001 01 | I. DESCRIPTION OF EVENT A. PRE-EVENT PLANT CONDITIONS: Prior to the event, Nine Mile Point Unit 1 (NMP1) was in the Power Operating Condition at 21 % reactor power. Post maintenance testing was being performed on main turbine stop valve #13 (VLV-SV-2). The main turbine was at full speed of 1800 rpm, and no-load conditions. B. EVENT: On April 14, 2019, at approximately 0003 with the reactor at approximately 21 % power, NMP1 experienced a reactor scram due to high reactor pressure. This occurred during post maintenance testing (PMT) of Turbine Stop Valve (TSV) 13. During reactor startup, the TSV 13 internal bypass valve would not open to allow for turbine chest heating. This resulted in the need for system troubleshooting. During the troubleshooting effort, a lack of procedural guidance and system Subject Matter Expertise resulted in improper adjustment of Mechanical Hydraulic Control (MHC) system linkage that caused the valve to respond too quickly. During post maintenance testing, the valve was stroked closed and then back open. During the open stroke, the valve opened too quickly, stop valve oil header pressure dropped allowing all four disc dumps to open and all four turbine stop valves to close. A full turbine trip signal was not experienced, and the turbine control system remained in speed control with the Control Valves and Bypass Valves operational. During turbine coast down, the turbine speed control system attempted to maintain turbine speed by opening the control valves and subsequently closing the bypass valves. This resulted in a rapid increase in reactor pressure and an automatic scram signal at 1080 psig. At the high reactor pressure setpoint of 1080 psig, an automatic reactor scram and subsequent turbine trip occurred. The turbine trip resulted in a HPCI initiation as designed. Troubleshooting following the event identified the Restoring Arm Breakdown was loose. The Restoring Arm Breakdown provides fine control of the Stop Valve position to control the internal bypass of main turbine stop valve #13, which is used for shell warming. Nine Mile Point Unit 2 (NMP2) was unaffected by the scram at NMP1. Operations performed the ENS notification (#53998) required by 1O CFR 50.72(b)(2)(iv)(B) and 1O CFR 50.72(b)(3)(iv)(A) for the automatic reactor scram and specified system activations. This event has been entered into the plant's corrective action program as IR 4239350. NRG FORM 366A (04-2017) Page _2_ of _5_ | ML19211B169
Brunswick Steam Electric Plant (BSEP) | Unit 2 | High Pressure Coolant Injection (HPCI) Inoperable | 07-31-2019 | At 21:27 Eastern Daylight Time (EDT) on June 12, 2019, during routine testing on Unit 2, the High Pressure Coolant Injection (HPCI) turbine experienced an overspeed trip. Following the overspeed trip, the turbine coasted down and reset, then restarted and rolled to rated conditions as-designed. As a result, the response time of the system exceeded the 60-second acceptance criteria, thereby rendering the system inoperable. Reactor Core Isolation Cooling (RCIC) System and Automatic Depressurization System (ADS) remained operable during this event. Failure of Unit 2 HPCI to meet the 60 second response time acceptance criteria was caused by a momentary failure of the Electric Governor – Remote (EG-R) to control HPCI Turbine speed during the initial turbine roll. The EG-R Actuator was replaced and the testing was repeated successfully with the response time acceptance criteria met. Historical data was reviewed on Unit 1 and it was confirmed that this condition was isolated to Unit 2. The safety significance of this event is minimal. There was no impact on the health and safety of the public or plant personnel. This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D). NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB control number, the NRC may not conduct or http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant (BSEP), YEAR 05000324 NUMBER NO. Unit 2 2019 - 003 - 00 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. Background Initial Conditions At the time of the event, Unit 2 was in Mode 1 (i.e., Power Operation), at approximately 100 percent of rated thermal power (RTP). There was no inoperable equipment that contributed to the event. Reportability Criteria The High Pressure Coolant Injection (HPCI) [BJ] inoperability is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented the fulfillment of the function needed to mitigate the consequences of an accident. The event was initially reported to the NRC on June 13, 2019 (i.e., Event Number 54116). Event Description At 21:27 Eastern Daylight Time (EDT) on June 12, 2019, during routine testing, the Unit 2 High Pressure Coolant Injection (HPCI) turbine experienced an overspeed trip. Following the overspeed trip, the turbine coasted down and reset, then restarted and rolled to rated conditions as-designed. As a result, the response time of the system exceeded the 60-second acceptance criteria, thereby rendering the system inoperable. Event Cause Failure of Unit 2 HPCI to meet the 60 second response time acceptance criteria was caused by a momentary failure of the Electric Governor – Remote (EG-R) to control HPCI Turbine speed during the initial turbine roll. Safety Assessment There was no adverse impact on the health and safety of the public. The safety significance of this event is minimal. The event occurred during testing, and Reactor Core Isolation Cooling (RCIC) System and Automatic Depressurization System (ADS) remained operable during this event. Though the HPCI system did not meet the surveillance requirement response time, the system was available to perform its safety function of injecting the required flow rate into the Reactor Pressure Vessel. Corrective Actions The following corrective actions were completed. • On June 15, 2019, the EG-R Actuator was replaced and the testing was repeated successfully with the response time acceptance criteria met. • Historical data was reviewed on Unit 1 and it was confirmed that this condition was isolated to Unit 2. This action was complete on June 13, 2019. | ML19213A159
Limerick Generating Station | Unit 2 | Valid Actuation of the Reactor Protection System due to a Trip of 0214-24 Load Center | 08-05-2019 | On June 3, 2019, with Limerick Unit 2 at approximately 100% power, the 0214-24 Load Center tripped due to an invalid undervoltage signal; resulting in de-energization of a 480 VAC Divisional Motor Control Center (MCC) 0214-G-O. The power failure impacted several components in the Offgas System resulting in water building up in the system and causing stalling of the Steam Jet Air Ejectors and a resultant degradation of Main Condenser vacuum. At 01 :45 June 4, Operators inserted a manual SCRAM due to Main Condenser vacuum approaching the Main Turbine trip setpoint. The cause of the event is the procedure used to stabilize the plant did not fully address the loss of power to the Offgas System. The corrective action is to revise the procedures used to stabilize the plant to address the loss of power to the Offgas System. NRC FORM 366 (02·2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response lo comply wilh !his mandatory collection request 80 hours Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated Into the licenslng process and fed back to industry. Send comments regarding burden estimate lo lhc Information Services Branch (T-2 F43), U S Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, ot by e·mail lo lnfocollecls Resourte@nn: gov, and to the Desk Officer, OfflC8 ol lnlotmation and Regulatory Atta.is, NEOB-10202, (3150-0104) Office of Management and Budget, Washington, DC 20503. H e means used to Impose an inlormation (See NUREG-1022, R 3 for Instruction and guidance for completing this form colleclion does nol display a currently valid OMS control number, Ille NRC may not conduct or hUp //\V\WI nrc gov/reading-rm/doc collect1ons/n!,Jregslslaff/sr1022/r3') sponsor, and a person is not required to respond to, the lnlormallOn colection 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 0YE AR SEQUENTIAL REV Limerick Generation Station, Unit 2 05000-1 353 Iu -1 NU ° MBER 1- NO 0 . 01 | Unit Condition Prior to the Event Unit 2 was in Operational Condition (OPCON) 1 (Run) at approximately 100 percent power. There were no structures, systems or components out of service that contributed to this event. Description of the Event On June 3, 2019, with Limerick Unit 2 at approximately 100% power, the 0214-24 Load Center tripped due to an invalid undervoltage signal; resulting in de-energization of a 480 VAC Divisional Motor Control Center (MCC) 0214-G-D [EC] . Operators took immediate actions to stabilize the plant in accordance with procedure E-0214-G-D for loss of the MCC. With the loss of control power, the 'A' After-Condenser Drain Valve failed closed. This prevented the automatic draining of the Unit 2 Offgas [WF] Recombiner After-Condenser. As a result, the After-Condenser and downstream piping slowly filled with water. At 22:36 water was entering the Offgas System pipes as indicated by After-Condenser outlet temperatures decreasing, and holdup pipe outlet temperature rising. The Unit 2 'B' After-Condenser Drain Valve Level Controller was placed in Auto which began draining the Offgas System of water. However, water already in the Offgas System blocked flow through the Offgas System, increasing backpressure at the second stage stream jet air ejectors. This backpressure stalled the stream jet air ejectors. At approximately 01 :22, Unit 2 began to lose Main Condenser vacuum. As Main Condenser vacuum was lost, Operations lowered reactor power. At 01 :45, Operations initiated a manual scram due to degrading condenser vacuum. Analysis of the Event Following the scram, troubleshooting was performed to identify the cause of the fuse failure. The troubleshooting identified that the upper lead on the undervoltage relay had degradation of the insulation and exposed the conductor. This resulted in a short of the 'A' phase to ground, causing the 'A' phase fuse to fail, which de-energized the MCC. The Offgas Recombiner After-Condenser system is designed with a redundant drain cooler drain valve to maintain level in the After-Condenser. The in service After-Condenser drain cooler valve was operating in the automatic mode and the redundant drain cooler valve was in the manual mode and closed, by design. With the loss of power to the in service After-Condenser drain cooler valve, the in-service valve closed. The controller for the in service After-Condenser drain cooler controller failed in the AS IS position. The procedure used to stabilize the plant contained immediate actions but did not fully address the Offgas System. With the redundant After-Condenser drain cooler valve controller in the manual mode the system required Operator action to return the system to service. The immediate actions in procedure E-D214-G-D did not instruct the Operator to place the redundant offgas controller train into service. Safety Consequences There was no actual safety consequence associated with this event. The potential safety consequences of this event were minimal. All control rods were verified to be fully inserted following the manual RPS actuation. Operators performed required safety actions in accordance with procedures and training. The trip was not complex with all systems responding normally. | ML19217A289
Nine Mile Point | Unit 1 | Manual Reactor Scram due to Pressure and Power Oscillations | 08-02-2019 | On April 29, 2019 at 16:33, Nine Mile Point Unit 1 inserted a manual reactor scram due to pressure and power oscillations. The High Pressure Coolant Injection (HPCI) System automatically initiated, on low reactor vessel water level, as designed. This event is reportable under 10 CFR 50. 73(a)(2)(iv)(A) as any event or condition that resulted in a manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B). The cause of the event is the organization did not effectively incorporate appropriate learnings from previous NMP events and operating history that would have provided adequate flexibility in the operating strategy to mitigate the risks of increased oscillations. The scope of the corrective actions is to incorporate operational history and events into Special Operating Procedures (SOPs) The event described in this LER is documented in the plant's corrective action program. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid 0MB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Nine Mile Point Unit 1 05000220 NUMBER NO. 2019 - 003 01 | I. DESCRIPTION OF EVENT A. PRp-EVENT PLANT CONDITIONS: Prior to the event, Nine Mile Point Unit 1 (NMP1) was in the Power Operating Condition at I 84.6% reactor power. Power ascension was in progress. B. EVENT: On April 29, 2019, at approximately 16:30, NMP1 experienced oscillations in reactor pressure, level and power during power ascension. A manual reactor scram was inserted when the procedural limits were reached. The scram resulted in shrink of the water level in the reactor vessel and the low level set point was reached. This resulted in a HPCI initiation as designed. Nine Mile Point Unit 2 (NMP2) was unaffected by the scram at NMP1. Operations performed the ENS notification (#54035) required by 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) for the reactor scram and specified system activations. This event has been entered into the plant's corrective action program as IR 4244521. C. INOPERABLE STRUCTURES, COMPONENTS, OR SYSTEMS THAT CONTRIBUTED TO THE EVENT: No other systems, structures, or components contributed to this event. D. DAT ES AND APPROXIMATE TIMES OF MAJOR OCCURRENCES AND OPERAT OR ACTIONS: The dates, times, and major occurrences and operator actions for this event are: April 29, 2019 16:29-Control Rod 14-39 withdrawn to position 30 from position 08 16:29-0perators observe reactor power, pressure and level oscillations 16:30-0perator places the feedwater flow control valve in manual to check for controller malfunction 16:30-0perators enter SOP for pressure regulator malfunctions 16:33-Mode switch placed in shutdown 16:33-HPCI initiation due to low reactor vessel water level 16:34-HPCI reset | ML19218A108
Watts Bar Nuclear Plant | Unit 1 | Loss of Control Room Emergency Air Temperature Control System Due to Air Filter Failure | 08-07-2019 | On June 12, 2019 at 0849 Eastern Daylight Time (EDT) a significant air leak on an inline air filter was identified. At 0908 EDT the leak on the filter was bypassed. This air leak impacted operation of the Control Room Emergency Air Temperature Control System (CREATCS) A Train. Two CREATCS trains are required to be operable in accordance with Technical Specification 3.7.11. At the time of this event, CREATCS B Train iwas out of service for planned maintenance. The direct cause of this event is an air filter gasket leak. As corrective action, a different vendor approved gasket has been installed. This condition is being reported as an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident in accordance with 10 CFR 50.73(a)(2)(v)(D). NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION •n u•a: nu. ,nau-u1U4 ~,no:o: --··--- (04-2018) Estlmald 11u111n pa,-'8lpOlll8 mC llllff will 1111s mandaby co1111ct1on n,qUIII: eo IIDln. Repcrllld lessons la11ld n lnc:orpar-,cl Intl Ille llcanalng prl)Cllll8 and 111d back m {\;v:".".""!tI.t: \ lndusty. Send CIIIIIIIBlll llglldng IJullln eatlmall mI lle lnbmalon Slrvlclls Bnllch (T· ..... LICENSEE EVENT REPORT (LER) l 2 n l F a 4 c 3 a ) l , l e U c . l S l. . N R u ll d o e u a 1 " : R IQ eg m u : la .g lD a r v y , C a o n n d rn l m salo t n ie , W D m e l s ll k n g O m l n ll , c a D r, C O 20 t 5 b 55 -0 D 0 I 0 l 1 n , b cr m b a J l 1 o -1 n 111 11 a 1 n m d \~--/ CONTINUATION SHEET W Ra m g l u ll l n lD gm y n , A D ll C an 2 . 0 50 N 3 E . O w B- a 10 , 2 , 02 . , . . ( 3 U 15 lll 0 d - 0 m 104 , ) . . . .. O ,. ll . c :e an D ln I b M ma IN llo Q n l ln c: l a n l l la c a la n n d do B l u ls d g n a o t t . d . ll . p . l . a . , • a C no ll t l n ll , l q l l y il v ll a d li d m 0 II M I IIP B O c n o d r m n , l I l n le u m ln b fD er n , n t l i ll e la n N R co C ll ll m c1 a l y o n n . ot conduct er sparm", and a 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Watts Bar Nuclear Plant, Unit 1 05000390 YEAR NUMBER NO. 2019 - 002 00 | I. Plant Operating Conditions Before the Event Both Watts Bar Nuclear Plant (WBN) Units 1 and 2 were at 100 percent rated thermal power (RTP). 11. Description of Event A. Event Summary On June 12, 2019 at 0849 Eastern Daylight Time (EDT) a significant air leak on an inline air filter {EIIS:FLT } was identified. At 0908 EDT the leak on the filter was bypassed. This air leak impacted operation of the Control Room Emergency Air Temperature Control System (CREATCS){EIIS:VI} A Train. Two CREATCS trains are required to be operable in accordance with Technical Specification (TS) Limiting Condition for Operation (LCO) 3. 7 .11. At the time of this event, the B Train of CREAT CS was out of service for planned maintenance. This event is being reported to the Nuclear Regulatory Commission (NRC) under 10 CFR 50. 73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event The B-8 MCR chiller was out of service for maintenance when this event occurred. C. Dates and approximate times of occurrences Date Time Event !§ill 6/03/19 NIA Preventative Maintenance (PM) Work Order (WO) 119539837 performed to replace 0-FLT R-32-393 charcoal filter. 6/11/19 0400 Entered TS LCO 3. 7 .11 Condition A due to placing a clearance on the 8-8 Main Control Room (MCR) chiller in support of maintenance. 6/12/19 0325 Received 1058 and 1068 MCR HVAC SYSTEM A/8 ABNORMAL alarms. 6/12/19 0332 Discovered O-FCV-31-3, MCR Outside Air Isolation damper, had closed. 6/12/19 0345 Initiated B Train Control Room Isolation (CRI) in accordance with the Annunciator Response Instruction (ARI). 6/12/19 0844 MCR temperatures are above limit of 76 degrees Fahrenheit. | ML19219A219
Grand Gulf Nuclear Station | Unit 1 | Reactor Manual Shutdown Due to Turbine Pressure Control Valve Position Chanaes | 03-31-2020 | On January 30, 2018, Grand Gulf Nuclear Station (GGNS) was operating in Mode 1 at 91 % power and was in the process of increasing power. At 1739 hours CST on January 30, 2018, GGNS experienc~d main turbine control valve (TCV) position changes of between 3 and 5 percent and main generator output lo~d:changes of approximately 20 megawatts with a periodicity of approximately 3 seconds. _: O,:/~'tk'>.: .. At 1822 on ·January 30, 2018, operators performed a manual shut down of the reactor by moving the reactor mode switch from RUN to SHUTDOWN to place the unit in Mode 3. Upon reactor shutdown all systems performed as designed and no subsequent safety system actuations occurred. The TCV position changes were caused by an inappropriately high gain setting in one channel of the TCVs resonance compensator circuit. Corrective actions include adjustments to the control circuit, and revision of work task documents for adjustment of the control circuits. There were no consequences to the general safety of the public, nuclear safety, industrial safety and radiological safety for this event. · NRG FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed · back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear CONTINUATION SHEET Regulatory Commission, Washington, DC 2055.5-0001, or by e~mail to lnfocollects.Resource@nrc.gov, and to the Desk. Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently'valid OMB control number, the http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D NRG may not conduct or sponsor, and a person is not required to respond to,· the information collection: · 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 05000-416 NUMBER NO. 2018 . -001 -001 | A. PLANT CONDITIONS PRIOR TO THE EVENT Grand Gulf Nuclear Station (GGNS) .Unit 1 was operating at 91 % power in Mode 1 and increasing power. There were no Structures, Systems, or Components that were inoperable th~t contributed to the event. B. DESCRIPTION At 1739 hours CST on January 30, 2018, while the plant was operating at approximately 91 % reactor power/1322 megawatts electric power (mwe), operators observed a 20 mwe electrical oscillation (peak to peak) with a periodicity of approximately 3 seconds. Concurrent oscillations of between 3. and 5% were noted on all four turbine control valves. At 1822 hours on January 30.; 2018, operators performed a manual shutdown of the reactor by moving the reactor mode switch from RUN to SHUTDOWN. Upon reactor shutdown all systems performed as designed and no subsequent safety system actuations occurred. C. REPORTABILITY This report is 'made pursuant to 10CFR50.73(a)(2)(iv)(A) for any event or condition that resulted in a · manual or automatic actuation of any of the systems listed in 1O CFR50.73(a)(2)(iv)(B) . . This event was reported under 1O CFR50.72(b)(3)(iv)(B)(1) in ENS notification 53115. D. CAUSE The cause of the reactor scram was a manual shutdown of the reactor due to operator concerns about main generator output variations, caused by unanticipated turbine pressure control valve (TCV) motion. The turbine pressure control system controls turbine speed, operates the steam bypass system to . keep reactor pressure within limits and avoid transients, and controls mairi turbine inlet pressure. The unanticipated TCV motion was caused by an inappropriately high gain setting in the main steam line resonance compensator circuit. Investigation revealed that the high gain setting of the R.esonance Compensator circuitry occurred because the work order steps used to calibrate the card · when it was installed in June of 2016 were incorrect. The incorrect setting did not 1create an error of such magnitude as to be automatically excluded from the circuit internal diagnostics, but did create enough compensatory response from the TCV to be discernable by the operating crew. of NRG FORM 3668 (02-2018) Page 2 3 NRC.FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LEA) lessons learned are incorporated into the licensing process and· fed back to industry. Send comments regarding _burden estimate to the Information Services Branch {T-2 F43), U.S. Nuclear -CONTINUATION SHEET Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, {3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMB control number, the http://www.nrc.gov/readinq-rm/doc-collections/nuregs/staff/sr1022/r3l) NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Grand Gulf Nuclear_ Station, Unit 1 05000-416 NUMBER NO. 2018 -001 001 1 • NARRATIVE· E. CORRECTIVE ACTIONS The. following corrective actions are completed or planned. Completed: • The main .steam line resonance compensator circuit was recalibrated. • Work instructions to setup steam line compensator were revised to provide corrected work steps. F. SAFETY SIGNIFICANCE The safety significance of this event is low because·au systems operated as designed and the TCV changes did not challenge any safety parameters. The manual scram was performed as a conservative measure. There w'ere no actual nuclear safety consequences or radiological consequences during the event. G. PREVIOUS SIMILAR EVENTS Entergy conducted a three-year review of the relevant licensee event reports and determined that there was·one similar known event reported as GGNS Licensee Event Report 2016-05-00 "Automatic Reactor SCRAM." The failure in that event was a failed amplifier card, which is different from this event which was an incorrect potentiometer setting. Therefore, the corrective actions for the previous event would not have prevented this event. NRG FORM 366A (06-2016) Page 3 of 3 | ML19219B328
Susquehanna Steam Electric Station | Unit 2 | Valid Actuation of the Primary Containment Isolation System due to a Trip of Reactor Protection System Bus 2B | 02-02-2019 | On June 27, 2019, at 0937 a half scram signal was received on Unit 2, Division 2 of the Reactor Protection System (RPS). The half scram signal resulted in a trip of the 2B RPS instrument bus, a trip of the 2A Residual Heat Removal Service Water (RHRSW) Pump, a loss of the 2A and 2B Containment Radiation Monitors (CRMs), and Primary Containment Isolation System (PCIS) actuations. The loss of both CRMs resulted in entering Condition B of Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.4.6, “RCS Leakage Detection Instrumentation.” The PCIS actuation resulted in isolation of containment isolation valves in multiple systems and was determined to be reportable in accordance with 10 CFR 50.72(b)(3)(iv)(A) for the valid isolation signal. The 2B RPS instrument bus was transferred to its alternate power supply and the 2A and 2B CRMs were restored. The 2B RPS instrument bus was realigned to its normal source on July 2, 2019. The condition was also determined to be reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) for the valid PCIS signal. The event was determined to be caused by an age-related failure of a control relay on the normal power supply to the 2B RPS instrument bus. Corrective actions included replacing the failed relay. There were no actual safety consequences associated with the condition. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to CONTINUATION SHEET the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB control number, the NRC may not conduct or http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station Unit 2 05000-388 NUMBER NO. 2019 002 00 | CONDITIONS PRIOR TO EVENT Unit 1 – Mode 1, approximately 100 percent Rated Thermal Power Unit 2 – Mode 1, approximately 100 percent Rated Thermal Power There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. EVENT DESCRIPTION On June 27, 2019, at approximately 0937, a half scram signal was received on Susquehanna Steam Electric Station (SSES) Unit 2, Division 2 of the RPS [EIIS Code: JC]. Concurrently, operators were performing SO-216-A03, “Quarterly Residual Heat Removal Service Water (RHRSW) System Flow Verification Division I,” The half scram signal resulted in a trip of the 2B RPS instrument bus, a trip of the 2A RHRSW Pump [EIIS System / Component Code: BO/P], a loss of the 2A and 2B CRMs [EIIS System / Component Code: IL / MON], and PCIS [EIIS Code: JM] actuations. The loss of both CRMs resulted in entering Condition B of SSES TS LCO 3.4.6, “RCS Leakage Detection Instrumentation.” The 2B RPS instrument bus was transferred to its alternate power supply at 0941 and the 2A and 2B CRMs were restored at 0956 and 0959, respectively; Condition B of LCO 3.4.6 was exited at 1000; all TS Completion Times were met. Upon tripping the 2B RPS instrument bus, SSES personnel performed troubleshooting on the normal power supply to the bus. It was determined that Control Relay 2Y201BC72BK1B [Component Code: RLY] (hereafter referred to as the K1B relay) failed. The K1B relay was replaced and SSES personnel restored the 2B RPS instrument bus to its normal source on July 2, 2019. The PCIS actuations resulted in isolations of multiple systems as designed. As a result, this condition was determined to be reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of a system as identified in 10 CFR 50.73(a)(2)(iv)(B)(2). CAUSE OF EVENT The direct cause of the event was determined to be an age-related failure of the K1B relay. ANALYSIS/SAFETY SIGNIFICANCE Failure of the K1B relay caused a loss of power to one of two power distribution systems of the ‘B’ RPS. The RPS is “one out of two taken twice” logic. The loss of power resulted in a valid isolation signal on the ‘B’ logic division. This response is consistent with the safety analysis. Since the plant response was as designed, all accident functions would have been met. Therefore, there was no loss of safety function. Accordingly, this event will not be counted as a safety system functional failure in the Reactor Oversight Process Performance Indicators. | ML19234A257
Cooper Nuclear Station 05000298 1 of 4 | Unknown Unit | Valve Test Failures Result in a Condition Prohibited by Technical Specifications and a Loss of Safety Function | 08-09-2019 | On March 4, March 5, and March 6, 2019, three of eight Target Rock safety relief valve (SRV) pilot assemblies, removed during Refueling Outage 30, failed to lift within Technical Specifications (TS) lift setpoint requirements. The pressure setpoint of the first failed pilot assembly was 1090 psig; the SRV pilot assembly lifted at 1256.2 psig. The pressure setpoint of the second failed pilot assembly was 1080; the SRV pilot assembly lifted at 1208.5 psig. The pressure setpoint of the third failed pilot assembly was 1090; the SRV pilot assembly lifted at 1124.2 psig. Three subsequent lifts were performed for all failed SRV pilot assemblies and the results were within the TS pressure setpoint tolerances. The cause of the failures was determined to be corrosion bonding. Although the setpoint lift pressures of the SRV pilot valve assemblies exceeded TS requirements, an analysis of this event concluded the thermal limits and American Society of Mechanical Engineers overpressure transients did not exceed allowable limits. Public safety was not at risk. Safety to plant personnel and plant equipment was not at risk. A TS Amendment to TS 3.4.3 will be submitted that will address the failure to meet the TS criteria for the Target Rock two-stage SRVs. Following submittal, a tracking mechanism will be established for TS change approval. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: N0.·3150-0104 EXPIRES: 3/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid 0MB control number, the http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITYNAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL_ REV Cooper Nuclear Station 05000-298 NUMBER NO. 2019 - 001 - 01 | PLANT STATUS Cooper Nuclear Station (CNS) was in Mode 1, Power Operation, at 100 percent power, when the event was discovered; i.e., March 6, 2019. BACKGROUND The pressure relief system includes three American Society of Mechanical Engineers (ASME) code safety valves (SV) [El IS: SB] and eight safety relief valves (SRV) [El IS: RV], all of which are located on the main steam lines [EIIS: SB] within the drywall [EIIS: NH], between the reactor vessel [EIIS: RPV] and the first main steam isolation valve [EIIS: ISV]. The SVs provide protection against over pressurization of the nuclear system and discharge directly into the interior space of the drywell. The SRVs discharge to the suppression pool and provide three main functions: overpressure relief operation to limit the pressure rise and prevent safety valve opening, overpressure safety operation to prevent nuclear system over pressurization, and depressurization operation ( opened automatically or manually) as part of the emergency core cooling system [EIIS: BJ, BM, BO]. Technical Specification (TS) Limiting Condition for Operation 3.4.3 requires the safety function of seven SRVs and three SVs to be operable. The nominal set pressure tolerances for these valves are established in CNS TS Surveillance Requirements (SR) 3.4.3.1. The SRVs installed at CNS are Target Rock Model 7567F, two-stage, pilot-actuated valves with pilot assemblies comprised of Stellite 21 pilot discs and Stellite 6B pilot body seats. The pilot assemblies had been in continuous service since installation in Refueling Outage (RE) 29, (Fall of 2016). Corrosion bonding is an industry known problem with Target Rock Model 7567F two-stage relief valves in which the pilot valve bonds/sticks to the in-body seat, resulting in an increased pressure needed to lift the valve. After the corrosion bonding is "broken" following the initial lift, the subsequent lifts are within tolerance. EVENT DESCRIPTION In the Fall of 2018, two main SRVs body assemblies and eight SRV pilot assemblies were removed during RE30. In March 2019, the SRVs were as-found tested at National Technical Systems Laboratories. The pressure setpoint for SRV pilot assembly serial number 1242 is 1090 psig. The TS SR 3.4.3.1 as-found limit of acceptance is 1090 +/- 3%. The first actual lift pressure of this SRV pilot assembly was recorded at 1256.2 psig, 15.2% above the pressure setpoint. A second, third, and fourth lift was performed and the results were 1095. 7 psjg, 1092.4 psig, and 1092.9 psig, all three within 3% of the pressure setpoint. The pressure setpoint for SRV pilot assembly serial number 387 is 1080 psig. The TS SR 3.4.3.1 as-found limit of acceptance is 1080 +/- 3%. The first actual lift pressure of this SRV pilot assembly was recorded at 1208.5 psig, 11.9% above the pressure setpoint. A second, third, and fourth lift was performed and the | ML19241A241
Limerick Generating Station | Unit 2 | Emergency Diesel Generator Lube Oil Pressure Sensing Line Leak Resulting in a Condition Prohibited by Technical Specifications | 09-20-2019 | On 7/22/19, the instrumentation line threaded pipe connection for a pressure indicator, was found sheared during Emergency Diesel Generator (EOG) 024 slow start monthly run. The one-quarter inch instrumentation line threaded connection tees off the four-inch main lube oi.1p iping near the discharge of the engine driven lube oil pump. Prior to the run there was no indication of a leak at this connection. This threaded pipe was pro-actively replaced on 5/23/18, and on 1/21/19 the threaded pipe connection failed due to high-cyclic fatigue. The corrective actions to address the failure on 1/21/19 were to install a support on the threaded connection and repair a broken U-bolt. These actions did not resolve ttie underlying condition. The cause of the failure on 7 /22119 was high-cyclic fatigue experienced at the threaded pipe connection. The corrective action is to redesign the connection to reduce the stress on the threaded pipe connection. In the interim, the instrument line was removed from service. NRC FORM 366 (02-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U. S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfoco~ecls.Resoun:e@nn:.gov, and lo the Desk Officer, Office of Information and Regulatory Affars, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used lo impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB control number, the NRC may not conduct or http;/lwww .. n.rc.govtreading-n:nJdo!:.:collection..sJnur..eg_s/staff/!\f102'2.lr3/) sponsor, and a person is not required to respond lo, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Limerick Generation Station, Unit 2 05000-1 353 | Unit Condition Prior to the Event Limerick Generating Station (LGS), Unit 2 was operating in Operational Condition (OPCON) 1 at 100 percent power at the time of the event. There were no other structures, systems, or components inoperable that contributed to the event. Description of the Event On 7/22/19, an instrumentation line threaded pipe connection for a pressure indicator, was found sheared during the Emergency Diesel Generator (EOG) 024 [EllS:EK] slow start monthly run. The one-quarter inch instrumentation line threaded connection tees off the four-inch main lube oil piping near the discharge of the engine driven lube oil pump. EOG 024 was started at 21 :01, loaded at 21 :22, and fully loaded at 21 :33. A dirty drip pan alarm came in at 22:05 and subsequently the lube oil leak was identified. The discovery time of the leak at approximately 22:05 is very close to the actual failure time of the threaded pipe. Prior to the failure, there were no leaks or degraded conditions present. There have been leaks identified at this connection. On 3/21/2013, a 1-2 drop per minute (DPM) leak was identified on the same threaded connection. One month later, on 4/27/2013, the EOG was made inoperable when a threaded connection failed and the 1-2 DPM leak became a 140 DPM leak. The investigation performed for this failure determined the cause to be high-cycle fatigue from engine vibration exacerbated by a missing grommet on one of the downstream supports. The missing grommet was re-installed, and the threaded pipe was replaced. For approximately six years following this repair, no additional leakage occurred at this location. On 12/12/16, a leak developed on this connection on EDG 013. The investigation determined that the cause was cyclic fatigue of the threaded connection with a contributing factor of manipulation of the valve downstream of the threaded connection. The investigation determined that this fitting should be replaced on all the EDGs during the next scheduled system outage. The EOG 024 threaded pipe was replaced on 5/23/18. On 1/21/19, the threaded connection developed a leak and the EOG 024 was declared inoperable. An investigation determined the cause was high-cycle fatigue due to the instrument line vibrating at its resonant frequency during engine operation. Contributing to this was the specific design for the piping arrangement and a U-bolt that was found broken on the 4-inch lube oil header. The failed threaded connection was replaced, and the broken U-bolt was reinstalled on the main header. To account for the design deficiency with the instrument line piping arrangement, a clamp was installed between the main header and the instrument line to reduce vibrations until a design change could be implemented to change the instrument line configuration. Vibration readings taken following implementation of these actions found a significant reduction in the vibration of the instrument line; however, on 7/22/19, the threaded pipe connection failed again. Analysis of the Event The failures that occurred in 2013 were caused by a missing grommet on a support for the piping. The threaded connection and the grommet were replaced, and the connection performed without an issue for five years. After a proactive replacement was completed for EOG 024 the connection failed twice. | ML19263A648
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Safety Relief Valves Out of Tolerance | 09-20-2019 | The As-Found test results for the eleven Safety/Relief Valve (S/RV) pilot assemblies removed and replaced during the 2018 Refueling Outage at James A. FitzPatrick Nuclear Power Plant (JAF) identified eight (8) S/RV pilot assemblies that lifted outside of the allowable tolerance required by Technical Specification Surveillance Requirement 3.4.3.1. Eight (8) two-stage S/RV’s were found out of tolerance high. The eight S/RV pilot assemblies are assumed to have been inoperable at some point in the operating cycle that preceded the 2017 Refueling Outage resulting in a condition reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). The S/RV design features an electric actuation capability that provides a diversified means of opening the S/RV’s despite the out of tolerance condition. However, the electric lift function is considered a backup to the mechanical S/RV’s and is not credited in the accident analysis. Therefore, the TS inoperability of the eight (8) S/RV’s also resulted in a condition reportable pursuant to 10 CFR50.73(a)(2)(v)(D). The cause of the two-stage failures has been identified as corrosion bonding. The safety consequences associated with this event are considered low due to the electric actuation capability. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments CONTINUATION SHEET regarding burden estimate to the Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a (S ee NUREG-1022, R.3 for instruction and guidance for completing this form person is not required to respond to, the information collection. http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 – 333 NUMBER N0. 2019 – 003 – 00 | Background The ASME Boiler and Pressure Vessel Code requires the reactor pressure vessel be protected from overpressure during upset conditions by self-actuated safety valves. As part of the nuclear pressure relief system, the size and number of S/RVs are selected such that peak pressure in the Reactor Coolant Pressure Boundary (RCPB) will not exceed the ASME Code limits. The James A. FitzPatrick Nuclear Power Plant (JAF) used eleven (11) two-stage Target Rock Safety/Relief Valves (S/RV) [EIIS Identifier: SB] for emergency pressure relief during operating Cycle 23. These valves are located on the main steam lines between the reactor vessel and the first isolation valve within the drywell. Each S/RV discharges steam through a discharge line to a point below the minimum water level in the suppression pool. The S/RVs can actuate by either of two modes: the safety mode or the relief mode. In safety mode (or spring mode of operation), the spring-loaded pilot valve opens when steam pressure at the valve inlet overcomes the spring force holding the pilot valve closed. Opening the pilot valve allows a pressure differential to develop across the main valve piston and opens the main valve. This satisfies the code requirement. Each S/RV can be opened manually in the relief mode from the control room by its associated two-position switch. If one of these switches is placed in the open position the logic output will energize the associated S/RV solenoid control valve directing the pneumatic supply to open the valve. Seven of the installed S/RV solenoid control valves can also be energized by the relay logic associated with the Automatic Depressurization System (ADS). During each refueling outage all eleven of the pilot assemblies are removed and replaced with vendor tested and certified components. The pilots that are removed are sent to a vendor facility for testing, refurbishment, and certification. The test results for pilot assemblies removed in 2018, during Refueling Outage 23, identified eight (8) S/RV pilot assemblies that were out of allowable tolerance. Eight (8) of the pilots (all two-stage) lifted at greater than the allowable setpoint range. In order to address the concerns with corrosion bonding, JAF has replaced two-stage S/RVs with new design of three-stage Target Rock S/RVs in the Fall 2018 Refueling Outage (RO). Industry experience has shown that the three stage S/RVs are less susceptible to corrosion bonding. The design of the three-stage S/RVs produces a greater mechanical force on opening, resulting in a greater likelihood of overcoming any potential effects of corrosion bonding that might occur. Event Description As-Found testing was performed on all eleven main S/RV pilot assemblies removed in 2018, during RO23. The testing was conducted by NWS Technologies. The TS setpoint for each S/RV is 1145 +/- 34.3 psig. During the initial lift test, eight of the eleven pilot assemblies failed to open within the allowable range (1110.7 to 1179.3 psig). Eight of the eleven two-stage S/RV pilots failed high. As-Found failed test results are tabulated below. Page 2 of 4 | ML19263B250
Fermi 2 05000 341 1 OF 3 | Unknown Unit | Division 2 Mechanical Draft Cooling Tower Fan "D" Tripped when Placed in High Speed Due to a Blown Fuse | 09-30-2019 | On July 30, 2019, at 1014 EDT, the Division 2 Mechanical Draft Cooling Tower (MDCT) Fan "D" was declared inoperable due to a trip of the fan while placing it in high speed. The MDCT Fans are required to support operability of the Ultimate Heat Sink (UHS). The UHS is required to support operability of the Division 2 Emergency Equipment Cooling Water (EECW) system. The EECW system cools various safety related components, including the High Pressure Coolant Injection (HPCI) system room cooler. An unplanned HPCI inoperability occurred based on a loss of the HPCI Room Cooler. The cause of the event was a blown high speed breaker control power fuse. The control power fuse was replaced, the MDCT Fan "D" was tested satisfactorily, and HPCI was declared operable on July 30 at 1431 EDT. The blown fuse was quarantined and will be sent for failure analysis. The remaining fuses in the system are being replaced and sent to the vendor for comparison with the blown fuse. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process andfe d back to industry. Sendc omments a regarding burden estimate to the Information Services Branch(T -2 F43),U . S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of (SeeNUGR-1 22,R.3fonridn stuuicdtnonc efor ompetig tis orm Management andB udget, Washington, DC2 0503. It a means coedto impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form i does not display a currently valid MB control number, theN RC may not conduct or htto://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/srl022/r3/ sponsor, anda person isn ot required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000- NUMBER NO. Fermi 2 341 2019 - 04 - 00 | INITIAL PLANT CONDITIONS Mode 1 Reactor Power 100% There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT On July 30, 2019, at 1014 EDT, the Division 2 Mechanical Draft Cooling Tower (MDCT) [CTW] Fan [FAN] "D" was declared inoperable due to a trip of the fan when placing it in high speed during a Technical Specification Surveillance test. The MDCT Fans are required to support operability of the Ultimate Heat Sink (UHS) [BS]. The UHS is required to support operability of the Division 2 Emergency Equipment Cooling Water (EECW) system. The EECW system cools various safety related components, including the High Pressure Coolant Injection (HPCI) [BJ] system room cooler [CLR]. An unplanned HPCI inoperability occurred based on a loss of the HPCI Room Cooler. Investigation revealed that a high speed breaker control power fuse [FU] had blown. The control power fuse was replaced, the MDCT Fan "D" was tested satisfactorily, and the UHS and HPCI were declared operable on July 30, 2019 at 1431 EDT. The HPCI system is a single train safety system. The 10CFR50.72(b)(3)(v)(D) notification was made at 1542 on July 30, 2019 to the NRC Operations Center by Event Notification 54188. This 10CFR50.73(a)(2)(v)(D) notification is fulfilling the 10CFR50.73 report requirement. Based on the equipment history of the MDCT fans and the cause of the failure being a blown fuse, there is no firm evidence to identify that the failure would have existed previously. Therefore, the failure is assumed to have occurred at the time of its discovery based on the guidance in NUREG-1022 Section 3.2.2. SIGNIFICANT SAFETY CONSEQUENCES AND IMPLICATIONS There were no safety consequences associated with this event. At no time during this event was there a potential for endangering the public health and safety. There were no radiological releases associated with this event. Technical Specification 3.7.2 requires the UHS reservoir to be operable in Modes 1, 2, and 3. The UHS operability requirements in Modes 4 and 5 are determined by the systems the UHS supports. Each reservoir is the cooling source for that division's service water subsystems. A two-cell MDCT is located above each of the one-half capacity reservoirs. Each cell is equipped with a MDCT fan. Two MDCT fans above each one-half capacity reservoir are required for that division of UHS to be considered operable. The "A" and "C" MDCT fans are in Division 1 and the "B" and "D" fans are in Division 2. | ML19273A053
Surry Power Station | Unit 1 | Failure to Align Angle Drive to Pump Results in Inoperable Emergency Service Water Pump | 03-31-2020 | On June 23, 2019, with Units 1 and 2 at 100% power, the packing gland on the 1B Emergency Service Water Pump (ESWP) failed during periodic pump testing and the pump was declared inoperable. The packing gland was repaired and the pump was returned to service on June 24, 2019. During the next scheduled pump test on July 21, 2019, another packing failure occurred. Subsequent investigation revealed that both packing failures were caused by the angle drive to pump shaft not being aligned when the pump was replaced in May 2019. The decision making was not appropriate in that only first line supervisors were consulted before making the decision not to per:form the alignment. The decision should have been elevated to ensure a broader group of personnel were involved in the decision. The ESWP 1 B to angle drive alignment was performed in accordance with procedures and returned to service. Additionally, corrective actions will include a revision to the maintenance procedure and other changes focusing on . improving proficiency and decision making. This report is submitted pursuant to 10 CFR 50.73(a)(2)(i)(B) due to operations prohibited by Technical Specifications. Based on a risk assessment, the risk impact was determined to be of very low significance. NRG FORM 366 (04-2017) Page 1 of 3 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated Into the licensing process and led back to industry. LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects. CONTINUATION SHEET Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. II a (See NUREG-1022, R.3 for instruction and guidance for completing this form means used to impose an information collection does not display a currently valid 0MB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/} information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR NUMBER NO. Surry Power Station, Unit 1 05000- 280 2019 • 001 00 | 1.0 DESCRIPTION OF THE EVENT Three diesel-driven vertical Emergency Service Water Pumps (ESWPs) [EIIS-81-P] are provided at the James River intake structure [EIIS-KE-NN] to deliver service water (SW) makeup to the intake canal [EIIS-KE-NN] in the event of a total loss of station power coincident with a design basis Loss of Coolant Accident (LOCA). The three (3) ESWPs serve both Surry units. Two of three ESWPs provide sufficient heat removal for the design basis LOCA unit and the non-LOCA unit. Technical Specification (TS) 3.14.A.4 states that when the reactor coolant system temperature or pressure exceeds 350 degrees For 450 psig, three ESWPs shall be operable. TS 3.14.B allows one ESWP to remain inoperable for a period not to exceed 14 days. On April 29, 2019, ESWP 1B was tagged out in preparation for pump replacement. The pump was replaced without performing an angle drive to pump alignment and on May 4, 2019, the pump was started for its return to service run. During this run, multiple vibration points were elevated. The source of these elevated vibrations were determined to be resonance and did not impact operability. On May 7, 2019, the pump was successfully returned to service. On May 8, 2019, grouting was installed under the pump pit plate and on May 28, 2019, the pump was tested with results showing that the vibrations had decreased indicating the grout changed the resonance frequency of the angle drive to pump shaft assembly. On June 23, 2019, during periodic testing, ESWP 1 B was secured due to abnormal sounds after pump start. The pump was declared inoperable as a result of a failure of the pump packing gland. The failure was attributed to loosening of the packing gland follower clamping bolts during pump operation at elevated vibration levels. Following repacking, application of a liquid threadlocker to the pump gland follower clamping nuts, and successful testing, the pump was declared operable on June 24, 2019. During the next scheduled pump test on July, 21, 2019, ESWP 1 B was again secured and declared inoperable due to a packing failure. Subsequent investigation showed that the pump shaft and angle drive were misaligned resulting in excessive shaft movement, stuffing box bushing wear, and packing failure. On July 25, 2019, the ESWP 1 B angle drive to pump shaft were aligned and the pump declared operable. It was determined that the prior packing failures were caused by angle drive to pump misalignment which occurred in May 2019. At three (3) separate times during this period of ESWP 1 B inoperability (i.e., from May 7 to July 25), ESWPs 1A and 1 C were separately removed from service for scheduled maintenance, but at no time was either pump unable to be returned to operable status within the 2-hour time-critical operator action starting time should a design basis event have occurred. As a result there was not a loss of safety function. ESWP 1 B was determined to be unable to perform its design function since the time that the pump was replaced and as a result exceeded its 14-day TS allowed outage time. In addition, the period of time ESWP 1A and 1 C were separately removed from service resulted in exceeding the TS 3.0.1 criterion. Therefore, this report is submitted pursuant to 10 CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by Technical Specifications. 2.0 SIGNIFICANT SAFETY CONSEQUENCES AND IMPLICATIONS The risk associated with the ESWP 1 Bout-of-service condition is very low since the likelihood of a design basis accident coincident with loss of off-site power and a challenge to intake canal cooling water volume is extremely unlikely. Additionally, ESWP 1A and 1C were available during the period ESWP 1B was inoperable. Therefore, the impact of the condition was very low, and there were no safety consequences because of this event. | ML19273A424
Hope Creek Generating Station 05000354 I OF3 | Unknown Unit | Manual Scram and Manual Actuation of Reactor Core Isolation Cooling | 03-31-2020 | At 1906 EDT on August 3 2019, while in OPCON 1 at 93.8 percent power, operators identified degrading main condenser vacuum and commenced reducing power. Degrading vacuum was due to the circulating water cooling tower bypass valve failing open. At 1947, the reactor was manually scrammed from 37 percent due to loss of condenser vacuum. Reactor feedwater pumps (RFP) tripped when reactor pressure vessel (RPV) water level rose to level 8 (+54 inches) because the reactor feedwater startup level control valve (SULCV) failed open. Operators initiated the reactor core isolation cooling (RCIC) system, recovered a RFP and secured RCIC after establishing control of RPV water level. The failed equipment was replaced. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A). NRG FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-- LICENSEE EVENT REPORT (LER) 0001, or by internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and CONTINUATION SHEET Budget, Washington, DC 20503. If a means used to impose an information collection does not (See NUREG-1022, R.3 for instruction and guidance for completing this form display a currently valid 0MB control number, the NRC may not conduct or sponsor, and a person http://www.nrc.gov/readinq-rm/doc-collections/nu regs/staff/sr1 022/r3D is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 3. LERNUMBER YEAR SEQUENTIAL REVISION Hope Creek Generating Station NUMBER NUMBER 05000354 2019 - 001 - 00 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor (BWR/4) Feedwater System (SJ) - EIIS identifier {SJ}* Feedwater/Steam Generator Water Level Control System (JB) - EIIS identifier {JB}* Heat Rejection System (KE) - EIIS identifier {KE}* Reactor Protection (JC) - EIIS Identifier {JC}* Reactor Core Isolation Cooling (BN) - EIIS Identifier {BN}* *Energy Industry Identification System {EIIS} codes and component function identifier codes appear as {SS/CCC} IDENTIFICATION OF OCCURRENCE Event Dates: August 03, 2019 Discovery Dates: August 03, 2019 CONDITIONS PRIOR TO OCCURRENCE Hope Creek was in Operational Condition (OPCON) 1 - Power Operation, 37 percent power. DESCRIPTION OF OCCURRENCE At 1906 EDT on August 3, 2019, while in OPCON 1 at 93.8 percent power, operators identified degrading main condenser vacuum and commenced reducing power. Degrading vacuum was due to the circulating water {KE} cooling tower bypass valve failing open. At 1947, the reactor was manually scrammed from 37 percent due to loss of condenser vacuum. Reactor feedwater {SJ} pumps (RFP) tripped when reactor pressure vessel (RPV) water level rose to level 8 (+54 inches) because the reactor feedwater startup level control valve (SULCV){JB} failed open. Operators initiated the reactor core isolation cooling (RCIC){BN} system, recovered a RFP and secured RCIC after establishing control of RPV water level. The failed equipment was replaced. This event is reportable per 10 CFR 50. 73(a)(2)(iv)(A). CAUSE OF EVENT A Bailey solid-state logic module failure caused the cooling tower bypass valve to open; which led to loss of main condenser vacuum. A pneumatic relay failure caused the SULCV to fail open. SAFETY CONSEQUENCES AND IMPLICATIONS There were no safety consequences as a result of this event. The Reactor Protection System {JC} system operated as designed to shut down the reactor. The RCIC system operated as designed to inject water into the reactor core. PREVIOUS EVENTS A review of station Licensee Event Reports and the corrective action program for the past three years was performed. No LERs were identified and no issues were documented in the corrective action program for similar conditions. | ML19274D127
clinton power station | Unknown Unit | Turbine Driven Reactor Feed Pump Hydraulic Control Failure Results in Automatic SCRAM | 10-01-2019 | On August 3, 2019, at 0226 CDT, while operating at approximately 98% power, the Turbine Driven Reactor Feed Pump (TDRFP) 8 horizontal hardware connection to the Linear Variable Differential Transformer (LVDT) failed causing loss of feedback to the feedwater control system. Flow from TDRFP 8 decreased while TDRFP A flow increased and reactor level decreased to the scram setpoint, which caused an automatic Reactor Protection System (RPS) scram. All control rods fully inserted. The reactor water Leval 2 setpoint was reached and High Pressure Core Spray (HPCS), Reactor Core Isolation Cooling (RCIC), Division 3 diesel generator, Standby Gas Treatment Systems A and 8, and all safety related shutdown service water pumps started as expected. RCIC and HPCS injected as expected. All Leval 2 containment ' isolation valves closed as expected. As a result of automatic isolation of the containment ventilation system, the Primary Containment to Secondary Containment and the Drywell to Primary Containment differential pressure limits were exceeded. The cause of the event was the design of the horizontal connecting hardware to thaTDRFP 8 operating cylinder positron LVDT was not adequate to withstand cyclic loading. The failed LVDT was replaced on TDRFP 8, along with associated horizontal connecting hardware. A design change will be developed and installed to strengthen the connecting hardware to the TDRFP 8 operating-cylinder LVDT such that it is adequate to withstand cyclic loading. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A), 10 CFR 50.73(a)(2)(v)(D), 10 CFR 50.73(a)(2)(ii)(8), and 10 CFR 50.73 a 2 v C. NRG FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPAOVED BY 0MB: NO. 31!50-0104 EXPIRES: 03/31'2020 (CJ.4-2018!) w\ /--~ E le s s t s m on a s te l d e a tx rn Jr e d d e n a re p e l/ r 1 1 C '8 O S ! ! J )O X f ) 1 fl S lle e d lo in c to a n Ir p e ly l l ' c M el I l i S l l l r t i d g s p m ro a c n e d 8 a 8 t o e ! o y o c f c e t d B d b l a o c o k r t e o q 1 u n e d s Js t ti 8 y 0 h S o e u o r o s c R or e m po ,a rt n e t d s LICENSEE EVENT REPORT (LER) regartlllg burden es1imata to the nlormak,n Sernces Branch (T-2 F43), U.S Nuclear Regulatory • \ '*•»• ~·I CONTINUATION SHEET G th o e m D m e l s ss k 1 o ° n '1 , c W er l , ll !h O ln ft g lc t e o n a , D 1 C r1 o 2 r 0 rn 5 a 5 b 5 o - o 0 0 a 0 n 1 d , R or e g b u y a l & o - 1 m y a J A I ff t a o i rs lr , ro N c E d O le B c - t 1 s 0 R 20 e 2 s , ru (3 rc 1 e 5 0 Q - 0 rv 1 c 0 4 IP ), t' O , l a ft n c d e t a o Management and Budget, Wa.shil1Jlon, OC 20503 tt a means U88d to mpose 1¥1 mforrnallon (See NUREG-1022, R3 for lnstrucbon and guidance for complemg th1S form cdkdon does not c!is?aY a wrently Ya.:! 0MB cc:nrn ntJ11bar, the NRG may not cooducl or httpJ!www.nrc.gov/reaclna-rm/doc-cojlecbons/nu reas/staff/sr1022/r3/l sponsor, and a person Is not reqLJred to respond to, the 1rrorrnallon collection 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR Clinton Power Station, Unit 1 05000461 NUMBER NO. 2019 - 002 00 | PLANT AND SYSTEM IDENTIFICATION General Electric -- Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in text as [XX]. EVENT IDENTIFICATION Turbine Driven Reactor Feed Pump Hydraulic Control Failure Results in Automatic SCRAM A. Plant Operating Conditions Before the Event Unit: 1 Event Date: August 3, 2019 Event Time: 0226 Mode: 1 Mode Name: Power Operation Reactor Power: 098 B. Description of Event On August 3, 2019, at 0226 CDT, while operating at approximately 98% power, the Turbine Driven Reactor Feed Pump [SJ-P] (TDRFP) B horizontal hardware connection to Linear Variable Differential Transformer (LVDD 1ZT-FW199 failed causing loss of LVDT feedback fo the feedwater control system for TDRFP 8.- Flow from TDRFP B began decreasing due to the control system reducing speed demand in response to the LVDT failure. TDRFP A [SJ-P] speed and flow increased to maximum and reactor water level decreased to the scram setpoint within 15 seconds, which caused an automatic Reactor Protection System (RPS) scram. Operators placed the reactor mode switch in shutdown and completed the scram response actions. All control rods fully inserted. Due to the failure mode of TDRFP B (i.e., the pump slowed but did not trip), a trip 'of the feed pump was not sensed by the Reactor Recirculation [AD] (RR) flow control valve [FCV] runback circuitry. With TDRFP A injeding post scram, reactor water level continued to lower to below the Level 2 setpoint. When the reactor' water Level 2 setpoint was reached during the event, the High Pressure Core Spray (HPCS) system [BG], Reactor Core Isolation Cooling (RCIC) system [BN], Division 3 diesel generator [DG] (DG), Standby Gas Treatment Systems [BH] A and B, and all safety related shutdown service water pumps [81-P] started as expected. RCIC and HPCS injected as expected. All reactor water Level 2 containment isolation signals [JM] occurred as expected and all associated containment isolation valves [ISV] closed as expected. Following automatic initiation of HPCS as described above, the system was manually secured using station procedures after verification that additional Reactor Pressure Vessel [RPV] (RPV) injection was no longer required. The Primary Containment to Secondary Containment and the Drywell to Primary Containment differential pressure Technical Specification (TS) limits were exceeded as a NRG FORM 386A (04-201 B) Page _2_ of _..1._ | ML19277E367
Nine Mile Point | Unit 1 | Average Power Range Monitors Declared Inoperable | 10-03-2019 | On August 4, 2019 at 1745, Reactor Recirculation Pump #11 (RRP 11) tripped. Following the RRP trip, the Average Power Range Monitors (APRMs) flow bias trips were inoperable due to reverse flow through the RRP. The APRMs were restored to operable on August 4, 2019 at 1807 when the RRP 11 discharge blocking valve was manually closed by operations, eliminating the reverse flow condition through the pump. This event is reportable under 10 CFR 50.72(b)(3)(v)(A) and 10 CFR 50.73(a)(2)(v)(A) as any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: (A) Shut down the reactor and maintain it in a safe shutdown condition. The cause of the RRP 11 trip is a degraded tachometer generator on the associated motor generator set. Corrective actions to prevent recurrence are to revise the preventative maintenance strategy to replace the tachometer generator every two years. The event described in this LER is documented in the plant's corrective action program. NRG FORM 366 (04-2017) ( N 04 R -2 C 01 F 7) O ) RM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (Se h e t t N p U :// R w E w G w - . 1 n 0 rc 2 . 2 g L , o I R v C / . r 3 e E a fo d N r C i n in g S O s -r t m E r N u / c E d t T o io c I n E - N c a o V n l U l d e E c A g ti u N o T i n d T s a I / O n n c u R e r N e f E g o s r S P / c s o t H O a m ff E p R /s le r E T 1 ti 0 n T 2 g ( 2 L t / h r i E 3 s 1 f R ) o rm ) c u N N R l c l E n e o s R o E e f s s l e o l m G e O g s t d i c m o c u m B o t n l t m i a a l o - e o l s 1 e t t n a n o e 0 c i t y m . r d l 2 t s e y s 0 p a . n b r R 2 o e r o u , n s g e t r e e d a s (3 e c d o C rd 1 a o n u o i n 5 n n r a m c p 0 d g r i e e - e u n m 0 @ r c f b 1 o i t s r i u 0 n r e n s m r 4 o c s i r d o c ) o r p a e , n . r o t n g p s , i O o n o p o n s f v e o r f e i a , s c n c t t e s a e i t o W m o o n d l o l r d e a a c , f c t o s i e t M n t o h a m i o t n i a o n t n p t o d n h g l y a e t d t o t h a g h o w n e D e e e i , p m t e s h e l s I i e n c r n k t s n e f h o o o t O i n t s D r n s m a f d C f i m n n i i a c i s s d g e a p t i o r n l B a n , n p d y u o O r a 2 d t o S t a 0 f g o c f r e i 5 e e r e c c y r 5 t e s q u v , 5 s c u i r c - r W o o i 0 e e r f l e a 0 n l s a e I d n 0 t n s c l d y 1 B h f t o i t , i o r o n v r a f n m a e g n r l d t i a c e o r d e h t n s i o o q b p , 0 r n u a ( o M D T e c n a - C B k s d 2 n t : d 2 t c b F t o 8 o o 0 y R 4 0 , n 5 3 e i t 0 n h r ) t g h 3 o , d o u e . l u u U l e a n s rs . - i t t u I n S m o r f . m y f r . o a R a y . b r i N e l m m A e p u r f a S e , o f c a t a r e l i t e i o t h n r n e s t a n e s o d d , r 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER Nine Mile Point Unit 1 05000220 YEAR SE N Q U U M EN BE T R IA L R N E O V . 2019 - 004 - 00 | I. DESCRIPTION OF EVENT A. PRE-EVENT PLANT CONDITIONS: r P e r a io c r t o to r p th o e w e e r v . e n A t l , l N fiv in e e R M e i a le c t P o o r i R nt e c U ir n c it u 1 la t ( i N on M P P 1 u ) m w p a s s ( R in A t P he ) w po er w e e i r n o o p p e e ra ra ti t n io g n . c ondition at 100% B. EVENT: i t f f P O n h l l o o o o e n w w p i n a A e t i t l n r u h lo a U p r g w b o n u u l u i a t e s t g b t . t 1 o h l 4 , e , t t d h h T 2 u e e e 0 e c A 1 tr t h 9 P o ip n , R p i t a c h M e a t e d l 1 l f S o 7 p iv g : u p e 4 i m e c 5 A c , p r i R e f N . i c s P M a T u P t l h p t io i 1 i u n s n m g e r v e p x i a n v p d l e u e t e h r e r s s i e . e e i g n A A f n c l P o , s e R w a d a M t a c r r o e i p f t s n l r o i u d o p w l i f t t , o i a o b f O h n ia A p A s r R e e e R P r s d a P u t t 1 i l r o t a 1 i s p n t a s i p n s t o e d 1 a w t e n 0 p e c 0 o l r u a % i n w n r e c t i p l d o l b o n r e w t e h s i e n s e e u r g r . v A l t h a P A i i t n g i R t v h r e N M e e i v t r s n o e . t e t h r a s a M l e n i l e S t A e p t r m e 1 c 8 in i : f 0 i a c 7 t a i , n t i O g o n p th e 3 e r . a 6 r t e . i 2 o v a n e s r e s c x e l i o t f e s lo d e . w d c th o e n d A it R io P n . 11 T h d e is A ch P a R rg M e s v w al e v r e e in d e a c c la c r o e r d d a o n p c e e r a w b i l t e h a N n 1 d - S T O ec P h - n 1 i . c 3 a l Nine Mile Point Unit 2 (NMP2) was unaffected by the ARP trip at NMP1. f t a O h u n e l p f d i e l r l r e m 1 a O a t e c i o n C to n t F r s o R a f p n t 5 e h d 0 r e f . m o 7 s r 3 a a m ( f i a n e e ) t t d ( a y 2 i t n f ) h u ( e v n it ) c ( E in t A i N o ) a S n a s s o n a f o f a e s t n i t f s r y ic u h a e c u t v t t i u o e d r n n o e t w s ( o # n o r 5 r c c 4 o s o 1 y n n 9 s d d 9 t i i ) e t t i i o m o re n n s q . t u t h h ir a a e t t d c a o b re u y l n d 1 e 0 h e a C d v F e e d R p to 5 re : 0 v . ( 7 e A 2 n ) ( te S b d ) h ( u 3 th t ) ( e d v o )( w A n ) This event has been entered into the plant's corrective action program as IR 4269525. C. T IN H O E P E E V R E A N B T L : E STRUCTURES, COMPONENTS, OR SYSTEMS THAT CONTRIBUTED TO No other systems, structures, or components contributed to this event. D. D A A C T T E IO S N A S N : D APPROXIMATE TIMES OF MAJOR OCCURRENCES AND OPERATOR . f T o h ll e o w d s a . t es, times, and major occurrences and operator actions for this event are as · August 4, 2019 17:43 - G C e o n m e p ra u t t o e r r ( p R o R in M t K G 3 ) 1 1 1 1. a larm was received for Reactor Recirculation Motor NRG FORM 366A (04-2017) Page _2_ of _5_ ( N 04 R -2 C 01 F 7) O ) RM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (Se h e tt N p U :// R w E w G w - . 1 n 0 rc 2 . 2 g L , o I R v C / . r 3 e E a fo d N r C in in g S O s -r t m E r N u / c E d t T o io c I n E - N c a o V n U ll d e E c A g ti N u o T i n d T a s I / n O n c R u e N r e E fo g r s S P / c s o H O t m af E p f R / l s e E r T t 1 in 0 T g 2 ( 2 L th /r i E 3 s D f A o rm ) c N u N l R c l E n e o s R o E e f s s l e o l m G t e g s O d i c m o c u m o B t n t l m a i a l o - e o l s e 1 t t n a n e o 0 c i t m y . d r s l t 2 e y s 0 p a b . n r R 2 o e r u o n , s g e r t d e e a ( s 3 e d c r C o d 1 a n o u o i n 5 n n r a m p 0 c d g r i e e e - n u m 0 r @ c f b 1 o i t s r i u 0 n r e n s m r 4 c o s d r io c o ) p r a e , n . r o t g n p s , i O n o o o p s n f v e o r f e i a , s c n c t t e a s e t i o m o W o n d l o l r d e a c a , f c t o s i e t n M t o m a h i o t n i o a n t n p t o d h n g l y e a t d t o t h a g h o w n e D e e e , i p t m e s h e l s I i e n c r n k t s n e f h o o o O t n i t s r D n s m a f d C f i m n n i i a c s i d s g e a t p i o r n l B a , n n p d y u o O r a 2 d t o S t a 0 f g o c f r e i 5 e e r c e c y r 5 t s e q v u , 5 s i u c r c - r W o o i 0 e e r f l e a 0 n s l a e I n d 0 t n s l c d y 1 B h f t o t i , i o r o n v r a f n m a e g n d l r t i a c o e r d e h t n s i o o q b 0 p , r n u a ( o M T D e c n - a k C B s d 2 n t : d 2 c t b F t 8 o o o 0 y R 4 0 , n 5 3 e i t 0 n h r ) t g h 3 o , d o u e . l u u U l e a n r s s - . i t u t I n S m o r . f m y f r . o R a a y . b r N i e l m A m e p u r f a S e , f o c a t a e r l i t i e t o h r n n e s t a n e s o d d , r 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER Nine Mile Point Unit 1 05000220 YEAR SE N Q U U M EN BE T R IA L R N E O V . 2019 - 004 - 00 NARRATIVE 17:45 - Received annunciator F2-2-1 for "React Recirc M-G Set 11" indicating it had tripped. 17:46 - Entered N1-SOP-1.3, "Recirc Pump Trip at Power'' was entered 1 1 8 7: : 4 0 6 7 - -A R P R R P M 1 s 1 d d e is c c la h r a e r d g e in v o a p lv e e ra i b s le c lo a s n e d d T p e e c r h n N i 1 ca -S l O Sp P e -1 c . if 3 ic , a A ti P o R n M 3 s .6 d .2 e a c l w ar a e s d e o n p te e r r e a d b . l e and Technical Specification 3.6.2a was exited. E. METHOD OF DISCOVERY: T re h c i e s iv e e v d e n fo t r w " a R s e d a i c s t c o R v e e c r i e rc d M b - y G R S ea e c t t 1 o 1 r " O . perators when the control room alarm was F. SAFETY SYSTEM RESPONSES: t N h o is o c p o e n r d a i t t i i o o n n a . l conditions requiring the response of safety systems occurred as a result of II. CAUSE OF EVENT: b w T r h i u th e s i h n c e a t s u h s e a e n t a d o c f t h h th o e e m c e R o t m R er M m g G u e t n a tr e t i o p r r a . w t o a r s . d T e h t e e r m m o in s e t d li k t e o l y b e lo a c n a ti i o n n te w rm o i u tt l e d n b t e p o b o e r t w e e le e c n tr i o c n a e l c o o f n th n e e ction III. ANALYSIS OF THE EVENT: s s a T a t n h r f u y i e s c e t s e u v h v e r u e e n t n s d t t o o o i w s r r c n s r o e y c s n p o t d o e n i r t m d t i a o i s t b n i o l t e h n th a . u a t n t a d c r e o e r u n l 1 d e 0 e h C d a F e v d R e t p 5 o r 0 : e . ( v 7 A e 2 ) n (b S te ) h ( d 3 u ) t t h { d v e o ) ( w f A u n ) lf i a t ll h m n e d e r n 1 e t O a o c C f t o F th r R e a n 5 s d 0 a . f 7 m e 3 t a y ( i a n f ) u t ( a n 2 i c ) n ( t i v o it ) n ( i A n o ) a f a s d t v f r T h l e e a o h e m l s w e u i n a g r e - e b o i n n o i n e a w e f - d s d c e 1 . e o r 2 a d e n 2 v s p n % a e o o il r r a v o t a b i a f o c l t r e n t i a u v . t e a o e l A f d f n l t o h p t u h w e o c e r l h s e t r i m i i o a g g n r a h n s l a o n a p l f e f o a t e u h w n t t e y d r e o r c f r n . l o e o n m f w T lu s h - a x e b i i s n q i t a r e u p s ip d e o e s n r d a t c i w v o e tr a a n s ip i s l a o a f n b f s u o l s t n e h t o c e c t c t o i o i o s a n n e p te s t r p o c e d u o v r w v r i i d n v a i e t e t t h i c v t i u s h e th r e , c v e t l e s h a e c e m w v r a e t p a r m n e i s p t d . n t f r u o a i A p n t t l c t i a f h m u t i o m o n p u n c a a g t c i x h o t i e m n t d h u a e m b s y s S R a A (S e n L n e t L d M p a a M o c t C s r i t C n a o s P t P n e r R s s s O R . i s p e ) S w m n r w h n o t e o s e t a n e . u r s t c s l N d t ' o p i M o G f e o n t r P s r h f o o 1 c f e o u i r l m l p r i p a s o p e t O i a t o d o e n p s . n n a t t s T i u t o l i y h a l o n a z i l c s t e e I i c I m d . a d u T s p r f , i o s a h n r t e c s e h s t t t e h a O s o y e b m n p r i w l m t e i t i t o i h n y l a l n e t l e b - i h s I n v e I a y e c a a d f l n u e n u r t d a t a s t y o e u l y b m d l l i s i y m c i a a s t i i t h t n i r i c e s e m s a v t A p l i a i l n e y e P b i w m r i R d l f i o t e u M o y r t m m f e u f t c l e h s c o t d i e e r w n i r d t g t m - i o c b a t a a i h d n a l l e e d s p h m e o B y s d w d o u o r n p f i e l a l i s u p r n u t x r g r r l e i a a c s s W t t c i s e o s r e a t a t a d t h m e b e b r i l i y t y NRG FORM 366A (04-2017) Page _3_ of _5_ ( N 04 R -2 C 01 F 7) O ) RM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (Se h e t t N p U :// R w E w G w - . 1 n 0 rc 2 . 2 L g , o I R v C / . r 3 e E a fo d N r C i n in g S O s -r t E r m N uc / E d t T i o o c i n E - N c a o V n U ll d e E A c g t u N io T id n T a I s O n / n c R u e N r E f e o g r S P s c /s o H O t m af E p R f/ l s e E T r t 1 in T 0 g ( 2 L 2 th /r i E 3 s D f A o rm ) c u N N R c l l E n e o s o R E e s s f e l m o l G t s O e g d i c m o c u m B o n t t l m i a a o l - e o s l 1 e t t n a n e o 0 i c t m y . d r s l 2 t e y s 0 p a b n r . 2 R o e r u o n , g s e r t d e e a ( s 3 e d c r C o d a n 1 o u o i n 5 n n a r m p 0 c d g r i e e e - n u m 0 r @ c f b 1 o i t s r i u 0 n r e n s m r 4 c o s d i r o o ) c p r e a , n . r o n t g p s , i O n o o o p s n f e v o r f e a i , s c n c t t e a s t e i o m W o o n d l l o r d e a a c , f c t o s i e t n M t o h m a i o t i n o a n t p n t o d h n g l y e a t t d o h t a g h o w e n D e e e , i p t m e s h e l s I i e c n r n k t s n e f h o o o t O n i t s r D n s m a f d C f i m n i n i a c i s d s g a e t p i o r n l B a , n n d p y u o O a r 2 d t o S t a 0 f g o c f e r i 5 e r e c e c y r 5 t e s q v u , 5 s i c u r c - W r o o i 0 e e r f l e a 0 s n l a e I d n 0 t n s c l d y 1 B h f t o i t , i o r o n v r a f n m a e g n l d t r a i c o r e d e h t n s i o o q b , 0 p r n u a ( o M T D e c n - a C s B k 2 d n t : d 2 c t b F t 8 o o o 0 y R 4 0 , n 5 3 e i t 0 n h r ) t g 3 h o , d o u e . l u u U l e a n s rs . - i t t I u n S m o r f . m y f r . o a R a y . b r i N e m l m A e p u r f a S e , f o c a t a r e l i t i e o t h r n e n t s a n e s o d d , r 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Nine Mile Point Unit 1 05000220 YEAR SE N Q U U M EN BE T R IA L R N E O V . 2019 - 004 - 00 NARRATIVE R i p i A t s n h r e s e o n c s t s o o t f e r u l t n o c i c c a j w t u h t t e n - c , h b d o c e w i t n a i r h o S c e s e n e g e L n r i d M o w n A n C A it b . P h P P a R t R R r h r M i . M e n s A g E n t a a x e r r d c a e u d l t t u e r d i o s t d e i i o n o c c n n l f o a a l u _ n r l a e x d r n d e i s d t a i c i o n R c r n a o t e o s m p s r e d t . r r r u e l T a c r c h b i t n i e i l r s e g c d , u a t r l h o n a e e p a t g i e o l i A y o r n s a P n i t s s f R o l o r M o c s w n r e a i t r n d r h e e o i e t d s p u r e p e t c h r o q t a i e w u o b i n e f r le l e r o a d t w s o n c - t d o b e f l i n o e a u a w n s s r t e e i r m o a d p , n a r f i c p l o n u e , c s x e t t i o a n s d b c t u o r i r l a i e t t m h y s e . t A V O a T d F h P a e r e o p s a l c R r e c v A n a r r e t M s a r a P y a i m t C e R s i n r o n e l i M s o t n o t a u i s e a s r d r a u e n l t i t c r n r i s t O e i o o p g u r , n c u . e . l t s c G l v s W d u A i i e e f n r i s b r w t n r o h e e w e s , m n u r r h d t a c e h c i e t c e t s h e r o c h s i p , p l r a R e p i t ( L f r h c A e i e o n o t e c O d a g n t i o r c O d e c o v o s c u p a R o r ) y e l e r f a , e c i r o t t j t t l a h i e e h h u o b c e e e s n s t l s r s e , p m c e P e M e o a u a e c m e g S m l v i v a f b I t e i e p i V r c n i n a n n , T t t n c t a r s s t l s r a t o h i i i p w n o t e s e e s n u n e a r i S s r r t m e n s e e L n d o ) i M n r t t f e o a S a a C r m n t t e n o e a P d a c a c l l R i o i c l a r n y M n c u r s w u e w r a e a l o a a i l s t t f h u d f h t u t i p e l i o i e n d r n e r e n r c e r s c p t a f f p i t t o o e o i l u A s r r l r n e m m m c R b s , r e e p i a P a s u d s m s r p n t e i f r r d a b o i o ( p o f i l T r n t f e e e h u a n A c c l r n e o i n t m t b e d r e t t i e i d n i d r c t b n e s e . i p e b t . s a f S y p u o t l o t e t r o e w d i p n e r r T A e h R s e p P e d 1 c ir 1 t e i . v c e O t c o p a p e u e ra s ra t e o t i r o n s f g w t h p e e r r o e A c P e a d b R u l M e r e s to s b s a e t n i a n d b g i r li e d z m e e c a p la i l n a r i e n n d t g c i i n o n o n c p d o e it m r io a p n b l s l i e a q n w u c a e ic s k w l t y i h th e b y T tr S i p p r r o a e p s q e s u r o i l r c y e i a e m t x e e e d n c t u w s t . i i t n h g th th e e t I h t r is e a c t o t n o c l t u h d e e h d e t a h lt a h t t a h n e d s s a a f f e e t t y y s o ig f n th if e ic p a u n b ce lic o o f r t h p i l s a n ev t e p n e t r s is o n lo n w e , l . and the event did not pose a f T u h n i c s t i e o v n e f n a t i l d u o re e s s . affect the NRC Regulatory Oversight Process Indicator for safety system IV. CORRECTIVE ACTIONS: A. S A T C A T T IO U N S: TAKEN TO RETURN AFFECTED SYSTEMS TO PRE-EVENT NORMAL b R a e c p k l a in ce to m s e e n r t v i o c f e t . h e tachometer generator was completed. The ARP 11 was placed B. ACTION TAKEN OR PLANNED TO PREVENT RECURRENCE: s C t o ra rr te ec g t y iv t e o a re c p ti l o a n c s e t t o h e p r t e a v c e h n o t m re e c te u r r r g e e n n c e e r a a t r o e r t e o v r e e r v y i s t e w o th y e e p a r r e s. v entative maintenance | ML19281A860
Edwin I. Hatch Nuclear Plant | Unit 2 | High Pressure Coolant Injection System Declared Inoperable Due to Brief Loss of Power to HPCI Pump Flow Controller | 01-06-2019 | On August 22, 2019 at 2234 EST with Unit 2 operating at 100% rated thermal power, the "High Pressure Coolant Injection (HPCI) system inverter circuit failure" alarm was received on a Main Control Room panel. This alarm indicates a loss of AC power from the HPCI inverter, and is caused by either a loss of DC power to. or a failure of, the inverter. Operating personnel immediately noticed the loss of indication on several digital recorders and on the HPCI flow controller. At 2235 EST, the "HPCI system inverter circuit failure" alarm cleared, and all referenced digital indications returned to normal. Subsequent investigation into the HPCI inverter circuit failure revealed a failed ceramic capacitor in the HPCI turbine speed control power supply. The failed capcitor caused a short-circuit condition that momentarily drew power down on the HPCI inverter. This caused a momentary loss of indication to the referenced digital recorders and a momentary loss of power to the HPCI flow controller. In the event of a valid HPCI initiation signal, the momentary loss of power to the HPCI flow controller would have resulted in a loss of HPCI function. Operations personnel therefore declared HPCI inoperable at 2234 EST. The cause of the capacitor failure was not determined. Ceramic capacitors of this type are not known to fail at a specified frequency and are not recommended for replacement on a periodic basis. The HPCI turbine speed control power supply was subsequently removed from service, replaced, and the new power supply tested satisfactorily. NRC FORM 366 (04·2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 0313112020 (04-2018) Eslimaled blln!en per response ID comply witll tllis mandatory coledion request 80 ho1Jis. Rsportad :: ~ ~ " ~ " ! . ' . - 1 ·· . i LICENSEE EVENT REPORT (LER) l r e e s g s a o rd ns in g le a b r u n n e S d e n a 1 e e s i t n im aJ a r t p e o I r D a te U d te i n ln iD fo U rm te a r l c io e n n s S in e g M p c r e o s c e B ss ra a n n ch d f ( e T d - 2 b a F d 4 e 3 ) ID . U in dU S. S i N ty u d S e e a n r d R co e m gu m la e to n r t y s \. ..... 1 CONTINUATION SHEET Commission, Washing!On. DC 20555-0001, or by a-ma~ 10 fnfocollecls.Resource@nn:.gov, and to Ute Desk Officer. Office of lnformi!tian and Regulatory Aflairs, NEOB-10202, (3150-0104), Office of Management and Budgel Washington, DC 20503. II a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form coDection does nat display a cunenlly val1d OMB conlnll number. Uta NRC may not conduct or t'lttp;//YI'fiW.nic.gqylr:e.ii!ling:rrnld..!l..C~coJle.cti.oo..stn_ur.egs/sta.Ws.d.0.22lr.3ll sponsor. and a parson is not requillld to respond to. lhe information coUectlan. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 05000-1 rY:E:ARJ SEQUENTIAL REV Edwin I. Hatch Nuclear Plant Unit 2 366 IL .:J·I NUMBER 1- NO 0 . 004 | EVENT DESCRIPTION On August 22, 2019 at 2234 EST with Unit 2 operating at 100% rated thermal power, the "High Pressure Coolant Injection (HPCI) system inverter circuit failure" alarm was received on a Main Control Room panel. Operating personnel immediately noticed the loss of indication on several digital recorders and on the HPCI flow controller. At 2235 EST, the "HPCI system inverter circuit failure" alarm cleared and all digital indications returned to normal. At 2234 EST, HPCI was declared inoperable due to the failure of a ceramic capacitor inside of the HPCI turbine speed control power supply. The failed capacitor caused a short-circuit condition that momentarily drew down power on the HPCI inverter and resulted in a loss of function to the HPCI flow controller. Failed Component Information: Master Parts List Number: 2E41 K065 Manufacturer: Lambda Electronics Model Number: LRS 52-48 Type: Power Supply The capacitor failure would have ultimately resulted in a loss of HPCI function during a demand and rendered HPCI inoperable. EVENT CAUSE ANALYSIS Upon investigation into the "HPCI system inverter circuit failure" alarm, a loss of indication was noticed on several digital indicators and a burning smell was noted on one of the Main Control Room back panels. Subsequent visual inspection revealed a failed ceramic capacitor in the HPCI turbine speed control power supply. The cause of the capacitor failure was not determined. Ceramic capacitors of this type are not known to fail at a specific frequency and are not recommended for replacement on a periodic basis. SAFETY ASSESSMENT This event is reportable per 10 CFR 50. 73(a)(2)(v)(D) due to an event or condition that could have prevented the fulfillment of the safety function of a structure or system that is needed to mitigate the consequences of an accident. The HPCI system is a single-train system that is designed to ensure that the reactor is adequately cooled to limit fuel-cladding temperature in the event of a small break in the nuclear system and a loss of coolant does not result in a rapid reactor pressure vessel depressurization. The HPCI system will continue to operate until the Reactor Pressure Vessel (RPV) is below the pressure at which either operation of the Low Pressure Coolant Injection (LPCI) mode of the Residual Heat Removal (RHR) system or the Core Spray (CS) system will maintain core cooling. Upon a small break which results in a loss of coolant accident (LOCA), HPCI provides sufficient inventory to prevent the core from becoming uncovered. In the event that HPCI is unavailable or inoperable, the Automatic Depressurization System (ADS) is credited to depressurize the RPV to enable operation of the low pressure ECCS systems, i.e., CS or LPCI. Reactor Core Isolation Cooling (RCIC) is also available to restore and maintain water level. Although HPCI was declared inoperable, ADS, CS, LPCI, and RCIC were operable and could have provided core cooling in the event of a small break LOCA or a Design Basis Accident (DBA) LOCA. Therefore. based on the ability of the station to mitigate the consequences of a potential loss of the HPCI system combined with a small break LOCA, this event is considered to have very low safety significance. | ML19289E222
Cooper Nuclear Station 05000298 1 of 4 | Unknown Unit | Secondary Containment Rise in Differential Pressure Results in Loss of Safety Function | 03-31-2020 | On August 8, 2019, a spike in Secondary Containment occurred with differential pressure (DP) exceeding the Technical Specification limit of 0.25 inch of vacuum water gauge (wg) causing Secondary Containment to be inoperable for 7 minutes. The spike was due to Reactor Building heating, ventilation, and air conditioning (HVAC) supply filter media being advanced excessively causing DP to rise to 0.19 vacuum wg. The DP was not immediately identified by Control Room personnel due to Secondary Containment DP not reaching the high pressure alarm setpoint and they were unaware of the filters being advanced. Causal factors were that the condition of the supply filters was not properly prioritized and risk associated with the supply filter activities was not recognized and controlled properly due to it being classified as a skill of the craft activity. The operations department skill of the craft list was revised to delete activities such as advancing the supply filters that have plant operational risk. More formal controls are being implemented for operation and maintenance of the reactor building HVAC supply filters. Operations department wide communications are planned to discuss the event, causal factors, and corrective actions. There was no impact on nuclear safety, plant reliability, radioloQical safety, or industrial safety. NRG FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported /"''-..,. lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) (~} comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear ...... Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid 0MB control number, the http://www.nrc.gov/readinq-rm/doc-collections/nureqs/staff/sr1022/r30 NRG may not conduct or sponsor, and a person is not required to respond to, the infonmation collection. 1. FACILITY NAME 2 DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Cooper Nuclear Station 05000298 NUMBER NO. 2019 - 002 - 00 | PLANT STATUS Cooper Nuclear Station was in Mode 1, Power Operation, at 100 percent power, when the event was discovered; i.e., August 8, 2019. BACKGROUND Technical Specification (TS) Surveillance Requirement 3.6.4.1.1 verifies that Secondary Containment vacuum is greater than or equal to 0.25 inch of vacuum water gauge (wg). Limiting Condition of Operation (LCO) 3.6.4.1, requires Secondary Containment to be operable in Mode 1. If Secondary Containment is not operable, LCO 3.4.6.1, Condition A, requires restoration of Secondary Containment to operable within 4 hours. The Secondary Containment system is designed with sufficient redundancy so that no single active system component failure can prevent the system from achieving its safety objectives, which includes preventing ground level releases of airborne radioactive materials to the environment. Secondary Containment consists of four main subsystems, two of these are the Reactor Building [EIIS: NG] and standby gas treatment system [EIIS: BH]. The Secondary Containment system is designed to be sufficiently leak tight to allow the standby gas treatment system to reduce the Reactor Building pressure to a minimum of 0.25 inch of water column vacuum when neutral wind conditions exist when the standby gas treatment system fans are exhausting Reactor Building atmosphere at a rate of 100% per day of the Reactor Building free volume. During normal operations, the Reactor Building ventilation system [EIIS: VA] is operated to produce a minimum of 0.25 inch of water column vacuum inside the Reactor Building as compared to the outside atmosphere. The Reactor Building supply filter consists of three separate rolls of filter media, each one being five feet wide. The new filter rolls load onto the filter unit at the top of the unit and the filter media is pulled out and connected to take up reels at the bottom of the unit. The bottom rolls are connected to motors that are operated by a switch. When the switch is activated, all three motors actuate and the three bottom take up spools pull the filter media down across the screen face to expose fresh filter media to the supply air flow. The filter rolls include paper leaders and trailers to assist in installation. EVENT DESCRIPTION In May 2019, the south roll of filter media was becoming depleted and needed replaced; however there was no replacement fan filter media on-site. This issue was not added to the short-term operational issues list and filter replacement was not appropriately prioritized, resulting in a delay of approximately three months to receive the filter media. | ML19295F428
Limerick Generating Station | Unit 1 | Multiple Trains of RHRSW Inoperable for Greater than Time Allowed by Technical Specifications due to Pipe Corrosion | 10-24-2019 | On 7 /11 /19 a pin hole leak was identified on the 18-inch distribution piping of the C Spray Network while the spray network was in operation for Spray Pond cooling. Subsequent NOE inspections identified wall thinning over a large arc of the piping's circumference; approximately 34 feet of piping required replacement. On 08/25/19, the extent of condition inspection of the A Spray Network identified similar corrosion damage. The condition was determined to be reportable for a condition prohibited by Technical Specifications and a common cause inoperability of independent trains. All four Spray Networks were inspected, and corrosion damage was identified on all four of the Spray Networks' 18-inch distribution piping. Although the 18-inch spray network distribution piping was degraded, the spray networks and the ultimate heat sink were determined to be functional. The cause of the pipe corrosion damage observed on the 18-inch distribution piping of each spray pond spray network was flow-induced film removal accompanied by high humidity electrochemical atmospheric corrosion. This condition was not identified prior to the piping becoming inoperable because there was a lack of understanding of this potential failure mechanism. The affected piping was replaced and an NDE inspection and proactive pipe replacement strategy will be established to ensure long term reliability of the above ground spray pond spray network piping. NRC FORM 366 (02-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request. 80 hours Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U. S Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects Resourte@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503 If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB control number, the NRC may not conduct or hl!pJ/www.nn:;,gov/read.ing-rmtd.oc-co!lection&lnY.r.egs/s!aff!sr102.2tr31) sponsor, and a person is not required to respond to, the information collection 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER REV NO. Limerick Generating Station, Unit 1 05000-1 352 1-0 | Unit Condition Prior to the Event Limerick Generating Station (LGS) Units 1 and 2 were both operating in Operational Condition (OPCON) 1 at 100 percent power at the time of the event. There were no other structures, systems, or components inoperable at the time of the event that contributed to the event. Description of the Event On 7/11/19 a pin hole leak was identified on the 18-inch diameter distribution piping of the C Spray Network while the spray network was in operation for Spray Pond cooling. Subsequent NOE inspections identified wall thinning over a large arc of the piping's circumference; approximately 34 feet of the 18-inch diameter piping required replacement. With this condition present, the spray network was successfully operating and performing its intended function. The Spray Pond [BS] serves both units at Limerick Generating Station (LGS) and is designed to supply and cool the safety-related cooling water for the Emergency Service Water (ESW) [CC] and the Residual Heat Removal Service Water (RHRSW) [CC] systems. The Spray Pond contains four spray networks. Each network contains 240 spray nozzles with all the piping and spray nozzles above the water level supported by concrete pillars. Only one spray network is required for the safe shutdown of one unit and any two networks provide sufficient cooling to safely shut down both units. During the piping preparation for Non-Destructive Examination (NOE) additional through-wall piping pin holes were identified. Due to the number and tight physical spacing between defects, ASME Code Case N-513 could not be applied to this condition to provide an interim operability justification. Subsequently, the C RHRSW spray pond spray network was isolated and declared inoperable on 07 /13/19 and Limerick entered an emergent 30-day dual unit Tech Spec LCO. The degraded condition on the east side of the supply manifold was corrected and the LCO was exited on 07/30/19. An extent of condition plan was developed to perform NOE on the remaining three spray pond spray networks. On 08/26/19 the A Spray Network was removed from service and the LCO was entered for an extent of condition inspection. On 08/27/19 during piping preparation for NOE, pin holes were identified on the east side of the 18-inch distribution piping at the same location as the C Spray Network piping. The piping corrosion damage was identified on the 18-inch distribution piping on both the east and west sides. The piping wall thickness readings on the east side were below the minimum required thickness; however, the piping wall thickness readings on the west side were above the required minimum thickness. This condition was determined to be reportable for a condition prohibited by Technical Specifications and common cause inoperability of independent trains. The east side 18-inch distribution piping was replaced and the LCO was exited on 09/07/19. On 09/10/19 the B Spray Network was removed from service and the LCO was entered for the extent of condition inspection. No pin holes were identified; however, NOE inspection identified similar corrosion damage on the 18-inch distribution piping on both the east and west sides. The piping wall thickness readings on the east side were below the minimum required thickness; however, the piping wall thickness readings on the west side were above the required minimum thickness. The east and west side 18-inch distribution piping was replaced and the LCO was exited on 09/21/19. On 09/23/19 the D Spray Network was removed from service and the LCO was entered for the extent of condition inspection. No pin holes were identified; however, NOE inspection identified similar corrosion damage on the 18-inch ·distribution piping on both the east and west sides. The piping wall thickness readings on the east side were below the | ML19297D391
Grand Gulf Nuclear Station | Unit 1 | Primary Containment Personnel Airlock Potential Loss of Safety Function due to Inadequate Door Closure | 11-07-2019 | On September 11, 2019 at 5: 19pm, the Grand Gulf Nuclear Station primary containment was unable to fulfill its safety function because both doors on one airlock were open simultaneously for approximately thirty seconds. I The cause of this event is that the 208 primary containment airlock inner door latch pin position is not included in the electrical interlock 'or indication circuits. This caused the condition by allowing the outer airlock door open permissive to be met when the inner airlock door was not properly latched in the closed position. The 208-foot elevation airlock doors were immediately closed and verified latched and sealed. Additional corrective actions include revising the system operating procedure and the local operating placard instructions and a modification to ensure the proper closure, latching, and sealing of the 208-elevation airlock door. I This report is made pursuant to 10 CFR 50.73(a)(2)(v)(C) for an event or condition that at the time of discovery could have[ prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an· accident. There were no consequences to the general safety of the public, nuclear safety, industrial safety and radiological safety for this event. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43),. U.S. Nuclear CONTINUATION SHEET Regulatory Commission, Washington, DC 20555-0001, or by ; e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Reg'ulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid OMS control number, the http://www. nrc.qov/readinq-rm/doc-collections/nureqs/staff/sr1022/r30 NRG may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER : YEAR SEQUENTIAL REV Grand Gulf Nuclear Station Unit 1 05000-416 NUMBER I NO. I I 2019 -005 I -00 : | Plant Conditions: Grand Gulf Nuclear Station Unit 1 was operating at approximately 100 percent power in MODE1. There were no structures, systems, or components that were inoperable that contributed to the event. i Description: On September 11, 2019; at 5:19pm, a Grand Gulf Nuclear Station Radiation Protection technician exited the pri'mary containment building [NH] through the personnel airlock located on 208-foot elevation. The individual opened the containment-side (inner) airlock door and entered the airlock. Once inside the airlock the technician closed the inner door using the established work practices and door operating instructions. The technician then opened the auxiliary building side (outer) door and exited the airlock and reclosed the outer door. I As the Radiation Protection technician was exiting the outer door, Maintenanc~ Personnel approached the inner ,door in preparation to exit containment through the airlock. The Maintenance Person·nel noticed that the inner door lcicking pins were extended to their locking position but outside the locking pin keepers. They also noticed the inner door's seals were inflated. They waited for the outer door to close before operating the containment airlock doors and hiting the containment-building. Both airlock doors were left in a closed, latched, and sealed configuration upon the '1 successful exit of the Maintenance Personnel. The time period that both doors were open, which prevented the containment from fulfilling its safety function, Vl,'.as approximately 30 seconds. : I What Happened: When the Radiation Protection technician began the automatic closing cycle of the inner door by depressing th~ CLOSE push· button in the barrel, the hydraulic system did not provide adequate pressure to the rotary actuator to close the door unassisted. The technician pulled the door handle to assist the door closed, which required significant effort. The technician assisted the door to what they believed was a full closed position and held it there. The door's full-closed limit switch was satisfied, ·and the subsequent time delay began. The door was not actually in a full-closed position at the end of the time delay, but the door had not reached an open position sufficient to reset the limit switch. The same-door mechanical interlocking pawl was also lifted from the ratchet. The seal mechanism.began closing. The pins extended outside of the keeper, and the seals were inflated. The pressurized seals energized the green I permissive lights in the barrel. The door-to-door Mechanical interlocking pawl was lifted. The red "door operatin:g" light was de-energized, and all electrical interlocks were satisfied. Seeing that all permissives were met, the technician depressed the open pushbutton for the outer door. The outer door operated as designed, and the technician exited the airlock barrel and closed the outer door. j Reportability: This event was reported to the NRC via the emergency notification system (ENS) at 0049 hours on September, 12, 2019, in accordance with 10 CFR 50. 72(b )(3)(v)(C). Reference ENS notification 54271 for the details. : A Licensee Event Report is required pursuant to Title 10 Code of Federal Regulations (10 CFR) 50. 73(a)(2)(v)(C) for an event or condition that had the potential to prevent the fulfillment of the safety function to control the release of radioactive material or mitigate the consequences of an accident. NRC FORM 3668 (02-2018) Page 2 of 3 | ML19311C250
Browns Ferrv Nuclear Plant | Unit 1 | High Pressure Coolant Injection System Declared Inoperable due to Steam Supply Isolation | 11-07-2019 | On July 12, 2019, at approximately 1640 Central Daylight Time (CDT), the Unit 1 High Pressure Coolant Injection (HPCI) system unexpectedly received a Group 4 Primary Containment Isolation System (PCIS) signal which closed the HPCI inboard and outboard steam supply valves. Operations personnel declared HPCI inoperable and entered Technical Specification (TS) 3.5.1, "Emergency Core Cooling System (ECCS) - Operating," Condition C. The causes of this event were that Electrical Maintenance personnel failed to follow EPl-0-075-RLY 001, "Functional Test of Pressure Suppression Chamber Head Tank Pump Suction Valve Interlock Relays," as written by not verifying panel number or wire number and by failing to use a peer check as required; and that the workers failed to apply maintenance fundamentals and technical skills with appropriate rigor when using test equipment. Corrective actions include implementing accountability actions for the individuals involved in this event in accordance with TVA's processes, briefing personnel in Electrical Maintenance on the causes and lessons learned from this event, and performing a dynamic learning activity with electricians involved to cover volt-ohm meter usage. NRG FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION ,. ,._ 'CU l:H UMl:5: l'IU. 31:>U-UlU4 CAP"'lr<c;:,: --•-••---- (04-2017)) Estima1ed burden per response to comply with this mandalo!y ccllection request BO hours. ReportBd lessons learned are illCOl])Ofa1ed into the licensing process and fed back to industry. Send ccmments regarding burden estima1e to the Information Services Branch (T- 2 F43), U.S. Nuclear Regulatc,y Commission, Washington, DC 20555--0001,or by e-mail lo LICENSEE EVENT REPORT (LER) lnfocollects. Resouri:e@nrc.gov, and to the Desk Officer, Office of lnfoana1ion and Regulalo!y Affairs, NEOB-10202, (3150-0104), Office of Management and Budget CONTINUATION SHEET Washington, DC 20503. If a means used to ilf!)OSI! an infoona1ion collection does not display a curren11y valid 0MB ccntrol number, the NRC may not ccnduct or sponsor, and a person is not required to respond lo, the infoona1ion collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 1 05000259 NUMBER NO. 2019 - 001 01 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN) Unit 1 was in Mode 1 at approximately 100 percent power. II. Description of Event A. Event Summary On July 12, 2019, at approximately 1640 Central Daylight Time (CDT), the High Pressure Coolant Injection (HPCI) system [EIIS:BJ] unexpectedly received a Group 4 Primary Containment Isolation System (PCIS) [EIIS:JM] signal which closed the HPCI inboard and outboard steam supply valves (1-FCV-73-0002 and 1-FCV-73-0003) [EIIS:ISV]. Operations personnel declared HPCI inoperable and entered Technical Specification (TS) 3.5.1, "Emergency Core Cooling System (ECCS) - Operating," Condition C and verified that Reactor Core Isolation Cooling (RCIC) [EIIS:BN] was operable as required. In response to the isolation, Abnormal Operating Instruction 1-AOl-64-2b, "Group 4 High Pressure Coolant Injection Isolation," was entered. Investigation of this event discovered that Electrical Maintenance personnel were performing procedure EPl-0-075-RLY 001, "Functional Test of Pressure Suppression Chamber Head Tank Pump Suction Valve Interlock Relays," at the time of this event and had tested terminal points in the incorrect panel [EIIS:PL]. This resulted in completing the circuitry for the Group 4 PCIS actuation. HPCI was returned to standby readiness and declared operable on July 12, 2019 at 2110 CDT, thus exiting TS 3.5.1 Condition C. The Tennessee Valley Authority (TVA) is submitting this report in accordance with Title 1O of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(v)(D), as any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. NRG FORM 366A (04-2018) Page _2_ of _ 6_ | ML19311C475
Browns Ferrv Nuclear Plant | Unit 1 | Unanalyzed Condition Due to Inoperable Security Doors Followin :i a Liqhtninq Strike | 11-12-2019 | On September 10, 2019, at approximately 1502 Central Daylight Time (CDT) a lightning strike caused a power surge which disabled signal repeaters between the Local Intelligence Units (LI Us) of some security doors and the monitoring stations at Browns Ferry Nuclear Plant (BFN). At 1830 CDT, it was discovered that some of the oncoming night shift personnel could not access particular areas which required keycard access. An extent of condition check conducted at 1934 CDT determined that access to the 1A and 3A Electric Board Rooms, which contain remote shutdown panels and Fire Safe Shutdown (FSS) equipment, was prohibited for the night shift personnel. This condition is reportable under Title 10 of the Code of Federal Regulations (1 O CFR) 50.7 3(a)(2)(ii)(B) as an event or condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety. Specifically, this condition impacted the ability of Operators to perform their required actions in FSS procedures within prescribed time limits if a fire had occurred. The event was caused by lightning strike, which created a power surge, resulting in a security equipment communications failure. Access was restored to all plant areas at 2106 CDT. The immediate corrective action was to have Security and Operations personnel reset the malfunctioning equipment. This cleared the error and allowed the LI Us of the affected security doors to receive roster updates. As a corrective action to reduce the probability of recurrence, Site Security created a constantly-activated, all-access emergency keycard, as a contingency against future door LIU communication failures. SSl-16.1, "Compensatory Measures," is being revised to proceduralize the emergency keycard's use. NRG FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION ~- ,,-.cu t:IT vmc: NU. .,,,,u-u104 CA.-1r<c;::,: U.>l.>11.<U.<U (04-2017)) Estimared burden per response to comply with this mandatory collection request BO hours, Repor1ed lessons lea-ned a"e incorporared into the licensing process and fed back to industry. Send commenls regarding burden estimate to the Information Selvices Branch (T- 2 F43), U.S. Nuclea" Regulatory Ccmnission, Washing1Dn, DC 20555--0001,(J( by e-mai to LICENSEE EVENT REPORT (LER) lnlocollecls. Resouice@nrc.gov, and to the Desk Officer, Office of lnfonnation and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budge~ CONTINUATION SHEET Washing1Dn, DC 20503. If a means used ID illl)OSe an information collection does oot display a currently valid 0MB control number, the NRC may not conduct (J( sponS(J(, and a person is not required to respond ID, the information collection. 1_ FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 1 05000259 NUMBER NO. 2019 - 002 00 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN) Units 1, 2, and 3 were all in Mode 1 at approximately 100 percent power. II. Description of Event A. Event Summary On September 10, 2019, at approximately 1502 Central Daylight Time (CDT) a lightning strike caused a power surge which disabled some of the security [IA] door [DR] card reader system equipment at Browns Ferry Nuclear Plant (BFN). At 1830 CDT, it was discovered that some of the oncoming night shift personnel could not access particular areas which required the use of security card readers. However, this did not affect access to plant areas for personnel who were already within protected area. An extent of condition check conducted at 1934 CDT determined that the access restriction only applied to night shift personnel attempting entry into the 1A and 3A Electric Board Rooms (EBRs), which contain remote shutdown panels and Fire Safe Shutdown (FSS) equipment. The event was caused by lightning strike, which created a power surge. Access was restored to all plant areas at 2106 CDT. No plant events occurred during the timeframe which required access to the 1A and 3A EBRs. The Tennessee Valley Authority (TVA) is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50. 73(a)(2)(ii)(B) as any event or condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety. Specifically, this condition impacted the ability of Operators to perform their required actions in FSS procedures within prescribed time limits. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. NRG FORM 366A (04-2018) Page _2_ of _6_ | ML19316B896
clinton power station | Unknown Unit | Main Feed Breaker Failed to Close During Bus ~hift | 11-01-2019 | On May 22, 2019, at 0925 CDT, at approximately 98.4% power while attempting to transfer 4160V bus 1A1 to the Reserve Auxiliary Transformer (RAn (main) from the Emergency Reserve Auxiliary Transformer (ERAT) (reserve), RAT 4160V bus 1A 1 main feed breaker 1A P07EK failed to close and immediately indicated tnpped. A walkdown of feed breaker 1A P07EK showed no abnormal indications or relay flags. ·Feed breaker 1A P07EK was replaced and tested satisfactory. Initial troubleshooting identified that the latch check switch breaker closure permissive was not made up: As this pennissive makes up following breaker closure it has been determined that feed breaker 1AP07EK was inoperable since April 17, 2019. The cause of the breaker failure was determined to be establishment of a breaker preventive maintenance strategy which was beyond the capability of the Molykote BR-2 lubricant used in the breaker. Changes to DHP Breaker preventive maintenance frequencies will be implemented to ensure that lubrication periodicities support the effective life of the lubricant. In addition, DHP Breaker maintenance and refurbishment procedures will be revised to incorporate use of Molykote G-4700 grease in place of Molykote BR-2. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as, "any operation or condition which was prohibited by the plant's Technical Specifications." NRG FORM~ (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31f2020 (04-2018) / ..... Estimlllad burden poc respoose to canpfy 'Mlh tins mandatory cdleQon request 80 hru's Reported ~ lessons learned are ll1COfjlOf!lled inlo the ~C811S11Q process and fed back to m't.tslly Send commenls l~j LICENSEE EVENT REPORT (LER) regardng burden ennate to the lnfoonabon SeMces Branch (T-2 F43), US Nuclear Regulaloly ~ ......... CONTINUATION SHEET t C h o e m r D r1 e S a S k K J O 11 O . c W er a , sh O ln lh i; c c e > o o , f D lr C ro r 2 m 05 a 5 lk 5 w -0 l '.) e ( n )1 d , R or e b !µ y a ~ b'y A ff t a o i rs ln . f N or E o O le B c - t 1 s 0 2 R 0 e 2 s , o u (3 r 1 ce 6 O 0- 0 n 1 rc 0 . 4 g! ) W , O , l a li n ce d o to f Managemoot and Budget, We.sll~ DC 20503. If a means used IC Impose Bil rTlorrnatioo (See NUREG-1022, R 3 for mstrucbon and guidance for completing ttus form coleclron does not cisplay a rurentf valid Ot.13 contrd runb!lf, the NflC may nol coowct oc httpJlwww. nrc.aoy/read1na-rm/doc-collectJons/nu regs/staff/sr1022/r3/) sponsor, and a parson ls not recµred to respood to, the llllorrnatioo cdlecboo 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Clinton Power Station, Unit 1 05000461 NUMBER NO. 2019 - 001 01 | PLANT AND SYSTEM IDENTIFICATION General Electric -- Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in text as [XX]. EVENT IDENTIFICATION Main Feed Breaker Failed to Close During Bus Shift A. Plant Operating Contjitions Before the Event Unit: 1 Event Date: May 22, 2019 Event Time: 0925 Mode: 1 Mode Name: Power Operation Reactor Power: 098 B. . Description of Ever,t · On ·May 22, 2019, at 0925 C~T, at approximately 98.4% power while attempting to transfer 4160V bus 1A 1 [Bl,J] to the Reserve A\J):(iliary Transformer (RAT) (main) [XFMR] from the Emergency Reseirve Auxiliary Transformer (ERAT) (reserve) [XFMR] in accordance with procedure CPS 3501.01, ."High Voltage Auxilfary Pow~r. Systemt Section 8.1.8, RAT 4160V bus 1A 1 ·main ·feed breaker · , -. 1AP07EK[BKR] failed to close and immediately. indicated tripped. Annunciator-5060-1 B [ANN] for auto trip of breaker was received. The operator placed the synchronizing switch in OFF prior to releasing the hand switch to the AUTO position in accordance with CPS 3501.01, Section 8.1.8.5, to prevent auto trip of the load breaker and the resulting l_oss of the bus. A walkdown of feed breaker 1AP07EK showed no abnormal indications·or dropped relay flags. The 4160V bus 1 B 1 [BU] was being supplied by the RAT with the Static Var Compensator (SVC) in service and showed no abnormal indications. TJ,e 4160V bus 1 C1 [BU] was being supplied by the ERAT with the SVC in service and showed no abnormal indications. Feed breaker 1AP07EK·was last closed on April 17, 2019, during performance of procedure CPS 9080.01, "Diesel Generator 1A Operability - Manual and Quick Start Operability Surveillance." Initial troubleshooting identified that the latch check switch breaker closure permissive was not made up. As this permissive makes up following breaker closure it has been determined that feed breaker 1A P07EK had not been op~rable since its last closure on April 17, 2019. NRG FORM 366A (04-2018) Page~ of _4_ | ML19322A109
dresden nuclear power station | Unknown Unit | ,~ Degraded Drtferential Pressure Indicating Switch in the LPCI Loop Select Logic Caused by Water Damage Results in a Condition Prohibited by Technical Specifications _,, 5. EV8flt Date 6. LEA Number 7. Report Date 8. Other Facllltles Involved I Saquenbal Facdity Name Docket N<nber Month Day Veer Yaer Number Month Day Year NIA NIA 09 20 2019 2019 - 001 - 00 11 19 2019 F N a I c A fh ty Nome NIA Do cico! Numbor 9. Operating Mode 11. This Report Is Submitted Pursuant to the Requirements of 10 CFR §: (Check s/1 thst spply) D D 0 D 202201(bl 20 2203(a)(3)(1J 50 73(a){2){n)(A) 50 73(a)(2)(vm)(A) D D 0 0 202201(d) 20 2203(a){3)(11J 50 73(a}{2){11)(B) 50 73(a){2)(vl11)(B) 1 D D D 0 20 2203(a}{1) 20 2203(a}{4) 50 73(a)(2)(~1i 50.73(a)(2-)(1x)(A) 1 D D D 0 20 2200(a){2)(1J 50 36{c){1)(1){A) 50 73(a)(2)(iv)(A) 50 73(a)(2)Jx) 10. Power Level D 20 2203(a}{2)(11J 0 50 36(c)(1)(u)(A) 0 50 73(a)(2)(v)(A) D 73 71{aJ{4l D D 0 D 20 2203(a)(2)(111J 50 36{c)(2J 50 73(a)(2){v)(B) 73 71(a){5J D D 0 D 20 2203(a){2)(ivJ 50.4B{a)(3)(uJ 50 73(a)(2)(v)(C) 73 n(a){1J 100 0 20 2203(a){2){v) 0 50 73{a){2)(1)(A) D 50 73{a){2)(v)(D) D 73 n(a){2)(1J D D D 20 2203(a){2){vl) ~ 50 73{a)(2)(1)(B) 50 73(a){2)(vn) 73 77(a){2){n) ,. • • ~: ···- ,··d"}iw.t''':'fi - _ t , ~ \ ' J : ' ~ . ,-,. 1 .: 1 ;; --(-:~t,<..J. t': i' , f '\ \ : ~f-4 '!] ~ ..., 0 50 73(a)(2){1}{C) D Other (Specify in Abstract below or In NRG Form 366A) 12. Licensee Contacffor this LEA Licensee Contact relephone Number (Include Area Code) Bruce Franzen 815-416-2800 13. Complete One Line for each Component Fallure Descrlb~ In this Report Cauaa System Compon'!f'1 Manufacturer Reportable to ICES Cauae System Component Manufacturer Reportabla to ICES X AD POIS 1204 y 14. Supplemental Report Expected Month Day y.,,,, D 15. Expected Subml89lon Date Yes (If yes, complete 15. Expected Subm1ss1on Date) ~ No Abstract (Limit to 1400 spaces, 1e , approXJmately 14 single-spaced typewntten lines) On September 20, 2019, one of four channels for the 3A reactor recirculation pump high differential pressure function failed the channel functional test. Technical Specification 3.3.5.1, "ECCS Instrumentation," requires all four channels to be operable. Technical Specification 3.3.5.1, Condition C identifies a Completion Time of 24 hours to restore the failed channel to operable status. The degraded differential pressure switch was replaced. The channel was restored to operable within the 24 hour time limit. On June 20, 2019, the Unit 3 East Low Pressure Coolant Injection Room cooler was found leaking water onto the panel where recirculation pump differential pressure switches are installed. On July 30, 2019, a surveillance documented that all four channels were functional. The failed channel was determined to be inoperable between July 30 and September 20, 2019, which is longer than the 24 hours allowed by Technical Specification. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B), a condition which was prohibited by the plant's Technical Specifications. The cause of the degraded differential pressure switch was due to water dripping from the Low Pressure Coolant Injection room cooler onto the instrumentation rack. Service Water is isolated to the Unit 3 East Low Pressure Coolant Injection Room cooler until the room cooler is repaired. NRC FORM 366 (04-2018) NRC FORM36M U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03f.31fl020 (04-2018) Estimated burden per response to canply wrth tins mandaloly collection reqlJIISt 80 hours Repor1ed LICENSEE EVENT REPORT (LER) l r e e s g s a o m ns n g le a b .m l.l' e d d e n a re e e ir lr o n :: a o l r e p o t r o e te t d h e m l t n o l o !t o ie n a ll b c o en o s r S 1 e g M p C ro e c S e s B s r a a n n c d h l e ( d T - b 2 a c F k 4 3 to ), 1 U nc S iJs tr N y uc S le 11 a 1 r d R cc e m gt n ia e to n r t y s CONTINUATION SHEET CorrrrusslOll, WWlfl!jlon, DC 20555-0Xl1, or by ~ to inloccjects Resource ft nrc !JOY, Md to the Desk a!icer, OOce of Inform~ and Reg.J!aby Alla.lrs, NEOB-10202, (3150--0104), Office ci Managament and Budge~ Wash1ngtoo, OC 20503 If a means used lo rnpose an mlormafo1 ca!ectroo (See NUREG-1022, R.3 lor instruction and guidance for completmg this !Olm does nct CJ51JBY a cu:rootf;, valid 0MB contra number, the NRG may not conduct or httpJ/www.nrc goy/readmg-nn/doc-collecttons/nureos/stafVsr1022/r3/l sponso,-, and a person is not reqU1red to respond lo, the lnlormabon collecllon _ 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER ~ YEAR SEQUENTIAL REV Dresden Nuclear Power Station, Unit 3 05000249 NUMBER NO. 2019 - 001 - 00 NARRATIVE PLANT AND SYSTEM IDENTIFICATION Dresden Nuclear Power"Station (DNPS), Unit 3, is a General Electric Company Boiling Water Reactor with a licensed maximum power level of 2957 megawatts thermal. The Energy Industry Identification System codes used in the text are id.~ntified ·as [XX]. A. Plant Conditions Prior to Event: | 11-19-2019 | On September 20, 2019, one of four channels for the 3A reactor recirculation pump high differential pressure function failed the channel functional test. Technical Specification 3.3.5.1, "ECCS Instrumentation," requires all four channels to be operable. Technical Specification 3.3.5.1, Condition C identifies a Completion Time of 24 hours to restore the failed channel to operable status. The degraded differential pressure switch was replaced. The channel was restored to operable within the 24 hour time limit. On June 20, 2019, the Unit 3 East Low Pressure Coolant Injection Room cooler was found leaking water onto the panel where recirculation pump differential pressure switches are installed. On July 30, 2019, a surveillance documented that all four channels were functional. The failed channel was determined to be inoperable between July 30 and September 20, 2019, which is longer than the 24 hours allowed by Technical Specification. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B), a condition which was prohibited by the plant's Technical Specifications. The cause of the degraded differential pressure switch was due to water dripping from the Low Pressure Coolant Injection room cooler onto the instrumentation rack. Service Water is isolated to the Unit 3 East Low Pressure Coolant Injection Room cooler until the room cooler is repaired. NRC FORM 366 (04-2018) NRC FORM36M U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03f.31fl020 (04-2018) Estimated burden per response to canply wrth tins mandaloly collection reqlJIISt 80 hours Repor1ed LICENSEE EVENT REPORT (LER) l r e e s g s a o m ns n g le a b .m l.l' e d d e n a re e e ir lr o n :: a o l r e p o t r o e te t d h e m l t n o l o !t o ie n a ll b c o en o s r S 1 e g M p C ro e c S e s B s r a a n n c d h l e ( d T - b 2 a c F k 4 3 to ), 1 U nc S iJs tr N y uc S le 11 a 1 r d R cc e m gt n ia e to n r t y s CONTINUATION SHEET CorrrrusslOll, WWlfl!jlon, DC 20555-0Xl1, or by ~ to inloccjects Resource ft nrc !JOY, Md to the Desk a!icer, OOce of Inform~ and Reg.J!aby Alla.lrs, NEOB-10202, (3150--0104), Office ci Managament and Budge~ Wash1ngtoo, OC 20503 If a means used lo rnpose an mlormafo1 ca!ectroo (See NUREG-1022, R.3 lor instruction and guidance for completmg this !Olm does nct CJ51JBY a cu:rootf;, valid 0MB contra number, the NRG may not conduct or httpJ/www.nrc goy/readmg-nn/doc-collecttons/nureos/stafVsr1022/r3/l sponso,-, and a person is not reqU1red to respond lo, the lnlormabon collecllon _ 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER ~ YEAR SEQUENTIAL REV Dresden Nuclear Power Station, Unit 3 05000249 NUMBER NO. 2019 - 001 - 00 | PLANT AND SYSTEM IDENTIFICATION Dresden Nuclear Power"Station (DNPS), Unit 3, is a General Electric Company Boiling Water Reactor with a licensed maximum power level of 2957 megawatts thermal. The Energy Industry Identification System codes used in the text are id.~ntified ·as [XX]. A. Plant Conditions Prior to Event: Unit: 03 . Event Date: 09/20/19 Event Time: 1215 CDT Reactor Mode: 1 Mode Name: Power Operation Power Level: 100 percent B. Description of Event: On September 20, 2019, at 1215 Central Time, one of four channels [CHA] for the 3A recirculation [ADJ pump [P] high differential pressure function failed the channel functional test during the performance of Dresden Surveillance procedure DIS 1500-09, "LPCI Reactor Recirculating Pump A and B_ Differential Pressure Indicating Switch Channel Calibration and Channel Functional Test:" Technical Specijication {TS) 3.3.5.1, "ECCS Instrumentation," Table 3.3.3.5.1-1, "Emergency Core Cooling System Instrumentation," identifies four channels per recirculation pump are required for the Low Pressure Coolant Injection System (LPCI) [BO] recirculation pump high differential pressure function during Modes 1, 2, and 3. The recirculation pump high differential pressure function supports the LPCI Loop Select Logic to identify and direct LPCI flow to the unbr9ken recirculation loop if a Design Basis Accident (OBA) occurs. TS t.imhing Condition for Operation (LCO) 3.3.5.1, "The ECCS instrumentation for each Fun_ction in Table 3.3.5.1-1 shall be OPERABLE," was not met. TS 3.3.5.1, Condition C was entered for the failed ' channel of the recirculation pump high differential pressure function. A TS Completion Time of 24 nours is specified for TS 3.3.5.1, Required Action C, which requires the channel to be restored to an operable status. During the investigation of the event on September 20, 2019, c\. differential pressure indicating switch (DPIS) [POIS] was found degraded. On September 21, 2019; at approximately 1000 Central Time; the DPIS was replaced and TS LCO 3.3.5.1 was declared met. The channel to the recirculation pump high differential pressure function was restored to operable within the 24-hour TS Completion Time and the LPCI Loop Select Logic was restored. Prior to the event, on June 20, 2019, the Unit 3 East LPCI Room cooler [CLR] identified as leaking wate1 onto the electrical panel where recirculation pump differential pr!;3ssure switches are installed. A deflector was installed to prevent water from dripping onto the electrical panel. After this leak was discovered, an electrical ground was identified on the Unit 3 125 VDC battery system [EJ]. The DPIS that was found degraded during the September 20, 2019, ·event was not qualified for spray or submergence. NRG FORM 386A (04-2018) Page .J_ of _4_ U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES. 03/31/2020 E5'mated IHxden per response to cooiply 'Mlh 11116 manda!OI)' collecbon request 80 hours Reponed , LIC-ENSEE EVENT REPORT (LEA) r l e es g s a o rd n m s g le a b r u n r e o d o n a re e s m a c n o a r t p e o r t a o te t d h e i nt ln o l o th o e n e h b c o en /1 s1 1 S 1 e g r p .i r c o e c s e s B s ra a n n c d h f e ( d T - b 2 a c F k 4 3 to ), in U d . u s s tr N y o S o e ll n llf d R c e c g m u n la e tO nt ! s )' , CONTINUATION SHEET COITllllSS1on, Washington, DC 20555-0001, or by IHTIBII to lnfocollects Rescuce ft nrc.gov, and to the Desk' Ofhcer, Offtce ol lnfonnabon Blld RegL1Bby Al!a!rs, NEOB-1 0202, (3150-0104 ), Office a Managemoot ll!1d Budget. Washmgton, OC 20503 tt a means used to rnpose !I1 rnformallon coftactlon (See NUREG-1022, R.3 for instruction and guidance for complebng thlS loon does rd cisplay B CtKT8f1t!o/ v*1 0MB crntro number, the NR C may not cordJct or httD:/twww.nrc aov/roodtna-rm/c!oc-collecboQ&'nureos/staff/sr1022/Q/l spoosor, and a persoo is rd requred to l'86pOlld to, the mformatlon coiecion 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER YEAR SEQUENTIAL REV Dresden Nuclear Power Station, Unit 3 - 05000249 NUMBER NO. 2Q1~ - 001 00 NARRATIVE Prior to the event, the channel functional test surveillance on July 30, 2019, determined that the LPCI .. recirculation pump high differential pressure was functional with all required channels operable. ' ' . On September 20, 2019, at 2145, the degraded DPIS was removed from service. WJ:len the wires were removed from the DPIS, the 125 VDC battery electrical ground issue was resolved. It is concluded that the degraded DPIS was not operable after July 30, 2019. I Since the-DPIS was not operable after the July 30, 2019, surv.eillance, orie channel of the recirculation purr]p high differential pressure function was not operable be~een July 30 and September 20,-2019, (i.e., approximately 52 days). This duration is longer than the TS 3.3.5.1, Condition C, Completion Time of 24 hours._ Therefore, this event i.s being reported_ in accordance with to 1O CFR 50.73(a)(2)(i)(B), any condition which was prohibited by the plant's Technical Specifications. C. Cause of Event: The cause of the degraded DPIS was due to water dripping from the Unit 3 East LPCI Room cooler onto the instrumentation rack where the DPIS was installed. D. Safety Analysis: Recirculation Pump Differential Pressure signals are used by the LPCI Loop Select Logic to determine if either recirculat_ion pump is running. Recirculation Pump Differential Pre$si.Jre - High (i,e., Break Detection) signals are initiated from eight differential pressure switches, four of which sense the pressure differential between the suction and discharge of each reactor recirculation pump. The LPCI System initiation logic contains LPCI Loop Select Logic to identify and direct LPCI flow to the unbroken recirculation loop if a OBA occurs. The LPCI Loop Select Logic is initiated upon the receipt of an Emergency Core Cooling System [~E] initiation signal. When initiated, the LPCI Loop Select Logic first determines recirculation pump operation by ', sensing the differential pressure between the suction and discharge of each pump. NRG FORM 366A (04-2018) Page_3_ of _4_ | ML19325C091
Quad Cities Nuclear Power Station | Unit 1 | Loss of Safety Bus and Automatic Actuation of a Safety System During Undervoltage Relay Surveillance | 11-21-2019 | On 10/24/18 at 0901 CDT, during performance of the "Functional Test of Unit 1 Second Level Undervoltage," a loss of Bus 13-1 and Bus 18 occurred. The 1/ 2 Emergency Diesel Generator (EOG) automatically started due to a valid actuation on loss of power to Bus 13-1, but did not load due to surveillance test alignments. The loss of Bus 13-1 caused the loss Bus 18, resulting in a loss of logic power to both loops of Low Pressure Coolant Injection (LPCI). Additional equipment was also lost. This notification is being made in accordance with 10 CFR 50.73(a}(2)(iv)(A), "Any event or condition that results in manual or automatic actuation of any of the systems listed in paragraph (a}(2)(iv)(B)," because the 1/2 EOG auto started due to the loss of power condition. This notification is also being made in accordance with 10 CFR 50.73(a}(2)(v}(B), "Any event or condition that could have prevented fulfillment of the safetY function of structures or systems that are needed to remove residual heat," because both loops of LPCI were inoperable for a short time period. The most probable cause is concurrent direct current (DC) grounds resulting in actuation of relay logic to trip Bus 13-1 and start the 1/2 EOG. Additional 01 R25 refuel outage troubleshooting was completed and did not reveal any additional causes. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported ~.::,t;,'-Q-l\PEtt&('f,..O lessons learned are incorporated into the licensing process and fed back to industry. Send comments a§ LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory ,. CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to \; the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of ,., *** •• Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR Quad Cities Nuclear Power Station Unit 1 05000254 NUMBER NO. 2018 - 005 01 | PLANT AND SYSTEM IDENTIFICATION General Electric -Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Class 1 E 4.16 KV Bus 13-1 [EB] Undervoltage Protection [JE] Low Pressure Coolant Injection System [BO] Core Spray System [BM] Emergency Diesel Generator [EK] Energy Industry Identification System (EllS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Loss of Safety Bus and Automatic Actuation of a Safety System During Undervoltage Relay Surveillance A. CONDITION PRIOR TO EVENT Unit: 1 Event Date: October 24, 2018 Event Time: 0901 hours CDT Reactor Mode: 1 Mode Name: Power Operation Power Level: 100% There were no structure, systems, or components out of service or inoperable that contributed to the event. B. DESCRIPTION OF EVENT On October 24, 2018, at 0901 hours CDT, during performance of a second level undervoltage surveillance, Class-1 E 4.16 KV Bus 13-1 [EB] tripped on an Undervoltage Protection [JE] inadvertent signal. The loss of the safety bus caused the 1/2 Emergency Diesel Generator (EDG)[EK] to start automatically, although it did not load to the bus due to surveillance testing alignments. The loss of Bus 13-1 also causes a loss Bus 18, which causes a loss of logic leading to a loss of both loops of RHR Low Pressure Coolant Injection (LPCI) function. The loss of Bus 13-1 also caused a loss of the 1A Core Spray (CS)[BM] pump and the 1A and 1 B Residual Heat Removal Pumps (RHR)[BO]. The 1/2 Diesel Generator Cooling Water Pump did not start due to the loss of Bus 18. The following inadvertent actuations also occurred: Reactor Building Ventilation [VA] system tripped and Standby Gas Treatment System [BH] auto started; 1A Reactor Protection System [JD] power swapped; a full Group Ill Reactor Water Clean Up [CE] isolation occurred. All other plant equipment responded as expected to this bus transient. Full power operation was maintained. The affected busses were restored at 0911 hours CTD on October 24, 2018. Additional equipment recovery continued into the following day. During the ten minutes where LPCI was unavailable, Unit 1 was in the following Technical Specification (TS) LCOs: 3.5.1 Condition A for the A and B RHR Pumps | ML19325C263
Fermi 2 05000 341 1 OF 4 | Unknown Unit | Secondary Containment Pressure Exceeded Technical Specification Due to Reactor Building HVAC Damper Malfunction | 11-22-2019 | On September 29, 2019, at 2228 EDT, a planned train swap of the Reactor Building Heating Ventilation and Air Conditioning (RBHVAC) system resulted in the Technical Specification (TS) for secondary containment (SC) pressure boundary not being met for approximately 2 minutes and 15 seconds. The maximum secondary containment pressure recorded during that time was approximately 0.1 inches of water gauge (positive). Secondary containment pressure was restored to within TS limits by restarting the West RBHVAC train. There were no safety consequences or radiological releases associated with this event. The cause of this momentary loss of SC was determined to be the effect of the RBHVAC West exhaust fan discharge damper failing to close due to sticking of a time delay relay. For corrective actions, Fermi 2 will replace the relay and has temporarily modified the RBHVAC swap sequence until the relay has been replaced. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/312020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments z g regarding burden estimate to the Information Services Branch (T-2 F43), U. S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of (See NUREG-1 022, R.3 for instruction and guidance for completing this form Management andB udgeWta, shington, DC 20503. If a meansu sedto impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or http://www.nrc.gov/reading-rm/doc-collections/nureqs/staff/srl 022/r3/) sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000- NUMBER NO. Fermi-005 | INITIAL PLANT CONDITIONS Mode -1 Reactor Power - 100% There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT On September 29, 2019, while in Mode 1 at 100 percent power, a planned train swap of the Reactor Building Heating Ventilation and Air Conditioning (RBHVAC) [[VA]] trains was initiated to shut down the West train and place the East train in service. Following shutdown of the West RBHVAC train, the West exhaust fan [[FAN]] discharge damper [[DMP]] failed to close, resulting in an increase in secondary containment (SC) [[NH]] pressure. At 2228 EDT, the Technical Specification (TS) for SC pressure boundary was exceeded. The West RBHVAC train was restarted and restored SC vacuum to within the TS operability limit of greater than or equal to 0.125 inches of vacuum water gauge per TS Surveillance Requirement (SR) 3.6.4.1.1. It was noted that upon restart of the West RBHVAC train, the West exhaust fan discharge damper closed and then reopened normally during the train startup. The duration of the TS not being met was approximately 2 minutes and 15 seconds and the maximum SC pressure observed during the event was approximately 0.1 inches of water gauge (positive). SC was declared OPERABLE at 2235 EDT. An 8-hour event notification (EN 54299) was made to the NRC based on meeting the reporting criteria of Title 10 Code of Federal Regulations (10 CFR) 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. This Licensee Event Report (LER) is being made under the corresponding requirement in 10 CFR 50.73(a)(2)(v)(C). SIGNIFICANT SAFETY CONSEQUENCES AND IMPLICATIONS There were no safety consequences or radiological releases associated with this event. At no time during this event was there a potential for endangering the public health and safety. The specified safety function of the SC is to contain, dilute, and hold up fission products that may leak from primary containment following a Design Basis Accident (DBA). In conjunction with operation of the Standby Gas Treatment System (SGTS) [[BH]] and closure of certain valves [[V]] whose lines penetrate the SC, the SC is designed to reduce the activity level of the fission products prior to release to the environment and to isolate and contain fission products that are released during certain operations that take place inside primary containment, when primary containment is not required to be OPERABLE, or that take place outside primary containment. It is possible for the pressure in the control volume to rise relative to the environmental pressure (e.g., due to pump [[P]] and motor [[MO]] heat load additions). To prevent ground level exfiltration while allowing the SC to be designed as a conventional structure, the SC requires support systems to maintain the control volume pressure at less than the external pressure. For the SC to be considered OPERABLE, it must have adequate leak tightness to ensure that the required vacuum can be established and maintained. | ML19329C825
Columbia Generating Station 05000 397 1 OF 3 | Unknown Unit | LOSS OF DIESEL STARTING AIR DURING MAINTENANCE LEADS TO LOSS OF HIGH PRESSURE CORE SPRAY SYSTEM | 11-25-2019 | On September 24, 2019, at 2338 PDT during maintenance to drain an air receiver in the High Pressure Core Spray (HPCS) Diesel Starting Air (DSA) system a pressure control valve (PCV) vented, due to a leaking isolation valve, causing the in-service air receiver pressure to drop below the minimum Technical Specifications value. Operations declared the HPCS Diesel Generator, HPCS Service Water, and the HPCS system inoperable. The root cause of the event was that the plant procedure was revised in 2009 to open the air start motor cross connect valve to retain all 4 air start motors available for diesel start which is not in accordance with current licensing/design bases. Corrective actions include revision to station procedures and repair of the leaking isolation valve. This is reportable under 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. This event was reported under 10 CFR 50.72(b)(3)(v)(D) as Event Notification #54292. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported ,.j>flA£o<,l • ./ ~\ . LICENSEE EVENT REPORT (LER) r le e s g s a o rd n i s n g le a b r u n r e d d e n a r e e s i t n im co a r t p e o t r o a te th d e i n In to fo t r h m e a li t c io e n n s S in e g rv p ic r e o s c e B s r s a a n n c d h f ( e T d - 2 b a F c 4 k 3 ) to , U in . d S us . t N ry u . c S le e a n r d R c e o g m u m la e to n r ts y ~ ...... ~ • CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to '0/...,_,, +o' the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB control number, the NRC may not conduct or http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000- I □ NUMBER NO. Columbia Generating Station 397 D 2019 - I 001 - 00 I I I I | Plant Conditions Before the event, the plant was operating in Mode 1 at 100% power. All Emergency Core Cooling Systems (ECCS) were operable. Event Description On September 24, 2019, during maintenance, one of the High Pressure Core Spray (HPCS)[BG] Diesel Starting Air (DSA) [LC] air receivers [RCV] vented from the in-service air header through a DSA Pressure Control Valve (PCV) [PCV] causing the in-service air receiver's pressure to lower. As part of the maintenance evolution, the DSA air receiver to be drained was isolated from the starting air header and the air start motor cross connect valve [V] was opened per procedure. The isolation valve [V] leaked by creating a lower pressure upstream of the PCV then downstream of the PCV which caused the PCV to relieve the pressure, dropping the in-service air receiver pressure below the Technical Specification operability limit for the HPCS DSA system. At 2338 PDT operators noted that pressure degraded below the operability limit for the HPCS DSA system. This resulted in the HPCS Diesel Generator (DG)[EK], HPCS Service Water (SW)[BI] and HPCS system being declared inoperable, per plant Technical Specifications. The leak was isolated and the in-service air receiver pressure was restored at 0104 PDT on September 25, 2019. All Technical Specifications entered due to the degraded air receiver pressure were exited. Total inoperable time was one hour and twenty-six minutes. This inoperability of HPCS is reportable under 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. An ENS report was made to the NRC at 0526 hours PDT (EN# 54292) on September 25, 2019 pursuant to 10 CFR 50.72(b)(3)(v)(D). Immediate Corrective Actions The air start motor cross connect valve was closed and in-service air header pressure was restored resulting in the HPCS DG, HPCS SW, and HPCS system being declared operable. Assessment of Safety Consequences Safety was maintained as the Automatic Depressurization System (ADS), Low Pressure Core Spray (LPCS) [BM], and Low Pressure Coolant Injection (LPCI)[BO] mode of Residual Heat Removal (RHR) [BO] system remained operable at the time of the event to mitigate the consequences of an accident. In addition, the Reactor Core Isolation Cooling (RCIC)[BN] system was operable and the HPCS system was maintained available during the period of HPCS inoperability using Dedicated Operators. Cause of Event The root cause of the event was that the plant procedure was revised in 2009 to open the air start motor cross connect valve to retain all 4 air start motors available for diesel start which is not in accordance with current licensing/design bases. The direct cause of the event was leak by of the isolation valve. A contributing cause was that a Condition Report to assess the controlling procedure for the maintenance was not fully evaluated. | ML19329E569
Browns Ferry Nuclear Plant | Unit 2 | Automatic Reactor Scram during Startup due to Intermediate Range Monitor Noise. | 12-02-2019 | On October 1, 2019, at approximately 0307 Central Daylight Time (CDT), Browns Ferry Nuclear Plant (BFN) Unit 2 received a reactor scram signal from less than 1% power that originated from the Neutron Monitoring System. There were no complications associated with this scram. All required safety systems functioned as designed. The initiating condition was discovered to be a scram signal due to electrical noise induced when the pushbutton was depressed for driving Source Range Monitors (SRMs) C and D out concurrently. On October 1, 2019, at approximately 0605 CDT, Operations personnel completed Event Notification 54302 to the NRC. The root cause of this event was that BFN engineering and leadership demonstrated weaknesses in risk perception related to the failure to advocate for and implement a permanent solution to the long standing Intermediate Range Monitor (IRM) noise susceptibility issue. Specifically, the IRM system design is not robust enough to mitigate the effects of noise intrusion. Corrective actions which will reduce or mitigate the probability of recurrence are to implement a process to manage the risk of identified equipment vulnerabilities; to implement time constant modifications to BFN Units 1, 2, and 3 which will make the system more robust against noise spiking; and to revise the Bridging and Mitigation Strategy Development procedure to explicitly require review of OE during bridging or mitigation strategy development. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T- 2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001,or by e-mail to LICENSEE EVENT REPORT (LER) Infocollects. Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, CONTINUATION SHEET Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 2 05000260 NUMBER NO. 2019 - 003 - 00 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Unit 2, was in Mode 2 at approximately 0 percent power. II. Description of Event A. Event Summary On October 1, 2019, at approximately 0307 Central Daylight Time (CDT), BFN Unit 2 received a reactor scram signal from less than 1% power that originated from the Neutron Monitoring System (NMS) [EIIS IG]. There were no complications associated with this scram. At approximately 0315 CDT, Operations personnel ceased reactor start-up, and placed the reactor in MODE 4 at approximately 0606 CDT. BFN Unit 2 began complex troubleshooting, with Maintenance personnel performing cable [EIIS CBL] characterization (CHAR) testing of Intermediate Range Monitor (IRM) [EIIS RR] cables as well as Source Range Monitor (SRM) drive [EIIS DRIV] motor [EIIS MO] testing. The initiating condition was discovered to be an invalid scram signal due to electrical noise induced when the pushbutton was depressed for driving SRMs C and D out concurrently. On October 1, 2019, at approximately 0605 CDT, Operations personnel completed Event Notification (EN) 54302 to the NRC. The Tennessee Valley Authority is submitting this report in accordance with Title 10 of the Code of Federal Regulations 50.73(a)(2)(iv)(A), as an event that resulted in an automatic actuation of the Reactor Protection System (RPS). B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. C. Dates and approximate times of occurrences Dates & Approximate Times Occurrence September 30, 2019, at 2356 CDT Unit 2 entered MODE 2. October 1, 2019, at 0255 CDT Unit 2 critical. October 1, 2019, at 0307 CDT Unit 2 received an automatic reactor scram. October 1, 2019, at 0605 CDT Completed EN# 54302 to the NRC. October 1, 2019, at 0606 CDT Unit 2 entered MODE 4. | ML19336B743
Susquehanna Steam Electric Station | Unit 1 | D Diesel Generator Inoperable due to Inadequate Post-Maintenance Test | 03-31-2020 | On October 13, 2019, at 10:08, during performance of surveillance testing, the D Diesel Generator (DG) failed to reach the required frequency within the time specified by the acceptance criteria. Operators declared Surveillance Requirement 3.8.1.7 failed and entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1, Condition B, on both Susquehanna Steam Electric Station units for the inoperable D DG. The other three DGs (A, B, and C) were verified to be OPERABLE before operators commenced a subsequent test of the D DG at 12:12, during which the D DG met all required acceptance criteria. The D DG was declared OPERABLE at 17:56 and LCO 3.8.1, Condition B, was exited for both units. The failure to reach the required frequency within the acceptance criteria was the result of inadequate oil pressure in the D DG mechanical governor internals which was caused by an inadequate Post Maintenance Test (PMT). The condition of the inoperable D DG was determined to have existed since September 17, 2019, and the event was determined to be reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. Due to a concurrent inoperability of the C DG, the event was also determined to be reportable in accordance with 10 CFR 50.73(a)(2)(v) as an event or condition which could have prevented the fulfillment of a safety function. Corrective actions include procedure updates to ensure adequate PMTs are performed in the future. There were no actual safety consequences associated with this event. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U. S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB control number, the NRC may not conduct or http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station Unit 1 05000-387 NUMBER NO. 2019 003 00 | CONDITIONS PRIOR TO EVENT Unit 1 – Mode 1, approximately 100 percent Rated Thermal Power Unit 2 – Mode 1, approximately 100 percent Rated Thermal Power There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. EVENT DESCRIPTION On October 13, 2019, at 10:08, operators started the D Diesel Generator (DG) [EIIS Code/Component Code: EK/DG] in accordance with the applicable surveillance procedure. The D DG reached the required frequency at a time of 10.75 seconds, which exceeds the acceptance criteria of 10 seconds. Operators declared Surveillance Requirement (SR) 3.8.1.7 failed and entered Technical Specification (TS) Limiting Condition of Operation (LCO) 3.8.1, Condition B, on both Susquehanna Steam Electric Station (SSES) units for the inoperable D DG. The other three DGs (A, B, and C) were verified to be OPERABLE before operators commenced a subsequent test of the D DG at 12:12, during which the D DG met all required acceptance criteria. The D DG was declared operable at 17:56 and LCO 3.8.1, Condition B, was exited for both units. Upon engine start, the engine cranked until the mechanical governor [EIIS Code/Component Code: EK/65] lever arm was able to travel to the maximum fuel position. The mechanical governor is not designed to hold pressure during standby; since the engine is not operating, there is no pressure being generated in the mechanical governor. During the next engine start, the governor will need to build up internal pressure prior to being able to move the output lever arm back to the maximum fuel position. On September 17, 2019, work was performed on the D DG which required draining the starting air receivers. Upon completion of the work, a Post-Maintenance Test (PMT) was performed to verify leak-tightness and proper operation of the Emergency Service Water System supply valve [EIIS Code/Component Code: BI/V] to the intercoolers. However, no PMT DG run was performed. Absent a PMT DG run, the DG mechanical governor was not primed with governor oil. This condition rendered the D DG inoperable due to its impact on the ability to reach the required frequency within 10 seconds. SSES TS LCO 3.8.1 requires, in part, that four DGs are OPERABLE in MODES 1, 2, and 3. Condition B requires that an inoperable DG be restored to OPERABLE status within 72 hours or that each unit be shut down to MODE 3 in 12 hours and MODE 4 in 36 hours. The D DG was inoperable from September 17, 2019, until it was declared OPERABLE at 17:56 on October 13, 2019. Both SSES units remained in MODE 1 during the 26-day period which exceeds the 72 hours allowed by Condition B. As a result, this condition was determined to be reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. The C DG was also inoperable from 07:54 on October 2, 2019, through 23:40 on October 3, due to a fuel oil leak and again from 20:14 on October 7 through 01:16 on October 8 during DG swap following repairs to the | ML19345F627
Susquehanna Steam Electric Station | Unit 1 | Loss of Both Control Structure Chillers due to Misaligned Breaker Stab | 03-31-2020 | On May 22, 2019, at 0240, the A Control Structure (CS) Chiller tripped due to a loss of power to Motor Control Center (MCC) 0B136. At the time of the trip, the B CS Chiller was out of service for planned maintenance on the Emergency Service Water (ESW) System. The CS Chillers are required to be operable by Technical Specifications (TS) Limiting Conditions for Operation (LCOs) 3.7.3, “Control Room Emergency Outside Air Supply (CREOAS) System” and 3.7.4, “Control Room Floor Cooling System.” The CREOAS and Control Room Floor Cooling systems provide cooling and ventilation to various safety- related loads including the control room, computer room, relay rooms, and emergency switchgear rooms. The loss of both chillers required entry in LCOs 3.7.3, 3.7.4, and 3.0.3, thereby requiring the commencement of a dual unit shutdown. As a result, this event was reported in accordance with 10 CFR 50.72(b)(3)(v) as a condition which could have prevented the fulfillment of a safety function and 10 CFR 50.72(b)(2)(i) for the initiation of a plant shutdown required by TS. The power reduction was halted upon restoration of the A CS Chiller. The condition was also determined to be reportable in accordance with 10 CFR 50.73(a)(2)(v) as a condition that could have prevented the fulfillment of a safety function. The direct cause was determined to be inadequate engagement of cubicle stabs. The root cause was determined to be vendor design differences in cubicle stab assemblies introduced during replacement of original plant equipment. Corrective actions include removing the misaligned breaker stab from service and de-energizing, cleaning, and inspecting MCC 0B136. There were no actual safety consequences associated with the condition. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U. S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB control number, the NRC may not conduct or http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station Unit 1 05000-387 NUMBER NO. 2019 001 01 | CONDITIONS PRIOR TO EVENT Unit 1 – Mode 1, approximately 100 percent Rated Thermal Power Unit 2 – Mode 1, approximately 100 percent Rated Thermal Power At the time of the event, Division II of the ESW System was out of service for planned maintenance. This rendered the B CS Chiller inoperable. EVENT DESCRIPTION On May 19, 2019, at approximately 2230, Division II of the ESW system was removed from service for planned maintenance. This rendered the B CS Chiller inoperable. Subsequently, on May 22, 2019, at 0240, the A CS Chiller [EIIS Code: VI] tripped due to a loss of power to MCC 0B136 [EIIS Code/Component Code: ED/MCC]. Susquehanna Steam Electric Station TS LCO 3.7.3, “Control Room Emergency Outside Air Supply (CREOAS) System,” and LCO 3.7.4, “Control Room Floor Cooling System,” require entry into LCO 3.0.3 upon loss of both CS Chillers. At 0256, operators declared the CREOAS and Control Room Floor Cooling Systems inoperable and entered LCO 3.0.3. Unit shutdown commenced at 0340 and 0350 for Units 2 and 1, respectively. The MCC 0B136-044 A-phase cubicle stab [Component Code: 52] was not engaged correctly on the vertical bus resulting in arcing conditions that created the conditions for a fault on the MCC bus. The bus was tested with satisfactory results and was reenergized. Power was restored to MCC 0B136 at 0901 on May 22, LCO 3.0.3 was exited, and the power reductions were halted. The CS Chillers are required to be operable to support operation of the CREOAS and Control Room Floor Cooling systems. The CREOAS and Control Room Floor Cooling systems provide cooling and ventilation to various safety-related loads including the control room, computer room, relay rooms, and emergency switchgear rooms. As a result, the condition was determined to be reportable in accordance with 10 CFR 50.73(a)(2)(v) as a condition that could have prevented the fulfillment of a safety function of systems that are required to; (A) shut down the reactor and maintain it in a safe shutdown condition; (B) remove residual heat; (C) control the release of radioactive material; or (D) mitigate the consequences of an accident. CAUSE OF EVENT The direct cause of the event was determined to be that the 0B136-044 A-phase primary disconnect cubicle stab was not engaged on both sides of the bus bar. The root cause of the event was determined to be vendor design differences between the previous Cutler Hammer and replacement Nuclear Logistics Industries (NLI) assemblies affected the self-aligning capability which ensure cubicle stab engagement on the bus bar. On October 4, 2019, in accordance with 10 CFR 21, AZZ Nuclear notified the NRC of a | ML19345F675
Susquehanna Steam Electric Station | Unit 1 | lnoperability of "C" Emergency Service Water Pump | 01-08-2019 | On August 28, 2019 at approximately 17:40, during lnservice Testing (1ST) of the "A" loop of Emergency Service Water (ESW), the differential pressure for the "C" ESW pump (OP504C) was found to be 88.875 psid, which was below the established 1ST acceptance criteria. Based on the test results, the "C" ESW pump was in the 1ST Required Action Range, which requires the pump to be declared inoperable. At the time of discovery of this condition, Susquehanna was already in Technical Specification (TS) 3.7.2 Condition C for "A" loop maintenance. On August 29, 2019, the pump lift setting was adjusted and the "C" ESW pump was retested. The retest resulted in an acceptable differential pressure of 91.9 psid, which was in the Alert Range and no longer in the Required Action Range. TS 3.7.2 Condition C was exited on August 29, 2019 at approximately 15:45. On October 04, 2019, Susquehanna completed replacement of the "C" ESW pump. The direct cause was determined to be separation of the lower pump casing flange (bottom column to top case) resulting in a loss of differential pressure. The apparent cause was determined to be corrosion of the carbon steel bolting in raw water. This was accelerated by galvanic interactions with silt, Copper never-seize, and alloy steel. Completed corrective actions include replacement of the "C" ESW pump. Planned corrective actions include a review of the appropriate preventive maintenance (PM) frequency for pump replacement. Based on available information, the condition is considered to have existed for longer than allowed by TS 3.7.2. The condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications and 10 CFR 50.73(a)(2)(v) as an event or condition that could have prevented fulfillment of a safety function. There were no actual safety consequences associated with the condition. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send LICENSEE EVENT REPORT (LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, CONTINUATION SHEET ~ ~ the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of (See NUREG-1022, R.3 for instruction and guidance for completing this form Management and Budget, Washington, DC 20503. If a means used to impose an information http :1/INWW. nrc.gov/readi ng-rm/doc-collections/n uregs/staff/sr1 022/r3D collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. L.ER NUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station Unit 1 05000-387 NUMBER NO. 2019 002 01 1 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, approximately 100 percent Rated Thermal Power Unit 2 - Mode 1, approximately 100 percent Rated Thermal Power There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. EVENT DESCRIPTION On August 28, 2019 at approximately 17:40, during lnservice Testing (1ST) of the "A" loop of Emergency Service Water (ESW) [EllS System Code: Bl], the differential pressure for the "C" ESW pump (OP504C) [EllS Component Code: P] was found to be 88.875 psid, which was below the established 1ST acceptance criteria. Based on the test results, the "C" ESW pump was in the 1ST Required Action Range, which requires the pump to be declared inoperable. At the time of discovery of this condition, Susquehanna was already in Technical Specification (TS) 3.7.2 Condition C for both units in support of maintenance activities on the "A" loop of ESW. On August 29, 2019, the pump lift setting was adjusted and the "C" ESW pump was retested. The retest resulted in an acceptable differential pressure of 91.9 psid, which was in the Alert Range and no longer in the Required Action Range. TS 3.7.2 Condition C was exited on August 29, 2019 at approximately 15:45. On October 04, 2019, Susquehanna completed replacement of the "C" ESW pump. The removed pump had notable degradation, including flange separation and bolting corrosion. The pump had been installed for slightly more than 10 years prior to replacement. Other pumps exposed to the same raw water environment include the "A", "B", and "D" ESW pumps and the "1A", "1 B", "2A", and "2B" Residual Heat Removal Service Water (RHRSW) pumps [EllS System/Component Code: BI/P]. Of these pumps, the "2B" RHRSW has been installed for the longest period of time (slightly more than 11 years). Based on available information, the condition is considered to have existed for longer than allowed by TS 3.7.2. The condition is therefore being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. The "B" loop of ESW was determined to have been out of service and inoperable for ten minutes for system valve testing on September 29, 2019; as a result, the condition is also being reported in accordance with 10 CFR 50. 73(a)(2)(v) as an event or condition that could have prevented fulfillment of a safety function. CAUSE OF EVENT The direct cause was determined to be separation of the lower pump casing flange (bottom column to top case) resulting in the flange o-ring protruding and subsequent loss of differential pressure. The apparent cause was determined to be corrosion of the carbon steel bolting in raw water. This was accelerated by galvanic interactions with silt, Copper never-seize, and alloy steel. | ML19352E175
Quad Cities Nuclear Power Station | Unit 1 | Water Found in Control Room Emergency Ventilation Air Filtration Unit | 12-20-2019 | On October 27, 2019, at 1605 hours CDT, the Quad Cities Nuclear Power Station (QCNPS) Unit 1 and Unit 2 Control Room Emergency Ventilation (GREV) system was declared inoperable due to finding water in the Air Filtration Unit (AFU) filter housing. Water leaked into the B GREV AFU through an air operated fire suppression system isolation valve and sprinkler heads internal to the AFU resulting in partial submersion of the AFU filters. Maintenance on the isolation valve actuator on October 10, 2019, did not include post-maintenance testing, which resulted in inadvertently leaving the valve in a condition that provided a path for leakage into the AFU. The cause of the event was an absence of adequate work instructions for the performance of effective post-maintenance testing. Immediate Corrective actions completed include replacement of the AFU filters. Followup Corrective actions include a repair of the valve, and improvements to the model work order. This is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), any operation or condition which was prohibited by the plant's Technical Specifications, for the GREV system being inoperable longer than the seven (7) days allowed by Technical Specification 3.7.4, "Control Room Emergency Ventilation (GREV) System.". It is also being reported under 10 CFR 50.73(a)(2)(v)(D), any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. http:/lwww.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR Quad Cities Nuclear Power Station Unit 1 05000254 NUMBER NO. 2019 - 003 00 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Water Found in Control Room Emergency Ventilation Air Filtration Unit A. CONDITION PRIOR TO EVENT Unit: 1 Event Date: October 27, 2019 Event Time: 1605 hours CDT Reactor Mode: 1 Mode Name: Power Operation Power Level: 100% There were no other structures, systems or components (SSC) inoperable during this event time period that could have contributed to this event. B. DESCRIPTION OF EVENT On October 10, 2019, maintenance was performed on the Fire Protection Air Operated Valve (AOV)[ISV] 0-4199-315 in the B Control Room Emergency Ventilation (CREV)[VI] System's Air Filtration Unit (AFU)[AHU]. AOV 0-4199-315 is a single isolation between the fire system header and the sprinkler heads in the AFU. These sprinkler heads are a system feature to address potential fires in the AFU charcoal beds. The scope of the AOV 0-4199-315 maintenance included a rebuild of the actuator. The expected post-maintenance test (PMT) requirement should be full stroke of the valve and verification of proper seating; however, there were no instructions provided for generating the proper system logic to fully stroke the AOV, so the PMT was not performed. Issue Report (IR) 4287032 was generated on October 11, 2019, to document the lack of an adequate PMT. AOV 0-4199-315 was left in a closed position, and the isolation valves related to the maintenance boundary were returned to their full open positions on October 11, 2019. This allowed fire header pressure to reach AOV 0-4199-315, which subsequently leaked water past the valve seat and through to the sprinkler heads in the AFU. On October 27, 2019, an Equipment Operator (EO) observed water dripping from the CREV system AFU. Further inspection revealed that approximately three (3) inches of the bottom Charcoal Filter Drawers, the Pre-filter, and Post HEPA Filters were submerged in water. Consequently, the AFU was determined to be unable to perform its design function and was declared inoperable. The source of the water intrusion was seat leakage from the AOV 0-4199-315. Therefore, this event is reportable under 10 CFR 50.73(a)(2)(v)(D), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident." On October 27, 2019, at 2236 hours ET, ENS #54355 was made to the NRC in accordance with 10 CFR 50.72(b)(3)(v)(D) as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. NRG FORM 366A (04-2018) Page _2_ of _4_ | ML19354A102
Peach Bottom Atomic Power Station | Unit 3 | Failure of Reactor Mode Switch Results in Condition Prohibited by Technical Specifications | 12-19-2019 | On 10/21/19, Unit 3 was being shut down for a scheduled refueling outage. When the Reactor Mode Switch was moved to the Shutdown position, a reactor scram did not occur as expected. The operator depressed the nearby manual scram pushbuttons in accordance with plant procedures, which resulted in a successful scram of the reactor. An Unusual Event was declared as a result of this condition. Local, State and NRC notifications were made (ENS #54340). Investigation determined an internal connection in the switch had failed. The switch was repaired during the refueling outage. There were no actual safety consequences as a result of this condition. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Otticer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Ottice of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid 0MB control number, the NRG may not conduct or sponsor. and a person is not required to respond to, the information collection. http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER SEQUENTIAL REV YEAR Peach Bottom Atomic Power Station Unit 3 05000278 NUMBER NO. 2019 - 001 0 | Unit Conditions Prior to the Event Unit 3 was operating in Mode 1 at approximately 5% rated thermal power. There were no structures, systems or components out of service that contributed to this event. Description of Event On 10/21 /19, Unit 3 was being shut down for a scheduled refueling outage in accordance with plant operating procedures. At approximately 0039 hours and approximately 5% of rated thermal power, the reactor operator rotated the Reactor Mode Switch [EIIS:HS] from Run (Mode 1) to Shutdown (Mode 3). The Mode Switch is a pistol grip type switch located on the reactor operator's console in the main control room. The switch is part of the Reactor Protection System (RPS) [EIIS:JC] instrumentation and provides input to each of the two manual scram logic channels. When the Mode Switch was rotated to Shutdown, a reactor scram did not occur as expected. The reactor operator pressed the nearby scram pushbuttons, which initiated a successful scram. It was determined that the internals of the Mode Switch had only partially rotated and where in the Startup (Mode 2) position. In accordance with site emergency plan procedures, an Unusual Event was declared on 10/21 /19 at 0050 hours for a manual scram failing to shut down the reactor. Local, State and NRG notifications were made (ENS #54340). The Mode Switch failure resulted in the following equipment becoming inoperable as required by the plant Technical Specifications (TS): • Reactor Mode Switch -TS 3.3.1.1, Condition C was entered at 0039 hours, which requires the Mode Switch trip capability to be restored in one hour. The Mode Switch was not repaired within one hour, which resulted in Condition G being entered at 0139 hours, requiring the unit to be in Mode 3 in 12 hours. • Control Rod Scram Accumulators - although all control rods were fully inserted and the scram accumulators were not needed, TS 3.1.5 requires the scram accumulators to be operable when in Mode 2. Since the Mode Switch was in Mode 2, TS 3.1.5, Condition C was entered at 0039 hours, which requires all control rods to be fully inserted and the control rods to be declared inoperable in one hour. • Control Rods - as required by the above, TS 3.1.3, Condition C was entered at 0139 hours, which requires control rods to be inserted and the control rod drives to be disarmed. All control rods had previously been inserted and they were disarmed in accordance with plant procedures. The Unusual Event was terminated at 0230 hours on 10/21/19. Station personnel were able to access the internal portion of the Mode Switch and manually rotate the switch to the Shutdown position, which placed the unit in Mode 3. The TS requirements for the equipment identified above are no longer applicable in Mode 3 and TS required actions were exited at 0724 hours on 10/21 /19. The equipment was inoperable for approximately 6 hours and 45 minutes as a result of this event. NRG FORM 366A (04-2018) Page _2_ of _3_ | ML19354A927
i | Unknown Unit | .. - ·•·-. | 12-23-2019 | On 24 October 2019, the Automatic Depressurization System (ADS) air supply header pressure began to lower. This header provides air for the automatic or manual operation of the Safety Relief Valves (SRV's) from the Control Room. A loss of header pressure was caused by leaking Air Operated Valves (AOV's) on the 'B' Train Dryer of ADS which was worked on during a scheduled maintenance window. When a tagout was removed on the 'B' Train ADS AOV's, header pressure began to lower. Attempting to control header pressure, the 'A' Train ADS Safety Vent Valve (SW) Compressor (SW-C4A) tripped on a thermal overload. This trip was due to excessive start/stops caused by the air leak on the 'B' Train Dryer ADS AOV's. During this time the 'B' Train compressor, SW-C48, was still tagged out for maintenance. The tagout for SW-C48 was then removed and the compressor started, but header pressure continued to lower. Maintenance personnel were dispatched to assist Operations to investigate why header pressure continued to lower. SW-C4A was reset and started and SW-C4B secured. ADS header pressure then recovered to its normal operating pressure. Seven SRV's were declared inoperable due to ADS header pressure lowering below the Technical Specification limit of 131 psig. This required entry into a 12-hour shutdown LCO. Approximately 40 minutes after the LCO was entered, header pressure recovered and the LCO was exited. NRG FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO .. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U. S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid 0MB control number, the NRG may not conduct or ht1Q://www.�ov/reading:1_m/doc-collections/nureg_s_L.staff/sr1_Q_2_21QD. sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER River Bend Station -Unit 1 458 05000- 1 | BACKGROUND The Emergency Core Cooling System (ECCS) is designed, in conjunction with primary and secondary containment, to limit the release of radioactive materials to the environment following a Loss Of Coolant Accident (LOCA). The Automatic Depressurization System (ADS) is a component of the ECCS and on receipt of an initiation signal, the ADS action is delayed by a timer. This allows the operator to interrupt the timed sequence and determine if ADS is needed. If, upon ECCS actuation, High Pressure Core Spray (HPCS) fails to maintain water level, it is backed up by automatic initiation of ADS in combination with Low Pressure Coolant Injection (LPCI) and Low Pressure Core Spray (LPCS). The ADS timed sequence would then be allowed to time out and open the selected safety relief valves (SRVs), depressurizing the RCS and allowing the LPCI and LPCS to overcome Reactor Coolant System (RCS) pressure and inject coolant into the vessel. The key event that shaped this conditi0,n was removing the tagout for the 'B' Train ADS AOV's following planned maintenance. Prior to this, there were no indications of lowering ADS header pressure and SW-C4A had been maintaining header pressure as designed. Once this tagout was removed, header pressure began to fall. With both trains of ADS declared Inoperable, River Bend Station issued an 8-hour report under 10 CFR 50.72(b)(3)(v)(A) and 10 CFR 50.72(b)(3)(v)(D) as an Event or Condition that Could Have Prevented Fulfillment of a Safety Function. svv·j t SVV 'Bj. A COMPRESS-OB: -COMPRESSPR cH.�6: CHECK V�L�E 11-iL:�•� . P-Riissi:JP.e< , P?.ESS\lll:E· :tNDIC.o,rroN 1NciJc.i'r1c5t:t . ·suii,i>i,e:,,;1i:>ri ;.;i,/9.isun,�i�r c�u:cK';: C_fficCV.:': ,�di:�ir \f�LVE.•, | ML19357A229
Hope Creek Generating Station | Unknown Unit | Safety Relief Valve (SRV) As-found Set-point Failures | 03-31-2020 | On November 08, 2019, Hope Creek Generating Station (HCGS) received results that the second 'as-found' set-point test for safety relief valve (SRV) pilot stage assemblies had exceeded the lift setting tolerance prescribed in Technical Specification (TS) 3.4.2.1. The TS requires the SRV lift settings to be within +/-3% of the nominal set-point value. During the twenty-second refueling outage (H1 R22), all fourteen SRV pilot stage assemblies were tested at an offsite facility. Between October 22 and November 25, 2019, HCGS received the test results for all fourteen of the SRV pilot valve assemblies. A total of six of the fourteen SRV pilot stage assemblies were outside of the TS 3.4.2.1 specified values. All of the valves failing to meet the limits were Target Rock Model 7567F two-stage SRVs. Exceeding the set points for five of the six SRV pilot stage assemblies is attributed to corrosion bonding between the pilot discs and seating surfaces, which is consistent with industry experience. The cause of exceeding the sixth SRV set-point was pilot failure or spindle/disc contact wear. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 COMMISSION Estimated burden per response to comply with this mandatory collection request: 80 (04-2018) hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Privacy and Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by internet e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, LICENSEE EVENT REPORT (LER) Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and CONTINUATION SHEET Budget, Washington, DC 20503. If a means used to impose an information collection does not (See NUREG-1022, R.3 for instruction and guidance for completing this form display a currently valid 0MB control number, the NRC may not conduct or sponsor, and a person http://www. nrc.qov/reading-rm/doc-collectio ns/n ur egs/staff/sr1 022/r30 is not required to respond to, the information collection. 1. FACILITYNAME 2. DOCKET 3. LER NUMBER I I YEAR SEQUENTIAL REVISION Hope Creek Generating Station NUMBER NUMBER 05000354 2019 - 002 - 00 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor (BWR/4) Main Steam - EIIS Identifier {SB}* Safety Relief Valves - EIIS Identifier {SB/RV}* *Energy Industry Identification System {EIIS} codes and component function identifier codes appear as {SS/CCC} IDENTIFICATION OF OCCURRENCE Event Date: November 7, 2019 Discovery Date: November 8, 2019 CONDITIONS PRIOR TO OCCURRENCE When the reports of the 'as-found' results were received, Hope Creek was in Operational Condition (OPCON) 4, Cold Shutdown, at O percent rated thermal power. No other structures, systems or components that could have contributed to the event were inoperable at the time of the event. DESCRIPTION OF OCCURRENCE During the twenty-second refueling outage (H1 R22) at Hope Creek Generating Station (HCGS), all fourteen Main Steam safety relief valves (SRV) pilot stage assemblies {SB/RV} were tested at NWS Technologies. The SRVs are Target Rock Model 7567F two-stage SRVs. During the period from October 22 through November 25, 2019, HCGS received the results of the 'as-found' set pressure testing required by Technical Specification (TS) Surveillance Requirement (SR) 4.4.2.2. A total of six of the fourteen SRV pilot stage assemblies had set-point drift outside of the required TS 3.4.2.1 tolerance values of +/-3% of nominal value. The 'as-found' test results for the six SRVs not meeting the TS requirements are as follows: Valve ID As Found TS Lift Setting Acceptable Band % Difference (psig) (psig) (psig) Actual F013A 1187 1130 1096.1-1163.9 5.04% F013C 1209 1130 1096.1-1163.9 6.99% F013D 1166 1130 1096.1-1163.9 3.19% F013H 1194 1108 1074.8-1141.2 7.76% F013J 1191 1120 1086.4 - 1153.6 6.34% F013K 1055 1108 1074.8-1141.2 -4.78% Technical Specification (TS) 3.4.2.1 requires that the safety function of at least 13 of 14 SRVs be operable with a specified code safety valve function lift setting, within a tolerance of+/- 3%. Action (a) of TS 3A.2.1 specifies "With the safety valve function of two or more of the above listed fourteen safety/relief valves inoperable, be in at least HOT SHUTDOWN within 12 hours and in COLD SHUTDOWN within the next 24 hours." This is a condition reportable under 10 CFR 50.73(a)(2)(i)(B). The extent of condition for this event is to expand the scope of the SRV Group 1 valve testing, per ASME OM Code Section 1-1320 for Class 1 Pressure Relief Valves. All fourteen SRV pilot stage assemblies were removed and replaced with tested spares during the refueling outage (H1R22), therefore the extent of condition was satisfied. | ML20006E541
Watts Bar Nuclear Plant | Unit 1 | Control Room Emergency Ventilation System Inoperable due to Main Control Room Door Being Left Open | 01-13-2020 | On November 15, 2019, on two occasions, a Main Control Room (MCR) alarm was received for low control room positive pressure. At 2234, and again at 2353 Eastern Standard Time (EST), a Control Room Envelope (CRE) door was found ajar and immediately closed. Technical Specification (TS) Limiting Condition for Operation (LCO) 3. 7.10, Control Room Emergency Ventilation System (CREVS), was declared not met for both trains and Condition B entered for both instances. At 2236 EST, and at 2355 EST on November 15, 2019, the alarm cleared, CREVS was declared operable and LCO 3.7.10, Condition B was exited. These events were caused by human performance errors when individuals traversing the control building complex failed to confirm the MCR envelope boundary door was properly latched. The open control room door was identified and promptly closed. Contributing to this event, maintenance had been performed on the door sweep which resulted in the door involved not closing on its own. Immediate corrective actions included posting a door watch, coaching the individuals involved, and correcting the door sweep issue. Actions to prevent recurrence include training on proper door maintenance post maintenance testing and increased observations of plant staff related to door operation. This condition is being reported as an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident in accordance with 10 CFR 50.73(a)(2)(v)(D). NRG FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION 1m (04-2018) Estimated burden per response to comply with this mandaklry collection request 80 hours. Reporled lessons leaned a-e incorporated into the licensing process and fed back to industJy. Send commen1s regarding bt.rden estimate to the lnfonnation Services Branch (T- 2 F43), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001,or by e-mai to LICENSEE EVENT REPORT (LER) lnfocollecis. Resource@nrc.gov, and to the Desk Officer, Office of lnlbnnation and Regulaklry Affairs, NEOB-10202, (3150-0104), Office of Management and Budget CONTINUATION SHEET Washington, DC 20503. If a means used to i~ose an infonnation collection does not display a currentiy valid 0MB control number, the NRG may not conduct or sponsor, and a person is not required to respond to, the infonnation colection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Watts Bar Nuclear Plant, Unit 1 05000390 NUMBER NO. 2019 - 004 00 | I. Plant Operating Conditions Before the Event Watts Bar Nuclear Plant (WBN) Unit 1 was at 100 percent rated thermal power (RTP) and Unit 2 was at 10 0 percent RTP. II. Description of Event A. Event Summary At 2234 Eastern Standard Time (EST) on November 15, 2019, a Main Control Room (MGR) alarm was received for low control room positive pressure. At 2236 EST, a Control Room Envelope (CRE) door {EIIS:DR} was found ajar and immediately closed. Technical Specification Limiting Condition for Operation (LCO) 3. 7 .10, Control Room Emergency Ventilation System (CREVS) {EIIS:VI}, was declared not met for both trains and Condition B entered. At 2236 EST on November 15, 2019, the alarm cleared, CREVS was declared operable and LCO 3. 7 .10, Condition B was exited. At 2353 EST on November 15, 2019, a MGR alarm was received for low control room positive pressure. At 2355 EST, a CRE door was found ajar and immediately closed. TS LCO 3.7.10, CREVS, was declared not met for both trains and Condition B entered. At 2355 EST on November 15, 2019, the alarm cleared, CREVS was declared operable and LCO 3.7.10, Condition B was exited. This event is being reported to the Nuclear Regulatory Commission (NRG) under 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event No inoperable structures, systems, or components contributed to this condition. C. Dates and approximate times of occurrences Date Time (EST) 11/14/19 N/A Door C053 door sweep modified by Work Order 117093204. 11/15/19 2234 MGR alarm was received for low control room positive pressure. Technical Specification (TS) 3.7.10 was declared not met for both trains and Condition B entered 11/15/19 2236 CRE door was found ajar and immediately closed. TS 3.7.10 Condition B exited with cleared alarm NRG FORM 366A (04-2018) Page _2_ of _5_ | ML20013D726
Nine Mlle Point | Unit 2 | High Pressure Core Spray Declared Inoperable | 12-31-2019 | IAt 03: 16 on November 1, 2019, the Nine Mile Point Unit 2 (NMP2) High Pressure Core Spray (HPCS) System !Was declared inoperable when the Control Room Annunciation for HPCS SYSTEM INOPERABLE and INOP Status Light Indication for TRIP UNITS OUT OF FILE/POWER FAIL was received. The unplanned lnoperabllity of the HPCS System per T.S. 3.5.1 Is reportable in accordance with 1O CFR 50. 72(b)(3)(v)(D) and 1O CFR 50.73(a)(2)(v)(D). Further investigation determined the 24VDC HPCS Trip Unit Power Supply (E22A-PS1) had failed. The Power Supply was replaced, and HPCS was declared operable on 11/01/19 at 15:55. NRG FORM 366 (0-4·2017) .. NRC FORM 386A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OLIIB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Emllled blrden per rupon,a to carpy w!lh 1h11 mendato!y odlectm request 80 houra. Reported f~~-;\ LICENSEE EVENT REPORT (LEA) c l R e a e A i g m o Ja o e 1 i n o l , l s y e a ~ rned C o a n re ll b i5 i u n l r l c o d o e n t n p , O u fa tl le m W d D a i s n I h to i IO l g t t ! h o h e n e , b ln n fo l! r D m ln C a g ll oo p r 2 o s 0 c 5 e 5 s . a 5 - - 0 a 0 n 0 d B 1 , r f a e n d c h o b r ( a T c - k 2 I b F O y 4 3 1 ) 1 , l O U e O - ! S b m y . . u f' «. S d m ee t . : o r ! \f'.~..-..l '/ CONTINUATION SHEET 1nb:o1ec1s ResourceO nrc p, and 10 tie Desk Olbcer, Office of lnfonnallln and FlegAllofy Allaira, NEC8-10202, (3160-010o4i Olce o/ Management and BuciJel, Wa!lr,gla,. DC 20503 U a lll9llS (Sae h tt N p U lt R w E w G w - , 1 n 0 rc 2 . 2 g , o v R l . r 3 e a f d o 1 r n 1 o 11 :c a n tr Y uc d ll o o c n - c a o n ! d le c g t u K id Jn a s n / c n e u r f e o o r s c ! o st m at p t l 's e r t f 1 n 0 g 2 2 th . 1 / @ 11 l 'l o rm l N ~ . A - C 1 t m o a r y n p ll o D s t e c a o n n w in c l t o o Of n l a p ~ O II c S x O t r e , oo an n d d a o e p s e n r o a 1 o n d l I p s lir n y o t a r C eq l . m me l d iy l v o a r d e s 0 p M a, B d c lo a . t tr 1 o h l e n l i n .e l m on e n r, a b ti a e i 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER Nine Mile Point Unit 2 05000410 YEAR SE N Q U U M EN BE T R IA L R N E O V . 2019 - 001 - 00 | L DESCRIPTION OF EVENT A. PRE-EVENT PLANT CONDffiONS: Prior to the event, NMP2 was operating at rated reactor power. B. EVENT: At 03:16 on November 1, 2019, NMP2 received Control Room Annunciation for HPCS SYSTEM INOPERABLE and INOP Status Light Indication for TRIP UNITS OUT OF FILE/POWER FAIL. Operators attempted to close 2CSH*MOV105, HPCS Minimum Flow Valve, to secure draining Condensate Storage Tanks (CST's) to Suppression Pool. However, the valve Immediately re opened. At that time, the HPCS pump suction was swapped from Condensate Storage Tanks (CSTs) to Suppression Pool per N2-0P-33 H.6.0. As a result, Operations declared the HPCS System inoperable. The 04:03, the failed 24VDC Power Supply E22A-PS1 was identified. It was then replaced at 13:30. At 15:55, 2CSH*MOV105, the HPCS Dlesel, and HPCS were declared OPERABLE. Subsequently, T.S. 3.6.1.3 Condition C.1, T.S. 3.8.1, and T.S. 3.5.1 Condition B were exited. Nine Mile Point Unit 1 (NMP1) was unaffected by the HPCS System lnoperabllity at NMP2. Operations performed the ENS notification (#54364) required by 10 CFR 50.72(b)(3)(v)(D) and 1O CFR 50. 73(a)(2)(v)(D) as any event or condition that could have prevented the fulfillment of the safety function of structures or systemi;, that are needed to: (D) Mitigate the consequences of an accident. This event has been entered into the plant's corrective action program as IR 04293482. C. INOPERABLE STRUCTURES, COMPONENTS, OR SYSTEMS THAT CONTRIBUTED TO THE EVENT: No other systems, structures, or components contributed to this event. NRC FORM 368A (04-2017) Page _a_ of _5_ ., NRC FORM 386A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3160-o104 EXPIRES: 03131/2020 (04·2017l) ........ E!lmllled b\rnen par respaJ58 lo C00W ¥Ml tTI1 mandalo!y coleclon requeat 80 Inn, Repo,1ed / l .),, . · )'t LICENSEE EVENT REPORT (LEA) l C ~ e O ss lt a lJ i 1 s m l l e ! a r r a n g ed a C t o t n r q r r ~ n 1 J i 1 n r 1 tl a t B a i p l , l c1 e 1 s 1 t t h W ed a l l l l e l n l l m O IO g t t h t o h e n e , i l r c l e o n D r s m l C n n g o o p 2 r S o 0 e 5 c 5 M m 5- : 0 e . 0 - t . 0 d 1 8 I , W le 'i d C h e b r a ( t c - k 2 l b F o y 4 3 II ) W , U 5 e ! . - S r m y . a . N il u S c a le n l a o d r ~~.-.~..".J "/ CONTINUATION SHEET lriccolec15 AewJcel rsc l10\'. ir,d lo Ille Desk Offlcel, Oll;e of lnlorma!lon and Re<}.ialoly A/la!,,s, NE0!!-10202, (315<HJ10,4), Office o/ Management and Bod,;i!!. Wulinglm, DC 20503 HB rrMl9 (Se h e t t N pJ U 1 R w E w G w - . 1 n 0 rc 2 . 2 g , o v R /r .3 sa f d o i r n g m -r e m tru 'd c o t c ,o -c n o a U n a d c t g 1 u Q ld J1 ll S nc 'n e u r fo o r o s c / o s m tel p f! l s e r t 1 i, o g 2 2 th 1 i Q s : f l o rm c u lf o l a l C e l c b l I o I o I I o I 1 Y !1 1 n p o o t l 8 c 1 o 1 r 1 w lrl c o t r m ()( d o IJ) n O O c S d O ll! r C , l i c r n ,d d B o s p s e n tS o a t 1 d is IS p l! n ly o t I i C e I q II J T r 8 e 01 d ly J v O a r d D l 0 p M Ql B d ~ kl, fie ru m 1 l 1 o b o e n r a , b f o ie o 1, FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER Nine Mile Point Unit 2 YEAR SEQUEN11AL REV 05000410 NUMBER NO. 2019 - 001 00 NARRATIVE D. DA TES AND APPROXIMATE TIMES OF MAJOR OCCURRENCES AND OPERAT OR ACTIONS: The dates, times, and major occurrences and operator actions for this event are as follows. November 1, 2019 03:16- Received annunciator 601706 for "HPCS SYSTEM INOPERABLE" and associated computer point CSHBC01. lnop Status Light "TRIP UNITS OUT OF FILE/POWER FAIL" lit concurrently. Multiple HPCS trip units were Indicating incorrectly, and HPCS minimum flow valve 2CSH*MOV105 repositioned open. 03:16 HPCS is INOPERABLE but remains AVAILABLE. T.S. 3.5.1 Condition B entered with B.1 met with "RCIC OPERABLE". Restoration Is required within 14 days per 8.2. 03:22 Operator attempted to close 2CSH*MOV105 to secure draining Condensate Storage Tanks (CST's) to Suppression Pool. Valve immediately re-opened. 03:24 HPCS pump suction swapped from CST to Suppression Pool per N2-0P-33 H.6.0. 04:03 HPCS Trip Unit Power Supply Breaker verified on and fuses verified good in accordance with N2-ARP-601700. Suspect Power Supply E22A-PS1 has failed. 10:03 Contacted NRC Operations Center, and notified' of Unplanned HPCS lnoperability pursuant to 1 OCFR50.72(b)(3)(v)(D). Event Notification #54364. 13:30 Power Supply E22A-PS1 replaced. 14:00 HPCS Pump placed in Pull-To-Lock (PTL). Declared HPCS Diesel INOPERABLE per T.S. 3.8.1. 15:39 Performed N2-0SP-LOG-S001 for HPCS Trip Units to verify surveillance criteria met and consistent with associated reading prior to HPCS INOPERABILITY. 15:55 Declared HPCS Diesel OPERABLE, EXIT T.S. 3.8.1. Declared HPCS OPERABLE, EXIT T.S. 3.5.1 Condition B. E. METHOD OF DISCOVERY: This event was discovered by Reactor Operators when the Control Room Annunclatlon for HPCS SYSTEM INOPERABLE and INOP Status Light Indication for TRIP UNITS OUT OF FILE/POWER FAIL was received. F. SAFETY SYSTEM RESPONSES: No operational conditions requiring the response of safety systems occurred as a result of this condition. NRC FOAM 366A (04-2017) Page -1._ of _§_ | ML20014D450
Cooper Nuclear Station 05000298 1 of 5 | Unknown Unit | Division 2 Service Water Discharge Blockage Resulting in Unplanned Service Water lnoperability | 02-04-2020 | On December 5, 2019, while attempting to place Reactor Equipment Cooling Heat Exchanger B in service, Service Water flow to the heat exchanger was unable to be established. Reactor Equipment Cooling Subsystem B was declared Inoperable at 02: 15 on December 6, 2019 following validation of the condition. On December 8, 2019, troubleshooting determined the flow blockage was on the common buried Division 2 Service Water piping downstream of Diesel Generator 2, Reactor Equipment Cooling Heat Exchanger B, and Residual Heat Removal Heat Exchanger B. Service Water Subsystem B and Diesel Generator 2 were declared Inoperable at 05:00 on December 8, 2019. Manual sounding of the discharge canal was performed to determine the sediment levels above the Division 2 Service Water pipe outfall. The sounding identified approximately 15 feet of sediment. A Work Order was prepared for removing the sediment by dredging the discharge canal. Dredging commenced on December 12, 2019. Within one hour, Service Water flow was established through the Division 2 outfall. Dredging continued to remove sediment from around the Division 2 outfall, then proceeded to remove sediment from around the Division 1 outfall. A Compensatory Measure was implemented to maintain continuous Service Water flow from the outfalls above 1000 gallons per minute (gpm). Operability was restored at 05:00 on December 13, 2019. NRG FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 3/31/2020 (04-2018) ....... Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported /' lessons learned are incorporated into the licensing process and fed back to industry. Send l'lJA!/{\ LICENSEE EVENT REPORT {LER) comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear \~/j Regulatory Commission, Washington, DC 20555-0001. or by e-mail to ·~··· CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs. NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means (See NUREG-1022, R.3 for instruction and guidance for completing this form used to impose an information collection does not display a currently valid 0MB control number, the http://www.nrc.gov/readinq-rm/doc-collections/nureqs/staff/sr1022/r3/) NRC may not conduct or sponsor, and a person is not required to respond to. the information collection. 1. FACILITYNAME 2 DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Cooper Nuclear Station 05000298 NUMBER NO. 2019 -003 - 00 | PLANT STATUS Cooper Nuclear Station was in Mode 1, Power Operation, at 100 percent power, on December 6, 2019, when the event was discovered. At the start of the event, Service Water Pump A was inoperable for planned maintenance. BACKGROUND The Service Water System is designed to provide cooling water for the removal of heat from equipment, such as the diesel generators [EIIS: EK] and Reactor Equipment Cooling System heat exchangers [EIIS: CC], and to provide a supply of water for the Residual Heat Removal-Service Water Heat Exchangers [EIIS: BO] through the Residual Heat Removal-Service Water Booster System pumps [EIIS: BO], required for a safe reactor shutdown following a Design Basis Accident or transient. The Service Water System also provides cooling to unit components, as required, during normal operation. The Service Water System also provides cooling water to turbine building non-essential loads [EIIS: KB]. The Service Water System consists of the Ultimate Heat Sink and two independent and redundant subsystems. Each of the two Service Water subsystems is made up of a header, two 8000 gpm pumps, a suction source, valves, piping and associated instrumentation. Either of the two subsystems is capable of providing the required cooling capacity to support the required systems with one pump operating. The two subsystems are separated from each other so failure of one subsystem will not affect the Operability of the other system. Cooling water is pumped from the Missouri River by the Service Water pumps to the essential components through the two main headers. After removing heat from the components, the water is collected into two discharge headers and routed to the discharge canal where the water is returned to the river. Service Water discharge from the turbine equipment cooling heat exchangers is routed to the circulating water discharge tunnel. EVENT DESCRIPTION On December 5, 2019 at 23:40, Operations personnel attempted to place Reactor Equipment Cooling Heat Exchanger B in service to support the performance of post maintenance testing for Service Water Pump A. Service Water flow to Reactor Equipment Cooling Heat Exchanger B was established to match the flow through Reactor Equipment Cooling Heat Exchanger A at approximately 1700 gpm at which time Service Water flow to Reactor Equipment Cooling Heat Exchanger A was secured by closing the Service Water Reactor Equipment Cooling Heat Exchanger A outlet valve. At that time, Service Water flow to Reactor Equipment Cooling Heat Exchanger B was noticed to be O gpm. The Service Water Reactor Equipment Cooling Heat Exchanger B outlet valve was opened an additional 10 seconds with no response noted. Reactor Equipment Cooling temperature began to rise at which time Operations personnel placed Reactor Equipment Cooling Heat Exchanger A back in service. | ML20043D739
Fermi 2 05000 341 1 OF 4 | Unknown Unit | Secondary Containment Pressure Exceeded Technical Specification Due to Reactor Building HVAC Damper Malfunction | 02-14-2020 | On December 18, 2019, at 0908 EST, with the East and Center Reactor Building Heating Ventilation and Air Conditioning (RBHVAC) trains in service, secondary containment (SC) pressure degraded to the point where the Technical Specification (TS) for SC pressure was exceeded for approximately 4 minutes. The maximum SC pressure recorded during that time was 0.064 inches of vacuum water gauge. SC pressure was restored to within TS limits by manually starting the Division 1 Standby Gas Treatment System. There were no safety consequences or radiological releases associated with this event. The cause of this momentary loss of SC TS requirements was determined to be a failure in the Center RBHVAC exhaust fan inlet damper positioner. For corrective actions, Fermi 2 has upgraded two of the three RBHVAC exhaust inlet damper positioners and scheduled an upgrade replacement of the third. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/3112020 (04-2018) Estimated burden per response to comply with this mandatory collection request 80 hours. Reported ' LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed bachto industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43),U . S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of (See NUREG-1022, ( R RSe . . 3 3e Nf f o o U r r Ri i n n Gs s - t r1 r u u 0c c 2 t i2o io n n a a n n d d guuitddannccee ffoorr c c o om m p p le e t t in ig g t t h is is fo o r r m m c M ol a le n c a t g io e n m e d n o t e s a n n d o B td u i d s g p e la t, y W a a c s u h r i r n e g n t t o ly n , va D li C d 2 O 05 M 03 B . c on If tr o a l m nu e m an b s e r, us th ed e N to R im Cm p os a e yn a o n t i c n o f n o d rm ec a t t io o n r http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/srl022/r3) sponsor, and a person isn ot required to respond to, thei nformation collectiono 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER [YELAR 7S EQUE7NT IAL 1~ REV Fermi 2 052005-0030-4 1 NUMBER NO. 2019 - E 0067 - 00 | INITIAL PLANT CONDITIONS Mode - 1 Reactor Power - 100% There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT On December 18, 2019, at 0908 EST, with the unit in Mode 1 at 100 percent power and the East and Center Reactor Building Heating Ventilation and Air Conditioning (RBHVAC) [[VA]] trains in service, an alarm indicated that secondary containment (SC) [[NH]] pressure had degraded to the point where the Technical Specification (TS) requirement for SC pressure was exceeded and SC was declared inoperable. SC pressure was returned to within the TS operability limit of greater than or equal to 0.125 inches of vacuum water gauge per TS Surveillance Requirement (SR) 3.6.4.1.1 by manually starting Division 1 of the Standby Gas Treatment System (SGTS) [[BH]]. SC was declared OPERABLE on December 18, 2019, at 0912 EST. The duration of the TS not being met was approximately 4 minutes and the maximum SC pressure observed during the event was approximately 0.064 inches of vacuum water gauge. A modulating damper [[DMP]] associated with the Center train of RBHVAC was identified as not properly controlling. An 8-hour event notification (EN 54452) was made to the NRC based on meeting the reporting criteria of Title 10 Code of Federal Regulations (10 CFR) 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. This Licensee Event Report (LER) is being made under the corresponding requirement in 10 CFR 50.73(a)(2)(v)(C). SIGNIFICANT SAFETY CONSEQUENCES AND IMPLICATIONS There were no safety consequences or radiological releases associated with this event. At no time during this event was there a potential for endangering the public health and safety. The specified safety function of the SC is to contain, dilute, and hold up fission products that may leak from primary containment following a Design Basis Accident (DBA). In conjunction with operation of the SGTS and closure of certain valves [[V]] whose lines penetrate the SC, the SC is designed to reduce the activity level of the fission products prior to release to the environment and to isolate and contain fission products that are released during certain operations that take place inside primary containment, when primary containment is not required to be OPERABLE, or that take place outside primary containment. It is possible for the pressure in the control volume to rise relative to the environmental pressure (e.g., due to pump [[P]] and motor [[MO]] heat load additions). To prevent ground level exfiltration while allowing the SC to be designed as a conventional structure, the SC requires support systems to maintain the control volume pressure at less than the external pressure. For the SC to be considered OPERABLE, it must have adequate leak tightness to ensure that the required vacuum can be established and maintained. | ML20045E360
Surry Power Station | Unit 1 | Items Non-Conforming to Design for Tornado Missile Protection | 02-04-2020 | On December 11, 2019, Surry Nuclear Power Plant determined that the certain Unit 1 and 2 Class 1 Structures, Systems, and Components (SSCs) did not conform with the licensing basis for protection against a design basis tornado generated missile. The affected equipment was declared inoperable and enforcement discretion invoked in accordance with NRG Enforcement Guidance Memorandum (EGM) 15-002, Rev. 1, "Enforcement Discretion for Tornado Missile Protection Noncompliance." Initial compensatory measures were implemented pursuant to the guidance of NRG Interim Staff Guidance DSS-ISG-2016-01, Appendix A, within the time allowed by the applicable Limiting Conditions for Operation and the associated systems were then declared operable, but nonconforming. Since the condition was part of the original plant design and licensing of the station, there was no specific cause identified. There were no safety consequences as a result of this event. Actions are underway to address the condition. NRC FORM 366 (04-2018) l ! I NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U. S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of lnfonmation and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an infonmation (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid 0MB control number, the NRG may not conduct or http://www.nrc.gov/reading-rm/doc-collections/nuregs/staffisr1022/r3/) sponsor, and a person is not required to respond to, the infonmation collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER cYE:ARl SEQUENTIAL REV 05000- I 280 ~-I NUMBER 1-NO0. Surry Power Station Unit 1 I 002 | Background: Surry Nuclear Power Station, Units 1 and 2, are Westinghouse 3-Loop Pressurized Water Reactors [EIIS: AC] with a licensed maximum power level of 2546 megawatts thermal. Surry Unit 1 received its initial operating license on May 25, 1972, and Surry Unit 2 received its initial operating license on January 29, 1973, based in part on the design as described in Surry Power Station's Updated Final Safety Analysis Report (UFSAR). As described in Chapter 2.0 of the UFSAR, Class 1 structures and systems, or parts thereof, whose failure might prevent the simultaneous cold shutdown of both reactor units during a loss-of-power incident will withstand by design a tornado missile with the following characteristics and associated effects: • Missile equivalent to a wooden utility pole 40-foot long, with 12-inch diameter, weighing 50 lbs/ft3, and traveling in a vertical or horizontal direction at 150 mph. • Missile equivalent to a 1-ton automobile traveling at 150 mph. A: Plant Operating Conditions Prior to Event: Units 1/2 Date: December 11, 2019 Power level: 100 percent/100 percent Mode: N/f\J There were no SSCs out-of-service that contributed to this event. B: Description of Event: On December 11, 2019, at 1356 [EST], it was concluded that certain Class 1 SSCs are vulnerable to design basis tornado missiles which could render the equipment inoperable and unable to perform its design function. Specifically, this condition affected the following equipment: 1. Component Cooling Water [cl IS: CC] piping for the 'A' Spent Fuel Cooling Water system heat exchanger [El IS: DA HX]. This heat exchanger is vulnerable to a horizontal missile traveling through the fuel building roll-up door. 2. All three (3) Emergency Service Water (ESW) pumps [EIIS: BI-P] and their diesel fuel oil supply tank [EIIS: DC-TK]. The ESW pumps and diesel fuel oil tank are vulnerable to a horizontal missile penetrating the tornado missile screens [EIIS: SCN]. 3. Certain Component Cooling Water system pump discharge piping is vulnerable from a vertical missile penetrating the auxiliary building [EIIS: NF] roof. 4. The Unit 1 Auxiliary Feedwater (AFW) system pumps [EIIS: BA-P] and the pump suction and discharge piping are vulnerable to a missile traveling through the tornado missile screens on the sides and roof of the main steam valve [EIIS: SB-VJ house. This vulnerability also exists for the Unit 2 AFW system. 5. The Unit 2 Service Water (SW) supply valves [EIIS: KE-V] to the river water make-up pump are vulnerable to a vertical missile traveling through the turbine building roof. | ML20054A141
River Bend Station 05000 458 1 OF 3 | Unknown Unit | Loss of Control Building Chill Water due to Chiller Control Panel Installation Error / I | 03-04-2020 | On January 9, 2020 at 11 :32 CST with the reactor at 100% power, a post modification test was performed on Division I Control Building Chilled Water System Chiller A (HVK-CHL 1A). During the test, both Division I and Division II Control Building Chilled Water Systems (HVK) were declared Inoperable resulting in a condition that could have prevented fulfilment of a safety function. The event occurred while transferring from operation with HVK Chiller B (HVK-CHL 1 B) to HVK-CHL 1A as part of the test. With HVK-CHL 1A in standby, HVK-CHL 1B was secured to start the transfer sequence. HVK-CHL 1A should have auto started but instead tripped on a Phase Reversal alarm within the digital control logic. An attempt was made to place HVK-CHL 1B back in service but it also failed to start rendering both Divisions Inoperable. HVK was restored by placing the alternate Division I Chiller (Chiller 'C') in service and the alternate Division II Chiller (Chiller 'D') in standby approximately 17 minutes after the event. This event is being reported in accordance with 10 CFR 50. 73(a)(2)(v)(A) and 10 CFR 50. 73(a)(2)(v)(D). The Environmental Design Criteria maximum temperatures for the critical areas that the HVK system cools were not challenged. Therefore, this event was of minimal significance to the health and safety of the public. - NRG FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 ho.urs. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U. S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information (See NUREG-1022, R.3 for instruction and guidance for completing this form collection does not display a currently valid 0MB control nuniber, the NRC may not conduct or http://www.mc.gov/readfrig-rm/doc-collections/nuregs/staff/ sr1022/r3D sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER I I ~~~ !River Bend Station 05000-1 458 - 1 Y EAR' 1 •. -_ - SE~:~L I-~ . 1 | BACKGROUND The Control Building Chilled Water System (HVK) is designed to remove heat generated within the Control Building to maintain the required environmental conditions. HVK is a closed loop cooling water system and·provides a continuous flow of chilled water to the Control Building Air Conditioning Units. The chllled water is supplied by two independent trains, or Divisions. Each Division can meet the total chilled water demand. Each HVK Division consists of two 100% capacity Chillers. During normal system operation one HVK Division is in service supplying all system loads and the other HVK Division is in standby. The in-service Division consist of one running Chiller and one locked out Chiller. The standby Division consist of one standby Chiller and one locked out Chiller. The standby Chiller is designed to auto start if the running Chiller in the other Division trips. REPORTED CONDITION On January 9, 2020 at 11 :32 CST with the reactor at 100% power, both Division I and Division II Control Building Chilled WaJer Systems (HVK) were declared Inoperable resulting in a condition that could have prevented fulfillment of a safety function. A post maintenance test was in progress on Division I HVK Chiller A (HVK-CHL 1A) following the installation of a digital control modification. The test called for a transfer from the Division II HVK Chiller B (HVK-CHL 1 B) in service to the HVK-CHL 1A in service. To perform the transfer HVK-CHL 1 B was secured with HVK-CHL 1A in standby. HVK-CHL 1A .failed to start do to a Phase Reversal alarm. An attempt was made to place HVK-CHL 1 B back in service but it also failed to start, rendering both Divisions of HVK Inoperable. HVK was restored by placing the Division I HVK Chiller C (HVK CHL 1C ) in service and Division II HVK Chiller D (HVK-CHL 1 D) in standby approximately 17 minutes after the event. The cause of the Phase Reversal alarm was identified and corrected. HVK-CHL 1A has been successfully tested and restored to an Operable status. HVK-CHL 1 B was extensively tested but a fault could not be detected, and the failure could not be repeated. Chiller performance was carefully monitored with no anomalies noted and the Chiller has been declared Operable. This event is being reported in accordance with 10 CFR 50. 73(a)(2)(v)(A) and 10 CFR 50. 73(a)(2)(v)(D) as an event that could have prevented the fulfillment of the safety function of structures or systems that are needed to shut down the reactor and maintain it in a safe shutdown condition and mitigate the consequences of an accident. A post event evaluation determined that the actions taken by operators met the criteria· for substitution of the automatic action. Therefore, this event is not considered a Safety System Functional Failure. PREVIOUS OCCURRENCE EVALUATION Although there have been several instances of HVK failures at River Bend Station (RBS), none were caused by the same failure mechanism of this event. CAUSAL ANALYSIS The HVK-CHL 1A Phase Reversal alarm was caused by a wiring configuration error made during installation of a digital control system modification. Installation instructions and associated drawings for the modification were found to be inadequate and/or vague. | ML20064D511
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Automatic Scram due to Main Turbine Trip on High RPV Water Level | 03-31-2020 | On January 31, 2020, an automatic scram occurred as a result of a main turbine trip on high Reactor Pressure Vessel (RPV) water level. The plant was at reduced power in preparation for maintenance activities. When the ‘A’ Reactor Feed Pump (RFP) was removed from service, the ‘A’ RFP discharge check valve (34FWS-4A) failed to immediately close resulting in a rapid increase in RPV level. A high RPV level trip signal resulted in the ‘B’ RFP trip and Main Turbine trip. This event resulted in the automatic actuation of the Reactor Protection System and containment isolations in multiple systems, reportable per 10 CFR 50.73(a)(2)(iv)(A). When Secondary Containment automatically isolated, a differential pressure excursion momentarily exceeded Technical Specification limits, a condition reportable in accordance with 10 CFR 50.73(a)(2)(v)(C). The cause of the event was determined to be due to a failure of the A’ RFP discharge check valve (34FWS-4A) to close. There were no actual safety consequences as a result of this event. The ‘B’ RFP was restored to service and the condensate and feedwater systems remained available for post-scram recovery. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments CONTINUATION SHEET regarding burden estimate to the Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a (S ee NUREG-1022, R.3 for instruction and guidance for completing this form person is not required to respond to, the information collection. http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 – 333 NUMBER N0. 2020 – 001 – 00 | Background Unit Conditions Prior to the Event The James A. FitzPatrick Nuclear Power Plant (JAF) was in Mode 1 at approximately 38% rated thermal power to perform planned maintenance. There were no structures, systems, or components out of service that contributed to this event. Event Description On January 31, 2020 at approximately 0555 hours, after the operators removed the ‘A’ Reactor Feed Pump (RFP) from service, the ‘A’ RFP discharge check valve 34FWS-4A failed to close and ‘B’ RFP started to short cycle flow back through ‘A’ RFP. The feedwater control system responded to a lowering reactor water level and increased the ‘B’ feedwater turbine speed to automatically maintain RPV water level. When the 34FWS-4A, ‘A’ RFP Discharge Check Valve rapidly closed, the elevated ‘B’ RFP flow was redirected to the RPV resulting in a rapid increase in RPV level until the RPV Water Level - High (Level 8) condition was reached. The trip signal resulted in the ‘B’ RFP trip and Main Turbine trip. The Main Turbine trip signal resulted in the Reactor Protection System (RPS) [JC] actuation and resultant Reactor Scram. A subsequent low RPV water level resulted in a Group 2 isolation. The initiation of the RPS due to the automatic scram signal at critical power and the general containment Group 2 were reported per 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) as ENS 54503. In addition, when Secondary Containment was isolated with Group 2 isolation, the transitory differential pressure change exceeded Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.1 of greater than or equal to 0.25 inches of vacuum water gauge to 0.09 inches of vacuum water gauge for approximately 4 seconds. The Secondary Containment DP did not exceed 0 inches of vacuum water gauge. The cause of the DP change during the transition phase is the difference in closure time for the RBV supply and exhaust isolation valves. Event Analysis 34FWS-4A, ‘A’ RFP Discharge Check Valve, was removed and inspected. It was identified that several sub- components were found degraded or broken. This deficiency was determined to have originated at some point prior to this event, during normal operation. Under the current piping design, during a plant startup, makeup water to the RPV is aligned through a low flow line. This flow rate is insufficient to fully open the model DRV-B discharge check valve causing the check valve to “flutter,” exercising the internal valve parts. During normal power operations the main block valves are opened allowing sufficient flow. The high water level trip of the main turbine resulted in the actuation of RPS. A low water level from the scram resulted in containment isolations in multiple systems; an event reportable per 10 CFR 50.73(a)(2)(iv)(A). In this LER event, the transitory the secondary containment DP change exceeded SR 3.6.4.1.1 of greater than or equal to 0.25 inches of vacuum water gauge for a few seconds. When the SR is not met then TS 3.6.4.1 was not met and Secondary Containment was Inoperable; therefore, this event is also reportable per 10 CFR 50.73(a)(2)(v)(C). Page 2 of 3 | ML20091L895
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Unanalyzed Condition Due to Unprotected Control Circuits Running Through Multiple Fire Areas | 04-14-2020 | During a review of industry Operating Experience, James A. FitzPatrick Nuclear Power Plant (JAF) identified that unprotected control circuits for non-safety related oil pumps routed through different fire areas. The concern is that a postulated fire in one area can cause short circuits potentially resulting in secondary fires or cable failures in other fire areas where the cables are routed. The control circuits for the Turbine Generator Emergency Bearing Lube Oil Pump (94P-2), Emergency Seal Oil Pump (94P-13), and Reactor Feed Pump Turbine Emergency Oil Pumps (31P-7A and 31P-7B) are unfused and would not be protected. Cables for these control circuits are routed in safety-related trays with safety-related cables thru fire zones in Battery Charger Rooms, Battery Room Corridor, Cable Spreading Room, Relay Room, and Control Room. The cause of the condition is that the original plant design, prior to 10 CFR 50 Appendix R, did not include overcurrent protection for control circuits in all applicable Safe Shutdown Analysis circumstances. Compensatory actions were established for the affected Fire Zones until the affected circuits were modified. NRC FORM 366 (04-2018) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2018) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments CONTINUATION SHEET regarding burden estimate to the Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid OMB control number, the NRC may not conduct or sponsor, and a (S ee NUREG-1022, R.3 for instruction and guidance for completing this form person is not required to respond to, the information collection. http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 – 333 NUMBER N0. 2020 – 002 – 00 - | Background The James A. FitzPatrick Nuclear Power Plant (JAF) 10 CFR 50 Appendix R Safe Shutdown Analysis is based on the occurrence of a single fire. The only failures that are considered are those directly attributable to the fire, and spurious operations that can be postulated to occur as a result of the fire. No other failures are assumed to occur (i.e., single failure). Fire areas are established to meet the separation requirements of Section III.G of Appendix R for safe shutdown systems. It is postulated that a fire in one fire area could cause a short-circuit resulting in an overcurrent condition that overheat cables, and then possibly produce secondary fires in other fire areas where the cables are routed. Secondary fires or cable failures are outside the assumptions of the 10 CFR 50 Appendix R Safe Shutdown Analysis. Fuses in electrical circuits prevent this type of fire propagation. Event Description On June 24, 2019, during a review of industry operating experience, Electrical Engineering identified similar conditions at JAF where non-safety related direct current (DC) control circuits lack adequate overcurrent protection. Specifically, the control circuits for the Turbine Generator Emergency Bearing Lube Oil (EBOP) Pump (94P-2), the Emergency Seal Oil Pump (ESOP) (94P-13), and the Reactor Feed Pump Turbine (RFPT) DC Emergency Oil Pumps (31P-7A and 31P-7B) are unfused. Circuit breakers associated with these control circuits are insufficient to prevent a postulated overcurrent event from damaging additional cables or propagating secondary fire because the circuit breakers are designed to protect the power supply to each pump and not the control circuit portion. Portions of these non-safety related control cables are routed in safety-related trays with safety-related cables thru some fire zones. This event was initially reported to the NRC on June 24, 2019 (ENS 54130) and letter JAFP-19-0080 dated August 23, 2019 (LER: 2019-002-00). An engineering analysis determined that no credible hot short scenario will result in damage to adjacent cables in other fire zones and the current configuration would not degrade plant safety. Based on this analysis, ENS 54130 and LER 2019-002-00 were withdrawn by letter JAFP-19-0095 dated September 30, 2019. The adequacy of the analysis was later challenged, and a conservative decision was made to implement actions per Technical Requirement Manual (TRM) 3.7.M Fire Barrier Penetrations. In February 2020, the site determined that the short circuit current would exceed the values assumed in the initial evaluation resulting in temperatures in excess of the cable insulation rating of 250C. As a result, the event was reported to the NRC on February 20, 2020 (ENS 54533) per 10 CFR 50.72(b)(3)(ii)(B). The required actions of the Technical Requirement Manual (TRM) 3.7.M remained in place. Event Analysis The failure mechanism is overheating of a faulted (inadequately protected) cable that causes damage to that cable and to other cables routed in common enclosures (cable trays, conduits, panels, etc.). This creates the potential for a fire in one fire area to damage cables located in a different fire area, which could impact the equipment credited for fire safe shutdown and possibly invalidate credited safe shutdown methods. Based on a review of the cables contained within common enclosures, additional failures resulting Page 2 of 3 | ML20105B225
Perry Nuclear Power Plant 05000-440 1 OF 3 | Unknown Unit | Combustible Gas Mixing Compressor Inoperability resulting in a Technical Specification Violation 5. EventDate 6. LERNumber 7. ReportDate 8. OtherFacilities Involved Month Day Year Year Se N q u u m en b t e i r al R N e o. v Month Day Year FacilityName Do 0 c 5 ke 0 t 0 N 0 umber 2020-001-00 FacilityName DocketNumber 03 06 2020 05 04 2020 05000 9. Operating Mode 11.ThisReportisSubmitted PursuanttotheRequirementsof10CFR§: (Checkallthatapply) 20.2201(b) 20.2203(a)(3)(i) □ 50.73(a)(2)(ii)(A) □ 50.73(a)(2)(viij)(A) □ 20.2201(d) □ 20.2203(a)(3)(ii) □ 50.73(a)(2)(ii)(B) □ 50.73(a)(2)(viii)(B) □ 20.2203(a)(1) □ 20.2203(a)(4) □ 50.73(a)(2)(iii) □ 50.73(a)(2)(ix)(A) □ 20.2203(a)(2)(i) □ 50.36(c)(1)(i)(A) □ 50.73(a)(2)(iv)(A) □ 50.73(a)(2)(x) 10. PowerLevel □ 20.2203(a)(2)(ii) □ 50.36(c)(1)(ii)(A) 50.73(a)(2)(v)(A) □ 73.71(a)(4) □ 20.2203(a)(2)(iii) □ 50.36(c)(2) □ 50.7.3(a)(2)(v)(B) □ 73.71(a)(5) □ 20.2203(a)(2)(iv) 50.46(a)(3)(ii) 50.73(a)(2)(v)(C) □ 73.77(a)(1) 100 □ 20.2203(a)(2)(v) □ 50.73(a)(2)(i)(A) □ 50.73(a)(2)(v)(D) □ 73.77(a)(2)(i) □ 20.2203(a)(2)(vi) 50.73(a)(2)(i)(B) □ 50.73(a)(2)(vii) □ 73.77(a)(2)(ii) □ 50.73(a)(2)(i)(C) Other(SpecifyinAbstractbeloworin NRC Form 366A) 12. LicenseeContactforthis LER LicenseeContact TelephoneNumber(IncludeAreaCode) Hali Jenkins- Regulatory Compliance 440-280-6378 13. CompleteOneLineforeachComponentFailureDescribed inthisReport Cause System Component Manufacturer ReportabletoICES Cause System Component Manufacturer ReportabletoICES D BB RLY C770 Y 14. Supplemental ReportExpected Month Day Year 15. ExpectedSubmission Date Yes(Ifyes,complete15. ExpectedSubmissionDate) [x\ No Abstract(Limitto 1400spaces, i.e., approximately 14single-spacedtypewritten lines) On February 3, 2020, while performing testing on Combustible Gas Mixing Compressor (CGMC) B ittripped on thermal overload approximately20 seconds afterstart. Thetrip resulted in Ihoperabilityforthe B compressor. Troubleshooting determined that the overload relaywas degraded. On March 6th, 2020 itwas discovered thata procedure inadequacyforoverload relaytesting resulted in a past inoperability ofthe CGMC B from November 1, 2019 to February 14, 2020. This is in violation ofTechnical Specification 3.6.3.3, which requires restoration within 30 days orbe in in mode 3within 12 hours. Dueto instances of inoperability ofCGMCA during thistime period, this also resulted in a loss ofsafetyfunction forthe system. The directcausewas determined to be a degraded overload relay. The apparentcausewas determined to be inadequate procedural guidancefortesting the overload relay. The procedurewas revised forclarification oftesting thistype ofoverload relay. The safety significance ofthis event is considered very small in accordancewith the Regulatory Guidance. This event is reported in accordancewith 10 CFR 5073(a)(2)(i)(B) as an operation orcondition prohibited bythe planttechnical specifications, and 10 CFR 50.73(a)(2)(v)(C) as an eventorcondition that could have prevented thefulfillmentofa safety function ofthe Combustible Gas Mixing System. NRCFORM366(04-2020) NRC FORM366A U.S. NUCLEA/^GULATORYCOMMISSION APPROVED BYOF**"NNO.3150-0104 EXPIRES: 04/30/2020 (04-2020) EstimatedburdenperrespoiWrtaoicomplywiththismandatorycollectionrequest:80hours.Reportec lessonslearnedareincorporatedintothelicensingprocessandfedbacktoindustry.Sendcomment: LICENSEE EVENT REPORT (LER) regarding1burdenestimatetotheInformationServicesBranch(T-6A10M), U.S. NuclearRegulator) CONTINUATION SHEET Commission, Washington, DC20555-0001, orbye-mailtolnfocollects.Resource@nrc.gov, andth OMBreviewerat:OMBOfficeofInformationandRegulatoryAffairs,(3150-0104),Attn:DeskOfficerfoi the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail (See NUREG-1022, R.3forinstruction andguidanceforcompletingthisform oira submissionOomb.eoD.aov.TheNRCmaynotconductorsponsor,andapersonisnotrequiredti http://www.nrc.qov/readinq-rm/doc-collections/nureqs/staff/sr1022/r3A respond to, a collection ofinformation unless the document requesting orrequiring the collection displaysacurrentlyvalidOMBcontrolnumber 1. FACILITY NAME 2. DOCKETNUMBER 3.LERNUMBER YEAR SEQUENTIAL REV Perry Nuclear Power Unit 1 05000- 440 NUMBER NO. 202C 001 00 NARRATIVE Energy Industry Identification System (ENS) codes are identified in the textas [XX]. INTRODUCTION On February 3, 2020, while the plantwas at 100 percent rated thermal power, surveillancetesting was being performed on the Combustible Gas Mixing Compressor (CGMC) B [BB]. CGMC B tripped on thermal overload [RLY] approximately20 seconds afterstart. The local panel had High MotorAmp S/D alarm locked in afterthetrip. Thetrip resulted in Inoperabilityforthe B compressor underTechnical Specification (TS) 3.6.3.3, ConditionA, Combustible Gas Mixing System, at2150 on February 3, 2020. Troubleshooting determined thatthe overload relaywas degraded. The overload relaywas replaced, and post maintenancetesting was satisfactoryforCGMC B. TS 3.6.3.3 was meton February 14, 2020 at 1210when CGMC Bwas returned to OPERABLE. On March 6, 2020, as a resultofthe investigation intothe February 3rd event itwas determined thatthe procedural guidancefortesting was inadequate. Based on the procedural guidance being inadequate itwas determined that when thethermal overload relaywas tested in Novemberof2019 itwas in a degraded condition when itwas returned to operability. EVENT DESCRIPTION On February 3, 2020, while performing surveillance testing, CGMC Btripped on thermal overload approximately20 seconds afterstart. The local panel had High MotorAmp S/D alarm locked in afterthetrip. Thetrip resulted in Inoperabilityforthe B compressor underTechnical Specification (TS) 3.6.3.3, ConditionA, Combustible Gas Mixing System, at2150 on February 3, 2020. Troubleshooting, performed forthe CGMC B motor, determined thatthe overload relaywas degraded. Theoverload relaywas replaced, and post maintenancetestingwas satisfactoryfor CGMC B. TS 3.6.33 was meton February 14, 2020 at 1210when CGMC B was returned to OPERABLE. Surveillancetesting is performed once per92 days. A reviewofthe pastthree yearswas performed, and a similar issuewas identified. A Condition Reportdocumented CGMC B tripping on thermal overload on November 1, 2019, during testing. TS 3.6.3.3, ConditionAwas entered at 0915 on November 1, 2019. Awork orderresetthe overload relay and ran the compressorsuccessfully on November 1,2019, with normal amperages and voltages. The overload relaywas also bench tested on November4, 2019with satisfactory results. TS 3.6.3.3was meton November4, 2019 at 1411. On March 6, 2020, as a resultofthe investigation intothe February 3, 2020 trip itwas determined that inadequate procedural guidance iswhythe degraded thermal overload relay passed testing during the previoustrip in November of2019. Therefore, based upon this new information, CGMC Bwas determined to be inoperablefrom November 1, 2019 at0915 to February 14, 2020 at 1210. This is in violation ofTS 3.6.3.3, which requires restorationwithin 30 days, orbe in in mode 3within 12 hours. This issue is reportable under 10 CFR 50.73(a)(2)(i)(B) as an operation orcondition prohibited bythe plant's technical specifications. During this same time period the oppositetrain, CGMCA, was also inoperable atvarious timesforsurveillancetesting. This results in a reportable loss ofsafetyfunction per50.73(a)(2)(v)(C) as an eventor condition thatcould have prevented fulfillmentofthe safetyfunction. NRCFORM366A(04-2020) Page 2of3 NRC FORM366A U.S. NUCLE GULATORYCOMMISSION APPROVED BY NO.3150-0104 EXPIRES: 04/30/202 (04-2020) EstimatedburdenperrespoHetocomplywiththismandatorycollectionrequest:80hours.Reportec lessonslearnedareincorporatedintothelicensingprocessandfedbacktoindustry.Sendcommen LICENSEE EVENT REPORT (LER) regarding burdenestimatetotheInformationServicesBranch(T-6A10M), U.S. NuclearRegulatoi CONTINUATION SHEET Commission, Washington, DC20555-0001,orbye-mailto lnfocollects.Resource@nrc.gov, andth OMBreviewerat:OMBOfficeofInformationandRegulatoryAffairs,(3150-0104),Attn:DeskOfficerf the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-m? (See NUREG-1022, R.3forinstruction and guidanceforcompletingthisform oira submission@omb.e6D.Qov.TheNRCmaynotconductorsponsor,andapersonisnotrequired http://www.nrc.aov/readinq-rm/doc-collections/nuregs/staff/sr1022/r3/) respond to, a collection ofinformation unless the document requesting or requiring the collectio displaysacurrentlyvalidOMBcontrolnumber. 1. FACILITY NAME 2. DOCKET NUMBER 1LL-HNUMBER YEAR SEQUENTIAL REV Perry Nuclear Power Unit 1 05000- 440 NUMBER NO. 202C 001 00 NARRATIVE CAUSE The directcausewas determinedto be a degraded overload relay. The apparent causewas determined to be inadequate procedural guidancefortesting the overload relay. EVENTANALYSIS A Probabilistic RiskAssessment (PRA) evaluation was performed forthe November 1, 2019 to February 14, 2020 Combustible Gas Mixing Compressor B Inoperability event. The Combustible Gas Control System is not modeled in the PRA. The Combustible Gas Control System'sfunction isto protectthe Containmentvessel following a core damage event. As such, inoperability ofthe Mixing Compressor Bwould have no effect on core damage frequency. The Combustible Gas Mixing Compressors, Hydrogen Recombiners, and Hydrogen Igniters, are used to control hydrogenwhilethe hydrogen concentration is belowthe Hydrogen Deflagration Overpressure Limit in the Containment and Drywell. Ifthe hydrogen concentration is abovethe Hydrogen Deflagration Overpressure Limit, then Containment Spray and ContainmentVenting are utilized to reduce Containment hydrogen concentrations. As the Hydrogen Ignition System, the Hydrogen Recombiners, Containment Spray, and ContainmentVenting were not compromised bythis event and provide defense-in-depth for mitigation ofhydrogen and combustible gas accumulation in the Containment, this demonstratesthatthe risk impactofthe Combustible Gas Mixing Compressor B Inoperability isvery small. CORRECTIVEACTIONS The procedurewas revised forclarification oftesting thistype ofoverload relay. PREVIOUS SIMILAR EVENTS None COMMITMENTS None *CFORM366A(04-2020) Page 3of3 | 04-09-2020 | On February 3, 2020, while performing testing on Combustible Gas Mixing Compressor (CGMC) B ittripped on thermal overload approximately20 seconds afterstart. Thetrip resulted in Ihoperabilityforthe B compressor. Troubleshooting determined that the overload relaywas degraded. On March 6th, 2020 itwas discovered thata procedure inadequacyforoverload relaytesting resulted in a past inoperability ofthe CGMC B from November 1, 2019 to February 14, 2020. This is in violation ofTechnical Specification 3.6.3.3, which requires restoration within 30 days orbe in in mode 3within 12 hours. Dueto instances of inoperability ofCGMCA during thistime period, this also resulted in a loss ofsafetyfunction forthe system. The directcausewas determined to be a degraded overload relay. The apparentcausewas determined to be inadequate procedural guidancefortesting the overload relay. The procedurewas revised forclarification oftesting thistype ofoverload relay. The safety significance ofthis event is considered very small in accordancewith the Regulatory Guidance. This event is reported in accordancewith 10 CFR 5073(a)(2)(i)(B) as an operation orcondition prohibited bythe planttechnical specifications, and 10 CFR 50.73(a)(2)(v)(C) as an eventorcondition that could have prevented thefulfillmentofa safety function ofthe Combustible Gas Mixing System. NRCFORM366(04-2020) NRC FORM366A U.S. NUCLEA/^GULATORYCOMMISSION APPROVED BYOF**"NNO.3150-0104 EXPIRES: 04/30/2020 (04-2020) EstimatedburdenperrespoiWrtaoicomplywiththismandatorycollectionrequest:80hours.Reportec lessonslearnedareincorporatedintothelicensingprocessandfedbacktoindustry.Sendcomment: LICENSEE EVENT REPORT (LER) regarding1burdenestimatetotheInformationServicesBranch(T-6A10M), U.S. NuclearRegulator) CONTINUATION SHEET Commission, Washington, DC20555-0001, orbye-mailtolnfocollects.Resource@nrc.gov, andth OMBreviewerat:OMBOfficeofInformationandRegulatoryAffairs,(3150-0104),Attn:DeskOfficerfoi the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail (See NUREG-1022, R.3forinstruction andguidanceforcompletingthisform oira submissionOomb.eoD.aov.TheNRCmaynotconductorsponsor,andapersonisnotrequiredti http://www.nrc.qov/readinq-rm/doc-collections/nureqs/staff/sr1022/r3A respond to, a collection ofinformation unless the document requesting orrequiring the collection displaysacurrentlyvalidOMBcontrolnumber 1. FACILITY NAME 2. DOCKETNUMBER 3.LERNUMBER YEAR SEQUENTIAL REV Perry Nuclear Power Unit 1 05000- 440 NUMBER NO. 202C 001 00 | Energy Industry Identification System (ENS) codes are identified in the textas [XX]. INTRODUCTION On February 3, 2020, while the plantwas at 100 percent rated thermal power, surveillancetesting was being performed on the Combustible Gas Mixing Compressor (CGMC) B [BB]. CGMC B tripped on thermal overload [RLY] approximately20 seconds afterstart. The local panel had High MotorAmp S/D alarm locked in afterthetrip. Thetrip resulted in Inoperabilityforthe B compressor underTechnical Specification (TS) 3.6.3.3, ConditionA, Combustible Gas Mixing System, at2150 on February 3, 2020. Troubleshooting determined thatthe overload relaywas degraded. The overload relaywas replaced, and post maintenancetesting was satisfactoryforCGMC B. TS 3.6.3.3 was meton February 14, 2020 at 1210when CGMC Bwas returned to OPERABLE. On March 6, 2020, as a resultofthe investigation intothe February 3rd event itwas determined thatthe procedural guidancefortesting was inadequate. Based on the procedural guidance being inadequate itwas determined that when thethermal overload relaywas tested in Novemberof2019 itwas in a degraded condition when itwas returned to operability. EVENT DESCRIPTION On February 3, 2020, while performing surveillance testing, CGMC Btripped on thermal overload approximately20 seconds afterstart. The local panel had High MotorAmp S/D alarm locked in afterthetrip. Thetrip resulted in Inoperabilityforthe B compressor underTechnical Specification (TS) 3.6.3.3, ConditionA, Combustible Gas Mixing System, at2150 on February 3, 2020. Troubleshooting, performed forthe CGMC B motor, determined thatthe overload relaywas degraded. Theoverload relaywas replaced, and post maintenancetestingwas satisfactoryfor CGMC B. TS 3.6.33 was meton February 14, 2020 at 1210when CGMC B was returned to OPERABLE. Surveillancetesting is performed once per92 days. A reviewofthe pastthree yearswas performed, and a similar issuewas identified. A Condition Reportdocumented CGMC B tripping on thermal overload on November 1, 2019, during testing. TS 3.6.3.3, ConditionAwas entered at 0915 on November 1, 2019. Awork orderresetthe overload relay and ran the compressorsuccessfully on November 1,2019, with normal amperages and voltages. The overload relaywas also bench tested on November4, 2019with satisfactory results. TS 3.6.3.3was meton November4, 2019 at 1411. On March 6, 2020, as a resultofthe investigation intothe February 3, 2020 trip itwas determined that inadequate procedural guidance iswhythe degraded thermal overload relay passed testing during the previoustrip in November of2019. Therefore, based upon this new information, CGMC Bwas determined to be inoperablefrom November 1, 2019 at0915 to February 14, 2020 at 1210. This is in violation ofTS 3.6.3.3, which requires restorationwithin 30 days, orbe in in mode 3within 12 hours. This issue is reportable under 10 CFR 50.73(a)(2)(i)(B) as an operation orcondition prohibited bythe plant's technical specifications. During this same time period the oppositetrain, CGMCA, was also inoperable atvarious timesforsurveillancetesting. This results in a reportable loss ofsafetyfunction per50.73(a)(2)(v)(C) as an eventor condition thatcould have prevented fulfillmentofthe safetyfunction. NRCFORM366A(04-2020) Page 2of3 NRC FORM366A U.S. NUCLE GULATORYCOMMISSION APPROVED BY NO.3150-0104 EXPIRES: 04/30/202 (04-2020) EstimatedburdenperrespoHetocomplywiththismandatorycollectionrequest:80hours.Reportec lessonslearnedareincorporatedintothelicensingprocessandfedbacktoindustry.Sendcommen LICENSEE EVENT REPORT (LER) regarding burdenestimatetotheInformationServicesBranch(T-6A10M), U.S. NuclearRegulatoi CONTINUATION SHEET Commission, Washington, DC20555-0001,orbye-mailto lnfocollects.Resource@nrc.gov, andth OMBreviewerat:OMBOfficeofInformationandRegulatoryAffairs,(3150-0104),Attn:DeskOfficerf the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-m? (See NUREG-1022, R.3forinstruction and guidanceforcompletingthisform oira submission@omb.e6D.Qov.TheNRCmaynotconductorsponsor,andapersonisnotrequired http://www.nrc.aov/readinq-rm/doc-collections/nuregs/staff/sr1022/r3/) respond to, a collection ofinformation unless the document requesting or requiring the collectio displaysacurrentlyvalidOMBcontrolnumber. 1. FACILITY NAME 2. DOCKET NUMBER 1LL-HNUMBER YEAR SEQUENTIAL REV Perry Nuclear Power Unit 1 05000- 440 NUMBER NO. 202C 001 00 NARRATIVE CAUSE The directcausewas determinedto be a degraded overload relay. The apparent causewas determined to be inadequate procedural guidancefortesting the overload relay. EVENTANALYSIS A Probabilistic RiskAssessment (PRA) evaluation was performed forthe November 1, 2019 to February 14, 2020 Combustible Gas Mixing Compressor B Inoperability event. The Combustible Gas Control System is not modeled in the PRA. The Combustible Gas Control System'sfunction isto protectthe Containmentvessel following a core damage event. As such, inoperability ofthe Mixing Compressor Bwould have no effect on core damage frequency. The Combustible Gas Mixing Compressors, Hydrogen Recombiners, and Hydrogen Igniters, are used to control hydrogenwhilethe hydrogen concentration is belowthe Hydrogen Deflagration Overpressure Limit in the Containment and Drywell. Ifthe hydrogen concentration is abovethe Hydrogen Deflagration Overpressure Limit, then Containment Spray and ContainmentVenting are utilized to reduce Containment hydrogen concentrations. As the Hydrogen Ignition System, the Hydrogen Recombiners, Containment Spray, and ContainmentVenting were not compromised bythis event and provide defense-in-depth for mitigation ofhydrogen and combustible gas accumulation in the Containment, this demonstratesthatthe risk impactofthe Combustible Gas Mixing Compressor B Inoperability isvery small. CORRECTIVEACTIONS The procedurewas revised forclarification oftesting thistype ofoverload relay. PREVIOUS SIMILAR EVENTS None COMMITMENTS None *CFORM366A(04-2020) Page 3of3 | ML20107F741
Fermi 2 05000 341 1 OF 3 | Unknown Unit | Secondary Containment Inoperable Due to Both Airlock Doors Open | 04-22-2020 | On March 5, 2020, at 1235 EST, with the reactor at 100 percent core thermal power and steady state conditions, both doors in the secondary containment (SC) airlock on the reactor building fifth floor were open at the same time for a period of approximately three seconds. Both doors being open at the same time resulted in the Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.3 not being met. The cause of the event was a brief, inadvertent, simultaneous opening of both doors due to normal personnel ingress/egress. No equipment failures or human performance errors occurred. The doors were closed in approximately 3 seconds and SC was restored in accordance with the TS. No further corrective actions were required. The maximum SC pressure observed during the time both doors were open remained within TS limits. There were no safety consequences or radiological releases associated with this event. NRC FORM 366 (04-2020) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2020 (04-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported ,.j>flA£o<,l lessons learned are incorporated into the licensing process and fed back to industry. Send comments ./ ~\ . LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-6 A10M), U.S. Nuclear Regulatory • Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the ~ ...... ~ • CONTINUATION SHEET OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer '0/...,_,, +o' for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: (See NUREG-1022, R.3 for instruction and guidance for completing this form oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000- I □ NUMBER NO. Fermi 2 341 D 2020 - I 001 - 00 I I I I | INITIAL PLANT CONDITIONS Mode – 1 Reactor Power – 100% There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT On March 5, 2020, at 1235 EST, with the reactor at 100 percent core thermal power and steady state conditions, plant personnel notified the main control room that both doors [[DR]] in the secondary containment (SC) [[NH]] airlock on the reactor building [[NG]] fifth floor were open at the same time for a period of approximately three seconds (i.e., from 12:35:00 to 12:35:03 EST). Both doors being open at the same time resulted in the Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.3 not being met. The maximum SC pressure observed during that time remained within TS limits. There were no radiological releases associated with this event. Declaring SC inoperable as a result of not meeting TS SR 3.6.4.1.3 is reportable under 10 CFR 50.73(a)(2)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. The doors were closed in approximately 3 seconds and SC was restored. An 8-hour event notification (EN 54567) was made to the NRC based on meeting the reporting criteria of Title 10 Code of Federal Regulations (10 CFR) 50.72(b)(3)(v)(C) as an event or condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. This Licensee Event Report (LER) is being made under the corresponding requirement in 10 CFR 50.73(a)(2)(v)(C). SIGNIFICANT SAFETY CONSEQUENCES AND IMPLICATIONS There were no safety consequences or radiological releases associated with this event. At no time during this event was there a potential for endangering the public health and safety. The SC reactor and auxiliary building [[NF]] fifth floor airlock maintains one door closed when traversing into or out of the reactor building fifth floor. A negative pressure is maintained in the reactor building and portions of the auxiliary building. Radioactive materials remain in the auxiliary building and reactor building and any release of radioactive material is monitored for radiation before exhausting to the environment during normal operation. When both air lock doors were open for approximately 3 seconds on March 5, negative pressure was maintained in SC and the auxiliary building. The SC vacuum remained within the TS operability limit of greater than or equal to 0.125 inches of vacuum water gauge per TS SR 3.6.4.1.1. Therefore, there was no unmonitored release during the event. As described in DTE letter NRC-19-0075 (ML19340A088), dated December 6, 2019, the brief, inadvertent, simultaneous opening of both an inner and outer personnel access door during normal entry and exit conditions, and their prompt closure by normal means, is bounded by existing dose consequence analysis. In the unlikely event that an accident would | ML20114E190
Peach Bottom Atomic Power Station | Unit 2 | Emergency Diesel Generator Shutdown Due to Intercooler Low Pressure Results in Condition Prohibited by Technical Specifications | 04-24-2020 | On 2/26/20, Emergency Diesel Generator #1 (E-1) was started for a monthly surveillance test. Shortly after reaching full speed, E-1 tripped due to low intercooler coolant pressure. Troubleshooting identified air in the coolant system. Further investigation determined the air was introduced into the system during maintenance activities earlier in the month and not adequately vented at the conclusion of the maintenance. The system was vented and returned to an operable status on 2/27/20. Corrective actions include revising procedures to improve guidance for venting. There were no actual safety consequences as a result of this event. This event is being reported pursuant to the requirements of 10 CFR 50.73(a)(2)(i)(B) for an operation or condition prohibited by Technical Specifications. NRC FORM 366A (04- Page 2 of 4 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2020 (04-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden LICENSEE EVENT REPORT (LER) estimate to the Information Services Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of CONTINUATION SHEET Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not (See NUREG-1022, R.3 for instruction and guidance for completing this form conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Peach Bottom Atomic Power 05000- 277 NUMBER NO. Station Unit 2 2020 - 001 00 | Unit Conditions Prior to the Event Unit 2 and Unit 3 were both operating in Mode 1 at approximately 100% rated thermal power. There were no structures, systems or components out of service that contributed to this event. Description of Event On 2/26/20, at approximately 2110, operators began a monthly surveillance test of the E-1 Emergency Diesel Generator [EIIS:DG]. At 2126, a slow start of E-1 was performed in accordance with station procedures. Shortly after the engine was raised to full speed, a local alarm indicated low pressure in the intercooler coolant system. While the equipment operator was in the process of reporting the alarm to the Main Control Room, the engine automatically tripped at approximately 2129. The test was aborted and the engine placed in its normal shutdown lineup. In accordance with Technical Specifications (TS), offsite and onsite electrical power breaker alignment and a power availability check was performed to verify critical loads are connected to their preferred power source and that appropriate independence of offsite circuits was maintained. Troubleshooting identified air in the intercooler coolant system, which prevented the pump from establishing the normal system pressure. A series of venting evolutions was performed to remove the air. During the first venting, it was estimated that approximately one cubic foot of air was released. Smaller amounts were released during subsequent ventings, which were performed when the diesel was not running, when it was running unloaded and running loaded. A final run of the diesel was performed on 2/27/20 at 1436 and the engine ran without incident for approximately three hours. A final vent produced no air and E-1 was returned to operable on 2/27/20 at 2030. For the above testing and venting, the E-1 diesel was inoperable for approximately 23.3 hours from the start of the test on 2/26/20 until the engine was returned to operable on 2/27/20. Analysis of Event The site’s four Emergency Diesel Generators are standby units that provide adequate power to safely shutdown both units in the event of a design basis accident with a loss of offsite power (LOOP). The accident analysis assumes one of the four diesel generators fails. Each diesel generator starts automatically on a LOOP, low reactor water level or high drywell pressure. Periodic testing ensures the diesel engines can start automatically and reach full speed within 10 seconds. The engines can also be started manually for testing and maintenance purposes. Each diesel engine has several protective features that automatically trip the engine under the following abnormal conditions: 1. Engine overspeed 2. Jacket coolant high temperature or low pressure 3. Lube oil high temperature or low pressure | ML20115E369
Nine Mile Point | Unit 2 | Manual Scram due to an Electro-Hydraulic Control Fluid Leak on the Turbine Control System | 05-04-2020 | On March 4, 2020 at 12:05, Nine Mile Point Unit 2 (NMP2) inserted a manual reactor scram due to lowering Electro-Hydraulic Control System (EHC) level in the turbine control system. An un-isolable leak occurred when a %-inch stainless steel tube failed on the EHC supply header. The plant responded as designed following the o manual scram with all safety systems remaining in a normal standby lineup. This event is reportable under 1 CFR 50.73(a)(2)(iv)(A) as any event or condition that resulted in a manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B). The cause of the event is inadequate procedure quality that prevented the performance of appropriate preventative maintenance resulting in cyclic fatigue failure of the EHC line. The corrective actions include improving the preventative maintenance procedure and system monitoring strategies. NRC FORM 366 (04-2017) NRC FORM 368A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150·0104 EXPIRES: 03/31/2020 (04-2017)) Esttmated burden per response to comply with this mandatory collection request: 80 hours. Reported J:.,...,...,o.,i.,,, lessons learned are incorporated into the licensing prat:ess and led back to induslry. Send l-~ ..J \ LICENSEE EVENT REPORT (LER) R co e m gu m la e l n o l r s y rega C rd o in m g m b is u s rd io e n n , esti W ma a t s e h in to g to th n e , Info D rm C a tion 2 S 0 e 5 r 5 v 5 ic -0 e 0 s 0 B 1, r anch o r ( T·2 b F y 4 3), U e . - S m . a N il ucle l a o r a \~ . ~ ~ ,., . · < · . . l .: . o : : . '/i . ,,t f. ~,i': CONTINUATI0" 1111 SHEET N ln E lo O co B l - le 1 c 0 l 2 s 0 .R 2, e s (3 o 1 u 5 rc 0 e -0 @ 10 n 4 rc ), . g O o f v fi , c e a n o d f l M o a lh n e ag D em es e k n O t a ff n ic d e r B , u O d f g fi e c t e , o W f a ln sh lo in rm gt a o l n io , n D a C n d 2 0 R 5 e 0 g 3 u . lat I o f r a y A m f e fa a ir n s s , used lo impose an information collection does not display a currently vatid 0MB contrcl number, lhe (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may nol conduct or sponsor, and a person is not required to respond lo, the information http://www.nrc.gov/reading-rm/doc-colleclions/nuregs/staff/sr1022/r3/} collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Nine Mile Point Unit 2 VEAR SEQUENTIAL REV 05000410 NUMBER NO. 2020 - 001 - 00 | I. DESCRIPTION OF EVENT A. PRE-EVENT PLANT CONDITIONS: Prior to the event, NMP2 was operating at 88% reactor power. B. EVENT: At 11 :34 on March 4, 2020, NMP2 received Control Room Annunciation, Turbine Controls EHC Storage Tank low-level alarm. Following receipt of the low-level alarm, investigation by Operations identified a significant EHC leak on Turbine Building elevation 277' in the area of the Turbine Stop and Control Valves. Based on field assessments, the Control Room staff determined that the continuing lowering trend in EHC reservoir level was unable to be mitigated and a manual reactor scram was inserted at 1205. The plant responded as designed following the manual scram with all safety systems remaining in a normal standby lineup and operators stabilized the plant in Mode 3. The EHC leak was then isolated and the station entered a forced outage. Nine Mile Point Unit 1 was unaffected by the scram at NMP2. Operations performed the ENS notification (#54562) required by 10 CFR 50.72(b)(2)(iv)(B) and 1O CFR 50. 72(b )(3)(iv)(A) for the reactor scram. This event has been entered into the plant's corrective action program as IR 4323670. C. INOPERABLE STRUCTURES, COMPONENTS, OR SYSTEMS THAT CONTRIBUTED TO THE EVENT: No other systems, structures, or components contributed to this event. D. DATES AND APPROXIMATE TIMES OF MAJOR OCCURRENCES AND OPERATOR ACTIONS: The dates, times, and major occurrences and operator actions for this event are as follows. March 4, 2020 1134: Annunciator received for Low Turbine Generator Hydraulic Fluid Storage Tank Level. A lowering trend for the EHC reservoir level was observed on a local level gauge via cameras in the Control Room. 1138: A fire alarm was received for southeast Turbine Building 277. Fire Brigade Leader was dispatched and reported at 1142 a large leak and aerosol spray of EHC in this area. Fire Brigade Leader (FBL) reported no presence of fire or smoke. | ML20132A108
Quad Cities Nuclear Power Station | Unit 2 | Loss of Both Divisions of Residual Heat Removal Low Pressure Coolant Injection Due to Swing Bus Failure to Transfer ~ | 05-19-2020 | On March 20, 2020, at 1025 hours CDT at Quad Cities Nuclear Power Station (QCNPS) Unit 2, a Motor Control Center (MCC) failed to transfer between buses during the performance of the Auto-Transfer Logic Operability Surveillance. This resulted in declaring both loops of the Residual Heat Removal (RHR) Low-Pressure Coolant Injection (LPCI) safety system function inoperable, due to preventing LPCI Motor Operated Valves (MOVs) from opening from the LPCI Loop Select Logic. The apparent cause of the event was a manufacturing error in the LPCI swing bus time delay relay. The barrel spring, which aids in closing the normally closed contacts, was not properly positioned, allowing inconsistent contact closure. This is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of systems needed to mitigate the consequences of an accident. NRG FORM 366 (04-2020) Page 1of4 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150·0104 EXPIRES: 04/30/2020 (04-2020) Estimated burden per response to comply with this mandatmy collection request: 80 hours. Repartee lessons learned are incorporated into the licensing process and fed back to industiy. Send comment~ LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-6 A1 O M), U.S. Nuclear Regulate!) CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the OMS reviewer at: OMS Office of Information and Regulatoiy' Affairs, (3150-0104), Attn: Desk Office for the Nuclear Regulatoiy Commission, 725 17th Street NW, Washington, DC 20503; e-mail (See NUREG· 1022, R.3 for instruction and guidance for completing this form oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not requirec http:/iwww.nrc.gov/reading-rm/doc-collections/nuregsistaff/sr1022ir31) to respond to, a collection of information unless the document requesting or requiring the collectior displays a currently valid OMS control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Quad Cities Nuclear Power Station Unit 2 05000-265 NUMBER NO. 2020 - 001 00 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Loss of Both Divisions of Residual Heat Removal Low Pressure Coolant Injection Due to Swing Bus Failure to Transfer A. CONDITION PRIOR TO EVENT Unit: 2 Event Date: March 20, 2020 Event Time: 1025 hours CDT Reactor Mode: 1 Mode Name: Power Operation Power Level: 100% There were no other structures, systems or components (SSC) inoperable during this event time period that could have contributed to this event. B. DESCRIPTION OF EVENT On March 20, 2020, at 1025 hours, during performance of the Residual Heat Removal (RHR) Low Pressure Coolant Injection (LPCl)[BO] swing bus [BU] surveillance, the Motor Control Center (MCC)[MCC] 28/29-5 did not auto transfer feed from Bus 29 to Bus 28. At the time of the event, LPCI was already inoperable under Technical Specification (TS) 3.5.1 Condition E for two LPCI systems inoperable. However, the failure to auto-transfer would have prevented LPCI Loop Select Logic from opening motor operated valves (MOV) 2-1001-29A/B, resulting in the loss of the LPCI safety function. Following the failure to transfer, power was restored to MCC 28/29-5 by Operations. Operations and Electrical Maintenance (EMs) began troubleshooting following restoration of power. They identified that the Bus 29 feed breaker to MCC 28/29-5 did not trip as expected. Upon this discovery they began taking voltage and resistance checks along the trip circuitry associated with the feed breaker. The initial results indicated that during the surveillance, installation of a jumper per surveillance instructions resulted in the contactor at MCC 28/29-5 02 opening but the associated feed breaker did not open. This indicated that the most likely causes of failure were either the auxiliary contact 2-3 on the M-contactor for the feed from Bus 29 or the LPCI Swing Bus Time Delay Relay. Operations then performed another swap of MCC 28/29-5 from Bus 29 to Bus 28 to de-energize the Time Delay Relay [RL Y] for testing. Resistance checks were performed for Contacts 1-5 for the Bus 28 feed closing circuit and Contacts 2-6 for the Bus 29 feed trip circuit. Contacts 1-5 were found closed with a reading of less than 1 ohm, and Contacts 2-6 were found open with a reading of 131 mega-ohms. The open reading for Contacts 2-6 indicates that they were likely hung-up, which explains why the auto-transfer didn't occur, since the Bus 29 feed breaker never received a trip signal. Following this finding, the Time Delay Relay was replaced, and the surveillance was NRG FORM 366 (04-2020) Page 2 of 4 | ML20140A093
Brunswick Steam Electric Plant (BSEP) | Unit 1 | Manual Reactor Scram During Startup due to all Bypass Valves Fully Opening | 05-20-2020 | At 12:55 Eastern Daylight Time (EDT) on March 22, 2020, with Unit 1 in Mode 2, stabilized at 2% power, during startup from a refueling outage, all four main turbine Bypass Valves (BPVs) fully opened unexpectedly. This created an unexpected reactor depressurization and cooldown which resulted in the operating crew inserting a manual reactor scram. The scram was uncomplicated and all control rods inserted as expected during the scram. All BPVs fully opened as a result of the Turbine Control System (TCS) pressure setpoint not being set correctly. This error went undetected until the low main condenser vacuum isolation signal to the BPVs cleared during the startup sequence, at which time the BPVs fully opened. There was no impact on the health and safety of the public or plant personnel. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) due to manual actuation of the Reactor Protection System (RPS). NRC FORM 366 (04-2020) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2020 (04-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-6 A10M), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: (See NUREG-1022, R.3 for instruction and guidance for completing this form oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant (BSEP), 05000325 YEAR NUMBER NO. Unit 1 2020 - 001 - 00 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. Background Initial Conditions At the time of the event, Unit 1 was in Mode 2 (i.e., Startup), at approximately 2 percent rated thermal power. Reportability Criteria This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) because it involved actuation of a system listed in 10 CFR 50.73(a)(2)(iv)(B). Specifically, the Reactor Protection System [JC] actuated during this event. The NRC was notified of this event per 10 CFR 50.72(b)(2)(iv)(B) via Event Notification 54597 at 16:39 Eastern Daylight Time (EDT) on March 22, 2020. Event Description At 12:55 EDT on March 22, 2020, with Unit 1 in Mode 2, stabilized at 2% power, during startup from a refueling outage, all four main turbine Bypass Valves (BPVs) [JI] fully opened unexpectedly. This created an unexpected reactor depressurization and cooldown which resulted in the operating crew inserting a manual reactor scram. The scram was uncomplicated and all control rods inserted as expected during the scram. In accordance with plant procedures, the main control room closed all Main Steam Line Isolation Valves (MSIVs) [JM] to arrest the cooldown resulting from BPVs remaining open. The condensate system [SD] remained aligned for injection and pressure control was initially via main steam line drains [JM]. Residual Heat Removal (RHR) shutdown cooling [BO] was placed in operation for decay heat removal and pressure control once the MSIVs were closed. All systems responded as designed. Event Cause The direct cause of all Unit 1 BPVs fully opening during startup was the Turbine Control System (TCS) [JJ] pressure setpoint being set incorrectly. Procedure 0GP-01, “Prestartup Checklist,” requires the pressure setpoint be set to 100 psig at this point during startup. However, at the time of this event, the pressure setpoint was incorrectly set to 1 psig. This error went undetected until the low main condenser vacuum isolation signal to the BPVs cleared during the startup sequence, at which time the BPVs fully opened. This event resulted from a less than adequate technical review of procedure 0GP-01, “Prestartup Checklist,” during development for the TCS upgrade project. In addition, there was a lack of proficiency in adjusting pressure set. Safety Assessment There was no adverse impact on the health and safety of the public. The safety significance of this event is minimal. The manual reactor trip was not complicated and all safety related systems operated as designed. Corrective Actions Upon restart from this event, the Unit 1 TCS pressure setpoint was set to 100 psig in accordance with 0GP-01, “Prestartup Checklist,” utilizing the appropriate guidance from 1OP-25, “Main Steam System Operating Procedure,” for adjusting the pressure setpoint. In addition, remediation plans were developed for the operators involved with this event, and lessons learned from this event were disseminated to appropriate Operations Department personnel. On April 1, 2020, 0GP-01, “Prestartup Checklist,” was revised to have specific reference to 1OP-25, “Main Steam System Operating Procedure,” for adjusting the TCS pressure setpoint. In addition, the procedure step to set pressure was identified as a critical step. | ML20141L763
Quad Cities Nuclear Power Station | Unit 2 | Electromatic Relief Valve 30 Did Not Actuate Due to Out of Specification Plunger | 05-28-2020 | On March 30, 2020, with the unit in shutdown, Quad Cities Nuclear Power Station (QCNPS) Unit 2, Electromatic Relief Valve (ERV) 2-0203-3D, 2D Main Steam Line Relief Valve, did not stroke in accordance with work package instructions. The valve was being tested to satisfy Technical Specification Surveillance Requirement (TS SR) 3.5.1.10, Verify each Automatic Depressurizing System (ADS) valve actuator strokes when manually actuated. All other Unit 2 ADS valves were found to stroke satisfactorily. The cause of the failure was an out of specification plunger received from the vendor. The failure will be prevented by determining and implementing appropriate purchase requirements to ensure new plungers meet the vendor specifications for this part. This is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), any operation or condition which was prohibited by the plant's Technical Specification. TS 3.5.1 Condition Hallows one ADS valve to be inoperable for a period of 14 days. This ADS valve was found to be inoperable for the entire cycle. NRG FORM 366 (04-2020) Paqe 1 of 4 NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2020 (04-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Repartee lessons learned are incorporated into the licensing process and fed back to industry. Send comment! LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-6 A1 O M). U.S. Nuclear Regulator\ CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and thE OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Office for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail (See NUREG-1022, R.3 for instruction and guidance for completing this form oira_submission@omb.eop.gov. The NRG may not conduct or sponsor, and a person is not requirec http:/iw1w1.nrc.qov/readinq-rmidoc-collectionsinuregs/staff/sr10221r31) to respond to, a collection of information unless the document requesting or requiring the collectior displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Quad Cities Nuclear Power Station Unit 2 05000-265 NUMBER NO. 2020 - 002 00 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Electromatic Relief Valve 3D Did Not Actuate due to Out of Specification Plunger A. CONDITION PRIOR TO EVENT Unit: 2 Event Date: March 30, 2020 Event Time: 0530 hours CDT Reactor Mode: 4 Mode Name: Cold Shutdowff- Power Level: 0% There were no other structures, systems or components (SSC) inoperable during this event time period that could have contributed to this event. B. DESCRIPTION OF EVENT On March 30, 2020, with Unit 2 in shutdown for refueling outage 02525, during performance of the Technical Specification (TS) Surveillance Requirement (SR) 3.5.1.10, the 2-0203-3D Electromatic Relief Valve (ERV)[RV] failed to actuate. TS SR 3.5.1.10 requires each Automatic Depressurizing System (ADS)[BF] valve actuator stroke when manually actuated. All other ADS valves on Unit 2 were found to stroke successfully. The 2-0203-3D actuator was replaced and stroked successfully prior to completion of refueling outage Q2R25 restoring the system to operable. The failed actuator for the 2-0203-3D ERV had been originally installed in March 2018 after having been rebuilt in February 2018 in preparation for the Q2R24 refueling outage. The actuator had been rebuilt in accordance with site maintenance rebuild procedure. On April 5, 2018, during an Auto Slowdown Functional Test operating surveillance, the 2-0203-3D ERV did not initially actuate as expected with the ERV remaining in the closed position. An Issue Report {IR) was generated, and troubleshooting was performed to smooth the actuator plunger sides to correct the actuator sticking. It was subsequently cycled three times successfully and was returned to service. Following the 2020 failure, the removed 2-0203-3D ERV actuator was dissembled and inspected to determine the cause of the failure. The initial observations and stroking of the actuator with the cover removed noted that the upper guide bracket was tilted down on the left end. As the actuator was stroked and returned to the standby state, the tilt of the upper guide bracket would vary from stroke to stroke causing the sticking of the actuator to be intermittent. Observation of the plunger during testing noted that it would intermittently rub with the lever arm on the left side. The plunger width was found to be different from the top to mid-length indicating the legs are splaying. This plunger width was outside the manufacturer's tolerance for plunger width. The measured width of 2.592" is 0.027" larger than the manufacturer's toleranc.e for plunger width of 2.565". NRC FORM 366 (04-2020) Page 2 of 4 | ML20149K600
Quad Cities Nuclear Power Station | Unit 1 | Control Room Emergency Ventilation Air Conditioning System Inoperable Due to Incorrect Breaker Setting | 06-11-2020 | On April 14, 2020, at 1645 hours CDT, the Quad Cities Nuclear Power Station (QCNPS) Unit 1 and Unit 2 Control Room Emergency Ventilation (CREV) Air Conditioning (AC) system was declared inoperable due to a trip of the Refrigeration Condensing Unit (RCU) feed breaker. Technical Specification (TS) 3.7.5 Condition A was entered at that time. Control Room operators discovered that the indicating light for the RCU was not lit. An operator was dispatched and found that the feed breaker had tripped. At 1705 hours CDT the feed breaker was reset restoring RCU light indication in the control room. A full RCU feed breaker inspection, adjustment of the breaker trip setting, and post maintenance testing (PMT) of the breaker and system were completed on April 16, 2020 with TS 3.7.5 Condition A exited at 0453 hours. The causes of the event were (1) failure to adequately update guidance documents in a timely manner and (2) maintenance not adequately documenting the difference between as-found and work instruction breaker setting values during the RCU feed breaker preventative maintenance (PM) in 2013. This is being reported in accordance with 10 CFR 50. 73(a)(2)(v)(D), any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. NRC FORM 366 (04-2020) Page 1of4· NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150·0104 EXPIRES: 04/30/2020 (04·2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Repartee lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T·6 A10M), U.S. Nuclear Regulator} CONTINUATION SHEET Commission, Washington, DC 20555·0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Office1 for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail (See NUREG· 1022, R.3 for instruction and guidance for completing this form oira_submission@omb.eop.gov. The NRG may not conduct or sponsor, and a person is not requirec http:iiwww.nrc.gov/reading-rmidoc-collectionsinuregsistaff/sr1022/r3i) to respond to, a collection of information unless the document requesting or requiring the collectior displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Quad Cities Nuclear Power Station Unit 1 05000254 NUMBER NO. 2020 - 001 00 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Control Room Emergency Ventilation Air Conditioning System Inoperable Due to Incorrect Breaker Setting A. CONDITION PRIOR TO EVENT Unit: 1 Event Date: April 14, 2020 Event Time: 1645 hours CDT Power Level: 100% There were no other structures, systems or components (SSC) inoperable during this event time period that could have contributed to this event. 8. DESCRIPTION OF EVENT On April 14, 2020 at 16:45, Operations noticed that there was no indicating light for the Control Room Emergency Ventilation (CREV)[VI] Refrigeration [RFU] Condensing Unit (RCU) 0-9400-102 on the Main Control Room (MCR)[NA] Panel 912-5. This was noted during the hourly general panel walk down. An operator was dispatched and found that local indications also showed the RCU to have no power and the breaker in a tripped condition. The breaker was reset, and light indication [IL] was restored. The Station entered Technical Specification (TS) 3.7.5 Condition A for an inoperable CREV Air Conditioning (AC) system. ENS Notification #54665 was made in accordance with 10 CFR 50.72(b)(3)(v)(D). Electrical Maintenance performed a breaker [52] and cubicle inspection on April 16, 2020 and found that the breaker trip setting was set at 8.8. A review of the breaker parameters showed that the trip setting should have been set at 10. No other issues with the function of the breaker or cubicle were found. In F'ebruary 2012, after a series of short duration nuisance CREV RCU breaker trips, additional troubleshooting and an investigation was performed on this breaker. The investigation concluded that breaker instantaneous thermal trip settings needed to be increased to the maximum manual setting (10) to avoid continued nuisance trips. The trip setting of 8.8 was acceptable, but due to the high importance of the system, the trip setting of 10 was recommended for additional margin to ensure continuity of service. The breaker setting was changed to the 10 and an engineering change was initiated to update the breaker trip setting in the Passport Database. Design Engineering incorrectly assumed that the breaker preventative maintenance (PM) would be credited to recently completed breaker troubleshooting and that the next PM occurrence would be in 8 years. However, maintenance did not credit the troubleshooting work to the PM and the normal PM schedule remained with the next PM due in 18 months. The Engineering Change to update the Passport Database breaker trip setting was not completed until four days after the breaker PM work order task instructions were completed. NRC FORM 366 {04-2020) Page 2 of 4 | ML20163A145
Edwin I. Hatch Nuclear Plant | Unit 2 | HPCI and RCIC Inoperable When Required by Technical Specifications | 06-18-2020 | At 1015 EST, on 04/22/2020, while Unit 2 was at approximately 0.4 percent power in MODE 2 reactor steam dome pressure reached and subsequently exceeded 150 psig while High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) were inoperable due to not being placed in standby. Technical Specification (TS) Limiting Conditions of Operation (LCO) 3.5.1 and 3.5.3 are applicable in Mode 2, when Reactor steam dome pressure is greater than 150 psig. TS LCO 3.5.1, Conditions C and E were entered. TS LCO 3.5.3 Conditions A and B were also entered. HPCI does not have a redundant system; therefore, this condition is being reported per 1o CFR 50.7 3(a)(2)(v)(D) as an event that could have prevented fulfillment of a safety function. Contrary to the requirements of LCO 3.0.4, LCO 3.5.1 and LCO 3.5.3 were not met before entering the mode of applicability. Therefore, this event is also being reported under 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by technical specifications. The Automatic Depressurization System and the Low Pressure Emergency Core Cooling system were OPERABLE during this time. HPCI was returned to OPERABLE status at 1109 EST on 04/22/2020. RCIC was returned to operable status at 1143 EST on 04/22/2020. This event was caused a by human performance error. There was no impact on the health and safety of the public or plant personnel. NRC FORM 366 (04-2020) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3160-0104 EXPIRES: 04/30/2020 (04-2020) Estimated burden par response to comply Ylith this mandatory collection request 80 hours. Reported lessons learned are incorpomted into the licensing process and fed back to indusby. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Informs on Services Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnlocollects.Resource@nrc.gov. and the CONTINUATION SHEET ...... OMB reviewer at OMB Office of Information and Regulatory Affairs, (3150.0104). Attn: Desk Officer lor the Nuclear Regulatory Commission. 725 17th Street NW, Washingtoo. DC 20503; e-mail: (See NUREG-10 22, R.3 for instruction and guidance for completing this form o;nt_submisston@omb.eQP.gay. The NRC may not conduct or sponsor, and a person is not required http://www .nrc.govLLeading:.rrnldoc-collections/nuregs/staff/sr1 022/r3/) to respood to, a collection ollnformalion unless lhe document requesting or requiring the collectioo displays a currently va OMB conlrol number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER DYEA R SEQUENTIAL REV Edwin I. Hatch Nuclear Plant Unit 2 05000- j 366 NUMBER 1-0NO. ~- 1 I 002 | EVENT DESCRIPTION: On 04/22/2020 at 0600, Unit 2 was in Startup (Mode 2) following a maintenance planned outage. While withdrawing control rods and after reaching the point of adding heat (POAH), the shift team focused on establishing Intermediate Range Monitor (IRM) overlaps. After reaching the POAH, the team continued to withdraw control rods to obtain IRM overlaps and avoid going subcritical as reactor coolant system heat up was adding negative reactivity. Those efforts led to rising moderator temperature. At 1015 EST, on 04/22/2020, while Unit 2 was at approximately 0.4 % power in MODE 2, reactor pressure reached and subsequently exceeded 150 psig while High Pressure Coolant Injection (HPCI) [EllS BJ] and Reactor Core Isolation Cooling (RCIC) [EllS BN] were inoperable due to not being placed in standby. Technical Specification (TS) Limiting Condition of Operation (LCO) 3.5.1 and 3.5.3 are applicable in Mode 2, when pressure is greater than 150 psig. EVENT CAUSE ANALYSIS: This event was caused by a human performance error. Oversight of crew performance was narrowly focused on specific tasks and as a result did not identify gaps in the crew's preparation and execution of the plant startup procedure. REPORTABILITY AND SAFETY ASSESSMENT: HPCI does not have a redundant system; therefore, this condition is being reported as an event or condition that at the time of discovery could have prevented the fulfillment of the safety function per 10 CFR 50.73(a)(2)(v)(D). LCO 3.0.4 states, in part, that "When an LCO is not met, entry into a mode or other specified condition in the Applicability shall only be made ... " under three specific circumstances. None of these circumstances were applicable for this event. Therefore, entry into the specified Applicability Conditions of MODE 2 and reactor steam dome pressure greater than 150 psig was not allowed for LOC 3.5.1 and LCO 3.5.3 while HPCI and RCIC were inoperable. Contrary to the requirements of LCO 3.0.4, LCO 3.5.1 and LCO 3.5.3 were not met before entering the mode of applicability. Therefore, this event is also being reported under 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by technical specifications. The Automatic Depressurization System (ADS) and Low Pressure Emergency Core Cooling Systems (ECCS) were OPERABLE during this time. The safety significance of this event is minimal due the short duration that HPCI and RCIC were declared inoperable. CORRECTIVE ACTIONS: HPCI and RCIC were declared inoperable. Technical Specification Required Action Statements were entered for LCO 3.5.1 Conditions B (HPCI inoperable), LCO 3.5.1 Condition E (Shutdown actions), LCO 3.5.3 Condition A (RCIC inoperable) and LCO 3.5.3 Condition B (Shutdown actions). HPCI and RCIC were returned to OPERABLE status. A case study will be delivered to the operations department and station leadership focusing on remaining in oversight roles and looking ahead at the broader perspective assigning clear responsibilities, the proficiency model and responding to changing plant conditions. PREVIOUS SIMILAR EVENTS: None | ML20170A531
i | Unknown Unit | Salem Unit 1 and Unit 2 RHR availability for Emergency Core Cooling in Mode 4 | 07-06-2020 | On 5/5/2020, an evaluation determined that in MODE 4, the temperature of the fluid in the residual heat removal (RHR) pump suction header exceeded the temperature which, under postulated shutdown loss of coolant accident (LOCA) conditions, could have resulted in cavitation of the RHR system. The condition is postulated to occur during both the injection phase, when suction is aligned to the refueling water storage tank (RWST) as well as the recirculation phase when suction is aligned to the Emergency Core Cooling (ECCS) sump. This postulated condition results in the inoperability of the RHR system while in MODE 4. Corrective actions to revise the affected procedures have been created. Interim corrective actions are in place until procedure revisions are completed. This event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(D), 10 CFR 50.73(a)(2)(i)(B), and 10 CFR 50.73(a)(2)(vii). NRC FORM 366 (04-2020) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2020 (04-2020) .... ,...... Estimated burden per response to comply with this mandatory collection request: 80 hours. ~ Reported lessons learned are incorporated into the licensing process and fed back to ~ industry. Send comments regarding burden estimate to the FOIA, Privacy and Information -, ~ Collections Branch (T-5 F53), U.S. Nuclear Regulatory Commission, Washington, DC 20555- •11·11!...., LICENSEE EVENT REPORT (LER) 0001, or by internet e-mail to Infocollects.Resource@nrc.gov, and to the Desk Officer, Office of (See Page 2 for required number of digits/characters for each block) Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of Management and (See NUREG-1022, R.3 for instruction and guidance for completing this form Budget, Washington, DC 20503. If a means used to impose an information collection does not http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) display a currently valid OMB control number, the NRC may not conduct or sponsor, and a person is not required to respond to, the information collection. 1. FACILITY NAME 2. DOCKET 3. LER NUMBER l I YEAR SEQUENTIAL REVISION Salem Generating Station ─ Unit 1 05000272 NUMBER NUMBER 2020 - 002 - 00 | PLANT AND SYSTEM IDENTIFICATION Westinghouse-Pressurized Water Reactor (PWR/4) Residual Heat Removal (RHR) ─ Low Pressure Safety Injection System {BP} IDENTIFICATION OF OCCURRENCE Event Date: May 5, 2020 CONDITIONS PRIOR TO OCCURRENCE Salem Unit 1 was in MODE 1, operating at 100 percent power. Salem Unit 2 was in MODE 5 restoring from a refueling outage. DESCRIPTION OF OCCURRRENCE On 5/5/2020, an evaluation determined that in MODE 4, the temperature of the fluid in the residual heat removal (RHR) pump suction header exceeded the temperature which, under postulated shutdown loss of coolant accident (LOCA) conditions, could have resulted in cavitation of the RHR system. The condition is postulated to occur during both the injection phase, when suction is aligned to the refueling water storage tank (RWST) as well as the recirculation phase when suction is aligned to the Emergency Core Cooling (ECCS) sump. This postulated condition results in the inoperability of the RHR system while in MODE 4. CAUSE OF THE EVENT Westinghouse NSAL 09-08 was evaluated during recent procedure upgrades and the adequacy of the procedure temperature limitations was evaluated by engineering. The engineering evaluations determined that in MODE 4, the temperature of the fluid in the residual heat removal (RHR) pump suction header exceeded the temperature which, under which a postulated shutdown loss of coolant accident (LOCA) conditions, could have resulted in cavitation of the RHR system for both injection phase and recirculation . SAFETY CONSEQUENCE AND IMPLICATIONS The potential exists for cavitation of the RHR suction header if the RHR system is actuated for ECCS following RHR operation in shutdown cooling at coolant temperatures that are within technical specification allowances. The RHR suction header for each train is cross-connected to share a common flow path from the RCS or RWST. Therefore, this could affect both RHR trains and is considered a safety system functional failure. Both Salem units have operated in this condition for short time periods. When in MODE 4, technical specifications require one operable ECCS that includes a train of RHR. Review of plant operating history found brief instances in which RHR was operated in shutdown cooling at elevated coolant temperatures where cavitation is expected if RHR pressure is reduced when actuated for ECCS operation. Therefore, this is considered operation in a condition prohibited by technical specifications and common cause inoperability of independent trains. No component failures contributed to this event. CORRECTIVE ACTIONS Corrective actions to revise the affected procedures have been created. Interim corrective actions are in place until procedure revisions are completed. PREVIOUS EVENTS There were no similar events in the past three years. COMMITMENTS There are no regulatory commitments contained in this LER. | ML20188A010
Browns Ferry Nuclear Plant | Unit 3 | Main Steam Relief Valves Lift Settings Outside of Technical Specifications Required Setpoints | 07-07-2020 | On May 8, 2020, the Tennessee Valley Authority was notified of as-found testing results that two Main Steam Relief Valves (MSRVs) from Unit 3 were outside the +/- 3 percent setpoint band required for operability. More than the one allowed MSRV was considered to be inoperable during the entire operating cycle and longer than permitted by Technical Specifications. Additionally during this time, BFN, Unit 3 entered a Mode of operation which was not allowed under this condition. The affected valves remained capable of maintaining reactor pressure within American Society of Mechanical Engineers code limits. It was determined that these MSRVs failed due to corrosion bonding between the pilot valve disc and seat. As a corrective action for this condition, all thirteen of the MSRV pilot valves were replaced during the Unit 3 Spring 2020, refueling outage with pilot discs coated in platinum utilizing the Plasma Enhanced Magnetron Sputtering (PEMS) Deposition method. PEMS provides a more consistent and forgiving finish on the pilot valve seating surface and gives the platinum more inherent ductility than what the previous disposition method provided. BFN began using the PEMS method in 2019, so the valves involved in this event did not receive PEMS deposited platinum coatings during their last rebuild. The PEMS method was used for the pilot discs of the rebuilt valves installed during the Unit 3 Spring 2020 refueling outage, and will be used for all pilot discs going forward. NRC FORM 366 (04-2020) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2020 (04-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T- 6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail LICENSEE EVENT REPORT (LER) to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, CONTINUATION SHEET 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov . The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number.. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 3 05000296 NUMBER NO. 2020 - 002 - 00 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN) Unit 3 was in Mode 1 at approximately 100 percent power. II. Description of Event A. Event Summary On May 8, 2020, NWS Technologies notified the Tennessee Valley Authority (TVA) with the as-found testing results of the thirteen Main Steam Relief Valves (MSRVs) [RV], which were removed during the Spring 2020 Unit 3 Refueling Outage 19 (U3R19). Two MSRVs (BFN- 3PCV-001-0023 and BFN-3-PCV-001-0034) had as-found lift settings which were outside of the +/- 3 percent band of their setpoints required for operability. Technical Specification (TS) 3.4.3, Safety/Relief Valves (S/RVs), requires twelve of the thirteen S/RVs to be operable for S/RV system [SB] operability. The two MSRVs were found to have been inoperable for an indeterminate period of time during the entire operating cycle between April 5, 2018, and February 22, 2020, and longer than permitted by TS 3.4.3. Throughout this event, the two-stage MSRV pilot valves remained capable of maintaining the reactor pressure below 1375 pounds per square inch gauge (psig), which is the American Society of Mechanical Engineers (ASME) code limit of 110 percent of the vessel design pressure. The valves remained capable of performing their required safety function. The TVA is submitting this report in accordance with Title 10 of the Code of Federal Regulations 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant’s TS. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML20189A179
Browns Ferry Nuclear Plant | Unit 2 | Core Spray System Inoperable for Longer than Permitted by Technical Specifications | 08-31-2020 | On July 1, 2020, the motor thermal overloads associated with the 2A Core Spray Room Cooler Fan were found tripped during a surveillance test. The breaker was not tripped, and was found still in the "on" position. Operators reset the thermal overloads, which restarted the room cooler fans without resetting the breaker. The thermal overloads were replaced on July 2, 2020. After a recurrent trip on July 6, 2020, troubleshooting determined that mechanical binding within the motor sporadically increased the running current, which tripped the thermal overloads. An engineering evaluation later determined that the non-functional Core Spray Room Cooler Fan rendered the Loop I Core Spray subsystem inoperable from May 29, 2020 until July 12, 2020, which is longer than allowed by Technical Specification (TS) 3.5.1, “Emergency Core Cooling Systems (ECCS) -- Operating”. On June 13, 2020 a planned surveillance rendered the Loop II Core Spray System inoperable. This resulted in a period of time with both Loops I and II of the Core Spray System concurrently inoperable resulting in a Safety System Functional Failure (SSFF) of systems that are needed to mitigate the consequences of an accident. As a corrective action, the motor, thermal overloads, temperature switch, and starter coil were replaced. As a corrective action to prevent recurrence, BFN is creating a new Preventative Maintenance (PM) to measure the motor current readings to the thermal overloads every two years, during the summer months when the fan is in high use. This will detect possible changes in continuous running current prior to overcurrent trips or motor damage. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 2 05000260 NUMBER NO. 2020 - 001 - 00 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN) Unit 2 was in Mode 1 at approximately 100 percent power. II. Description of Event A. Event Summary On July 1, 2020, at 2240 Central Daylight Time (CDT), the motor thermal overloads [TS] associated with the 2A Core Spray Room Cooler Fan (BFN-2-FAN-064-0072) [FAN] were found tripped during the performance of a surveillance test. This trip prevented the fan from starting. The breaker [BKR] was not tripped, and was found still in the "on" position. This resulted in the inoperability of the 2A and 2C Core Spray pumps [P], which the fan supported, and rendered the Loop I Core Spray system inoperable. Operators were dispatched to reset the thermal overloads, and the room cooler fans started without resetting the breaker. The thermal overloads were replaced on July 2, 2020 at 2010 CDT. An engineering evaluation determined that the thermal overload replacement provided a reasonable assurance of restoring and maintaining operability in the absence of contrary information. After a recurrent trip on July 6, 2020, the breaker was reset and instrumentation was installed to determine the cause of the trip. This additional troubleshooting determined that mechanical binding within the motor [MO] was sporadically increasing the running current, and tripping the thermal overloads. This challenged the previous assumption of operability. An engineering evaluation later determined that the 2A Core Spray Room Cooler Fan had been inoperable since May 29, 2020. Operators declared the 2A Core Spray Room Cooler functional, and the 2A and 2C Core Spray pumps and Loop I Core Spray system operable on July 12, 2020, after replacing the motor, thermal overloads, temperature switch, and starter coil. Technical Requirement Manual (TRM) 3.3.3.2, Low Pressure ECCS Area Cooler Instrumentation, states that the non-functionality of the Core Spray Area Cooler Fan Thermostat Instrument Channel is a requirement for Core Spray system [BM] operability. Additionally, Technical Specification (TS) 3.5.1, ECCS – Operating, requires that each Emergency Core Cooling System (ECCS) injection/spray subsystem shall be operable when BFN, Unit 2 is in Modes 1, 2 and 3. An engineering evaluation determined that the Low Pressure ECCS Area Cooler Instrumentation was non-functional between May 29, 2020 and July 12, 2020, and incapable of performing its required safety function. This resulted in the inoperability of the 2A and 2C Core Spray pumps, which rendered the BFN, Unit 2 Loop I Core Spray system inoperable for longer than permitted by TS 3.5.1. | ML20244A273
Watts Bar Nuclear Plant | Unit 1 | Control Room Emergency Ventilation System Inoperable due to Main Control Room Door Being Left Open | 09-10-2020 | At 0835 Eastern Daylight Time (EDT) on July 15, 2020, a Main Control Room (MCR) alarm was received for low control room positive pressure. In response to the alarm, a Control Room Envelope (CRE) door was found ajar and immediately closed. Technical Specification Limiting Condition for Operation (LCO) 3.7.10, Control Room Emergency Ventilation System (CREVS), was declared not met for both trains and Condition B entered. At 0839 EDT on July 15, 2020, the alarm cleared, CREVS was declared operable and LCO 3.7.10, Condition B was exited. This event was caused by a human performance error when an individual traversing the control building complex did not fully challenge and ensure a MCR envelope boundary door was properly latched and secured. The open control room door was identified and promptly closed. The worker was coached. Actions to prevent recurrence include briefing affected work groups, developing a video on door operation and to establish a dynamic learning activity for contract personnel that will be part of outage training. This condition is being reported as an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident in accordance with 10 CFR 50.73(a)(2)(v)(D). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Watts Bar Nuclear Plant, Unit 1 05000-390 NUMBER NO. 2020 - 003 - 00 | I. Plant Operating Conditions Before the Event Watts Bar Nuclear Plant (WBN) Unit 1 and Unit 2 were in Mode 1 at 100 percent rated thermal power (RTP). II. Description of Event A. Event Summary At 0835 Eastern Daylight Time (EDT) on July 15, 2020, a Main Control Room (MCR) alarm was received for low control room positive pressure. In response to the alarm, a Control Room Envelope (CRE) door {EIIS:DR} was found ajar and immediately closed. Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.10, Control Room Emergency Ventilation System (CREVS) {EIIS:VI}, was declared not met for both trains and Condition B entered. At 0839 EDT on July 15, 2020, the alarm cleared, CREVS was declared operable and LCO 3.7.10, Condition B was exited. This event is being reported to the Nuclear Regulatory Commission (NRC) under 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event No inoperable structures, systems, or components contributed to this condition. C. Dates and approximate times of occurrences Date Time Event (EDT) 7/15/20 0835 Received MCR alarm 105-B and 106-B [MCR HVAC System A/B Abnormal]. In response to the alarm, Units 1 and 2 entered TS LCO 3.7.10, Control Room Emergency Ventilation System, CREVS, Condition B for one or more CREVS trains inoperable due to an inoperable CRE Boundary 7/15/20 0837 Discovered door C036 not fully closed. Door was able to be manually closed and latched. 7/15/20 0839 MCR Alarm 105-B and 106-B are clear. Units 1 and 2 exited TS LCO 3.7.10, CREVS, Condition B due to annunciators 105-B and 106-B clearing. CR 1622991 written to document the unplanned LCO entry. | ML20254A015
Nine Mile Point | Unknown Unit | Failure to Meet Technical Specification MSIV Stroke Times | 05-05-2020 | On March 6, 2020 while at 0% power and in Cold Shutdown (Mode 4), Nine Mile Point Unit 2 determined through surveillance testing that three Main Steam Isolation Valves did not to meet their Technical Specification (Tech Spec) closure time of less than 5 secs. Two of the three valves are in a common Main Steam Line. This event is reportable under 10 CFR 50. 73(a)(2)(v)(C) and 10 CFR 50. 73(a)(2)(vii) for the failure of two MSIVs in a common line not meeting Technical Specification MSIV Stroke Times. The cause of the MSIV failures has been determined to be delayed air pack response. The delay was caused by a buildup of corrosion product and waxy foreign material believed to be dried pipe thread sealant or O-ring assembly lube that accumulated on the internal surfaces of the air pack during refurbishment by the vendor Trillium (previously Hiller). This report also is intended to satisfy the reporting requirements of 10 CFR Part 21. NRC FO.RM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: BO hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currenUy valid 0MB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRG may not conduct or sponsor, and a peison is not required to respond to, the information http:// www.nrc.gov/readi ng-rm/doc-collections/nu regs/staffl s r1 022/r3/l collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Nine Mile Point Unit 2 05000410 NUMBER NO. 2020 - 002 01 | I. DESCRIPTION OF EVENT A. PRE-EVENT PLANT CONDITIONS: Prior to the event, Nine Mile Point Unit 2 (NMP2) was in the Cold Shutdown Condition conducting its scheduled refueling outage. On March 6th , surveillance procedure N2-OSP MSS-CS001 was begun to meet the requirements of Tech Spec Sections 3.6.1.3.7 and 5.5.6 to verify the full closure time of the MSIVs is between 3.0 and 5.0 seconds. B. EVENT: On March 6, 2020 during the performance of the two-year surveillance procedure to verify .MS IV-stroke times, -it was determined that _three of eight MSIVs (2MSS* AOV6A,--- 2MSS* AOV6D and 2MSS*AOV7A) were "slow" in that they failed to meet their maximum Tech Spec required closure time of 5.0 seconds. As a result, Operations declared the three MSIVs inoperable. NMP2 is designed with four Main Steam Lines. Two of the three valves (2MSS*AOV6A and 2 MSS* AOV7 A) are the inboard and outboard isolation valves on the common Main Steam Line A. Troubleshooting was conducted during the refueling outage that inspected for oil leaks from the dashpots, nitrogen check, checked for loose/broken speed control needle valves, and checked for loose/broken air fittings and SOVs. No adverse conditions were identified. The air packs for the valves were replaced and the MSIVs tested satisfactory in accordance with the maximum 5.0 second requirement of Tech Spec 3.6.1.3.7. The air packs were sent for 1· examination by the vendor for further casual determination. Nine Mile Point Unit 1 (NMP1) was unaffected by the three MSIVs being declared inoperable at NMP2. Since the plant was in Mode 4 when MSIVs are not required to be operable per the Tech Specs, no ENS notification was required .. This_event has been entered into the plant's corrective action program as IR 4324557. C. INOPERABLE STRUCTURES, COMPONENTS, OR SYSTEMS THAT CONTRIBUTED TO THE EVENT: No other systems, structures, or components contributed to this event. | ML20255A078
Quad Cities Nuclear Power Station | Unit 2 | Oscillation Power Range Monitors (OPRMs) Count Setpoint Discrepancy Due to Inadequate Instructions | 09-17-2020 | On July 22, 2020 during the performance of an Oscillation Power Range Monitor (OPRM) time test it was identified that the as- found OPRM maximum confirmation count setpoint on the Unit 2 OPRMs did not match the values in the Quad Cities Unit 2 Core Operating Limits Report (COLR). All Unit 2 OP RMS were declared inoperable at 1030 on July 22, 2020. Operations entered Technical Specification (TS) 3.3.1.3 Condition A for OPRMs 1-8 and Condition B for loss of trip capability. The setpoint discrepancy was corrected and all the Unit 2 OPRMs were declared operable on July 23, 2020 at 1210. TS 3.3.1.3 Condition A and Condition B were exited at that time. The cause of the incortect OPRM count setpoint was due to insufficient work package guidance and a lack of verification to ensure that the work instructions contained the proper setpoints. This is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), operation or condition prohibited by Technical Specifications, 1O CFR 50. 73(a)(2)(v)(D), event or condition that could have prevented fulfillment of a safety function, and 1 O CFR 50. 73(a)(2)(vii), common cause inoperability of independent trains or channels. No 10 CFR 50. 72 report was made for this event. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch {T-6A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov. and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission. 72517th Street NW, Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www. nrc.qov/reading-rm/doc-collections/nuregs/staff/sr1 022/r30 requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Quad Cities Nuclear Power Station Unit 2 05000- 265 NUMBER NO. 2020 - 003 00 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Oscillation Power Range Monitors (OPRMs) Count Setpoint Discrepancy Due to Inadequate Instructions A. CONDITION PRIOR TO EVENT Unit: 2 Event Date: July 22, 2020 Event Time: 1030 hours CDT Reactor Mode: 1 Mode Name: Power Operation Power Level: 100% There were no other structures, systems or components (SSC) inoperable during this event time period that could have contributed to this event. B. DESCRIPTION OF EVENT During the Q2R25 refueling outage (April 2020), all Unit 2 Oscillation Power Range Monitor (OPRM) Trip Amplitude Setpoints were updated per Quad Cities Unit 2 Core Operating Limits Report (COLR) Rev 13. The work order (WO) written to update the OPRM setpoints only directed an update to the amplitude setpoint. There were no instructions to update the confirmation count setpoint. During the refueling outage the Quad Cities Unit 2 COLR was emergently changed to Rev 14, however this revision did not change any OPRM setpoint values. On July 22,2020 at 1030 CDT, while performing an OPRM response time test, it was identified that the as-found OPRM maximum confirmation count setpoint on the Unit 2 OPRMs did not match the value in the Quad Cities Unit 2 COLR. The setpoint was found to be set at 16 counts to trip but per the COLR it should have been set at 15 counts. All Unit 2 OPRMs were declared inoperable. Operations entered Technical Specification (TS) 3.3.1.3 Condition A for OPRMs 1 through 8 and Condition B for loss of trip capability. The setpoint discrepancy was entered into the corrective action program and corrected under a work order (WO). All the Unit 2 OPRMs were declared operable on July 23, 2020 at 1210 CDT. TS 3.3.1.3 Condition A and Condition B were exited at that time. There were no other safety systems or components inoperable at the time of this event. This is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B),operation or condition prohibited by Technical Specification for having incorrect confirmation count setpoint and 10 CFR 50.73(a)(2)(vii), common cause inoperability of independent trains or channels since the incorrect setpoint caused all Unit 2 OPRMs to be declared inoperable. During evaluation of the event, it was determined that 10 CFR 50. 73(a)(2)(v)(D), event or condition that could have prevented fulfillment of a safety function also applies. NRG FORM 366A (08-2020) Page _2_ of _4_ | ML20261H588
Brunswick Steam Electric Plant (BSEP) | Unit 1 | Automatic Specified System Actuations due to Loss of Offsite Power | 09-21-2020 | At 23:02 Eastern Daylight Time on August 3, 2020, with Unit 1 in Mode 1 at approximately 19% power during Hurricane Isaias, a loss of the transformer bus powering the Startup Auxiliary Transformer (SAT) resulted in a Loss of Offsite Power (LOOP). By design, all Main Steam Isolation Valves closed and an automatic reactor scram occurred. All control rods inserted as expected on the scram. At the time of this event the main generator was removed from service due to unrelated generator ground issues and all plant loads were being supplied by the SAT. By design, the LOOP resulted in automatic actuation of Primary Containment Isolation System (PCIS) Group 1, 2, 3, 6, and 8 isolation valves. In addition, all four emergency diesel generators (EDGs) started, with EDGs 1 and 2 loading to their respective emergency buses per design. Reactor water level reached low level 1 following the scram resulting in automatic actuation of PCIS Groups 2, 6, and 8, by design. The electrical fault that caused the transformer bus powering the SAT to trip and subsequent LOOP was determined to be a result of storm generated debris. There was no impact on the health and safety of the public or plant personnel. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) due to valid actuation of the Reactor Protection System, PCIS, and EDGs. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant (BSEP), 05000- 325 YEAR NUMBER NO. Unit 1 2020 - 003 - 00 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. Background Initial Conditions At the time of the event, Unit 1 was in Mode 1 (i.e., Power Operation), at approximately 19 percent rated thermal power. Unit 2 was in Mode 1 (i.e., Power Operation), at approximately 100 percent rated thermal power. Reportability Criteria This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) because it involved actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B). Specifically, the Reactor Protection System (RPS) [JC], Primary Containment Isolation System (PCIS) [JM], and the Emergency Diesel Generators (EDGs) [EK] actuated during this event. Per 10 CFR 50.72(a)(1)(i), the NRC was notified of an Unusual Event (UE) being declared via Event Notification 54812 at 23:31 Eastern Daylight Time (EDT) on August 3, 2020. The NRC was notified of the RPS [JC] actuation while critical and the valid specified system actuations per 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A), respectively, via an update to Event Notification 54812 at 01:20 EDT on August 4, 2020. Event Description At 23:02 EDT on August 3, 2020, with Unit 1 in Mode 1 at approximately 19% power during Hurricane Isaias, a loss of the transformer bus powering the Startup Auxiliary Transformer (SAT) [EA] resulted in a Loss of Offsite Power (LOOP). By design, all Main Steam Isolation Valves (MSIVs) [JM] closed and an automatic reactor scram occurred. All control rods inserted as expected on the scram. At the time of this event the main generator was removed from service and all plant loads were being supplied by the SAT. Power had been lowered to 19% prior to the event in preparation for shutting down for maintenance associated with unrelated generator ground issues. By design, the LOOP resulted in automatic actuation of Primary Containment Isolation System (PCIS) Group 1 (i.e., main steam), Group 2 (i.e., floor and equipment drain), Group 3 (i.e., reactor water cleanup), Group 6 (i.e., monitoring and sampling), and Group 8 (i.e., shutdown cooling) isolation valves. In addition, all four emergency diesel generators (EDGs) started, with EDGs 1 and 2 loading to their respective emergency buses per design. Reactor water level reached low level 1 following the scram resulting in automatic actuation of PCIS Groups 2, 6, and 8, by design. At 23:12 EDT on August 3, 2020, Unit 1 declared a UE due to the LOOP. The UE was exited at 14:54 on August 4, 2020. Event Cause Extensive investigation and testing concluded that the electrical fault that caused the transformer bus powering the SAT to trip and subsequent LOOP was not a result of an equipment failure. The fault was determined to be a result of storm generated debris from Hurricane Isaias. Safety Assessment There was no adverse impact on the health and safety of the public. The safety significance of this event is minimal. The automatic reactor trip was as expected, and all safety related systems operated as designed. | ML20265A162
Nine Mile Point | Unit 1 | Control Room Air Treatment System Inoperable | 09-15-2020 | On May 3, 2020 at 17:50 while at 100% power in Mode 1, Nine Mile Point Unit 1 (NMP1) discovered that the fan bearing of the Control Room Ventilation Circulation Fan was inoperable. Upon investigation of a step change in noise from the Control Room Ventilation Circulation Fan, maintenance discovered that the fan bearing had failed. Since the fan is a single component (supported by redundant motors), the Control Room Air Treatment System (CRATS) was in a condition that could have prevented the fulfillment of its safety function. Therefore, this condition is reportable under 1O . CFR 50. 73(a)(2)(v)(D) as any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: (D) Mitigate the consequences of an accident. The #11 fan pillow block bearing, #11 motor sheave and key were replaced, and the system was restored to operable on May 8· 2020 at 20: 11 . NRG FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2020 (04-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Collections Branch (T-5 F53), U.S. Nuclear Regulatory LICENSEE EVENT REPORT (LER) Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, NEOB-10202, (3150-0104), Office of CONTINUATION SHEET Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid 0MB control number, the NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, the information collection. http://www.nrc.gov/reading-rm/doc-collections/nureqs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Nine Mile Point Unit 1 05000220 NUMBER NO. 2020 - 001 01 | I. DESCRIPTION OF EVENT A. PRE-EVENT PLANT CONDITIONS: Prior to the event, Nine Mile Point Unit 1 (NMP1) was in the power operating condition at 100% power. The Control Room Air Treatment System was operable with #11 motor for the Circulation Fan in service and the #12 motor in standby. B. EVENT: On May 3, 2020, at approximately 11 :00 hours, control room operators detected a step change in Control Room Ventilation Circulation Fan/Motor #11 noise level and vibrations. The circulation fan configuration is a single fan with a drive motor (#11 and #12) on either end of the fan shaft. The two motors are connected to the blower shaft with belts on either end of the shaft. This fan is located inside a sealed plenum and as such is not able to be visually inspected while in service. Operators swapped from Control Room Circulation Fan #11 motor to the #12 motor, but the noise continued after the motor swap until the fan was secured. The station entered an unplanned seven (7) day Limiting Condition for Operation per Technical Specifications 3.4.5.e at 11 :18 hrs for an inoperable Control Room Air Treatment System and the alternate control room ventilation system (Smoke Purge Removal) was placed into service. At 1750, Maintenance technicians entered the ventilation plenum to perform a visual inspection of the equipment. The visual inspection identified that the pillow block fan bearing had failed, rendering the fan inoperable for both motors. The pillow block bearing was replaced. Additionally, during post maintenance testing mechanics identfied that the #11 motor shaft/key/sheave engagement was not adequate, allowing the sheave rotational and angular movement. The #11 fan pillow block bearing, #11 motor sheave and key were replaced. The fan with its two redundant motors was reassembled, successfully passed post maintenance testing and the system restored to operable on May 8, 2020. Nine Mile Point Unit 2 (NMP2) was unaffected by the event. Operations performed the ENS notification (#54692) required by 10 CFR 50.72(b)(3)(v)(D) for, "Any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: (D) Mitigate the consequences of an accident." This event has been entered into the plant's corrective action program as IR 4340639. NRG FORM 366A (04-2020) Page _· _2_ of _5_ | ML20269A248
Brunswick Steam Electric Plant (BSEP) | Unit 1 | Setpoint Drift in Main Steam Line Safety Relief Valves Results in Three Valves Inoperable | 09-29-2020 | On August 12, 2020, BSEP received test results for the eleven main steam line safety relief valves (SRVs) removed from Unit 1 during the spring 2020 refuel outage (RFO). Three of the eleven valves were found to have as found pilot valve lift setpoints outside the +/-3 percent tolerance required by Technical Specification (TS) 3.4.3, which requires ten of the eleven installed SRVs to be operable. Since less than ten SRVs were operable, this event is being reported per 10 CFR 50.73(a)(2)(i)(B) as operation prohibited by the plant’s TS. At the time the test results were received, Unit 1 was shutdown for an unrelated maintenance outage. The direct cause of the out of tolerance as-found lift setpoints was corrosion bonding of the SRV pilot discs to the pilot seats. The root cause of the corrosion bonding was inadequate procedures in place when these valves were refurbished and installed in the 2018 RFO. Subsequent to the 2018 installation of these SRVs, as a result of the Root Cause Evaluation associated with LER 1-2018-003, dated August 9, 2018 (i.e., ADAMS Accession Number ML18221A552), corrective actions were completed revising the associated procedures to prevent this condition from recurring. All eleven of the SRV pilot valves were replaced with certified spares before Unit 1 startup from the spring 2020 RFO. These spares were rebuilt utilizing the revised procedures. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant (BSEP), 05000- 325 YEAR NUMBER NO. Unit 1 2020 - 004 - 00 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. Background Initial Conditions At the time of the event, Unit 1 was in Mode 4 (i.e., Cold Shutdown), for an unrelated maintenance outage. Reportability Criteria Unit 1 Technical Specification (TS) 3.4.3 requires at least ten of eleven main steam [SB] line safety relief valves (SRVs) to be operable. Per Surveillance Requirement (SR) 3.4.3.1, each valve is required to open within +/- 3 percent of its opening setpoint. As- found testing of the valves indicated that three of the valves had lift setpoints outside this tolerance. Consequently, the plant operated in a condition which is prohibited by the TS, that is, with fewer than the required number of SRVs having lift setpoints within the +/-3 percent tolerance. Therefore, the condition is being reported per 10 CFR 50.73(a)(2)(i)(B) as operation in a condition prohibited by the plant TSs. Event Description During the spring 2020 Unit 1 refueling outage, all eleven pilot valve assemblies in the SRVs were replaced with certified spares. The removed SRV pilot valves were sent to National Technical Systems (NTS) to determine the as-found set pressure. On August 12, 2020, test results were reported to BSEP. The test results showed that three of the eleven valves actuated at pressures outside of the +/-3 percent tolerance allowed by TS 3.4.3. Specifically, all three of the valves that lifted outside of the tolerance, lifted at greater than +3%. Event Cause The change in SRV lift setpoints resulted from corrosion bonding of the SRV pilot discs-to-the pilot seats. Corrosion bonding between the pilot disc and seat is an inherent problem with the two-stage SRV design used at BSEP. BSEP mitigates corrosion bonding of SRVs by coating each pilot disc surface with platinum. The integrity of the platinum coating is critical to mitigating corrosion bonding. The platinum coating of these SRVs was found to be degraded in large areas of the pilot disc, including the seating surface; which was determined to be caused by circumferential machining marks in the substrate surface that led to increased circumferential cracking of the platinum coating. The root cause was attributed to the procedures in place when these valves were refurbished and installed in the 2018 refueling outage lacking sufficient detail to ensure consistent surface preparation and proper quality checks of surface condition prior to platinum coating. Safety Assessment The purpose of the SRVs is to provide overpressure protection for the reactor coolant system. The as-found condition of the Unit 1 SRVs was compared to cases analyzed in the Brunswick Unit 1 Cycle 22 Reload Safety Analysis Report (RSAR). Each as-found SRV was bounded by the opening pressures assumed in the analysis; therefore, the overall RSAR analysis bounds the overall as- found condition of the SRVs. The results from the RSAR analysis demonstrate that the pressure limits are not exceeded for the overpressurization events. Therefore, it is concluded that the Unit 1 Cycle 22 SRVs always remained capable of performing their safety function of preventing overpressurization of the reactor coolant system. Based on the foregoing analysis, it is concluded that this event had no adverse impact on nuclear safety. | ML20274A324
McGuire Nuclear Station | Unit 1 | Condition prohibited by Technical Speclflcatlon 3.4.15, Reactor Coolant System (RCS) Leakage Detection Instrumentation | 06-29-2020 | On June 29, 2020 with Unit 1 In Mode 1 at.approximately 100 percent power and Unit 2 in Mode 1 at approximately 100 percent power, McGuire detennined that Revision O of calculation MCC-1223.15-01-0015, Containment Floor and Equipment Sumps Volume Calculation, contained non-conservative assumptions that would have prevented the containment floor and equipment (CFAE) sump level monitors from detecting and alarming on a one gallon per minute input within one hour. Revision O of calculation MCC-1223.15-01-0015 was approved for use on April 15, 1994. Discovery of the non-conservative assumptions in Revision O of calculation MCC-1223.15-01-0015 resulted in a condition prohibited by Technical Specification (TS) 3.4.15, Reactor Coolant System (RCS) Leakage Detection Instrumentation, since the CFAE Sump Monitors for both Units was determined to be inoperable for longer than allowed by the TS 3.4.15 Limiting Condition for Operation (LCO) action statements. No causal analysis was performed due to the legacy nature of Revision O of calculation MCC-1223.15-01-0015. An Engineering Change has been implemented to Insert the revised containment floor and equipment sump monitor rate of rise set point, from revised calculation MCC-1223.15-01-0015, on the Operator Aid Computer. NRC FORM 300 (04-2020) NRC FORM 368A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3180-0104 EXPIRES: 04l30l2020 (0+2020) Estimated lxm:len per r86p0fl&e to comply wrth tins mandatoly collect!on request 80 hoU re Reported lessoos lea med are mcorporated mto the ltcenslng procellll and fed LICENSEE EVENT REPORT (LER) back to llldustry Send commenl!I regarding burden estimate to the lnforme!Jon SeMC86 Branch (f-6 A10M), U.S. Nuclear Regulatory CommlSSlOn, Wahmgton, DC 20555- CONTINUATION SHEET 0001, or by EHll8ll to lnfocollect8 Resource@nrc gov, and the 0MB ffN'tt!IWt!lf at 0MB Office of lnforma!lon and ~ry Affalra, (3150--0104 ), Attn Desk Officer for the (See NUREG-1022, R 3 for mstruclJon and guidance for completmg this fonn Nuclear Regulatory Commlulon, 725 17th Street NW, Was!unglon, DC 20603, e-mail http /fww:N nrc gov/read1Qg-rm/doc-collectJone{nuregs/staff/sd 022/@ P!Clil subm1ssion1t'f!Qmb eoo ggv The NRC may not conduct Of sponsor, and a pef90ll 111 not requrred to respond to, e coftectlon of mformation unless the document reqoeeting or raauJ1na the collecllon dlADlav9 a currently vahd 0MB control number 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NO. NUMBER McGuire Nuclear StatJon 05000369 2020 01 00 | BACKGROUND The following infonnation Is provided to assist readers in understanding the event described In this LER. Applicable Energy Industry Identification [EIIS] System and component codes are enclosed within brackets. McGuire Nuclear Station unique system and component identifiers are contained within .parentheses. n. Liquid Waste Recycle [WO] (WL}, [LIT] (L Containment Floor and Equipment (CFAE;) Sump Level Monitors The CFAE Sump Level Monitors function by taking the CFAE sump level change, rate•of rise, as measured by the level transmitters (1/2WLLT5250 and 5260) and calculated by the Operator Aid Computer to provide indication in the Control Room of possible leakage from Reactor Coolant System [AB] (NC), Main Steam System [SB] (SM), Main Feedwater System [SJ] (FW), or Auxlliary Feedwater System [BA] (CA). The sump level monitor Is capable of detecting a 1 gpm leak In 1 hour. The sensitivity Is based upon the ability of the sump level Indication to sense a change in level of 1/4 Inch and the following assumptions • Sump level Indication is between 5. 75 to 17 Inches • Sump level indication moves in quarter-inch increments • Operator Aid Computer rate alarm set at 0.0167 in/min Operator Ald Computer [ID] (IKE) The Operator Aid Computer System (OAC) at the McGuire Nuclear Station Is a non-QA system used to monitor parameters and events in various plant systems and to provide data and alanns to the Control Room Operators and other station personnel. The daw and alarms provided by the OAC are Important to the Control Room Operators' ability to perform routine surveillances and other required activities during nonnal operation, as well as to respond quickly to changing plant conditions during transients and abnormal events. The OAC perfonns the CFAE Sump Level Monitor function as described below. CFAE Sump Level Instrumentation Is used to monitor changes in level due to Inputs and/or pump downs of the sump as necessary. To convert the change in sump level values Into units that can be directly correlated to leakage, OAC algorithms were developed. The algorithms are based on functional relationships (e.g. geometry and mathematics) and rate of change transform calculations. The algorithm uses standard computer point types and predefined transform and logic functions on the OAC to convert the level Instrumentation signals for comparison against a calculated threshold. The output of the algorithm Is a displayed rate value for both sumps that is updated every minute on the OAC. The algorithm Includes rate alarm logic which is processed every 5 seconds. The OAC alann threshold is selected to detect a total Jeakage rate change of 1 GPM within one hour. Page2 of4 | ML20304A152
cooper nuclear station | Unknown Unit | Secondary Containment Differential Pressure Perturbation Results in Potential Loss of Safety Function | 10-15-2020 | On October 6, 2020, a spike in Secondary Containment differential pressure occurred exceeding the Technical Specifications limit of -0.25 inch of water gauge causing Secondary Containment to be inoperable for 3 minutes. The spike was due to a Reactor Building heating, ventilation, and air conditioning vortex damper that was binding and had an air leak in an associated instrument tubing. Causal factors were an elevated operating force necessary to reposition the vortex damper and an air-line leak that developed due to contact between instrument tubing and a support brace. The instrument tubing for the vortex damper was replaced and rubber material placed to prevent contact with the support brace. In addition, action will be taken to reroute the instrument tubing. Maintenance was performed to reduce the closing forces of the vortex damper. Maximum acceptable opening and closing forces will be determined and maintenance plans updated. There was no impact on nuclear safety, plant reliability, radiological safety, or industrial safety. NRC FORM 366 (08-2020) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 31~1().4 EXPIRES: 08/31/2023 (('6-2020) conw Eslll11ated burden per response to wl1l1 this m<11daby colectroo request. 80 hours. Reported lessons leaned a-a mcorporated mto the hcensiflg process and fed ba;k to 1ndustry Send comments LICENSEE EVENT REPORT (LER) regardmg bl.l"doo eslrnale to Iha FO!A, I.Jbrary, 811d lnformaoon Collecbons Braich (T-6 A10M), Us Nucla.I" Regulatory Corrmssron, Wash1ngton, DC 20555-0001, or by e-marl to CONTINUATION SHEET lnfocollects Resoorce@nrc gov, and the 0MB reviewer at 0MB Office of lnformallon "1d Regulatory AffaJrs. (3150-0104), Attn Desk arl orra subrrmiooC)omb 00D goy The NR C may not conduct or (See NU RE G-1 022, R 3 for 1nstrucbon and guidance for com pl etmg this form sponsor, and a person is noi requred lo respood to, a collecboo of mfornmon unless the document https·/tw,w,,.nrc.goy/readl{)g-rrn/doc-collecbons/mregs/staff/sr1022/r3{) requestmg or requmng the collecilon displays a currently vwd 0MB control nurrt>er 1. FACILITY NAME 2 DOCKET NUMBER 3. L.ERM.MBER YEAR SEQUENTIAL REV Cooper Nuclear Station 05000-298 NUMBER NO 2020 - 002 - 00 | PLANT STATUS Cooper Nuclear Station was in Mode 1, Power Operation, at 100 percent power at the time of the event on August 6, 2020. BACKGROUND Secondary Containment serves as a barrier to confine and monitor potential releases during fuel handling operations and is a system that limits the release of radioactive materials to the environment and consists of four subsystems. One of the subsystems is the Reactor Building [EIIS: NG], which encloses the Reactor Pressure Vessel [EIIS: RPV] and Primary Containment [EIIS: NH]. The secondary containment area (most of the Reactor Building) has supply and exhaust ventilating systems. The supply system furnishes filtered 100% outdoor air to all floors of the building through ductwork. The supply unit has an operating and standby ( 100% capacity) fan with vortex dampers [COMP] to provide regulation of air capacity. The fans will deenergize in the event of loss of offsite power. The exhaust air is induced from the ventilated areas to a common plenum connected to the two exhaust fans, each of 100% capacity. The air is then exhausted to the atmosphere. During normal plant operation, a minimum average negative pressure of 0.25 inches water gauge (wg) is maintained by differential pressure controllers which receive signals proportional to the pressure difference between outside air and the secondary containment atmosphere, and control the position of the exhaust fan vortex dampers. The differential pressure is detected by four separate probes, with one on each side of the Reactor Building. Control action is initiated from the average value of the four sensor probes. If a Loss of Coolant Accident should occur, all ventilation systems of the primary containment area and secondary containment area will be isolated automatically, and the Standby Gas Treatment system will be automatically initiated. EVENT DESCRIPTION On August 6, 2020, at 1355, the Control Room received a computer alarm for Reactor Building differential pressure exceeding -0.25 inches wg and a change was noted on the Reactor Building differential pressure recorder. Personnel were dispatched to walk down the Reactor Building ventilation and Reactor Recirculation Motor Generator ventilation systems. No equipment deficiencies were identified during the walkdowns and Reactor Building differential pressure returned to normal without operator action after approximately three minutes. Operations personnel reviewed meteorological data including wind speed, wind direction and barometric pressures and concluded meteorological changes were enough to cause the momentary transient. Technical Specifications Surveillance Requirement (SR) 3.6.4.1.1 basis considers momentary transient due to gusty wind conditions acceptable and are not a cause for failure to meet the Surveillance Requirement. On August 13, 2020, at 1500, Operations personnel identified an unexplained rise in Reactor Building pressure. Pressure rose from -0.34 inches wg to just below -0.25. inches wg. A review of this event NRC FORM 366B (06-2020) Page 2 of 4 | ML20304A209
Susquehanna Steam Electric Station | Unit 2 | Manual Scram Due to Rising Main Condenser Backpressure Caused by Failure of an Offgas Recombiner Inlet Valve | 08-31-2023 | On February 14, 2020 at 00:25, Susquehanna Steam Electric Station (SSES) Unit 2 reactor was manually scrammed due to rising Main Condenser backpressure caused by a loss of the Unit 2 Offgas Recombiner. This event was reported by Notification EN 54525 in accordance with 10 CFR 50. 72(b)(2)(iv)(B) and (b)(3)(iv)(A). This event is also reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a manual actuation of the Reactor Protection System (RPS) (including reactor scram), as well as associated isolation and actuation of other systems listed in 10 CFR 50. 73(a)(2)(iv)(B), including the Reactor Core Isolation Cooling (RCIC) system. The most probable cause was an inadvertent closure (drifting closed) of the Unit 2 Offgas Recombiner System Inlet Control Valve. Stroking, disassembly, reassembly, and air operated valve diagnostics alleviated the cause of the inadvertent closure. There were no actual safety consequences associated with the condition. U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to Industry. Send comments LICENSEE EVE NT REPORT ( LE R) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: olra submlsslon@omb.eop.gov. The NRC may not conduct or (See NUREG-1 022, R.3 for instruction and guidance for completing this form sponsor, and a person Is not required to respond to, a collection of information unless the document https:/lwww.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1 022/r3D requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LERNUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station Unit 2 05000-388 NUMBER NO. 2020 001 01 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, approximately 86 percent Rated Thermal Power Unit 2 - Mode 1, approximately 98 percent Rated Thermal Power Loss of the Unit 2 Offgas Recombiner caused rising Main Condenser backpressure, which resulted in the need for a manual scram. EVENT DESCRIPTION On February 14, 2020 at 00:25, Susquehanna Steam Electric Station Unit 2 reactor was manually scrammed due to rising Main Condenser [EllS System Code/Component Code: SG/COND] backpressure caused by a loss of the Unit 2 Offgas Recombiner [EllS System/Component Code: WF/RCB]. Following is a timeline of the events associated with the scram: February 14, 2020 at approximately 00:12- Unit 2 Offgas Recombiner OC145 Panel Trouble and 2C198 Hydrogen Water Chemistry Panel Trouble alarms were received along with indication of rising Main Condenser backpressure. Initial Main Condenser backpressure was 2.6 inches HgA (Mercury Absolute) and was rising at approximately 0.3 inches HgA/minute. February 14, 2020 at approximately 00:15- A Recirculation Limiter 2 run back was inserted to lower reactor power. Main Condenser backpressure continued to rise following the reduction in reactor power. February 14, 2020 at approximately 00:25-A manual scram was inserted by placing the Reactor Mode Switch to Shutdown when Main Condenser backpressure rose to 6 inches HgA. All control rods inserted. Reactor water level lowered to -30 inches causing a Level 3 (+13 inches) isolation and a partial (Division 2) Level 2 (-38 inches) isolation. The Reactor Core Isolation Cooling (RCIC) system [EllS System Code: BN] actuated as expected for given plant conditions. Operators subsequently maintained reactor water level at the normal operating band using the Reactor Feed Water system [EllS System Code: SJ]. No steam relief valves [EllS System/Component Code: SB/RV] opened. The Reactor Recirculation Pumps [EllS System Code/Component Code: AD/P] remained in service. This event was reported by Notification EN 54525 in accordance with 10 CFR 50.72(b)(2)(iv)(B) and (b)(3)(iv)(A). This event is also reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a manual actuation of the Reactor Protection System (RPS) (including reactor scram), as well as associated isolation and actuation of other systems listed in 10 CFR 50. 73(a)(2)(iv)(B), including RCIC. CAUSE OF EVENT The most probable cause was an inadvertent closure (drifting closed) of the Unit 2 Offgas Recombiner System Inlet Control Valve (HV26912) [EllS System/Component: WF/FCV]. Indications, system responses, and troubleshooting narrowed the failure to HV26912 inadvertently drifting closed, resulting in increased Main Condenser backpressure and the stalling of the Steam Jet Air Ejector [EllS System/Component Code: SH/EJR]. | ML20310A258
Quad Cities Nuclear Power Station 05000-0254 1 OF 4 | Unknown Unit | Main Steam Line Drain Valve Declared Inoperable Due to Improper Torque Switch Setting | 11-10-2020 | On July 1, 2020 and July 23, 2020, engineering identified the torque switch setting on the Unit 2 and Unit 1 Main Steam Line (MSL) outboard drain (1(2)-0220-2) motor operated valves (MOV) were found to be nonconservative with respect to the valve's design function under the expected worst-case operating conditions. Both valves were initially evaluated and declared operable because the valve was closed (safety function position) and was not required to be opened during the normal two-year operating cycle. On September 11, 2020 at 1100 CDT, Operations determined that although the valves were performing their isolation function, operability was no longer supported and the MSL outboard drain valves were declared inoperable. This issue is being reported under 1OCFRSO.73(a)(2)(i)(B) for any operation or condition which was prohibited by the plant's Technical Specifications (TS) because TS 3.6.1.3 Action Statement A.1 was not completed within the required time in July 2020 during the initial discovery of the torque switch setting issue. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 72517th Street NW, Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1 022/r3/} requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Quad Cities 05000- 0254 YEAR NUMBER NO. 2020 002 00 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Main Steam Drain Valve Declared Inoperable Due to Improper Torque Switch Setting A. CONDITION PRIOR TO EVENT Unit: 1&2 Event Date: September 11, 2020 Event Time: 1100 Reactor Mode: 1 Mode Name: Power Operations Power Level: 100% There were no other structures, systems or components (SSC) inoperable during this event time period that could have contributed to this event. B. DESCRIPTION OF EVENT On July 1, 2020, following review of an industry operating experience report, engineering identified the torque switch setting on the Unit 2 Main Steam [SB] Line outboard drain valve [ISV] (2-0220-2) motor operated valve (MOV) was nonconservative with respect to its design function under the expected worst case operating conditions. The cause of as-left torque switch setting being lower than the required value was determined to be a latent error in the calculation used for these valves. The valve was initially called operable with a request for a formal Operability Evaluation (Op Eval), because the valve was closed (safety function position) and was not required to be opened during the normal two-year operating cycle. Revision 00 of the Op Eval, completed on July 7, 2020, provided compensatory actions for the degraded automatic isolation function by revising procedures to have a dedicated operator ready to enter the Main Steam Isolation Valve (MSIV) room to manually ensure full closure of the valve should the valve need to be opened. On July 23,2020, following an extent of condition review, engineering identified that the Unit 1 Main Steam Line outboard drain valve (1-0220-2) MOV torque switch setting was also incorrect. The Op Eval that was written to cover the previously identified Unit 2 valve was revised on August 5, 2020 to include the Unit 1 valve and requested similar compensatory actions. The basis for the Unit 2 valve operability was also applied to the Unit 1 valve. On September 11, 2020 at 1100 CDT, Operations determined that the Op Eval no longer supported operability of the Unit 1 and Unit 2 Main Steam Line outboard drain valves because of an inability to meet Primary Containment Isolation Valve (PCIV) TS surveillance requirements (SR). The affected valves were declared inoperable and Technical Specification 3.6.1.3 Condition A was entered at that time. On | ML20315A447
Brunswick Steam Electric Plant (BSEP) | Unit 1 | Technical Specification Required Shutdown due to Unidentified Leakage | 11-17-2020 | At 12:05 Eastern Daylight Time on March 24, 2020, with Unit 1 in Mode 1, at approximately 22% power, coming out of a refueling outage, a Technical Specification required shutdown was initiated due to increased drywell leakage. The reactor was shutdown in accordance with normal shutdown procedures. Reactor water level reached low level 1 (LL1) following the shutdown. Per design, the LL1 signal resulted in automatic actuation of the Primary Containment Isolation System with closure of Group 2, 6, and 8 isolation valves. The shutdown was uncomplicated and all control rods inserted as expected. The increased drywell leakage was a result of an intermediate-position failure of Safety Relief Valve ‘1F’ in conjunction with opening of the associated vacuum breaker. The cause of this failure was determined to be susceptibility of the Target Rock two stage Safety Relief Valve design to fretting wear of the main disc stem to piston connection when the associated main body is subjected to a high number of cycles during testing, resulting in displacement of the piston and galling in the main body piston guide. Safety Relief Valve ‘1F’ pilot and main valve were replaced and retested upon restart from the reactor shutdown. There was no impact on the health and safety of the public or plant personnel. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(A) due to the completion of a Technical Specification required shutdown, and 10 CFR 50.73(a)(2)(iv)(A) due to valid actuation of the Primary Containment Isolation System. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant (BSEP), 05000- 325 YEAR NUMBER NO. Unit 1 2020 - 002 - 01 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. Background Initial Conditions At the time of the event, Unit 1 was in Mode 1 (i.e., Power Operation), at approximately 22 percent rated thermal power. Reportability Criteria This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(A) because a Technical Specification required shutdown was completed. Technical Specification Action 3.4.4.A, Unidentified Reactor Coolant System (RCS) [AD] leakage increase not within limit, requires RCS leakage to be reduced to within limits within 8 hours. The shutdown was required because the leakage would not have been reduced to within limits within the required Technical Specification Completion Time. In addition, this event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) because it involved actuation of a system listed in 10 CFR 50.73(a)(2)(iv)(B). Specifically, the Primary Containment Isolation System [JM] actuated during this event. The NRC was notified of this event per 10 CFR 50.72(b)(2)(i) and 10 CFR 50.72(b)(3)(iv)(A) via Event Notification 54603 at 16:02 Eastern Daylight Time (EDT) on March 24, 2020. Event Description At approximately 03:24 EDT on March 24, 2020, during startup testing, main steam [SB] Safety Relief Valve (SRV) ‘1F’ was provided an open signal from the control room. Tailpipe temperature trends indicated that the pilot valve opened, but that the main disc failed to properly reposition to complete the cycle. Thus, the pilot valve remained open and passed steam via the tailpipe to the suppression pool. Troubleshooting and other startup testing were ongoing when, at approximately 10:50 EDT, the control room received unexpected indication of 1.6 gallons per minute (gpm) unidentified leakage in the drywell. At approximately 11:54 EDT, a reading of 3.75 gpm was obtained, exceeding the Technical Specification limit of 2 gpm change in unidentified leakage within 24 hours while in Mode 1. As a result, at 12:05 EDT a Technical Specification required shutdown was initiated. The reactor was shutdown in accordance with normal shutdown procedures. Reactor water level reached low level 1 (LL1) following the shutdown. The LL1 signal caused Group 2 (i.e., floor and equipment drain isolation valves), Group 6 (i.e., monitoring and sampling isolation valves), and Group 8 (i.e., shutdown cooling isolation valves) isolations. The LL1 isolations occurred as designed; the Group 8 valves were closed at the time of the event. The shutdown was uncomplicated and all control rods inserted as expected. The SRV ‘1F’ pilot valve reseated with lowering reactor pressure following the shutdown. Event Cause The unidentified leakage was determined to be coming from the SRV ‘1F’ pilot valve through its associated vacuum breaker. The SRV ‘1F’ pilot valve was open because SRV ‘1F’ main body did not open during SRV testing. With the main body stuck shut, the discharge pressure would not lower to the pilot valve reseat pressure to allow it to shut. The SRV ‘1F’ vacuum breaker had remained closed until drywell purge was secured as part of startup activities, at which time the pressure difference between the SRV ‘1F’ discharge line and the drywell caused the vacuum breaker to unseat and steam flow from the open SRV ‘1F’ pilot valve diverted to the Drywell. Unit shutdown resulted in pressure reduction to the pilot valve reseat pressure and the pilot valve closed, terminating the source of unidentified leakage. The cause of this intermediate-position failure of SRV ‘1F’ was determined to be susceptibility of the Target Rock two stage SRV design to fretting wear of the main disc stem to piston connection when the associated main body is subjected to a high number of cycles during testing, resulting in displacement of the piston and galling in the main body piston guide. | ML20322A021
Browns Ferry Nuclear Plant | Unit 1 | Manual Reactor Shutdown of Two Units on Decreasing Condenser Vacuum due to Eel Grass Intrusion | 11-17-2020 | On July 20, 2020, at approximately 0955 Central Daylight Time (CDT), the Unit 1 control room received the traveling screen differential pressure high alarm. Assistant Unit Operators dispatched to the condenser circulating water (CCW) system forebay reported large masses of eel grass. The influx of eel grass resulted in fouling of the trash racks and traveling water screens for all three units which reduced the CCW flows during this event. As a result of degrading condenser vacuum on Unit 2, operators manually scrammed the reactor at 1325 CDT. On July 21, 2020, as Unit 1 condenser vacuum continued to degrade to the turbine trip setpoint, the Unit 1 operators manually scrammed the reactor at 0435 CDT. The root cause of the event is that existing permanently installed plant equipment at the BFN forebay was not adequate to mitigate the newly developed threat presented by large scale eel grass accumulation on Wheeler Lake. The action plan for addressing the root cause of this event has been developed which consists of deciding which equipment upgrades will be the most effective based on studies of river flow and environmental conditions, funding these upgrades, issuing design packages, and implementing the final designs. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 1 05000-259 NUMBER NO. 2020 - 001 - 01 | I. Plant Operating Conditions Before the Event Prior to this event, all three Browns Ferry Nuclear Plant (BFN) Units were in Mode 1 at approximately 100 percent power. II. Description of Event A. Event Summary On July 20, 2020, at approximately 0955 Central Daylight Time (CDT), the Unit 1 control room received the traveling screen [EIIS: SCN] differential pressure high alarm. Assistant Unit Operators (AUOs) dispatched to the condenser circulating water (CCW) system [EIIS: KE] forebay reported large masses of eel grass. The influx of eel grass resulted in fouling of the trash racks and traveling water screens for all three units which reduced the CCW flows during this event. Abnormal Operating Instructions (AOI) 0-AOI-27-1, "Component Biofouling," and 1/2/3-AOI-47-3, "Loss of Condenser Vacuum," were entered as required. Actions were taken to manipulate the CCW pumps and traveling water screens to clear the eel grass. Additionally, reactor power was reduced to compensate for the lowering main condenser [EIIS: SG] vacuum. At 1315, as a result of degrading condenser vacuum on Unit 2, operators began lowering reactor power and as condenser vacuum continued to degrade to the turbine trip setpoint, the Unit 2 operators manually scrammed the reactor at 1325 CDT. Primary Containment Isolation System (PCIS) [EIIS: JM] Groups 2, 3, 6, and 8 containment isolation signals were received. Upon receipt of these signals all required components actuated as required. All safety systems operated as expected. On July 21, 2020, as Unit 1 condenser vacuum continued to degrade to the turbine trip setpoint, the Unit 1 operators manually scrammed the reactor at 0435 CDT. PCIS Groups 2, 3, 6, and 8 containment isolation signals were received. Upon receipt of these signals all required components actuated as required. All safety systems operated as expected. During this event, Unit 3 also experienced degraded condenser vacuum and was able to maintain reactor operation at a reduced reactor power of approximately 75 to 80%. The Tennessee Valley Authority (TVA) is submitting this report in accordance with Title 10 CFR 50.73(a)(2)(iv)(A), as any event or condition that resulted in a manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B), including: the reactor protection system (RPS) [EIIS: JC] which includes a reactor scram or a reactor trip, and general containment isolation signals affecting containment isolation valves in more than one system. | ML20322A440
Edwin I. Hatch Nuclear Plant | Unit 1 | 1A EOG inoperable due to water in day tank | 12-10-2020 | On 5/8/20 at 1714, while taking a fuel sample from the 1A Emergency Diesel Generator (EOG) day tank, 14.73 gallons of water was found in the tank. The water was immediately drained from the day tank. Additionally, from 5/14/20 through 5/16/20, the day tank and the main fuel oil storage tank (FOST) were drained, cleaned, inspected and returned to service. A past operability review was conducted and on 12/03/20 the results concluded that the EOG would not have been able to perform its safety function with the amount of water found in the day tank. The source of water in the day tank was from accumulated water in the FOST being pumped to the day tank during a fuel transfer system surveillance on 4/29/20. Water from an underground pipe leak had entered a nearby pull box, traversed conduit connecting to the FOST manway, collected in the manway and then seeped into the FOST through threaded connections on top of the tank. The direct cause of the event was clogging of the FOST manway drains which allowed water to collect in the manway. There was no maintenance strategy to inspect and clean the manway drains. This was corrected by cleaning debris from the drains and implementing a maintenance strategy for periodic cleaning. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A1 0M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira submission@omb.eop.QQY.. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER D 05000-1 YEAR •. SEQUENTIAL REV NUMBER 1-NO0. Edwin I. Hatch Nuclear Plant - Unit 1 321 □ -f I 001 | Event Description: On 5/7/20, Unit 1 was in MODE 1 at 100 percent rated thermal power. While performing an Emergency Diesel Generator (EOG) fuel oil transfer pump surveillance, standing water was observed in the manway of the 1A EOG Fuel Oil Storage Tank (FOST). Due to the standing water on the FOST, a sample of the fuel was taken and analyzed. The sample found water in the diesel fuel. Subsequently, on 5/8/20 at 1714, the associated 1A EOG day tank was sampled and 14.73 gallons of water was found. Actions were taken to immediately drain the water from the day tank. Between 5/14/20 and 5/16/20 the day tank and FOST were drained, cleaned, inspected and returned to service. Analysis and testing were conducted in order to determine if the EOG was capable of performing its safety function with · the quantity of water found in the day tank. It was ultimately concluded on 12/03/20 that the EOG would not have been able to perform its safety function. Since the EOG was last successfully run on 4/29/20 and water was transferred from the FOST during this surveillance, it is likely the EOG would not have been able to perform its safety function beginning on 4/29/20 once the water settled in the day tank after the EOG surveillance. The time period between 4/29/20 and when the , water was drained on 5/8/20 exceeds the Technical Specification (TS) Completion Time of 72 hours, thus making this issue reportable as a condition prohibited by TS per 10 CFR50.73(a)(2)(i)(B). Event Cause Analysis: Causal analysis was performed to determine the source of the water in the day tank. It concluded that standing water on top of the 1A EOG FOST had seeped into the FOST through threaded connectors on top of the tank. The water then i settled to the bottom of the FOST and was pumped into the day tank during the EOG surveillance on 4/29/20. The source I , of the standing water on top of the FOST was from an underground pipe leak that entered a nearby pull box and then · flowed through conduit connecting to the FOST manway. It was found that drain holes in the FOST manway were clogged, allowing water to collect in the manway. There was no maintenance strategy to inspect and clean the manway drain holes to prevent clogging. It was also determined that the sump pump in the pull box was non-functional and that conduit seals between the pull box and the FOST manway were degraded. The non-functional sump pump and degraded conduit seals contributed to water collecting in the pull box and migrating to the FOST manway. Safety Assessment: There were no safety consequences as a result of this event. While the 1A EOG was not operable, both the 1 B and 1C EDG's remained operable on Unit 1. However, due to the 1A EOG being inoperable longer than allowed by TS, this event is reportable as a condition prohibited by TS per 10 CFR50. 73(a)(2)(i)(B). Corrective Actions: ' The FOST manway drains were cleaned. Additionally, a maintenance strategy for cleaning manway drains periodically was implemented. The pull box conduit seals, sump pump and the underground pipe leak have been repaired. Previous Similar Events: • None. | ML20345A083
Susquehanna Steam Electric Station 05000387 1 of 4 | Unknown Unit | Condition Prohibited by Technical Specifications due to Inoperable Turbine Stop Valve and Turbine Control Valve Instrumentation | 12-21-2020 | On May 9, 2020, operators at the Susquehanna Steam Electric Station (SSES), Unit 1, were raising power following a maintenance outage. SSES Technical Specifications (TS) require that certain Turbine Stop Valve (TSV) and Turbine Control Valve (TCV) instrumentation be operable at greater than or equal to 26 percent Rated Thermal Power (RTP). However, at approximately 15:23, Unit 1 reached 26 percent RTP and the TSV and TCV instrumentation was found to be inoperable. Operators declared the TSV and TCV instrumentation inoperable, and entered Conditions A and B of Limiting Condition for Operation (LCO) 3.3.1.1. Control rods were inserted and Unit 1 was brought below 26 percent RTP at approximately 15:37, thereby exiting Conditions A and B of LCO 3.3.1.1. Based on the investigation and identified cause of this event, the inoperable condition likely existed prior to entering the Mode of Applicability. LCO 3.0.4 prohibits reaching 26 percent RTP when the LCO 3.3.1.1 is not met. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. The cause of the event was determined to be two socket weld failures caused by high cyclic fatigue. Additionally, one of the socket welds was found to be undersized for its application. This condition was corrected by repairing the welds and upgrading the welds to the proper size. There were no actual safety consequences associated with the described condition. NRC FORM 366A U. S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station, 05000-387 NUMBER NO. Unit 1 2020 - 003 - 00 | CONDITIONS PRIOR TO EVENT Unit 1 – Mode 1, approximately 24 percent Rated Thermal Power (RTP) Unit 2 – Mode 1, approximately 98 percent RTP After the event, two steam leaks were discovered on instrument piping [EIIS System/Component Code: SB/PSF] leading from Turbine Control Valves (TCVs) 2 and 3 [TA/FCV] to turbine pressure switches [IT/PS] which feed into the Reactor Protection System [System Code JC]. The steam leaks rendered Unit 1 Turbine Stop Valve (TSV) [TA/SHV] and TCV instrumentation inoperable prior to the start of the event. EVENT DESCRIPTION On May 9, 2020, operators at the Susquehanna Steam Electric Station (SSES), Unit 1, were raising power following a maintenance outage. At approximately 15:19, with reactor power at 24 percent RTP, operators withdrew control rods to raise power to approximately 28 percent RTP. SSES Technical Specification (TS) Limiting Condition for Operation (LCO) 3.3.1.1, “Reactor Protection System (RPS) Instrumentation,” requires that TSV and TCV instrumentation be operable (i.e., not bypassed) at greater than or equal to 26 percent RTP. However, at approximately 15:23, Unit 1 reached 26 percent RTP and the TSV and TCV instrumentation was still bypassed. Operators immediately stopped withdrawing control rods, declared the TSV and TCV instrumentation inoperable, and entered Conditions A and B of LCO 3.3.1.1. Unit 1 was brought below 26 percent RTP at approximately 15:37, thereby exiting Conditions A and B of LCO 3.3.1.1 after approximately 14 minutes. Subsequent to reducing power below 26 percent RTP, Susquehanna discovered two steam leaks on instrument piping lines SPDCD117-2 (specifically from Field Weld-10 (FW-10)) and JD-5-3-1A (specifically from FW-60). These leaks resulted in the instrument lines being unable to provide adequate steam pressure to turbine instrument sensing lines, and were determined to have rendered the TSV and TCV instrumentation inoperable during startup. Susquehanna repaired the leaks by installing new socket welds on May 11, 2020, and resumed power ascension. The Completion Times associated with LCO 3.3.1.1, Required Actions A.1 and B.1 (12 hours and 6 hours, respectively), were not exceeded. However, SSES TS LCO 3.0.4 prohibits entering a mode of applicability (i.e., reaching 26 percent RTP) without meeting all required LCOs. Based on the investigation and determined cause for this condition, the instrumentation piping likely failed, rendering the TCV and TSV instrumentation inoperable, prior to entry into the Mode of Applicability for LCO 3.3.1.1. As such, this event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. CAUSE OF EVENT The cause of the event was determined to be FW-10 and FW-60 socket weld failure due to high cyclic fatigue. Additionally, the weld on FW-10 was determined to be undersized. | ML20356A217
Peach Bottom Atomic Power Station | Unit 2 | Degraded Condition due to RPV Instrument Nozzle Leakage | 12-22-2020 | The event occurred on October 29, 2020, while Peach Bottom Unit 2 was performing Class 1 system leakage test following a shut down for refueling outage P2R23. Leakage was identified from a 2-inch Reactor Pressure Vessel (RPV) instrumentation nozzle (N-16A) during the test at a location where no leakage was found during the initial shutdown inspections. The leakage amount was identified as light seepage and visual examination revealed a surface crack at the 6 o'clock position on the interior RPV-instrument nozzle interface where the nozzle penetrates the vessel wall. Prior to de-pressurizing, an extent of condition bare metal examination was conducted on other instrument nozzles. No leakage was identified from any other instrument nozzles. Although the exact cause is unknown, phased array UT examination recorded a radial flaw in the N-16A J-Groove weld. A half nozzle repair was completed, consisting of replacing the outer portion of the existing nozzle with a new nozzle that was welded to the outside of the RPV. The reactor maintained shutdown until the pipe repairs and testing were completed. The safety significance of this event was minimal given the leakage was very small and was found while the reactor was shut down. Given the impact on the RPV boundary, this report is submitted in accordance with the requirements of 10 CFR 50. 73 (a)(2)(ii)(A), which requires the reporting of any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being degraded. On November 6, 2020, verbal approval for relief request 15R-14 regarding alternate repair of instrument penetration nozzle N-16A on the reactor vessel was received via email from J. Tobin (U.S. Nuclear Regulatory Commission) to D. Helker (Exelon Generating Company, LLC.) reference ADAMS: ML20314A028. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA. Library, and lnfonnation Collections Branch (T-6 A10M), U. S Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn. Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of infonnation unless the document http:/lwww.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3Q requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER DYE AR SEQUENTIAL REV Peach Bottom Atomic Power Station Unit 2 05000-1 277 NUMBER 1- NO 0 . I ~-I 02 | Unit Conditions Prior to the Event Peach Bottom Atomic Power Station (PBAPS) Unit 2 was shut down for refueling outage P2R23 and in cold shutdown at the time of the event. The condition was identified during the RPV pressure test. Description of Event On October 29, 2020, at approximately 10:30 hours, while PBAPS Unit 2 was performing Class 1 system leakage test in cold shutdown, a through-wall leak was identified on instrument nozzle N-16A. The N-16A RPV penetration is a 2- inch instrument line nozzle located just above the Top-of-Active Fuel at 45-degree azimuth on the vessel. The leakage was observed on the outer RPV wall during the performance of the system leakage testing being performed in accordance with ASME IWB-5210(a) requirements and station procedures. Visual examination revealed a surface crack at the 6 o'clock position and active leakage at the nozzle interface (annular gap) with the RPV outside diameter during the Class 1 system leakage test. Based on the design, any leakage into the annulus region between the nozzle body and the RPV wall would likely be associated with a through-wall failure of the nozzle assembly at the nozzle body. Prior to de-pressurizing, an extent of condition bare metal examination (VT-2) of was performed on October 29, 2020, on the five other additional RPV instrument nozzles (N-11A, N-11 B, N-12A, N-12B, and N-16B), and there was no evidence of leakage on any of the other instrument nozzles during the examination. With the leakage confirmed to be originating from the N-16A nozzle assembly, a repair team was mobilized, consisting of station, corporate, and industry experts. The repair method involved installing a weld pad using Ambient Temperature Temper Bead (ATTB) welding in accordance with ASME Code Case N-638-7, "Similar and Dissimilar Metal Welding Using Ambient Temperature Machine GTAW Temper Bead Technique, Section XI, Division 1," and installing a half nozzle to the weld pad. This repair method will make the nozzle resistant to lntergranular Stress Corrosion Cracking (IGSCC). The original partial penetration attachment weld and a remnant of the original nozzle will remain in place. The repair was completed on November 11, 2020, and the post-repair leakage test immediately followed, which validated the integrity of the repair and the RPV Class 1 pressure boundary. On October 29, 2020, Emergency Notification System (ENS)# 54971 was made in accordance with 10 CFR 50.72 (b)(3) (ii)(A), for a degraded condition. Given the impact on the RPV boundary, this report is submitted in accordance with the requirements of 10 CFR 50.73 (a)(2)(ii)(A), which requires the reporting of any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded. Analysis of the Event There was no actual safety consequence associated with this event. The potential safety consequence of this event was minimal, given the leakage was small and was found while the reactor was shut down for refueling. Plant Technical Specification (TS) 3.4.4 requires monitoring of reactor coolant leakage. When leakage limits are exceeded, the TSs requires reactor shutdown. If any leakage did exist during previous plant operation; it did not exceed TS leakage limits. Prior to depressurizing from the RPV pressure test, an extent of condition bare metal examination (VT-2) on the five other | ML20357B113
Cooper Nuclear Station 05000298 1 OF3 | Unknown Unit | Manual Reactor Scram due to Digital Electro-Hydraulic Fluid Leak | 12-28-2020 | On November 1, 2020, at 0534, Cooper Nuclear Station (CNS) Control Room Operators inserted a manual reactor scram due to low Digital Electro-Hydraulic (DEH) tank level. Further investigation revealed that a leak had developed at governor valve (GV) 1, and a pencil-sized stream of EH fluid was discovered leaking out of the lower, outboard 1nspecbon ~ on the GV1 actuator. Investigation revealed one bolt on the actuator inspection port cover plate was bottomeck)Lrt and prevented appropnate bghtening for an adequate seal. The <Hing on this cover plate was ruptured, allowing excessive leakage. The causes were on-srte vendor craftsmanship was unsatisfactory in the failure to recognize the bottomed-out bolt during actuator installation and inspector port cover plate holes on the new GV1 actuator body were not threaded deep enough to meet vendor specrlications. CNS will appropriately classify cnbcal Turbine Generator Fluid connecbons that are subject to additional verificabon of bolting and torqueing performance. In addition, CNS will review the final vendor evaluation of the actuator manufactunng defects/field craftsmanship and detenrnne if additional actions are warranted. This event was not risk s1gnrf1cant. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Esbmated burdefl per response to comply with this mE11daory collectloo f"8!1.18Sl 80 hours Repor1ad lessoos IB!IT18d are mcorporaEd mil the 11C811811g proc868 ood fad brl Ki llldustry Send corrrnents LICENSEE EVENT REPORT (LER) regm!mg tuden astimale Ki the FOIA, l.Jbray, and lnformEb:lo Colecbons Br!r'ICh (T-6 A1™), US Nuclei!" Regtiatory Coomssloo, Waslmgton, DC 206S0001, or by e-mal Ki CONTINUATION SHEET lnfocollects Resource@nrc gov, and the 0MB - at Ot.ll Office of In fonn,iion .m Regulatory Al!alrs, (3150-0104), Attn Desk 111 olra submsSIOn@ornb eop goy The NR C may not cooduct or (See NU RE G-1 022, R.3 for 1nstrucllon and guidance for completmg 1h18 form Sj):Jnsor, and a person 18 not reqUlred to 1'86pond to, a colecbon of mformallon unless the document https·/lv,w.v.nrc.oov/readlnq-rm/doc-collections/nuregs/staff/sr1022/r3/) requeslllg or requmng the collecbon ci!plays a currootly valtd 0MB control number 1. FACILITY NAME 2. IXlCl<ET MJMBER 3. l.ffi NlMER YEAR SEQUENTIAL REV Cooper Nuclear Station 05000-298 NUIIEER NO. 2020 -003 -00 | PLANT STATUS Cooper Nuclear Station (CNS) was in Mode 1, Power Operation, at 100 percent pcmer at the time of the event on November 1, 2020. BACKGROUND The power conversion systems at CNS are designed to produce electrical energy through conversion of a portion of thermal energy contained in the saturated steam supplied from the reactor, condense the b.Jrbine exhaust steam into water, and reb.Jm the water to the reactor as heated feec:lwater. The saturated steam produced by the reactor is passed through the high pressure b.Jrbine [EIIS:TRB] where the steam is expanded and then exhausted through the moisture separators [EIIS:MSR]. The moisb.Jre separators reduce the moisture content of the steam to close to zero percent. The steam is then passed through the low pressure b.Jrbines where the steam is again expanded. From the low pressure b.Jrbines, the steam is exhausted into the condenser [EIIS:COND] where the steam is condensed and de-aerated and then returned to the cycle as condensate. The main b.Jrbine [EIIS:TA ] consists of a high pressure section and a low pressure section comprised of two b.Jrbines in tandem. Steam from the reactor is admitted to the high pressure b.Jrbine section through two main stop valve and governor valve assemblies [EIIS:PCV]. After expansion through the high pressure b.Jrbine section, steam flows to four moisb.Jre separators and reb.Jms to the low pressure b.Jrbine section by passing through four sets of combined intermediate valves (intercept valves and reheat stop valves combined into one assembly) [EIIS:ISV]. These intermediate valves, fully open during normal operation, limit or isolate steam flow from the moisb.Jre separators to the low pressure b.Jrbines under certain conditions. This action will prevent potential damage to the low pressure turbines. The b.Jrbine utilizes a Digital Electro-Hydraulic (DEH) [EIIS:TG] system to control reactor pressure by positioning governor valves and condenser bypass valves. It consists of solid state governor devices, governor, startup control devices, emergency devices for b.Jrbine and plant protection (overspeed governor, master trip, vacuum trip, motoring protection, tlYust bearing wear trip, low bearing oil pressure trip) and special control and test devices. The control system operates the main stop valves, governor valves, bypass valves, reheat stop and intercept valves and other protective devices. DEH system oU pressure is maintained by two hydraulic pumps [EIIS:P] located at the DEH reservoir tank [EIIS:T]. , EVENT DESCRIPTION During Refueling Outage 30 (Fall 2018) three governor valve actuators were replaced with refurbished actuators. Upon testing, a fourth governor valve actuator had to be emergently replaced due to a leak. The preventative maintenance frequency was changed from every 6 years to every 2 years to replace the four governor valve actuators fNery cycle. Three spare governor valve actuators had previously been installed at CNS and were refurbished for use in Refueling Outage 31 (Fall 2020). A fourth governor valve actuator had to be purd,ased. While staging the governor valve actuators for replacement of the existing installed actuators, it was noticed that the purchased actuator was missing inspection port cover plates. Per vendor recommendation, a decision was made to relocate covers from one of the actuators being removed to the new actuator prior to installation. In-field work to relocate the inspection port cover plates commenced by the vendor and the four ad:uators were installed. The DEH system was successfully post-work tested and in service for approximately two weeks. Three days after CNS reached 100% power, an on leak was discovered on the number one governor valve actuator inspecbon port cover plate. NRG FORM 366A (06-2016) Page 2 of 3 | ML21014A446
Brunswick Steam Electric Plant (BSEP) | Unit 1 | Condition Prohibited by Technical Specifications due to Ventilation Charcoal Sample Laboratory Results | 01-21-2021 | At 14:36 Eastern Standard Time on November 25, 2020, with Unit 1 and 2 in Mode 1 at approximately 100% power, the ‘2B’ Control Room Emergency Ventilation (CREV) subsystem was declared inoperable on both units per Unit 1 and Unit 2 Technical Specification (TS) 3.7.3, CREV System, as a result of receiving notification that the ‘2B’ charcoal adsorber efficiency laboratory results were below the acceptance criteria. A sample of the ‘2B’ CREV charcoal adsorber was sent to a vendor laboratory on November 11, 2020, for analysis as part of the Control Building Emergency Filter System Test. The failure of the ‘2B’ charcoal adsorber to meet acceptance criteria was most likely the result of variations in the charcoal manufacturing process which caused accelerated charcoal surface oxidation. The ‘2B’ charcoal filter trays were replaced on November 27, 2020, and the subsystem was returned to operable on November 28, 2020, following completion of operability testing. There was no impact on the health and safety of the public or plant personnel. The safety significance of this event is minimal. The ‘2A’ CREV subsystem remained operable during this time period; only one filtering train is required for system operation with the other serving as the fully redundant standby train. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) due to having a condition prohibited by Technical Specifications. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant (BSEP), 05000- 325 YEAR NUMBER NO. Unit 1 2020 - 005 - 00 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. Background Initial Conditions At the time of the event, Unit 1 was in Mode 1 (i.e., Power Operation), at approximately 100 percent rated thermal power. Unit 2 was in Mode 1 (i.e., Power Operation), at approximately 100 percent rated thermal power. Reportability Criteria This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) due to having a condition prohibited by Technical Specifications. The inoperable condition of the ‘2B’ Control Room Emergency Ventilation (CREV) [VI] subsystem existed at least from when the sample was taken on November 11, 2020, to when the ‘2B’ CREV subsystem was made operable on November 28, 2020. This is longer than the 7 days allowed out of service time allowed by Technical Specification 3.7.3, Condition ‘A’, combined with the Condition ‘C’ completion time to be in Mode 3 within 12 hours. Event Description At 14:36 Eastern Standard Time on November 25, 2020, with Unit 1 and 2 in Mode 1 at approximately 100% power, the ‘2B’ CREV subsystem was declared inoperable on both units (the CREV System is a shared system) per Unit 1 and Unit 2 Technical Specification (TS) 3.7.3, CREV System, as a result of receiving notification that the ‘2B’ charcoal adsorber efficiency laboratory results were below the acceptance criteria. A sample of the ‘2B’ CREV charcoal adsorber was sent to a vendor laboratory on November 11, 2020, for analysis as part of the Control Building Emergency Filter System Test. The results from this test demonstrated that the charcoal adsorber efficiency for organic iodine was 92.956% efficient, which is less than the acceptance criteria of 95.26% efficient. Event Cause The failure of the ‘2B’ charcoal adsorber to meet acceptance criteria was most likely the result of variations in the charcoal manufacturing process which caused accelerated charcoal surface oxidation. The ‘2B’ charcoal adsorber was installed in 2012 and was planned to be replaced in 2022. The increased degradation rate associated with the ‘2B’ charcoal adsorber is atypical, though not outside of industry operating experience. The untimely identification of the condition was a result of procedural guidance that allowed 31 days from sample removal to receive laboratory sample results. Safety Assessment There was no impact on the health and safety of the public or plant personnel. The safety significance of this event is minimal. The ‘2A’ CREV subsystem remained operable during this time period, and only one filtering train is required for system operation with the other serving as the fully redundant standby train. The ‘2A’ CREV subsystem was tested in May of 2020 with Satisfactory results. Corrective Actions Replacement of the ‘2B’ CREV subsystem charcoal filter trays was completed on November 27, 2020, and the subsystem was returned to operable on November 28, 2020, following completion of operability testing. | ML21021A366
cooper nuclear station | Unknown Unit | Secondary Containment Differential Pressure Perturbation Could Have Prevented Fulfillment of a Safety Function | 12-30-2020 | 12. Licensee Contact for this LER µcoosee Contact ~ Nunmer (Include hea Code) Linda Dewhirst, Reaulatory Affairs and Compliance Manager 402) 825-5416 13. Cu,....,.., One Line for each COIT = - ,. Falure Desauld i1 this Report Cause System Component Manufacturer Reportable To IRIS Cause System ~ Manufacturer Reportable To IRIS D NG COMP y 14. Supplemental Report Expected Month Day Year 15. Expected Submission Date D ~ No I Yes (If yes, complete 15 Expected SubmJSSlon Date) 16 Abstract (l.Jnrt to 1560 spaces, 1e , approxrnately 15 single-spaced typewntten ltl18S) On November 3, 2020, Secondary Containment differential pressure (dip) exceeded the Technical Specifications limit of -0.25 inches of water gauge (wg) causing Secondary Containment to be inoperable for 27 seconds. Two causal factors were identified for this event. The first being that the manual pressure regulator, a non- essential component, drifted causing an un-demanded increase in Reactor Building HVAC supply flow. The second factor is a lack of procedural guidance to optimize the tuning parameters of the reactor building differential pressure controllers to maintain the required d/p during changing conditions. The pressure regulator was replaced. Adoption of Technical Specification Task Force Traveler 551, Revise Secondary Containment Surveillance Requirements, will be pursued to eliminate the reporting requirements from exceeding -0.25 inches wg due to a failure of non-safety related equipment. Procedures will be updated to provide guidance to optimally tune the fans. There was no impact on nuclear safety, plant reliability, radiological safety, or industrial safety. NRC FORM 366A 106-2016) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) corrw Estimated oorde!l per response lo wrth Ills mandfmry colecbon request 80 hot.Js Repo,1Bd lessons le!r'ned are llCOl])Ol"8led mto the llcoo61!1Q p,'OC8SS 111d fed back to ridustry Send C011llTl81115 LICENSEE EVENT REPORT (LER) raga-ding burden esbmate kl the FOIA, lb")', 111d lnbma!lon Collecbons Branch [T-6 A10M), U.S Nuclea- Regulalay Corrmsslon, Washington, DC 20555-0001, oc by !HT1ail to CONTINUATION SHEET lnfocollects Resol.S'CEl@nrc gov, and the 0MB reviewer at 0MB Office of lnforrnalloo 111d Reg ulalory Affars, (31~104], Attn Desk ail oa:a subrruss!OO@ornb eop 09'!' The NRC may not conduct or (See NU RE G-1 022, R3 for inslrucbon and guidance for completing this form spoosor, ffid a persoo 18 not required to respond kl, a colecbon of lllfomlabon unless the dooument htlps//www.nrc.oov/readmg--rrn/doc-coQedJons/nuregs/staff/sr1022/r3I) requeslllg or raqt1mg the colloction dlSplays a CUT8l1lly valid 0MB control nuimer 1. FACDJTY NAME 2. DOCKET NUMBER 3. l.ffi ~ YEAR SEQUElfTIAL REV Cooper Nuclear Station 05000-298 NUIEER NO. 2020 -004 - 00 | PLANT STATUS Cooper Nuclear Station was in Mode 2, Startup, at 3 percent power at the time of the event on November 3, 2020. I BACKGROUND Secondary Containment serves as a barrier to confine and monitor potential releases during fuel handling operations and is a system that limits the release of radioactive materials to the environment and consists of four subsystems. One of the subsystems is the Reactor Building [EIIS: NG], which encloses the Reactor Pressure Vessel [EIIS: RPV] and Primary Containment [EIIS: NH]. The secondary containment area (most of the Reactor Building) has supply and exhaust ventilating systems. The supply system furnishes filtered 100% outdoor air to all floors of the building through ductwork. The supply unit has an operating and standby (100% capacity) fan with vortex dampers [CDMP] to provide regulation of air capacity. The fans will deenergize in the event of loss of offsite power. The exhaust air is induced from the ventilated areas to a common plenum connected to the two exhaust fans, each of 100% capacity. The air is then exhausted to the atmosphere. During normal plant operation, a minimum average negative pressure of 0.25 inches of water gauge (wg) is maintained by differential pressure controllers which receive signals proportional to the pressure difference between outside air and the secondary containment atmosphere, and control the position of the exhaust fan vortex dampers. The differential pressure is detected by four separate probes, with one on each side of the Reactor Building. Control action is initiated from the average value of the four sensor probes. If a Loss of Coolant Accident should occur, all ventilation systems of the primary containment area and secondary containment area will be isolated automatically, and the Standby Gas Treatment system will be automatically initiated. EVENT DESCRIPTION On November 3, 2020, at 08:14, Reactor Building differential pressure (dip) exceeded the Technical Specification limit of -0.25 inches of water gauge (wg) causing Secondary Containment to be inoperable for 27 seconds. Reactor Building HVAC Exhaust Fan 'B' (HV-FAN-EF-R-1 B) was operating with Reactor Building Differential Pressure Controller 'B' (HV-DPIG-835B) in automatic at a differential pressure at approximately - 0.34 inches wg. HV-DPIC-835B responded by raising output to restore d/p to -0.34 inches wg. A review of operating logs identified that on October 12, 2020, HV-FAN-SF-R-1A-A was placed in service and remained in operation through-out the event. Flow is modulated through the fan by changing the throttled position of the inlet vortex dampers, HV-VD-VD1005A and HV-VD-VD1005A 1. The position of these vortex dampers is controlled by a 3-18 psig manual pressure regulator (HV-FCV-1013). This regulator provides an output pneumatic air pressure signal to the vortex damper actuator control valve positioners. If more air flow is necessary, the output from the regulator is raised, increasing air flow through the in-service Reactor Building supply fan. Reactor building differential pressure will rise as a result of the higher influent flow. HV-DPIC- NRC FORM 366B (08-2020) Page 2 of 4 | ML21022A042
Susquehanna Steam Electric Station | Unit 1 | Automatic Reactor Scram Due to Main Turbine Trip Caused by an Electrical Ground Path in the B Main Transformer | 08-31-2023 | On May 3, 2020 at approximately 08:21, Susquehanna Steam Electric Station Unit 1 reactor automatically scrammed due to a main turbine trip. Both divisions of the Reactor Protection System (RPS) actuated and all control rods inserted. This event was reported by Event Notification 54691 in accordance with 10 CFR 50.72(b)(2)(iv)(B) and (b)(3)(iv)(A). This event is also reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in an automatic actuation of the RPS (including reactor scram), as well as associated isolation and actuation of other systems listed in 10 CFR 50.73(a)(2)(iv)(B). The direct cause of the event was an electrical path from a replacement current transformer inside the main transformer to the low voltage bus causing a ground on the 24 kV System (Main Generator). The apparent cause of the ground was a current transformer with the incorrect insulation characteristics installed as a result of the wrong current transformer being supplied to Susquehanna. Corrective actions included removing the current transformer and replacing it with a bus bar. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366A U. S. NUCLEAR REGULATORY COMMISSIONAPPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station Unit 1 05000-387 NUMBER NO. 2020 - 001 - 01 | CONDITIONS PRIOR TO EVENT Unit 1 – Mode 1, approximately 76 percent Rated Thermal Power Unit 2 – Mode 1, approximately 100 percent Rated Thermal Power There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. EVENT DESCRIPTION On May 3, 2020 at approximately 08:21, Susquehanna Steam Electric Station Unit 1 reactor automatically scrammed due to a main turbine [EIIS System/Component Code: TA/TRB] trip. The Unit 1 Control Room received indication of a main turbine trip with both divisions of the Reactor Protection System (RPS) [EIIS System Code: JC] actuated and all control rods inserted. The Reactor Recirculation Pumps [EIIS System/Component Code: AD/P] tripped on End of Cycle Recirculation Pump Trip (EOC-RPT). Operators subsequently maintained reactor water level at the normal operating band using the Reactor Feed Water system [EIIS System Code: SJ]. All safety systems responded properly during the event. This event was reported by Event Notification 54691 in accordance with 10 CFR 50.72(b)(2)(iv)(B) and (b)(3)(iv)(A). This event is also reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in an automatic actuation of the RPS (including reactor scram), as well as associated isolation and actuation of other systems listed in 10 CFR 50.73(a)(2)(iv)(B). CAUSE OF EVENT The direct cause of the event was an electrical path from a replacement current transformer (CT7) [EIIS System/Component Code: EL/XCT] inside the main transformer to the low voltage bus causing a ground on the 24 kV System (Main Generator) [EIIS System Code: TB]. The apparent cause of the ground was a current transformer with the incorrect insulation characteristics installed as a result of the wrong current transformer being supplied to Susquehanna. ANALYSIS/SAFETY SIGNIFICANCE The actual consequence of this event was a Unit 1 Reactor scram. The scram did not require or result in the actuation of Emergency Core Cooling System or Reactor Core Isolation Cooling system [EllS System Code: BN] and no main steam relief valves [EllS System/Component Code: SB/RV] opened. All safety systems responded properly during the event. The condition described herein did not result in a safety system functional failure. Accordingly, this event will not be counted as a safety system functional failure in the Reactor Oversight Process Performance Indicators. There were no actual consequences to the health and safety of the public as a result of this event. | ML21026A253
Susquehanna Steam Electric Station | Unit 1 | Inoperability of Unit 1 “B” Residual Heat Removal Service Water Pump Due to the Circuit Breaker Spring Charging Motor Contact Actuator Being Out of Adjustment | 02-10-2021 | On July 1, 2020 at approximately 20:26, the Unit 1 “B” Residual Heat Removal Service Water (RHRSW) pump did not start when being placed into service for Spray Pond Cooling testing, resulting in the pump being declared inoperable. Upon the discovery of the condition, Susquehanna entered Technical Specification (TS) 3.7.1 Condition B for one RHRSW subsystem being inoperable. Investigation at the pump circuit breaker identified the closing springs did not recharge following the circuit breaker’s last closing operation. Following maintenance, the spring charging motor operated as expected and the breaker was tested successfully. TS 3.7.1 Condition B was exited on July 2, 2020 at approximately 02:44. Based on the investigation completed, the condition is considered to have existed for longer than allowed by TS 3.7.1. The condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. The direct cause of the event was the Eaton/Cutler-Hammer 4.16kV vacuum circuit breaker spring charging motor contact actuator being out of adjustment. Actuator age was determined to be the most likely causal factor, combined with the original equipment manufacturer vendor’s failure to recommend a periodic replacement for the circuit breaker’s two limit switches. Key corrective actions include: replaced the 1B RHRSW pump circuit breaker and a planned revision to the preventive maintenance strategy for the spring charging motor actuator based on vendor recommendations. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366A U. S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station Unit 1 05000-387 NUMBER NO. 2020 - 002 - 01 | CONDITIONS PRIOR TO EVENT Unit 1 – Mode 1, approximately 100 percent Rated Thermal Power Unit 2 – Mode 1, approximately 100 percent Rated Thermal Power There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. EVENT DESCRIPTION On July 1, 2020 at approximately 20:26, the Unit 1 “B” Residual Heat Removal Service Water (RHRSW) pump (1P506B) [EIIS System Code/Component Code: BI/P] did not start when being placed into service for Spray Pond Cooling testing, resulting in the pump being declared inoperable. Upon discovery of the condition, Susquehanna entered Technical Specification (TS) 3.7.1 Condition B for one RHRSW subsystem being inoperable. On July 2, 2020, investigation at the pump circuit breaker (1A20408) [EIIS Component Code: 72] identified the closing springs did not recharge following the circuit breaker’s last closing operation on June 21, 2020 at approximately 07:35. Following maintenance, the spring charging motor operated as expected and the breaker was tested successfully. TS 3.7.1 Condition B was exited on July 2, 2020 at approximately 02:44. Based on the investigation completed, the condition is considered to have existed for longer than allowed by TS 3.7.1. The condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specification. CAUSE OF EVENT The direct cause of the event was the Eaton/Cutler-Hammer 4.16kV vacuum circuit breaker spring charging motor contact actuator being out of adjustment with the motor cut off cam, resulting in the spring charging motor contact not experiencing full travel. Additionally, age was determined to be the most likely causal factor, combined with the original equipment manufacturer vendor’s failure to recommend a periodic replacement for the circuit breaker’s two limit switches. ANALYSIS/SAFETY SIGNIFICANCE During the period the 1B RHRSW pump was inoperable, the 1A RHRSW pump was verified to be operable. An engineering evaluation was completed to analyze having only the 1A RHRSW pump available with the 1B RHRSW pump inoperable. The engineering evaluation concluded that, with only the 1A RHRSW pump in operation, the accident analysis assumptions were met and the RHRSW system could perform its design function. Based on the engineering evaluation and verification that the 1A RHRSW pump was operable during the period the 1B RHRSW pump was inoperable, the condition described herein did not result in a safety system functional failure. Accordingly, this event will not be counted as a safety system functional failure in the Reactor Oversight Process Performance Indicators. There were no actual consequences to the health and safety of the public as a result of this event. | ML21041A348
LaSalle County Station | Unit 2 | High Pressure Core Spray Inoperable due to Water Leg Pump Breaker Cubicle Motor Contactor | 02-18-2021 | On December 23, 2020, the Unit 2 high pressure core spray (HPCS) water leg pump (WLP) tripped off due to a fault within its breaker cubicle. The HPCS WLP is a support component required to maintain the HPCS system operable. With the loss of the WLP, the HPCS system was declared inoperable. The unit entered applicable technical specification required actions to immediately verify that the reactor core isolation cooling (RCIC) system was operable and to restore the HPCS system to operable within 14 days. This condition was previously reported under emergency notification system (ENS) 55046 as a single-train system inoperability that could have prevented the fulfillment of a safety function used to mitigate an accident. The condition is being reported under 1O CFR 50. 73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of a safety function. The system was restored to operable following replacement of the affected HPCS WLP breaker cubicle control power transformer and motor contactor. The cause was age-related failure of the breaker cubicle motor contactor. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 72517th Street NW, Washington, DC 20503; e-mail: oira submission@omb.eoo.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of infonnation unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV LaSalle County Station, Unit 2 05000- 374 NUMBER NO. 2021 001 00 | Plant and System Identification LaSalle Country Station Unit 2 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the Division 3 high-pressure core spray (HPCS). In accident situations, the HPCS system provides cooling to the reactor core to prevent excessive fuel cladding temperatures following a break in the nuclear system piping. Condition Prior to Event Unit(s): 2 Date: December 23, 2020 Time: 06:53 CST Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 100 percent Description On December 23, 2020, the main control room operating crew received an alarm for the Unit 2 HPCS water leg pump (WLP) having tripped off, followed shortly by a ground alarm for the associated electrical circuitry that cleared with 15 seconds. Field operators subsequently reported an acrid order in the Division 3 switchgear room and subsequently found the breaker for the HPCS WLP in the closed position but the breaker's cubicle was warm to the touch. The operating shift crew removed the HPCS WLP from service, declared the HPCS system inoperable, and entered applicable technical specifications {TS) 3.5.1 required action (RA) 8.1 to immediately verify by administrative means that the reactor core isolation cooling (RCIC) system was operable, and TS 3.5.1 RA 8.2 to restore the HPCS system to operable within 14 days. The operating shift established robust barriers to administratively protect the RCIC system following discovery through the subsequent restoration of the HPCS system inoperability period. The Unit 2 HPCS system was restored to operable the same day at 20:18 CST, after replacement of the WLP breaker cubicle control power transformer and motor contactor and post-maintenance testing. Cause Initial investigation identified that the WLP motor starter (2AP79E-2C) contactor and control power transformer were damaged. The cause was age-related failure of the contactor. The failure analysis found the motor starter damage had resulted from a heating event that began inside the contactor coil which eventually led to an open circuit in the coil. The increased current flow impacted the control power transformer, which overheated and failed. Reportability and Safety Analysis The HPCS system is part of the Division 3 emergency core cooling system (ECCS). In accident situations, HPCS provides cooling to the reactor core to prevent excessive fuel cladding temperatures following a break in the nuclear system piping. A secondary purpose of HPCS is to supply cooling water to the reactor pressure vessel as a backup to the RCIC system if the main condenser and feedwater were unavailable. The HPCS WLP is a support system required to maintain the HPCS system operable. With the loss of the HPCS WLP, HPCS was declared inoperable and the operating shift entered applicable TS RA statements. This condition could have prevented the HPCS system, a single train safety system, from performing its design function. Therefore, this condition is reportable in accordance with 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented the fulfillment of the safety function of structures or systems that are required to mitigate the | ML21049A048
Grand Gulf Nuclear Station | Unit 1 | Failure to meet Technical Specifications 5.5.7 for Division II Standby Gas Charcoal Filter Media Efficiency | 02-18-2021 | On September 20, 2019, Division II Standby Gas Treatment System (SBGT) was declared inoperable when test results from the Division II SBGT charcoal filter did not meet the acceptance criteria in Technical Specification (TS) 5.5.7, Ventilation Filter Testing Program (VFTP). The charcoal media was considered deficient starting from the September 4, 2019 date of sample. This exceeded the seven (7) day LCO action completion time. During this time Division I SBGT was declared inoperable for surveillance testing for approximately 11 minutes during the inoperability of the Division II SBGT because of the failed charcoal efficiency test. This report is made pursuant to 10 CFR 50.73(a)(2)(i)(B) for any operation or condition which was prohibited by the plant’s Technical Specification and condition that could have prevented the fulfillment of a safety function, pursuant to 10 CFR 50.73(a)(2)(v)(C). The Direct Cause is failure of the charcoal filter media. Causal Factor was that Operations control of LCO procedures does not include guidance for tracking system status while awaiting sample results. The immediate action taken was replacing the charcoal filter media and performing subsequent testing. There were no consequences to the general safety of the public, nuclear safety, industrial safety and radiological safety for this event. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed LICENSEE EVENT REPORT (LER) back to industry. Send comments regarding burden estimate to the Information Services Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC CONTINUATION SHEET 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer (See NUREG-1022, R.3 for instruction and guidance for completing this form for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 05000-416 NUMBER NO. 2019 - 006 - 01 | Plant Conditions: Grand Gulf Nuclear Station (GGNS) Unit 1 was operating at approximately 100 percent power in MODE 1. There were no Structures, Systems, or Components that were inoperable that contributed to this event. Event Description: On September 20, 2019, test results were received indicating that a sample from the Division II charcoal filter of the Standby Gas Treatment System (SBGT)[WF] had an efficiency of 98.90 percent which did not meet the Acceptance Criteria (greater than or equal to 99.5 percent) listed in Technical Specification (TS) 5.5.7, Ventilation Filter Testing Program (VFTP). As a result, SBGT was declared INOPERABLE, and TS Limiting Condition for Operation (LCO) 3.6.4.3 Standby Gas Treatment System, Condition A was entered on September 20, at 5:14 pm CDT, which placed the station in a seven (7) day action statement to restore SBGT subsystem to an Operable status. On September 22, 2019 at 10:05 pm, the charcoal bank was replaced. All testing, leak tests and Dioctyl-phthalate (DOP) test were completed verifying that all Acceptance Criteria were met, and TS 3.6.4.3 Condition A was exited on September 23, 1:41 am. The failed sample was obtained from the SBGT charcoal filter on September 4, 2019 at 2:38 am CDT and it was not replaced until September 22, 2019 at 10:05 pm. This exceeded the seven (7) day Completion Time for the SGTS listed in TS LCO 3.6.4.3 Condition A which placed the station in a condition prohibited by Technical Specifications. During this time SBGT Division I was declared inoperable for approximately 11 minutes during planned surveillance testing on September 19, 2019. The period that SBGT Division I was inoperable overlapped the inoperability of the SBGT Division II because of the failed charcoal efficiency test. This is reportable as a condition that could have prevented the fulfillment of a safety function, pursuant to 10 CFR 50.73(a)(2)(v)(C). Reportability: This event is reportable under 10 CFR 50.73(a)(2)(i)(B), Any operation or condition which was prohibited by the plant’s Technical Specification. This event is also being reported under 10 CFR 50.73(a)(2)(v)(C), as an event or condition that could have prevented fulfillment of a safety function of structures or systems that are needed to control the release of radioactive material. Direct Cause: The Direct Cause is failure of the charcoal filter media. Causal Factors: The failure was not detected beforehand because of inadequate monitoring and inadequate identification of adverse trends. Critical system parameters were not identified in the Performance Monitoring Plan (PMP). Operations control of LCO procedures does not include guidance for tracking system status while awaiting sample results. | ML21049A273
Clinton Power Station | Unit 1 | Simultaneous lnoperability of Main Control Room Ventilation Subsystems A and 8 | 01-15-2021 | The Main Control Room (MCR) Ventilation and Air Conditioning System (VC) subsystem A was removed from service for planned maintenance and declared inoperable on 11 /16/20. At 1918 on 11/16/20, MCR VC subsystem 8 supply air isolation dampers 0VC21YB, 0VC24YB and OVC27YB lost power and failed closed. Technical Specification (TS) 3.7.3, Control Room Ventilation System, Action F.1 and TS 3.7.4, Control Room AC System, Actions 8.1 and 8.2 were entered. VC subsystem A ventilation was restored to OPERABLE status and at 2036, TS 3.7.3 Action F.1 was exited. At 0350 on 11 /17 /20, VC subsystem A chiller was restored to OPERABLE status and TS 3.7 .4 Actions 8.1 and 8.2 were exited. Investigation determined that a shorted coil in breaker cubicle 0AP25E-48 motor starter caused fuse 0AP25E4A-F01 to blow, which resulted in dampers 0VC21YB, 0VC24YB and 0VC27Y8 losing power and failing closed. The failed motor starter coil and fuse were replaced and successfully tested. The condition where both required VC subsystems were simultaneously inoperable is reportable under 10 CFR 50.73(a)(2)(v)(D), any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. However, there was no impact to the health and safety of the public or plant personnel, as subsequent post-maintenance testing demonstrated VC subsystem A remained capable of performing its safety functions throughout the event. ( N 08 R -2 C 0 2 F 0) O RM 366A U.S. NUCLEAR REGULA TORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2( ..., ... Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry . { . t LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to the FOIA, Library, and Information Collections · .... l Branch (T-6 A1 0M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by , CONTINUATION SHEET e an -m d a R il e t g o u l l a n t f o o r c y o l A le f c fa ts ir . s R , e ( s 31 ou 5 r 0 c - e 0 @ 10 n 4 r ) c , . g A o tt v n , : an D d e s th k e O D ffi M ce B r f r o e r v i t e h w e e N r u a c t l : e a 0 r M Re B g u O la ffi t c o e ry o C f o In m fo m rm iss a i t o io n n (See NUREG-1022, R.3 for instruction and guidance for completing this form 725 17th Street NW, Washington, DC 20503; e-mail: !lira sob, 1issiu,@,,11b.eoognv. The NRC http-llwww.m:..~-colediolllSIJuegslstaffl022!r3i) may not conduct or sponsor, and a person is not required to respond to, a collection o information unless the document requesting or requiring the collection displays a currently valio 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Clinton Power Station, Unit 1 05000461 YEAR SE N Q U U M E B N E T R IA L R N E O V . 2020 - 002 00 | PLANT AND SYSTEM IDENTIFICATION General Electric -- Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in text as [XX]. EVENT IDENTIFICATION Divisions 1 and 2 Main Control Room Ventilation and Air Conditioning Systems Simultaneously Inoperable A. Plant Operating Conditions Before the Event Unit: 1 Event Date: November 16, 2020 Event Time: 1918 Mode: 1 Mode Name: Power Operation Reactor Power: 098 B. Description of Event On November 16, 2020 at 0153 CDT, Main Control Room (MCR) Ventilation [VI] and Air Conditioning [KM] System (VC) subsystem A was removed from service and declared inoperable for scheduled maintenance. At 1918 CDT, MCR VC subsystem B supply air isolation dampers [DMP] 0VC21 YB, 0VC24YB and 0VC27YB lost power and failed closed. Technical Specification (TS) 3.7.3, Control Room Ventilation System, Action F.1 and TS 3.7.4, Control Room Air Conditioning (AC) System Actions 8.1 and 8.2 were entered. TS 3.7.3 Action F.1 directs the plant be in MODE 3 within 12 hours. TS 3.7 .4 Action 8.1 requires verification of MCR temperature to be less than or equal to 86 degrees F and Action B.2 requires one VC subsystem to be restored to OPERABLE status within 7 days. VC subsystem A ventilation was restored to OPERABLE status at 2036 CDT and TS 3.7.3 Action F.1 was exited. At 0350 CDT on November 17, 2020, VC subsystem A chiller was restored to OPERABLE status and TS 3.7.4 Actions 8.1 and 8.2 were exited. At 1737 CDT on November 17, 2020, VC subsystem 8 was restored to OPERABLE and TS 3.7.3 and TS 3.7.4, Action A.1, were exited. Simultaneous inoperability of VC subsystems A and B resulted in a condition that could have prevented fulfillment of a safety function. Therefore, this condition was reported to the NRC Operations Center via ENS Notification 55002 on November 17, 2020, at 0340 CDT, in accordance with the reporting requirements of 10 CFR 50. 72(b)(3)(v)(D), any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. NRG FORM 3EEA (C8-2C20) P2ge_2_ of _ 3_ N (08 R -2 C 0 2 F 0) O RM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/21 { ._.,,» . t LICENSEE EVENT REPORT (LER) R S E e e s n t p im d o r a t c e t o e d m d l m e b s e u s n r o d t n e s s n r e le p g a e a r r r n d e r i e d n s g p a o r b e n u s r i d e n e c n o to r p e o c s o r t a i m m te p a d l t y e i n w l t o o it h t t h h t e e h i l s F ic O e m n IA a s n , in d L g a i b t p o r r a r o y r c y e , c s o a s ll n e d a c n ti I d o n n f f o e r r d m e q a b u t a io e c s n k t : t C o 8 o 0 i l n le d h c u o t s i u o t r r n y s s . . · .. ... l CONTINUATION SHEET e B - r m an a c il h t o (T l - n 6 fo A co 1 l 0 le M c ) t . s . U R . e S so . u N r u ce cl @ ea n r rc R . e go gu v, la a to n r d y t C he om 0 m M is B s i r o e n v , i e W w a e s r h a in t: g to 0 n M , B D C O f 2 fi 0 ce 5 5 o 5 f - 0 l 0 n 0 fo 1 rm , o a r ti o b r i and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Co1TVTiission (Se 1 e 1 t N tp U ·- REG- . 1 1 02 1 2, R 1 .3 f & or ins . tru ~ ctio ~ n a s nd r gu 1 idan 0 ce 2 for 2 com / p r letin 3 g t I his ) fo rm i m 7 n 2 f a o 5 y r m 1 n 7 a o t t h t io S n c t o r u n e n e d l u t e N s ct s W o th , r e W s a d p s o o h c n u in s m g o t r e o , n n t a , n r D e d C q u a e 2 s 0 p t 5 i e n 0 r g s 3 o ; o n e r - r m i e s a q u i n l: i o r i t o n i g r 1 e a q t h u S e ir l e c l d o b lle t to c ~ ti n o re n h s p d " o i ' s n 1 p d l 0 ay . to l s j , l a l a ) c I u c I r . o r e ll T e n h c tl t e y i o N v n a R li C o c 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Clinton Power Station, Unit 1 05000461 YEAR SE N Q U U M E B N E T R IA L R N E O V . 2020 - 002 00 NARRATIVE C. Cause of the Event Investigation determined that a shorted coil [CL] in breaker cubicle 0AP25E-48 motor starter [MSTR] caused fuse [FU] 0AP25E4A-F01 to blow, which resulted in dampers 0VC21YB, 0VC24YB and 0VC27YB losing power and failing closed. Based on the visual evidence and electrical testing, the motor starter coil failed due to electrical overheating. The motor starter coil is a high duty cycle component and cycles frequently when either of the two VC subsystems is in service. The failed motor starter coil was installed in July 2005 and failed after approximately fifteen years of service. D. Safety Consequences The condition where both required VC subsystems were simultaneously inoperable described in this LER is reportable under 10 CFR 50.7 3(a)(2)(v)(D), any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. There was no impact to the health and safety of the public or plant personnel, as subsequent post-maintenance testing demonstrated VC subsystem A remained capable of performing the safety functions of the VC system throughout this event. Engineering analysis has determined that this event does not meet the criteria for a Safety System Functional Failure. E. Corrective Actions The failed 0AP25E-48 motor starter coil and fuse 0AP25E4A-F01 were replaced and successfully post maintenance tested on November 17, 2020. F. Previous Similar Occurrences There were no previous events identified involving failed motor starter coils similar to the condition described in this LER. G. Component Failure Data GE, Magnetic Pickup (Motor Starter) Coil, Part 55-5372898002 Series A, VA1498, 115-120V, 60Hz MR:: FOR/,! 3E€ A (08-2020) Page_3_ of _3_ | ML21063A252
Prairie Island Nuclear Generating Plant | Unit 1 | 12 Diesel Driven Cooling Water Pump Auto Start Due to Low System Pressure | 03-22-2021 | On January 26, 2021, the Prairie Island Nuclear Generating Plant (PINGP), 12 Diesel Driven Cooling Water Pump (DDCLP) auto started. Maintenance was in progress on 22 DDCLP and 121 Motor Driven Cooling Water Pump (MDCLP) was aligned as the replacement safety related pump for 22 DDCLP while non-safety related 21 Cooling Water (CL) pump was supporting the system loads. The 12 DDCLP auto started on a sensed low header pressure following the isolation of 22 Cooling Water Strainer for maintenance and subsequent auto initiation of backwash of the other Cooling Water Strainers. This event is reportable under 10CFR 50.73(a)(2)(iv)(A) due to a valid Emergency Service Water system actuation. There were no nuclear safety impacts. The system operated as designed. All systems responded normally. The direct cause of this event was low pressure at the discharge of 12 DDCLP due to the isolation of the Cooling Water Strainer while 22 DDCLP was isolated during low CL system flow conditions. The corrective actions included securing the 12 DDCLP. In addition, procedure updates are planned. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Prairie Island Nuclear Generating Plant, 05000282 NUMBER NO. Unit 1 2021 - 001 - 00 | EVENT DESCRIPTION On January 26, 2021, the Prairie Island Nuclear Generating Plant (PINGP), Units 1 and Unit 2, were both in Mode 1 (Power Operation) at 100 percent power. The total Cooling Water (CL) system operating flow rates were in the range that operation of only one CL pump was desired. Non-safety related train B 21 CL Pump was supporting all the CL system loads for both trains of CL while the train B 22 Diesel Driven Cooling Water Pump (DDCLP) was out of service for maintenance and the 121 Motor Driven Cooling Water Pump (MDCLP) was aligned as the train B replacement safety- related pump. At 1044 CST, the train A 12 DDCLP auto started on a sensed low header pressure following the isolation of 22 Cooling Water Strainer for maintenance and subsequent auto initiation of backwash of the other Cooling Water Strainers which reduced system pressure slightly. The 12 DDCLP is designed to start automatically if the CL discharge header pressure drops to 75 pounds per square inch gauge (psig) for 15 seconds. This event is reportable under 10CFR 50.73(a)(2)(iv)(A) due to a valid Emergency Service Water system actuation per NUREG 1022, Revision 3. EVENT ANALYSIS The 12 DDCLP is a part of the PINGP CL System (EIIS CODE: BI). The CL system is a ring header which is shared by Units 1 and 2 that provides a heat sink for the removal of process and operational heat from safety-related components during a design basis accident or transient. During normal and shutdown operation, the CL system also provides this function for various safety-related and non-safety related components. The CL system consists of a common CL pump discharge header for five CL pumps: two non-safety related pumps, two safety related DDCLPs, and 121 MDCLP that can be aligned as replacement for either DDCLP by realigning its power supply and administratively disabling the CL pump discharge header valves to direct flow to the appropriate train. With 121 MDCLP replacing 22 DDCLP on train B, the operating 21 CL pump supplied the ring header via train B and back fed to train A, creating a lower pressure at the discharge of 12 DDCLP than what is indicated in the control room. The isolation of 22 Cooling Water Strainer and subsequent auto backwash of the other Cooling Water strainers further reduced pressure to the 12 DDCLP auto start setpoint. ASSESSMENT OF SAFETY CONSEQUENCES The auto start of 12 DDCLP did not challenge nuclear safety as all plant systems responded as designed. This event does not represent a safety system functional failure for Unit 1 or Unit 2. There were no radiological, environmental, or industrial impacts associated with this event. The health and safety of the public and site personnel were not impacted during this event. CAUSE OF THE EVENT The direct cause of this event was low pressure at the discharge of 12 DDCLP due to the isolation of the Cooling Water Strainer while 22 DDCLP was isolated during low CL system flow conditions. CORRECTIVE ACTIONS Operations restored CL system pressure by returning 22 CL Strainer to service, securing 12 DDCLP, and operating 11 CL pump through the duration of the 22 DDCLP maintenance. Procedure updates to perform mitigating actions while performing DDCLP and Cooling Water Strainer maintenance is a planned corrective action. PREVIOUS SIMILAR EVENTS No previous similar events have occurred at PINGP in the prior 3 years. | ML21081A290
Browns Ferry Nuclear Plant | Unit 1 | Main Steam Relief Valves Lift Settings Outside of Technical Specifications Required Setpoints | 04-02-2021 | On December 4, 2020, the Tennessee Valley Authority was notified of as-found testing results that four Main Steam Relief Valves (MSRVs) from Unit 1 were outside the +/- 3 percent setpoint band required for operability. More than the one allowed MSRV was considered to be inoperable during the entire operating cycle and longer than permitted by Technical Specifications. During this time, BFN, Unit 1 entered a Mode of Operation which was not allowed under this condition. The affected valves remained capable of maintaining reactor pressure within American Society of Mechanical Engineers code limits. It was determined that one MSRV failed due to corrosion bonding between the pilot valve disc and seat, and the other three failed due to setpoint spring relaxation. As a corrective action, all thirteen of the MSRV pilot valves were replaced during the Unit 1 Fall 2020 refueling outage with pilot discs coated in platinum utilizing the Plasma Enhanced Magnetron Sputtering (PEMS) Deposition method. PEMS provides a more consistent and forgiving finish on the pilot valve seating surface and gives the platinum more inherent ductility than what the previous disposition method provided. BFN began using the PEMS method in 2019, so the valves involved in this event did not receive PEMS deposited platinum coatings during their last rebuild. The PEMS method was used for the pilot discs of the rebuilt valves installed during the Unit 1 Fall 2020 refueling outage, and will be used for all pilot discs going forward. Additionally, the MSRV maintenance procedure will be revised to include stricter testing and acceptance criteria for pilot setpoint spring parameters based on industry best-practices. This stricter criteria during testing will drive us to replace springs prior to the point of significant relaxation that results in as-found setpoint testing failures. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 1 05000-259 NUMBER NO. 2020 - 003 - 01 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN) Unit 1 was in Mode 1 at approximately 85 percent power. II. Description of Event A. Event Summary On December 4, 2020, NWS Technologies notified the Tennessee Valley Authority (TVA) with the as-found testing results of the thirteen Main Steam Relief Valves (MSRVs) [RV], which were removed during the Fall 2020 Unit 1 Refueling Outage 13 (U1R13). Four MSRVs (BFN-1-PCV-001-0004, BFN-1-PCV-001-0019, BFN-1-PCV-001-0022, and BFN-1-PCV-001-0041) had as-found lift settings which were outside of the +/- 3 percent band of their setpoints required for operability. Technical Specification (TS) 3.4.3, Safety/Relief Valves (S/RVs), requires twelve of the thirteen S/RVs to be operable for S/RV system [SB] operability. The four MSRVs were found to have been inoperable for an indeterminate period of time during the entire operating cycle between November 20, 2018, and October 3, 2020, and longer than permitted by TS 3.4.3. Throughout this event, the two-stage MSRV pilot valves remained capable of maintaining the reactor pressure below 1375 pounds per square inch gauge (psig), which is the American Society of Mechanical Engineers (ASME) code limit of 110 percent of the vessel design pressure. The valves remained capable of performing their required safety function. The TVA is submitting this report in accordance with Title 10 of the Code of Federal Regulations 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant’s TS. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML21092A022
Cooper Nuclear Station | Unknown Unit | Secondary Containment Differential Pressure Perturbation Exceeds Technical Specifications | 04-12-2021 | On February 9, 2021, Reactor Building differential pressure (dip) became unstable and exceeded the Technical Specifications limit of -0.25 inches of water gauge (wg) resulting in Secondary Containment being declared inoperable. Two causal factors were identified for this event. The first being that Reactor Building d/p controller 'A' has not been tuned to quickly respond to changing environmental conditions. The second factor is that there were no interim actions in place to bridge the gap identified in previous events. Reactor Building d/p controller 'A' was optimally tuned. Follow up troubleshooting showed the as-left settings of the controller would be capable of maintaining Reactor Building d/p within limits when exposed to similar barometric pressure fluctuations. There was no impact on nuclear safety, plant reliability, radiological safety, or industrial safety. Event Notification 55098 was submitted on February 9, 2021, due to the unplanned inoperability of Secondary Containment. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08131/2023 (0B-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into lhe licensing process and fed back lo industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and lnfonnalion Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of lnfonnation and Regulatory Affairs, (3150-0104), Altn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: Qiruil.lmi§_sloll@Omb~ The NRC may nol conduct or sponsor, and a person is not required lo respond to, a collection of infonnation unless the documenl !11.lo;llwww me goy/reading-rmtdoc-collectioas1nuregs1sIaff1sr10221rJD requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER I YEAR SEQUENTIAL REV !cooper Nuclear Station 05000- 1 298 ~~ -I NUMBER 1-NO0. I 001 | PLANT STATUS Cooper Nuclear Station was in Mode 1, Power Operation, at 100 percent power at the time of the event on February 9, 2021. BACKGROUND Secondary Containment serves as a barrier to confine and monitor potential releases during fuel handling operations and is a system that limits the release of radioactive materials to the environment and consists of four subsystems. One of the subsystems is the Reactor Building [EIIS: NG], which encloses the Reactor Pressure Vessel [EIIS: RPV] and Primary Containment [EIIS: NH). The Secondary Containment area (most of the Reactor Building) has supply and exhaust ventilating systems. The supply system furnishes filtered 100% outdoor air to all floors of the building through ductwork. The supply unit has an operating and standby (100% capacity) fan with vortex dampers [EIIS: COMP] to provide regulation of air capacity. The fans will deenergize in the event of loss of offsite power. The exhaust air is induced from the ventilated areas to a common plenum connected to the two exhaust fans, each of 100% capacity. The air is then exhausted to the atmosphere. During normal plant operation, a minimum average negative pressure of 0.25 inches of water gauge (wg) is maintained by differential pressure controllers which receive signals proportional to the pressure difference between outside air and the Secondary Containment atmosphere, and control the position of the exhaust fan vortex dampers. The differential pressure is detected by four separate probes, with one on each side of the Reactor Building. Control action is initiated from the average value of the four sensor probes. If a Loss of Coolant Accident should occur, all ventilation systems of the Primary Containment area and Secondary Containment area will be isolated automatically, and the Standby Gas Treatment system will be automatically initiated. EVENT DESCRIPTION On February 9, 2021, at approximately 02:00 hours, control room operators noted that Reactor Building differential pressure (d/p) had exceeded -0.25 inches wg for less than 30 seconds. At the time, Reactor Building exhaust fan 'A' was in service maintaining Reactor Building d/p at a nominal -0.33 inches wg. The control room staff reviewed the meteorological conditions and decided to shift the Reactor Building exhaust fans. At 02:35 hours, Reactor Building exhaust fan 'B' was placed in service and maintained Reactor Building d/p less than -0.25 inches wg. Engineering personnel reviewed the event and concluded that peaks in Reactor Building d/p and barometric pressure occurred coincident with each other. Technical Specifications (TS) Surveillance Requirement (SR) 3.6.4.1.1 was reviewed and it was noted that the TS basis specifically states that momentary transients on installed instrumentation caused by gusty wind conditions are considered acceptable and are not cause for failure to meet this SR. Meteorological data was reviewed and there was no evidence of gusty wind conditions observed. NRG FORM 366A (0B-2020) Page 2 of 4 | ML21102A278
Watts Bar Nuclear Plant | Unit 1 | Control Room Emergency Ventilation System Inoperable due to Main Control Room Door Being Left Open | 04-20-2021 | At 1511 Eastern Standard Time (EST) on March 1, 2021, a Main Control Room (MCR) alarm was received for low control room positive pressure. In response to the alarm, a Control Room Envelope (CRE) door was found ajar and immediately closed. Technical Specification Limiting Condition for Operation (LCO) 3.7.10, Control Room Emergency Ventilation System (CREVS), was declared not met for both trains and Condition B entered. At 1513 EST on March 1, 2021, the alarm cleared, CREVS was declared operable and LCO 3.7.10, Condition B was exited. The direct cause of this event was a human performance error when an individual traversing the control building complex did not fully challenge and ensure a MCR envelope boundary door was properly latched and secured. Contributing to this event, standards had not been properly established, communicated, and reinforced with plant staff related to operation of plant doors. Immediate corrective actions included closing the MCR door and coaching the individual. Actions to reduce the probability of recurrence include the development and communication of management expectations associated with operating plant doors. This condition is being reported as an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident in accordance with 10 CFR 50.73(a)(2)(v)(D). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Watts Bar Nuclear Plant, Unit 1 05000-390 NUMBER NO. 2021 - 001 - 00 | I. Plant Operating Conditions Before the Event Watts Bar Nuclear Plant (WBN) Unit 1 was in Mode 1 at 100 percent rated thermal power (RTP) and Unit 2 was in Mode 1 at 90 percent RTP. II. Description of Event A. Event Summary On March 1, 2021 at 1511 Eastern Standard Time (EST), a Main Control Room (MCR) alarm was received for low control room positive pressure. In response to the alarm, a Control Room Envelope (CRE) door {EIIS:DR} was found ajar and immediately closed. Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.10, Control Room Emergency Ventilation System (CREVS) {EIIS:VI}, was declared not met for both trains and Condition B entered. At 1513 EST on March 1, 2021, the alarm cleared, CREVS was declared operable and LCO 3.7.10, Condition B was exited. This event is being reported to the Nuclear Regulatory Commission (NRC) under 10 CFR 50.73(a)(2)(v)(D), as an event or condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event No inoperable structures, systems, or components contributed to this condition. C. Dates and approximate times of occurrences Date Time (EST) Event 03/01/21 1511 MCR alarm was received for low control room pressue. TS LCO 3.7.10 was declared no met for both trains and Condition B entered. The MCR door was manually closed and latched. 03/01/21 1513 Units 1 and 2 exited TS LCO 3.7.10, Condition B due to annunciators clearing. D. Manufacturer and model number of each component that failed during the event No equipment failures occurred during the event. Page 2 of 5 | ML21110A087
Donald C. Cook Nuclear Plant | Unit 1 | Condition Prohibited by Technical Specifications Due to Loss of Train B Reserve Power | 04-29-2021 | On February 26, 2021, Donald C. Cook Nuclear Plant Unit 1 and Unit 2 were operating at 100 percent power when an electrical fault occurred between the high side of the Reserve Feed Auxiliary Transformer (RAT) and associated breaker on the Train B Reserve Feed for both units. This caused the circuit breakers to open, removing access to one of the two immediate offsite power sources, and Unit 1 and Unit 2 Train B Reserve Feed was declared inoperable. The Train A Reserve Feed offsite power source, all four Emergency Diesel Generators, and the backup offsite power source remained fully functional. Field investigations resulted in finding a failed bus structure in a loop feed enclosure, which supplied both units. Due to the extensive troubleshooting time required to identify the cause of the problem, enforcement discretion was requested to allow exceeding the 72 hour completion time of Required Action A.3 of Technical Specification 3.8.1 AC Sources - Operating, by an additional 48 hours to complete repairs. Enforcement discretion was granted and repairs were completed on March 2, 2021, within the period of enforcement discretion. The cause of the issue was due to insulator contamination and moisture inside the enclosure. Heaters were installed to prevent condensation of moisture inside the enclosure. The event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), Operation or Condition Prohibited by Technical Specifications. NRC FORM 366A U.S. NUCLEAR REGULATORYCOMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA. Library. and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/l requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NIIMBER YEAR SEQUENTIAL REV Donald C. Cook Nuclear Plant Unit 1 05000315 NUMBER NO. 2021 • 001 00 | EVENT DESCRIPTION On February 26, 2021, at 1008, Donald C. Cook Nuclear Plant Unit 1 and Unit 2 were operating at 100 percent power when multiple alarms indicated in both control rooms that 1-TR101AB and 2-TR201AB, Units 1 and 2 Train B Reserve Feed Auxiliary Transformers (RATs) [EA][XFMR] electrically isolated and de-energized. Operators entered alarm response procedures and suspected the condition was due to an electrical transient. Operations staff declared Train B Reserve Feed inoperable for both units, entering required actions for Limiting Conditions of Operation (LCO) 3.8.1 AC Sources - Operating, Condition A and Condition D. The Train A Reserve Feed offsite power source, all four Emergency Diesel Generators [EK][DG], and the backup offsite power source remained fully functional. Essential Service Water cross-tie valves [Bl]M were closed by operators at 1154, exiting LCO 3.8.1 AC Sources - Operating, Condition D. Initial investigations by station staff found no external visual abnormalities near either unit's RATs or in the switchyard. Transformer 1-TR101AB and 2-TR201AB Phase 1 Lead Differential Relay 12-87-TABLD-1 [EA][87] was found tripped. A clearance for reserve feed power was implemented to facilitate additional testing and inspections. Oil samples were obtained and tested from the RA Ts and indicated satisfactory results. Tan Delta testing was performed of the Phase A cables from the switchyard to the 12AB Loop Feed Enclosure and from the 12AB Loop Feed Enclosure to the RATs with satisfactory results. The 12AB Loop Feed Enclosure upper bus was megger tested with unsatisfactory results. A borescope visual inspection of the upper bus duct was performed and indicated physical evidence of an electrical fault. After removing the top of the upper bus duct, a visual inspection of the inside portion revealed signs of a phase to ground fault and indications of arc tracking along the insulating boots. Additionally, there was evidence of insulator contamination and moisture within the enclosure. Due to the extensive troubleshooting time required to identify the cause of the problem and the scope of repairs, enforcement discretion was requested to allow exceeding the 72 hour completion time of Required Action A.3 of Technical Specification 3.8.1 AC Sources - Operating, by an additional 48 hours to complete repairs. Without enforcement discretion, Unit 1 and Unit 2 were required to be in MODE 3 by 0408 on March 1, 2021, and Mode 5 by 1008 on March 2, 2021. Enforcement discretion (EA-21-04; ADAMS Accession Number: ML21063A568) was granted per phone conversation, for an additional 48 hours on February 28, 2021, which would expire on March 3, 2021 at 1008. Temporary heaters were installed at the 12AB and 12CD Loop Feed Enclosures, to prevent condensation of moisture inside of the enclosures. The faulted bus was splice-repaired, successfully post-maintenance tested, and the loop feed enclosure was re-terminated. Power was restored and Train B Reserve Feed was declared operable and exited the LCO on March 2, 2021, at 0522 within the period of enforcement discretion. The event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), Operation or Condition Prohibited by Technical Specifications, due to exceeding the 72 hour completion time of Required Action A.3 of Technical Specification 3.8.1 AC Sources - Operating. | ML21119A378
Susquehanna Steam Electric Station 05000387 1 of 3 | Unknown Unit | Unplanned lnoperability of the High Pressure Coolant Injection (HPCI) System due to a Primary Containment Isolation (PCIV) Valve Failure to Stroke Full Closed On-demand due to an Intermittent Break in the Close Control Circuitry | 05-06-2021 | On March 9, 2021 at approximately 03:13, during performance of quarterly Unit 1 High Pressure Coolant Injection System (HPCI) valve exercising, dual indication was received in the control room for the HPCI Turbine Exhaust Vacuum Breaker inboard isolation valve (HV155F079) due to the valve failing to stroke fully closed on demand. Upon discovery of the condition, Operations entered Unit 1 Technical Specification (TS) 3.6.1.3, Condition A for one or more penetration flow paths with one Primary Containment Isolation Valves (PCIV) inoperable. The HPCI Turbine Exhaust Vacuum Breaker inboard isolation valve was then closed, resulting in unplanned inoperability of HPCI. At the time the condition was identified, Unit 1 was already in TS 3.5.1, Condition D, HPCI system inoperable, due to the planned surveillance testing. This event was reported by Event Notification 55128 in accordance with 10 CFR 50.72(b)(3)(v)(D). The condition is also being reported in accordance with 10 CFR 50.73(a)(2)(v) as an event or condition that could have prevented fulfillment of a safety function. The cause of the event was an intermittent break in the valve's close control circuitry likely due to dirty contacts on HPCI Turbine Exhaust Vacuum Breaker inboard isolation valve hand switch. Key corrective actions include planned replacement of hand switch (HS15579). There were no actual consequences to the health and safety of the public as a result of this event. U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are Incorporated Into the licensing process and fed back to Industry. Send comments LICE NS EE EVE NT RE PORT { LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6A10M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira submisslon@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person Is not required to respond to, a collection of Information unless the document https://www.nrc.gov/reading-rm/doc-collections/n ur egs/staff/sr1 022/r3D requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LERNUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station, 05000-387 NUMBER NO. Unit 1 2021 001 00 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, approximately 100 percent Rated Thermal Power Unit 2 - Mode 1, approximately 75 percent Rated Thermal Power There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. EVENT DESCRIPTION On March 9, 2021 at approximately 03:13, during performance of quarterly High Pressure Coolant Injection System (HPCI) [EIIS System Code: BJ] valve exercising, dual indication was received in the control room for the HPCI Turbine Exhaust Vacuum Breaker inboard isolation valve (HV155F079) [EIIS Component Code: VACB] due to the valve failing to stroke fully closed on demand. Upon discovery of the condition, Operations entered Unit 1 Technical Specification (TS) 3.6.1.3, Condition A for one or more penetration flow paths with one Primary Containment Isolation Valve (PCIV) inoperable. The HPCI Turbine Exhaust Vacuum Breaker inboard isolation valve was then closed, resulting in unplanned inoperability of HPCI. At the time the condition was identified, Unit 1 was already in TS 3.5.1, Condition D, HPCI system inoperable, due to the planned surveillance testing. After the initial failure, operations personnel were dispatched to the valve and no issues were observed. The valve was successfully stroked open and closed within acceptance times. In addition, maintenance investigations observed and monitored the valve and valve closure circuitry during multiple subsequent valve strokes and no issues were noted. TS 3.6.1.3, Condition A was exited on March 10, 2021 at approximately 18:13 and TS 3.5.1 was exited on March 10, 2021 at approximately 18:59. This event was reported by Event Notification 55128 in accordance with 10 CFR 50.72(b)(3)(v)(D). The condition is also being reported in accordance with 10 CFR 50. 73(a)(2)(v) as an event or condition that could have prevented fulfillment of a safety function. CAUSE OF EVENT The direct cause of the event was an intermittent break in the valve's close control circuitry likely due to dirty contacts on HPCI Turbine Exhaust Vacuum Breaker inboard isolation valve hand switch (HS15579). | ML21126A316
Cooper Nuclear Station 05000 298 1 OF 4 | Unknown Unit | Valve Test Failures Result in Condition Prohibited by Technical Specifications | 05-17-2021 | On March 18 and March 20, 2021, two Target Rock safety relief valve (SRV) pilot assemblies, removed during Refueling Outage 31, failed to lift within Technical Specifications (TS) lift setpoint requirements. The pressure setpoint of the first failed pilot assembly was 1080 psig; the SRV pilot assembly lifted at 1191.9 psig. The pressure setpoint of the second failed pilot assembly was 1100 psig; the SRV pilot assembly lifted at 1180. 7 psig. Three subsequent lifts were performed for the failed SRV pilot assemblies and the results were within the TS pressure setpoint tolerance. The cause of the failure was determined to be corrosion bonding. Although the setpoint lift pressures of the SRV pilot valve assemblies exceeded TS requirements, an analysis of this event concluded the thermal limits, and American Society of Mechanical Engineers overpressure transients, did not exceed allowable limits. Public safety was not at risk. Safety of plant personnel, and plant equipment, was not at risk. A TS Amendment to TS 3.4.3 will be submitted that will address the failure to meet the TS criteria for the Target Rock two-stage SRVs. Following submittal, a tracking mechanism will be established for TS change approval and implementation. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or https://www.nrc.gov/reading-rm/doc-collections/nureqs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Cooper Nuclear Station 05000- 298 NUMBER NO. 2021 - 002 00 | PLANT STATUS Cooper Nuclear Station (CNS) was in Mode 1, Power Operation, at 100 percent power, when the event was discovered; i.e., March 20, 2021. BACKGROUND The pressure relief system includes three American Society of Mechanical Engineers (ASME) code safety valves (SV) [EIIS: SB] and eight safety relief valves (SRV) [EIIS: RV], all of which are located on the main steam lines [EIIS: SB] within the drywall [EIIS: NH], between the reactor vessel [EIIS: RPV] and the first main steam isolation valve [EIIS: ISV]. The SVs provide protection against over pressurization of the nuclear system and discharge directly into the interior space of the drywall. The SRVs discharge to the suppression pool and provide three main functions: overpressure relief operation to limit the pressure rise and prevent safety valve opening, overpressure safety operation to prevent nuclear system over pressurization, and depressurization operation ( opened automatically or manually) as part of the emergency core cooling system [EIIS: BJ, BM, BO]. Technical Specification (TS) Limiting Condition for Operation 3.4.3 requires the safety function of seven SRVs and three SVs to be operable. The nominal set pressure tolerances for these valves are established in CNS TS Surveillance Requirement (SR) 3.4.3.1. The SRVs installed at CNS are Target Rock Model 7567F, two-stage, pilot-actuated valves with pilot assemblies comprised of Stellite 21 pilot discs and Stellite 6B pilot body seats. The pilot assemblies had been in continuous service since installation in Refueling Outage (RE) 30, (Fall of 2018). Corrosion bonding is an industry known problem with Target Rock Model 7567F two-stage relief valves in which the pilot valve bonds/sticks to the in-body seat, resulting in an increased pressure needed to lift the valve. After the corrosion bonding is "broken" following the initial lift, the subsequent lifts are within tolerance. EVENT DESCRIPTION In the Fall of 2020, four main SRV body assemblies and four SRV pilot assemblies were removed during RE31. In March 2021, the SRVs were as-found tested at National Technical Systems Laboratories. The pressure setpoint for SRV pilot assembly serial number 378 is 1080 psig. The TS SR 3.4.3.1 as-found limit acceptance is 1080 +/- 3%. The first actual lift pressure of this SRV pilot assembly was recorded at 1191.9 psig, 10.36% above the pressure setpoint. A second, third, and fourth lift was performed and the results were 1103 psig, 1084 psig, and 1082 psig, all three within 3% of the pressure setpoint. | ML21137A329
Nine Mile Point | Unit 1 | Average Power Range Monitors Declared lnope·rable Due to Trip of Reactor Recirculation Pump 13 | 05-11-2021 | - At 98% power on March 12, 2021 at approximately 21 :02, Reactor Recirculation Pump #13 (RRP 13) tripped while lowering pump flow in preparation to secure it for planned maintenance. Following the RRP trip, the Average Power Range Monitors (APRMs) flow bias trips were inoperable due to reverse flow through the RRP. The APRMs were restored to operable on March 12, 2021 at 2110 when the RRP 13 discharge blocking valve was closed by operations, eliminating the reverse flow condition through the pump. This event is reportable under 10 CFR 50. 72(b)(3)(v)(A) and 10 CFR 50.73(a)(2)(v)(A) as any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: (A) Shut down the reactor and maintain it in a safe shutdown condition. The cause of the RRP 13 trip is generator field overcurrent due to a degraded voltage adjust potentiometer. Corrective actions included replacing the voltage adjust potentiometer. The event described in this LER is documented in the plant's corrective action program. NRC FORM 366 (04-2017) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2020 (04-2017)) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-2 F43), U.S. Nuclear LICENSEE EVENT REPORT (LER) Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and to the Desk Officer, Office of Information and Regulatory Affairs, CONTINUATION SHEET NEOB-10202, (3150-0104), Office of Management and Budget, Washington, DC 20503. If a means used to impose an information collection does not display a currently valid 0MB control number, the (See NUREG-1022, R.3 for instruction and guidance for completing this form NRC may not conduct or sponsor, and a person is not required to respond to, the information http://www.nrc. g ov/readi ng-rm/d oc-col leclions/nuregs/staff/sr1 022/r3/) ' collection. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Nine Mile Point Unit 1 05000220 NUMBER NO. 2021 - 001 00 | I. DESCRIPTION OF EVENT A. PRE-EVENT PLANT CONDITIONS: Prior to the event, Nine Mile Point Unit 1 (NMP1) was in the power operating condition at 98% · reactor power. All five Reactor Recirculation Pumps (RRP) were in operation. B. EVENT: On March 12, 2021, at approximately 21:02, NMP1 experienced a trip of RRP 13 at 98% power. At Nine Mile Point Unit 1, due to the five RRP pump design, a trip of an RRP at power will result in reverse flow through the tripped pump. This reverse flow condition results in an unconservative total flow input to the APRM logic resulting in the APRM flow biased trip set point being higher than the allowable Technical Specification value. As a result, Operations declared the APRMs inoperable. At 21: 10, Operations closed the RRP 13 discharge valve in accordance with special operation procedure N1-SOP-1.3 terminating the reverse flow condition. The APRMs were declared operable and Technical Specification 3.6.2a and g were exited. Nine Mile Point Unit 2 (NMP2) was unaffected by the RRP trip at NMP1. Operations performed the ENS notification (#55137) required by 10 CFR 50. 72(b)(3)(v)(A) and 10 CFR 50. 73(a)(2)(v)(A) as any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: (A) Shut down the reactor and maintain it in a safe shutdown condition. This event has been entered into the plant's corrective action program as issue report IR 4408605. C. INOPERABLE STRUCTURES, COMPONENTS, OR SYSTEMS THAT CONTRIBUTED TO THE EVENT: No other systems, structures, or components contributed to this event. D. DATES AND APPROXIMATE TIMES OF MAJOR OCCURRENCES AND OPERATOR ACTIONS: The dates, times, and major occurrences and operator actions for this event are as follows. March 12, 2021 | ML21144A050
Turkey Point | Unit 3 | Unrecognized Technical Specification Surveillance Requirement Non-Compliance | 06-03-2021 | On 4/15/2021 FPL identified that Reactor Protection System (RPS) Technical Specification Functional Unit (FU) 20 had not met Technical Specification Surveillance Requirements (TSSRs) during 5 discrete periods over the past 3 years. Due to RPS design limitations, FU20, Automatic Trip and Interlock Logic, could not be fully tested above the P8 interlock (45% reactor power). The trip functions not tested are automatically bypassed and not testable above the P8 interlock, but below P8 are active and TSSR 4.3.1.1 is applicable. During the identified periods the completion time was not met. Since the condition was unrecognized, action was not taken, resulting in discrete periods of non-compliance with the TSAS. The subject Actuation Logic Tests have since been completed and test frequencies adjusted in the Surveillance Frequency Control Program to accommodate the RPS system design. All FU20 trip functions are operable and within approved surveillance frequencies. This event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) for a condition prohibited by Technical Specifications. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported r;;)"all("Ot,<,t lessons learned are incorporated into the licensing process and fed back to industry. Send comments ! ..~ "h,. i , LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. = i . .,. , .. ~ " : CONTINUATION SHEET I N n u fo c c le o a ll r e cts R .R e e g s u o la u t r o c r e y @ nr C c o .g m o m v, is a s n i d o n th , e O W M a B s h r i e n v g ie to w n e , r at D : C O MB 2 0 O 5 f 5 fi 5 c - e 0 0 o 0 f 1 In , form or a tion b y a nd e R -m eg a u il l ator to y ·••f!· Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000- I □ NUMBER D NO. Turkey Point Unit 3 250 2001 I - 002 - 00 I I I I | EVENT DESCRIPTION On 4/15/2021 FPL determined that RPS FU20, Automatic Trip and Interlock Logic, had not met TSSR 4.3.1.1. The Actuation Logic Tests (ALT) that apply to several trip functions, due to the design of the RPS [JC], were not being performed at the frequencies specified by the SFCP. The FU20 TSSRs include the ALTs as described in TS 4.3.3.1 Table 4.3-1, the 92-day (quarterly) frequencies for which are assigned by the SFCP. The affected FU20 trip functions tested by the ALTs and their respective power interlocks include: - Power Range Neutron Flux (low setpoint); <P10 (10% power) - Intermediate Range Neutron Flux; <P10 - Source Range Neutron Flux; <P6 (10E-5 cps) - Reactor Coolant Low Flow (2/3 loops); <P8 (45% power) - Reactor Coolant Pump Breaker Open (2/3 loops); <P8 The SFCP previously prescribed a quarterly frequency to the ALT for each of these trip functions. However, the design of the RPS is such that reactor power must be below the associated interlock of each trip function to perform the ALT. The subject ALTs are active below the P8 interlock (45% reactor power). When the reactors are operating at full power these trip functions are bypassed and the ALTs cannot be performed. If the ALT surveillance is past due and reactor power is maneuvered to a level below the corresponding interlock, such as for equipment maintenance or a scheduled outage, the TSSR is not met, rendering the FU20 channel inoperable. TS 3.3.1 Table 3.3-1 Action 8 directs shutdown to Mode 3 within 6 hours if a single channel is inoperable. In cases where both channels are inoperable TS 3.0.3 applies, also directing shutdown to Mode 3 within 6 hours. Since the condition was unrecognized, action pursuant to the TSAS was not taken, resulting in 5 discrete periods of TSAS non-compliance that occurred over the Past Operability Review (POR) assessment period. All of the periods of TS non-compliance during the assessment range occurred during power reductions of Units 3 and 4 for equipment maintenance or scheduled outages. Since there were no load reductions that went below 10% power and scheduled outages begin with a manual reactor trip from approximately 15% power, only the trip functions associated with the P8 (45%) interlock were non-compliant. This includes the Reactor Coolant Low Flow (2/3 loops) and RCP Breaker Open (2/3 loops) reactor trip functions. The evaluation concluded that the discrete periods of TS 3.3.1 or TS 3.0.3 non- compliance were as follows: Unit Period Ch A Ch B Applicable TS 3 9/30/18 04:41 - 10/1/18 00:02 (19 hrs 21 min) X X TS 3.0.3 3 5/18/19 11:08 - 5/20/19 00:50 (37 hrs 42 min) X TS 3.3.1 3 9/26/19 20:54 - 9/27/19 19:31 (22 hrs 37 min) X X TS 3.0.3 3 3/29/20 05:43 - 3/30/20 00:02 (18 hrs 19 min) X X TS 3.0.3 4 3/10/19 05:45 - 3/11/19 00:02 (18 hrs 17 min) X X TS 3.0.3 All FU20 ALT surveillances that could not be performed above their respective interlock power levels had been completed regularly during outage conditions, which is consistent with the design of the Turkey Point RPS. There were no failures during the surveillance testing and therefore no loss of safety function during the periods of TS non-compliance. At no point had any completed surveillance frequency exceeded an 18-month fuel cycle. | ML21154A110
Clinton Power Station | Unit 1 | Reactor Core Isolation Cooling System Card Fuse Failure Results in a Condition Prohibited by Technical Specifications and That Could Have Prevented Fulfillment of a Safetv Function Needed to Control the Release of Radioactive Material | 02-22-2021 | On 12/26/20, at 0205 CST, during performance of Reactor Core Isolation Cooling (RCIC) surveillance procedures, the Division 2 RCIC indication response was not as expected. Troubleshooting determined the indication response was due to failure of the Div. 2 RCIC-5 card, which provides an isolation signal. Technical Specification (TS) 3.3.6.1, Primary Containment and Drywell Isolation Instrumentation, was entered. Past operability review found that the condition existed from 12/21 /20, through 12/26/20, exceeding the TS 3.3.6.1, Action D.1, 24-hour action statement. The Div. 2 RCIC-5 card failed due to an internal blown fuse. The cause of the missed opportunity to identify the failure on 12/21/20 was Operations did not properly recognize the risk associated with the condition and initiate timely actions to evaluate the impact on operability. The card was replaced and tested on 12/26/20, at 1506 CST. Refresher training will be conducted for appropriate Operations personnel regarding the need to perform manual self tests or use alternate indications when anomalous indications or alarms occur. This condition is reportable under 10 CFR 50. 73(a)(2)(i)(B) and 10 CFR 50. 73(a)(2)(v)(C). There was no impact to the health and safety of the public or plant personnel from this condition as the isolation safety function was maintained throughout the event. This event does not meet the criteria for a Safety System Functional Failure. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2C (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. (::·~-~'"'.'.'\ LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by \: ..'.!.'../ .l CONTINUATION SHEET e-mail to lnfocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, (See NUREG-1022, R.3 for instruction and guidance for completing this form 725 17th Street NW, Washington, DC 20503; e-mail: oira submission@omb.eoo.oov. The NRC http :/lwww .nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1 022/r3/) i m nf a o y r m n a o t t io n c o u n n d l u e c s t s o th r e s d p o o c n u s m or e , n t a n re d q u a e s p t e in r g s o o n r r i e s q u n i o ri t n g re q th u e i re c d o lle to c tio re n s p d o is n p d l ay to s , a a c u c r o re lle n c tl t y io v n a l o id 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Clinton Power Station, Unit 1 05000461 NUMBER NO. 2020 • 003 00 | PLANT AND SYSTEM IDENTIFICATION General Electric -- Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EllS) codes are identified in text as [XX]. EVENT IDENTIFICATION Reactor Core Isolation Cooling System Card Fuse Failure Results a Condition Prohibited by Technical Specifications and That Could Have Prevented Fulfillment of a Safety Function Needed to Control the Release of Radioactive Material A. Plant Operating Conditions Before the Event Unit: 1 Event Date: December 26, 2020 Event Time: 0205 Mode: 1 Mode Name: Power Operation Reactor Power: 098 B. Description of Event On December 26, 2020, at approximately 0205 CST, during performance of Reactor Core Isolation Cooling (RCIC) system [BN] steam line flow and supply pressure surveillance procedures 9030.01C034 and 9030.01C035, the Division 2 RCIC indication response was not as expected. Technical Specification (TS) 3.3.6.1, Primary Containment and Drywell Isolation Instrumentation, Action D.1, place affected channel in trip within 24 hours, was entered. Troubleshooting determined the indication response was due to a failure of the Division 2 RCIC-5 card, D-A 14-A 112, which was not sending an isolation signal during the surveillance. The failed Division 2 RCIC-5 card was replaced and successfully tested on December 26, 2020, at 1506 CST and TS 3.3.6.1, Action D.1, was exited. The failed Division 2 RCIC-5 card provides an isolation signal that automatically initiates closure of appropriate Primary Containment Isolation Valves (PCIVs) and drywell isolation valves. A review for past operability found that the condition could have been identified during performance of procedure 9030.01C041, RCIC Turbine Exhaust Diaphragm Pressure, on December 21, 2020, at 1515 CST, when an alarm did not occur as expected. Although the alarm was not required in order to meet TS surveillance requirements based on the procedure acceptance criteria, further investigation determined the failure was an indication the Division 2 RCIC-5 card was not providing an output isolation signal. Therefore, there is firm evidence that the condition existed from December 21, 2020, through December 26, 2020, which exceeded the TS 3.3.6.1, Action D.1, 24- hour action statement. NRC FORM 3E6A (08-2020) Page _2_ of _3_ | ML21159A106
i | Unknown Unit | Condition Prohibited by Technical Specifications due to Failure to Perform Breaker Functional Test | 06-24-2021 | On April 08, 2021 at 09:26 CDT, River Bend Station was operating at 65% reactor power. At that time, while alternating divisions of Control Building Chilled Water from Division 1 to Division 2, Control Building Chiller D (HVK-CHL 10) failed to start. Control Building Chilled Water was restored to service in accordance with station procedures at 09:38 CDT. HVK-CHL 1D did not start because the supply breaker position switch contacts did not connect. A required breaker functional test had not been performed to verify proper operation after HVK-CHL 1D supply breaker was racked to the connect position following tagout restoration on March 30, 2021. This caused HVK-CHL 1D to be aligned as the standby chiller while it was not operable. The cause of the event was a gap in human performance. Corrective Actions include procedure revisions and departmental briefings to ensure awareness and to avoid recurrence. NRC FORM 366A (08-2020) Page 1 of 2 C FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply wilh this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the lIcensIng process and fed back lo Industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate lo the FOIA. Library, and Information Collection Branch (T-6 A10M), U.S. Nuclear Regulatory Commission. Washington, DC 20555-0001, or by e-mail lo CONTINUATION SHEET lnfocollecls.Resource@nrc oov, and the 0MB reviewer at, 0MB Office of Information and Regulatory Affairs. (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Ccmmission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington. DC 20503: e-mail: oira submission@omb.eop.gov The NRG may not conduct or https ://www.nrc.gov/readi ng-rm/doc-collections/nu regs/staff/sr1 022/r3/) sponsor, and a person is not required lo respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV River Bend Station - Unit 1 05000-458 NUMBER NO. 2021 003 00 | EVENT DESCRIPTION On April 08, 2021 at 09:26 CDT, River Bend Station was operating at 65% reactor power. At that time, Control Building Chiller D (HVK-CHL 1D ) failed to start while alternating divisions of Control Building Chilled Water (KM). Control Building Chilled Water was restored to service in accordance with station procedures at 09:38 CDT. A required breaker functional test, which would have verified HVK-CHL 1D (CHU) operability, had not been performed when HVK-CHL 1D supply breaker was racked to the connect position following tagout restoration. This oversight resulted in equipment required by Technical Specifications to be placed in standby without being verified Operable. This condition existed from March 30,2021 at 15:32 CDT until this event occurred on April 08,2021. Technical Specification 3.7.7 Control Building Air Conditioning (CBAC) System 72-hour allowed outage time was exceeded and the required Action to be in Mode 3 within 12 hours was not met. Timeline of events: 03/12/2021 07:39 - HVK-CHL 1D supply breaker tag removed and racked to the connect position. 03/30/2021 15:32 - HVK-CHL 1D was placed in standby 04/08/2021 09:26 - HVK-CHL 1D failed to start during Divisional Swap 04/28/2021 21 :23 - Discovery date - Past Operability Evaluation Complete. This report is being made pursuant to 10 CFR 50.73(a)(2)(i)(B), any operation or condition which was prohibited by the plant's Technical Specifications. SAFETY ASSESSMENT There were no actual nuclear or radiological safety consequences due to this event. This event was of minimal significance to the health and safety of the public. The Control Building Chilled Water System was procedurally restored, and control building temperature margins were not challenged. EVENT CAUSE This event was caused by a gap in human performance. Senior Reactor Operators (SRO) failed to ensure completion of the required functional test due to perceived time pressure. The SRO authorizing the tagout assumed the breaker functional would be added to the Limiting Condition of Operability (LCO) when the tagout was removed. The SRO authorizing the tagout for removal assumed the breaker functional was added to the LCO already. Neither SRO validated their assumptions. All other equipment associated with the tagout was checked and no additional missed breaker functional tests were discovered. HVK-CHL 1D was successfully tested following an adjustment to the supply breaker. CORRECTIVE ACTIONS Operations procedure guidance will be revised to require adding the breaker functional test to the LCO separate from the tagout when the tag is hung. The intent is to standardize when every SRO adds required breaker functionals to LCOs. (Completion tracked by Corrective Action) An Operations Departmental briefing on this event will be developed and distributed. The intent is to ensure department personnel are aware of what occurred so it can be avoided in the future. (Completion tracked by Corrective Action) PREVIOUS SIMILAR EVENTS None | ML21175A038
Susquehanna Steam Electric Station 1 05000387 1 of 3 | Unknown Unit | Inoperability of Computer Room Floor Cooling Fan Caused by Extended Operation with Worn Belts Due | 06-28-2021 | On May 4, 2021 at 11:00, Technical Specification (TS) 3.7.3, “Control Room Emergency Outside Air Supply (CREOAS) System” and TS 3.7.4, “Control Room Floor Cooling System” were entered for Units 1 and 2 to support the investigation of elevated vibration associated with the Division II Computer Room Floor Cooling Fan (0V115B) identified on April 29, 2021. During the May 4, 2021 investigation, 0V115B was found with two of the five belts thrown (disengaged from the sheaves) and one belt beginning to loosen. In the as-found condition, mission time requirements for the Division II systems could not be justified. Concurrent with the elevated vibrations on Division II, the associated Division I systems were inoperable due to trip of the Division I Control Structure (CS) Chiller. Since the vibration is considered to have been the result of the degraded belts, both ventilation trains were concurrently inoperable from April 29, 2021 to April 30, 2021, when the Division I CS Chiller was returned to service. Based on information available, the concurrent inoperability is considered to have existed for longer than allowed by TS 3.0.3 and is reportable as a condition prohibited by TS (10 CFR 50.73(a)(2)(i)(B)) and a condition that could have prohibited the fulfillment of a safety function (10 CFR 50.73(a)(2)(v)(D)). The cause was determined to be extended operation with worn belts due to less than adequate preventive maintenance (PM) replacement interval. Key corrective actions include replacing the belts and revising the PM frequency from eight years to six years. There were no actual consequences to the health and safety of the public as a result of this event. N RC FORM 366 (08-2020) NRC FORM 366A U. S. NUCLEAR REGULATORY COMMISSIONAPPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station, 05000-387 NUMBER NO. Unit 1 2021 002 00 | CONDITIONS PRIOR TO EVENT Unit 1 – Mode 1, approximately 100 percent Rated Thermal Power Unit 2 – Mode 1, approximately 90 percent Rated Thermal Power The Division I Control Structure (CS) Chiller [EIIS System/Component Identifier: VI/CHU] was inoperable when the vibration in the Division II Computer Room Floor Cooling Fan (0V115B) [EIIS System/Component Identifier: VI/FAN] was identified. EVENT DESCRIPTION On May 4, 2021 at 11:00, Technical Specification (TS) 3.7.3, “Control Room Emergency Outside Air Supply (CREOAS) System” and TS 3.7.4, “Control Room Floor Cooling System” were entered for Units 1 and 2 to support the investigation of elevated vibration associated with the Division II Computer Room Floor Cooling Fan (0V115B) which was identified on April 29, 2021. During the May 4, 2021 investigation, 0V115B was found with two of the five belts thrown (disengaged from the sheaves) and one belt beginning to loosen. In the as-found condition, mission time requirements for the Division II systems could not be justified. Concurrent with the elevated vibrations on Division II, the associated Division I systems were inoperable due to trip of the Division I CS Chiller. Since the vibration is considered to have been the result of the degraded belts, both ventilation trains were concurrently inoperable from April 29, 2021 to April 30, 2021, when the Division I CS Chiller was returned to service. Based on information available, the concurrent inoperability is considered to have existed for longer than allowed by TS 3.0.3 and is reportable as a condition prohibited by TS (10 CFR 50.73(a)(2)(i)(B)) and a condition that could have prevented the fulfillment of a safety function (10 CFR 50.73(a)(2)(v)(D)). A detailed timeline of events is as follows: 4/28/2021 at approximately 12:14 - The Division I Control Structure Chiller tripped, and TS 3.7.3 and TS 3.7.4 were entered. 4/29/2021 at approximately 13:00 - Maintenance personnel performing routine predictive maintenance activities, identified that vibrations on the Division II Computer Room Fan were elevated. An immediate operability determination was performed that determined that the fan was operable, and a prompt operability determination was initiated. 4/30/2021 at approximately 20:35 - Division I components were declared operable and TS 3.7.3 and TS 3.7.4 were exited. Division I systems were subsequently placed in lead and Division II were placed in standby. 5/4/2021 at approximately 11:00 - Operations entered TS 3.7.3 and TS 3.7.4 to support investigation of the Division II Computer Room fan elevated vibrations. The fan plenum was inspected identifying two of the five belts thrown (disengaged from the sheaves) and one belt beginning to loosen. Belt replacement was initiated. 5/4/2021 at approximately 14:15 - Repairs were completed. 5/4/2021 at approximately 16:01 - Division II was declared operable and TS 3.7.3 and TS 3.7.4 were exited. Page 2 of 3 | ML21179A288
Susquehanna Steam Electric Station 2 05000388 1 of 3 | Unknown Unit | Condition Prohibited by Technical Specifications Due to Drift of Reactor Pressure Switches | 08-31-2023 | On December 5, 2017, the Unit 2 “C” and Unit 2 “D” Reactor Steam Dome Pressure – Low permissive pressure switches, Microswitch 2 (SW2), were found outside of the Technical Specification (TS) 3.3.5.1 allowable value. Both drifted outside of the upper allowable value which is intended to ensure that the reactor dome pressure has fallen to a value below the Core Spray and Residual Heat Removal (RHR)/Low Pressure Coolant Injection (LPCI) maximum design pressures to preclude over-pressurization of the low pressure systems prior to low pressure injection initiation. Based on the information available, the condition existed for longer than allowed by TS 3.3.5.1 and TS 3.5.1. As such, this is a condition prohibited by TS and is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B). This is also considered a common cause inoperability of independent trains or channels (10 CFR 50.73(a)(2)(vii)), a condition that could have prevented fulfillment of a safety function (10 CFR 50.73(a)(2)(v)(D)), and a single cause that could have prevented fulfillment of safety functions of trains or channels in different systems (10 CFR 50.73(a)(2)(ix)(A)). The cause was determined to be instrument setpoint drift due to temperature/humidity changes and mechanical hysteresis as a result of the original design inputs not accounting for temperature and humidity effects on the switch. Interim compensatory actions include performing calibration using the quarterly calibration procedures every 45 days on Unit 1 and every 30 days on Unit 2. Final corrective action will revise the allowable value for TS 3.3.5.1, Functions 1.c, 1.d, 2.c, and 2.d. There were no actual consequences to the health and safety of the public as a result of this event. N RC FORM 366 (08-2020) NRC FORM 366A U. S. NUCLEAR REGULATORY COMMISSIONAPPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station, 05000-388 NUMBER NO. Unit 2 2017 010 02 | CONDITIONS PRIOR TO EVENT Unit 1 – Mode 1, approximately 100 percent Rated Thermal Power Unit 2 – Mode 1, approximately 100 percent Rated Thermal Power There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. EVENT DESCRIPTION Susquehanna Steam Electric Station (SSES) had been utilizing International Telephone and Telegraph (ITT)-Barton 288A pressure switches in the Reactor Steam Dome Pressure – Low channels that provide the injection permissive for the Core Spray system [EIIS System Identifier: BM] (Technical Specification (TS) 3.3.5.1, Function 1d) and the Residual Heat Removal (RHR)/Low Pressure Coolant Injection system (LPCI) [EIIS System Identifier: BO] (TS 3.3.5.1, Function 2d). Each pressure switch has two microswitches, low (SW1) and high (SW2). All eight obsolete ITT-Barton 288A pressure switches were replaced with General Electric (GE) recommended Cameron-Barton 288A pressure switches between September 6, 2017 and November 15, 2017. The Cameron Barton 288A switches were bench tested prior to installation and calibration checked at the time of installation. Subsequent calibration checks were performed at intervals more frequent than the quarterly TS required calibrations. During these subsequent calibration checks, SW2 of the Unit 2 “C” (PIS-B21-2N021C) and Unit 2 “D” (PIS-B21-2N021D) pressure switches [EIIS System/Component Identifier: JE/PS], were found outside of the TS allowable value. A timeline of events is as follows: September 20, 2017 - the obsolete ITT-Barton 288A pressure switch for PIS-B21-2N021C was replaced with a GE recommended Cameron-Barton 288A pressure switch. October 9, 2017 - the obsolete ITT-Barton 288A pressure switch for PIS-B21-2N021D was replaced with a GE recommended Cameron-Barton 288A pressure switch. October 20, 2017 - PIS-B21-2N021C and PIS-B21-2N021D were calibration checked and were found within the TS allowable value. December 5, 2017 - PIS-B21-2N021C and PIS-B21-2N021D were found outside of the TS allowable value during the calibration check. Both drifted outside of the upper allowable value which is intended to ensure that the reactor dome pressure has fallen to a value below the Core Spray and RHR/LPCI maximum design pressures to preclude over-pressurization of the low pressure systems prior to low pressure injection initiation. PIS-B21-2N021C exceeded the TS allowable value by 1.3 psi. PIS-B21-2N021D exceeded the TS allowable value by 2.8 psi. Both switches were adjusted to within the TS allowable value. After submitting LER 50-388/2017-010-00, two additional instances of drift outside of the TS allowable value were identified. Specifically, the Unit 1 “B” (PIS-B21-1N021B) switch was found outside the TS allowable value on June 5, 2018 and the Unit 2 “C” (PIS-B21-2N021C) switch was again found outside of the TS allowable value on June 6, 2018. These conditions are addressed in LER 50-387(388)/2018-005. Page 2 of 2 | ML21182A041
Susquehanna Steam Electric Station (SSES) | Unit 1 | Condition Prohibited by Technical Specifications Due to Drift of Reactor Pressure Switches | 08-31-2023 | On June 5, 2018, the Unit 1 “B” Reactor Steam Dome Pressure – Low permissive pressure switch, Microswitch 2 (SW2) was found outside of the Technical Specification (TS) 3.3.5.1 allowable value during testing. Subsequently, on June 6, 2018, the Unit 2 “C” Reactor Steam Dome Pressure – Low permissive pressure switch, SW2, was found outside of the TS 3.3.5.1 allowable value during testing. Both drifted outside of the lower allowable value which is intended to ensure that the Emergency Core Cooling System (ECCS) injection prevents the fuel peak cladding temperature from exceeding the limits of 10 CFR 50.46. Based on the information available, the condition existed for longer than allowed by Units 1 and 2, TS 3.3.5.1 and TS 3.5.1. As such, this is a condition prohibited by TS and is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B). This is also considered a common cause inoperability of independent trains or channels (10 CFR 50.73(a)(2)(vii)), a condition that could have prevented fulfillment of a safety function (10 CFR 50.73(a)(2)(v)(D)), and a single cause that could have prevented fulfillment of safety functions of trains or channels in different systems (10 CFR 50.73(a)(2)(ix)(A)). The cause was determined to be instrument setpoint drift due to temperature/humidity changes and mechanical hysteresis as a result of the original design inputs not accounting for temperature and humidity effects on the switch. Interim compensatory actions include performing calibration using the quarterly calibration procedures every 45 days on Unit 1 and every 30 days on Unit 2. Final corrective action will revise the allowable value for TS 3.3.5.1, Functions 1.c, 1.d, 2.c, and 2.d. There were no actual consequences to the health and safety of the public as a result of this event. N RC FORM 366 (08-2020) NRC FORM 366A U. S. NUCLEAR REGULATORY COMMISSIONAPPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station, 05000-387 NUMBER NO. Unit 1 2018 005 02 | CONDITIONS PRIOR TO EVENT Unit 1 – Mode 1, approximately 100 percent Rated Thermal Power Unit 2 – Mode 1, approximately 100 percent Rated Thermal Power There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. EVENT DESCRIPTION Susquehanna Steam Electric Station (SSES) had been utilizing International Telephone and Telegraph (ITT)-Barton 288A pressure switches in the Reactor Steam Dome Pressure – Low channels [EIIS System/Component Identifier: JE/PS] that provide the injection permissive for the Core Spray system [EIIS System Identifier: BM] (Technical Specification (TS) 3.3.5.1, Function 1d) and the Low Pressure Coolant Injection system (LPCI) [EIIS System Identifier: BO] (TS 3.3.5.1, Function 2d). Each pressure switch has two microswitches, low (SW1) and high (SW2). All eight obsolete ITT-Barton 288A pressure switches were replaced with General Electric (GE) recommended Cameron-Barton 288A pressure switches between September 6, 2017 and November 15, 2017 to address drift issues. The Cameron- Barton 288A pressure switches were bench tested prior to installation and calibration checked at the time of installation. Subsequent calibration checks were performed at more frequent intervals than the quarterly TS required calibrations. After replacement, drift issues have continued. Only SW2 was found drifted outside of the TS allowable values. A detailed timeline of events is as follows:  September 20, 2017 - the obsolete ITT-Barton 288A pressure switch for Unit 2 PIS-B21-2N021C was replaced with a GE recommended Cameron-Barton 288A pressure switch.  October 9, 2017 - the obsolete ITT-Barton 288A pressure switch for Unit 2 PIS-B21-2N021D was replaced with a GE recommended Cameron-Barton 288A pressure switch.  November 15, 2017 - the obsolete ITT-Barton 288A pressure switch for Unit 1 PIS-B21-1N021B was replaced with a GE recommended Cameron-Barton 288A pressure switch.  December 5, 2017 – Unit 2 PIS-B21-2N021C and Unit 2 PIS-B21-2N021D were found outside of the TS 3.3.5.1 allowable value during the calibration check. Both drifted outside of the upper allowable value which is intended to ensure that the reactor dome pressure has fallen to a value below the Core Spray and RHR/LPCI maximum design pressures to preclude over-pressurization of the low pressure systems prior to low pressure injection initiation. Unit 2 PIS-B21-2N021C exceeded the TS 3.3.5.1 allowable value by 1.3 psi. Unit 2 PIS-B21-2N021D exceeded the TS 3.3.5.1 allowable value by 2.8 psi. Both switches were adjusted to within the TS allowable value. These conditions are addressed in LER 50-388/2017-010. Page 2 of 2 | ML21182A042
Susquehanna Steam Electric Station | Unit 2 | Condition Prohibited by Technical Specifications Due to Drift of Reactor Pressure Switch Caused by Lack of Requirements for Acclimation of the Instrument to the Operating Environment | 08-31-2023 | On August 10, 2020, the Unit 2 “D” Reactor Steam Dome Pressure – Low permissive pressure switch, Microswitch 2, was found outside of the Technical Specification (TS) 3.3.5.1 allowable value. The switch drifted outside of the upper allowable value which is intended to ensure that the reactor dome pressure has fallen to a value below the Core Spray and Residual Heat Removal (RHR)/Low Pressure Coolant Injection (LPCI) maximum design pressures to preclude over-pressurization of the low pressure systems prior to low pressure injection initiation. Based on the information available, the condition existed for longer than allowed by TS 3.3.5.1, TS 3.5.1, and TS 3.0.3. As such, this is a condition prohibited by TS and is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B). In addition, since the “C” channel (PIS-B21- 2N021C) was surveillance tested just prior to identification of the drift of the “D” channel (PS-B21-2N021D), redundant channels were inoperable at the same time impacting both Core Spray and LPCI functions; therefore, this is also considered a condition that could have prevented fulfillment of a safety function (10 CFR 50.73(a)(2)(v)(D)) and a common cause inoperability of independent trains or channels (10 CFR 50.73(a)(2)(vii)). Drifting outside of the TS allowable value on August 10, 2020 is attributed to vendor documents not specifying requirements related to soaking, acclimating, or exposing the instrument to the environment prior to installation and the switch not meeting vendor published repeatability of 0.25% of full scale. Key corrective actions include changing the Susquehanna vendor manual associated with the pressure transmitters to identify the need to acclimate new (or refurbished) switches to in service conditions for at least 48 hours prior to placing in service and calibrating. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366 (08-2020) NRC FORM 366A U. S. NUCLEAR REGULATORY COMMISSIONAPPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station Unit 2 05000-388 NUMBER NO. 2020 - 002 - 01 | CONDITIONS PRIOR TO EVENT Unit 1 – Mode 1, approximately 100 percent Rated Thermal Power Unit 2 – Mode 1, approximately 100 percent Rated Thermal Power There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. EVENT DESCRIPTION Prior to September 2017, Susquehanna Steam Electric Station (SSES) had been utilizing International Telephone and Telegraph (ITT)-Barton 288A pressure switches in the Reactor Steam Dome Pressure – Low channels [EIIS System/Component Identifier: JE/PS] that provide the injection permissive for the Core Spray system [EIIS System Identifier: BM] (Technical Specification (TS) 3.3.5.1, Function 1d) and the Residual Heat Removal (RHR)/Low Pressure Coolant Injection system (LPCI) [EIIS System Identifier: BO] (TS 3.3.5.1, Function 2d). Due to instrument drift concerns, all eight obsolete ITT-Barton 288A pressure switches were replaced with General Electric (GE) recommended Cameron-Barton 288A pressure switches between September 6, 2017 and November 15, 2017. Following replacement, instrument drift continued to be an issue, and additional corrective action was determined necessary to resolve the drift concerns. The additional corrective action included procuring and installing Cameron- Barton 288A instruments that had been modified to remove an over-range condition and the movement assembly/associated linkages that were determined to be affecting instrument drift. The first of these modified instruments was installed and calibrated on July 8, 2020 in the Unit 2 “D” channel (pressure switch for PS-B21-2N021D). On August 10, 2020, the new PS-B21-2N021D switch, Microswitch 2, was tested for its first surveillance interval and found to be outside of TS acceptance criteria. The switch drifted 1.2 psig outside of the upper allowable value which is intended to ensure that the reactor dome pressure has fallen to a value below the Core Spray and RHR/LPCI maximum design pressures to preclude over-pressurization of the low pressure systems prior to low pressure injection initiation. Based on the information available, the condition existed for longer than allowed by TS 3.3.5.1, “Emergency Core Cooling System (ECCS) Instrumentation,” TS 3.5.1, “ECCS-Operating,” and TS 3.0.3. As such, this is a condition prohibited by TS and is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B). In addition, since the “C” channel (PIS-B21-2N021C) was surveillance tested just prior to identification of the drift of the “D” channel (PS-B21-2N021D), redundant channels were inoperable at the same time impacting both Core Spray and LPCI functions; therefore, this is also considered a condition that could have prevented fulfillment of a safety function (10 CFR 50.73(a)(2)(v)(D)) and a common cause inoperability of independent trains or channels (10 CFR 50.73(a)(2)(vii)). CAUSE OF EVENT Drifting outside of the TS allowable value on August 10, 2020 is attributed to vendor documents not specifying requirements related to soaking, acclimating, or exposing the instrument to the environment prior to installation and the switch not meeting vendor published repeatability of 0.25% of full scale. Page 2 of 3 . | ML21182A044
Fermi 2 | Unknown Unit | Unrecognized Impact of Opening of Barrier Doors on High Energy Line Break Analysis | 07-01-2021 | The Fermi 2 Reactor Building Steam Tunnel (RBST) has a normally closed door which is credited as a hazard barrier for certain high energy line break (HELB) scenarios. On May 3, 2021, while Fermi 2 was operating at 100% reactor power in MODE 1, it was determined that the RBST door had been open on seven occasions within the past three years for longer than required for ingress/egress and that this condition was not bounded by site analyses. If a postulated HELB had occurred while the door was open during those seven occasions, equipment outside the RBST may have been adversely impacted by the post-HELB conditions. It was determined that the conditions were reportable as a condition prohibited by Technical Specifications (TS), loss of safety functions, an unanalyzed condition, a common cause inoperability, and a single cause preventing safety functions in different systems. Due to the door being open for only a short time in each case, a bounding risk evaluation determined that the safety significance was very low. There were no radiological releases associated with this event. The cause of this event was the failure of Operations personnel to properly follow site procedures which prohibited the opening of the door (other than during ingress/egress) without prior evaluation by site engineering. Immediate corrective action was taken to restrict opening of the RBST door to ingress/egress only. Additional longer-term corrective actions are planned to perform new HELB analyses that establish specific conditions under which the RBST door may remain open. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000- NUMBER NO. Fermi 2 341 2021 - 001 - 0 | INITIAL PLANT CONDITIONS Mode – 1 Reactor Power – 100% There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT At 0930 EDT on 5/3/2021, it was determined that, during entries into the Fermi 2 Reactor Building [NG] Steam Tunnel (RBST) on 4/17/2021, 4/18/2021, and 4/21/2021, the RBST door (R1-11) [DR] was not controlled according to site procedures. Door R1-11, when closed, is credited as a hazard barrier for certain high-energy line break (HELB) scenarios. On the identified dates, the RBST door was open for brief periods, but longer than needed for ingress/egress, while personnel were performing maintenance-related activities in the RBST. These brief periods with the door open are not bounded by existing analyses as the door is assumed to be closed throughout HELB events where the postulated break is inside the RBST. The time period that the door was open was less than one hour in each case, as stay times in the room were inherently limited by industrial and radiological conditions. Individuals remained in the area to close the door if needed, but existing analyses do not address the feasibility of performing those actions under the conditions that may be expected following one of the applicable HELB scenarios. The three dates in April 2021 where the door was left opened all occurred during MODE 1 with reactor power at 100%. On those dates, it was not recognized what the impact would be of having the door open. Due to questions raised by the NRC Resident Inspector, an investigation was performed with support by engineering personnel. After reviewing design basis information, it was determined on 5/3/2021 that the plant analyses did not support the opening of the RBST door for more than ingress/egress. Following the identification of this issue on 5/3/2021, a review of the extent of this condition identified other RBST entries during the past three years where the conditions may also not have been bounded by existing analyses. The additional occasions where the door may have been open for longer than needed for ingress/egress were on 9/22/2018 (MODE 3), 10/26/2018 (MODE 1), 11/2/2018 (MODE 1), and 3/21/2020 (MODE 3). Per unit logs, each of these entries were also less than one hour with the exception of the occurrence beginning on 10/26/2018 which lasted approximately 10 hours to support packing leak repairs on a High Pressure Coolant Injection (HPCI) [BJ] Outboard Isolation Valve [ISV]. Although few specifics about these occurrences are available due to the time elapsed, these previous occurrences are included in this LER. The narrative below, while written specifically for the more recent (i.e., April 2021) occurrences, is also generally applicable to these older occurrences. Indications of a steam leak in the RBST led to the decision for personnel to access the RBST and investigate the source of the leak and perform repairs if possible. Since door R1-11 opens into the room, a steam leak in the room could pressurize the room and make it difficult to open from the inside. For this reason, station personnel made the decision to leave the R1-11 door open while any personnel were inside the room. Door R1-11 was not disabled from closing but remained open to facilitate personnel safety to allow for prompt egress if needed. | ML21182A291
Peach Bottom Atomic Power Station | Unit 2 | Safety Relief Valve Inoperability Due to Nitrogen Leakage from Braided Hose Wear | 07-16-2021 | On March 21, 2021 it was identified that the Unit 2 instrument nitrogen compressors were increasing in run hours, with all other related parameters steady. The condition was monitored and trended, and investigation determined the most likely cause to be nitrogen leakage within primary containment. In May, a second step increase in nitrogen leakage occurred, after which the decision was made to down power the unit to permit entry into primary containment and investigate the source of leakage. The plant reached a minimum of approximately 10% power to support this evolution. On May 18, 2021 it was discovered by visual observation that the nitrogen supply to a safety relief valve (RV-2-02- 071K) was the source of the leak. Stainless steel braided hoses (1/2” Swagelok flexible hoses) which supply and return nitrogen from the actuating solenoid valve had rubbed together and worn such that both hoses had failed. The valve was declared inoperable for its Automatic Depressurization System (ADS) function on May 18, 2021 at 0117. The hoses were replaced, restoring operability on May 18, 2021 at 1225, and the unit was returned to full power. There were no other systems which were inoperable during this evolution that contributed to this event. This condition is reportable under 10 CFR 50.73(a)(2)(i)(B) for a condition not allowed by Technical Specifications and NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Peach Bottom Atomic Power Station, Unit 05000- 277 YEAR NUMBER NO. 2 2021 - 002 - 00 | also reportable under 10 CFR 50.73(a)(2)(v)(D) for a loss of safety function for the ADS system, based on subsequent analysis of the leakage. There were no actual safety consequences as a result of this event. Unit Conditions Prior to the Event Peach Bottom Atomic Power Station Unit 2 (PB2) was operating at approximately 10 percent power in MODE 1. There were no structures, systems, or components that were inoperable at the start of the event and contributed to the identified condition. Description of Event On March 21, 2021 it was identified that the PB2 nitrogen compressors were increasing in run hours, with all other related parameters steady. In May, a second step increase in nitrogen leakage occurred. Further investigation determined the most likely cause to be leakage within primary containment, after which the decision was made to down power the unit to permit entry into primary containment and investigate the source of any possible leakage. PB2 reached a minimum of approximately 10% power to support primary containment entry. On May 17, 2021 it was discovered by visual observation that the nitrogen supply to a safety relief valve (RV-2-02-071K) was the source of the leakage. The braided stainless steel hoses (i.e., 1/2” Swagelok flexible hoses) which supply and return nitrogen from the actuating solenoid valve for RV-2-02-071K had rubbed together and worn such that both hoses had failed. This valve which supports an Automatic Depressurization System (ADS) function was declared inoperable on May 18, 2021 at 0117. Analysis of Event The ADS system is an Emergency Core Cooling System (ECCS) which is designed to provide depressurization of the reactor coolant system during a small break loss of coolant accident if high pressure injection fails or is unable to maintain required water level in the reactor vessel. It reduces the reactor pressure vessel pressure to within the operating pressure range of the low pressure ECCS subsystems so that these subsystems can provide coolant inventory makeup. To accomplish this function, pneumatic power is used to actuate the safety relief valves, which are manufactured by Target Rock. The effect of this condition is that one of five ADS valves was not considered operable as required by Technical Specifications (TS) Section 3.5.1. The remaining four valves were operable for this function. As such, the unit would have experienced reduced capacity for depressurization if an emergency depressurization was needed. No conditions requiring depressurization were encountered during the period of inoperability. Failure of the nitrogen supply system did not impact the safety relief valve’s overpressure relief function and, therefore the valve remained operable for this function. This event is reportable under 10CFR 50.73(a)(2)(i)(B) since the safety relief valve was considered inoperable for a period greater than permitted by TS. Peach Bottom TS Limiting Condition for Operation 3.5.1, Condition E for one ADS valve inoperable has a Completion Time of 14 days. Since this condition existed for longer than the LCO duration, this reporting criterion applies. | ML21196A485
Perry Nuclear Power Plant | Unknown Unit | Division 3 EOG lnoperability Resulting in an Operation or Condition Prohibited by Technical Specifications | 06-27-2021 | On June 1, 2021, with the Perry Nuclear Power Plant operating at 100 percent power an operation or condition prohibited by Technical Specifications occurred. During the monthly Division 3 Diesel Generator (DG) run on June 1, 2021, erratic output voltage was noted for approximately 45 seconds after start. At the time operations had reasonable expectation of operability and requested a Follow-up Operability Determination (FOD). Results from the Division 3 DG FOD could not support continued Operability of the Division 3 DG. The Division 3 DG was declared inoperable and unavailable on June 3, 2021 at 18:15. The most plausible cause for the erratic output voltage falling below the allowable band during startup is an internal infant component mortality failure of the voltage regulator. The component will be sent for failure analysis. On June 1, 2021 at 10:15, when erratic output voltage was first noted for the Division 3 Diesel Generator, entry into TS 3.8.1 Condition B and the accompanying actions did not occur. Surveillance requirement 3.8.1.1 was not performed as required within one hour and subsequent action TS 3.8.1 Condition F was also not met to be in Mode 3 in 12 hours. Since completion times were not met for TS 3.8.1 Condition F, this issue is reportable under 50.73(a)(2)(i)(B) as an operation or condition prohibited by the plant's technical specifications. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document http://www. n re.gov/ read i nq-rm/doc-col lections/n u regs/staff/ sr1 022/r3/) requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER J. Lt:.KN YEAR SEQUENTIAL REV 05000- NUMBER NO. Perry Nuclear Power Plant 00440 -I 2021 00 001 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. EVENT DESCRIPTION During the monthly Division 3 Diesel Generator (DG) [EK] run on June 1, 2021, erratic output voltage was noted for approximately 45 seconds after start. Operations had reasonable expectation of operability and requested a Follow-up Operability Determination (FOO). Results from the Division 3 DG FOO could not support continued Operability of the Division 3 DG. The Division 3 DG was declared inoperable and unavailable on June 3, 2021 at 18:15. On June 4, 2021 the new voltage regulator [RG] was replaced and was tested satisfactory and the DG returned to operable status at 21 :25. A review of the Division 3 DG maintenance history revealed that the voltage regulator was replaced and passed the Post Maintenance Test (PMT) on May 15, 2021. No other failures of the Division 3 DG or the voltage regulator could be found during the previous three years. On June 1, 2021 at 10: 15, when erratic output voltage was first noted for the Division 3 Diesel Generator, entry into TS 3.8.1 Condition B and the accompanying actions did not occur. Surveillance requirement 3.8.1.1 was not performed as required within one hour and subsequent action TS 3.8.1 Condition F was also not met to be in Mode 3 in 12 hours. Since completion times were not met for TS 3.8.1 Condition F, this issue is reportable under 50.73(a)(2)(i)(B) as an operation or condition prohibited by the plant's technical specifications. CAUSE The most plausible cause for the erratic output voltage falling below the allowable band during startup is an internal infant component mortality failure of the voltage regulator. The component will be sent for failure analysis. EVENT ANALYSIS A Probabilistic Risk Assessment (PRA) evaluation was performed for the June 3, 2021 Division 3 Diesel Generator voltage regulator lnoperability event. Fire and other external hazards were qualitatively addressed to be of low risk. The analysis of this event results in delta CDF and delta LERF values that are below the acceptable thresholds of 1.0E-06/yr and 1.0E-07/yr, as discussed in Regulatory Guide 1.174 . The risk of this event is therefore considered to be of very low safety significance in accordance with the Regulatory Guidance. CORRECTIVE ACTIONS Completed Actions On June 4, 2021 the voltage regulator was replaced and was tested satisfactory. Scheduled Actions A corrective action was created to send the defective voltage regulator for failure analysis testing. Further corrective action will be taken based on the results. PREVIOUS SIMILAR EVENTS No failures of the Division 3 DG or the voltage regulator could be found during the previous 3 years. COMMITMENTS None | ML21209A105
Browns Ferry Nuclear Plant | Unit 2 | Main Steam Relief Valves Lift Settings Outside of Technical Specifications Required Setpoints | 08-02-2021 | On June 3, 2021, the Tennessee Valley Authority was notified of As-Found testing results that five Main Steam Relief Valves (MSRVs) from Unit 2 were outside the +/- 3 percent set-point band required for operability. More than the one allowed MSRV was considered to be inoperable during the entire operating cycle and longer than permitted by Technical Specifications. During this time, BFN Unit 2 made entries into Modes of Operation that were not allowed under this condition. The affected valves remained capable of maintaining reactor pressure within the American Society of Mechanical Engineers code limits. It was determined that one MSRV failed due to corrosion bonding between the pilot valve disc and seat, and the other four failed due to setpoint spring relaxation. As a corrective action, the MSRV maintenance procedure will be revised to include stricter testing and acceptance criteria for pilot setpoint spring parameters based on industry best-practices. This stricter testing criteria will drive spring replacement prior to a point of relaxation which results in as-found setpoint testing failures. Additionally, all thirteen of the MSRV pilot valves were replaced during the Unit 2 Spring 2021, refueling outage with pilot discs coated in platinum utilizing the Plasma Enhanced Magnetron Sputtering (PEMS) deposition method. PEMS provides a more consistent finish on the pilot valve seating surface and gives the platinum more inherent ductility than what the previous deposition method provided. BFN began using the PEMS method in 2019, so the valves involved in this event did not receive PEMS deposited platinum coatings during their last rebuild. The PEMS method was used for the pilot discs of the rebuilt valves installed during the Unit 2 Spring 2021 refueling outage, and will be used for all pilot discs going forward. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 2 05000-260 NUMBER NO. 2021 - 002 - 00 | I. Plant Operating Conditions before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN) Unit 2 was in Mode 1 at approximately 100 percent power. II. Description of Event A. Event Summary On June 3, 2021, NWS Technologies notified the Tennessee Valley Authority (TVA) with the as found testing results of the thirteen Main Steam Relief Valves (MSRVs) [RV], which were removed during the Spring 2021 Unit 2 Refueling Outage 2 (U2R21). Five MSRVs (BFN-2- PCV-001-0018, BFN-2-PCV-001-0005, BFN-2-PCV-001-0023, BFN-2-PCV-001-0034, and BFN-2-PCV-001-0004) had as found lift settings which were outside of the +/- 3 percent band of their setpoints required for operability. Technical Specification (TS) 3.4.3, Safety/Relief Valves (S/RVs), requires twelve of the thirteen S/RVs to be operable for S/RV system [SB] operability. The five MSRVs were found to have been inoperable for an indeterminate period of time during the entire operating cycle between April 8, 2019, and February 27, 2021, and longer than permitted by TS 3.4.3. Throughout this event, the two stage MSRV pilot valves remained capable of maintaining the reactor pressure below 1375 pounds per square inch gauge (psig), which is the American Society of Mechanical Engineers (ASME) code limit of 110 percent of the vessel design pressure. The valves remained capable of performing their required safety function. The TVA is submitting this report in accordance with Title 10 of the Code of Federal Regulations 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant’s TS. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML21214A128
Hope Creek Generating Station | Unknown Unit | Safety Relief Valve (SRV) As-Found Setpoint Failures | 08-31-2023 | OnJune 14,2021,Hope Creek Generating Station (HCGS) received results that two‘as-found’ setpoint testsfor safety relief valve (SRV) pilot stage assemblies (A and J) had exceeded the lift setting tolerance of +/-3% of the nominal setpoint value prescribed in Technical Specification (TS) 3.4.2.1. Additionally, one SRV(R)did not lift when tested. This is a condition reportable under 10CFR50.73(a)(2)(i)(B). Setpoint exceedancefortwoof theSRV pilot stage assemblies is attributed to corrosion bonding between the pilot discsand seating surfaces, which is consistent with industry experience. This conclusion is based on previous cause evaluations and the repetitive nature of this condition at HCGS and within the BWR industry. The cause of the R SRV not lifting wasmain disc and piston thread wear. This conclusion is based on a failure analysis performed at the vendor. The affected SRV pilot assemblies were replaced with pre-tested, certified spare assemblies. The R SRV was replaced. NRCFORM366A U.S. NUCLEAR REGULATORYCOMMISSION APPROVED BY OMB: NO.3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed LICENSEE EVENT REPORT (LER) back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, CONTINUATION SHEET Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: (See NUREG-1022, R.3 for instruction and guidance for completing this form Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Hope Creek Generating Station 05000-354 2021 - 001 - 00 | PLANT AND SYSTEM IDENTIFICATION General Electric –Boiling Water Reactor (BWR/4) Main Steam –EIIS Identifier {SB}* Safety Relief Valves –EIIS Identifier {SB/RV}* *Energy Industry Identification System {EIIS} codes and component function identifier codes appear as {SS/CCC} IDENTIFICATION OF OCCURRENCE Event Date: June14, 2021 Discovery Date: June 14, 2021 CONDITIONS PRIOR TO OCCURRENCE When the reports of the ‘as-found’ results were received, Hope Creek was in Operational Condition (OPCON) 1,Operation at Power, at 100percent rated thermal power. No other structures, systems or components that could have contributed to the event were inoperable at the time of the event. DESCRIPTION OF OCCURRENCE During the twenty-thirdrefueling outage (H1RF23) at Hope Creek Generating Station (HCGS), seven 2-stageMain Steam safety relief valve (SRV) assemblies {SB/RV}, and one 3-stage SRV assemblywere removed and tested at NWS Technologies. The SRVs are Target Rock Model 7567F two-stage SRVsand Target Rock Model 0867F 3-stage SRVs. On June 14, 2021, HCGS received the results of the 2-stage ‘as-found’ set pressure testing required by Technical Specification (TS) Surveillance Requirement (SR) 4.4.2.2. A total of twoof the sevenSRV pilot stage assemblies had setpoint drift outside of the required TS 3.4.2.1 tolerance values of +/-3% of nominal value. The ‘as-found’ test results for the two2-stage SRVs not meeting the TS requirements are as follows: Valve ID As Found TS Lift Setting Acceptable Band % Difference (psig) (psig) (psig) Actual F013A 1167 1130 1096.1 –1163.9 3.27% F013J 1161 1120 1086.4 –1153.6 3.66% During SRV Main Stage assembly testing required by TS SR 4.4.2.3 at NWS Technologies it was identified that the R SRV main valve did not lift. Technical Specification (TS) 3.4.2.1 requires that the safety function of at least 13 of 14 SRVs be operable with a specified code safety valve function lift setting, within a tolerance of +/-3%. Action (a) of TS 3.4.2.1 specifies “With the safety valve function of two or more of the above listed fourteen safety/relief valves inoperable, be in at least HOT SHUTDOWN within 12 hours and in COLD SHUTDOWN within the next 24 hours.” Therefore, this is a condition reportable under 10CFR50.73(a)(2)(i)(B). NRC FORM366A (08-2020) Page 2 of 3 NRCFORM366A U.S. NUCLEAR REGULATORYCOMMISSION APPROVED BY OMB: NO.3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed LICENSEE EVENT REPORT (LER) back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information (See NUREG-1022, R.3 for instruction and guidance for completing this form and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Hope Creek Generating Station 05000- 354 2021 - 001 - 00 NARRATIVE CAUSE OF EVENT Setpoint exceedancefortwoof the SRV pilot stage assemblies (A and J) is attributedto corrosion bonding between the pilot discs and seating surfaces, which is consistent with industry experience. This conclusion is based on previous cause evaluations, the second lift test being within the acceptable band and the repetitive nature of this condition at HCGS and within the BWR industry. The cause of the R SRV Main failing to actuate is attributed to the main disc and piston thread wear, resulting in side- loading of the main piston within the guide. This allowed slight grooves to form inthe guide in which the piston and rings could bind. This conclusion is based on a failure analysis performed at NWS Technologies. SAFETY CONSEQUENCES AND IMPLICATIONS There were no instances during operating cycle 23 that resulted in any of the fourteen SRVs being declared inoperable and there were no events during that cycle that required operation of the SRVs. The industry has recognized that corrosion bonding occurs during the operating cycle. Once an SRV lifts, the corrosion bond breaks and subsequent openings occur very close to the set point as demonstrated during testing. The deviations observed following H1RF23 testing of SRVs are bounded by margins which exist in current Hope Creek design analyses; thus, the aggregate effect of this conditionhas no safety significance. The R SRV was installed in H1RF20 and withoutfirm evidence of the time that the R SRV would not actuate, this LER assumes for a safety consequence review, that the R SRV was inoperable since it was installed in H1RF20. A review was performed of the additional SRVs that were inoperablein Cycle 21 (B, D, F, G, H, L, M, P–setpoint failures) and Cycle 22 (A, C, D, H, J, K-setpoint failures)anddetermined that the ASME overpressure protection and core thermal limits would not have been exceeded. PREVIOUS EVENTS Similar eventsoccurred during the 2016 (H1RF20) 2018 (H1RF21) and 2020 (H1RF22) Hope Creek refueling outages when multiple SRVs were found out of the TS required limits of +/-3%. These events were reported as LER 354/2016- 003-00, LER 354/2018-002-01 and LER 354/2019-002-00. Athree-year review was performed for other SRVs that failed to lift –no previous failures to lift were identified. CORRECTIVE ACTIONS 1. All seven 2-stage SRV assemblies were removed and replaced with pre-tested, certified 3-stage SRV assemblies (H1RF23). 2. The R SRV was replaced with a 3-stage SRV model. COMMITMENTS There are no regulatory commitments contained in this LER. NRC FORM366A (08-2020) Page 3 of 3 | ML21225A038
River Bend Station | Unit 1 | Core Monitoring System Software Modeling Error Resulted in Conditions Prohibited by Technical Specifications 5 EventDate 6 LERNumber 7 ReportDate 8 OtherFacilitiesInvolved Month Day Year Year S N eq u u m en b t e i r al R No. Month Day Year F N a / c A ilityName 05000 D N oc IA ketNumbe 06 17 202 2021 -004 - 00 06 , 6 21)21 F N a / c A ilityName 05000 D N oc I k A etNumbe 9.OperatingMode 10.PowerLevel 1 100 11.ThisReportisSubmittedPursuanttotheRequirementsof10CFR§: (Checkallthatapply) 10 CFR Part 20 El 20.2203(a)(2)(vi) El 50.36(c)(2) El 50.73(a)(2)(iv)(A) El 50.73(a)(2)(x) El 20.2201(b) El 20.2203(a)(3)(i) El 50.46(a)(3)Oi) El 50.73(a)(2)(v)(A) 10 CFR Part 73 El 20.2201(d) El 20.2203(a)(3)(it) El 50.69(g) El 50.73(a)(2)(v)(B) El 73.71(a)(4) El 20.2203(a)(1) El 20.2203(a)(4) El 50.73(a)(2)(i)(A) El 50.73(a)(2)(v)(C) El 73.71(a)(5) El 20.2203(a)(2)(i) 10 CFR Part 21 50.73(a)(2)(t)(B) El 50.73(a)(2)(v)(D) El 73.77(a)(1)(i) El 20.2203(a)(2)(ii) El 21.2(c) El 50.73(a)(2)(i)(C) El 50.73(a)(2)(vii) El 73.77(a)(2)(i) El 20.2203(a)(2)(iii) 10 CFR Part 50 El 50.73(a)(2)(ii)(A) El 50.73(a)(2)(viii)(A) El 73.77(a)(2)(ii) El 20.2203(a)(2)(iv) El 50.36(c)(1)(i)(A) El 50.73(a)(2)(ii)(B) El 50.73(a)(2)(vsi)(B) El 202203(a)(2)(v) El 50.36(c)(1)(ll)(A) El 50.73(a)(2)(iii) El 50.73(a)(2)(ix)(A) El Other(Specifyhere, inAbstract, orin NRC366A). 12. Licensee ContactforthisLER LicenseeContact Tim Schenk, ManagerRegulatoiy Assurance - . - P (2 ho 2 n 5 e ) N -3 um 8 b 1 e - r 4 t 1 nc 7 lu 7 deAreaCode( . , 13.CompleteOneLineforeachComponentFailureDescnbedinthisReport Cause System Component Masufactarer ReportableToIRIS Cause System Component Manufacturer ReportableToIRIS N/A N/A N/A N/A N/A N/A N/A N/A N/A N/A . 14. Supplemental ReportExpected Month Day Year ‘ NRC FORM366 U.S. NUCLEAR REGULATORYCOMMISSION 108-2020) LICENSEE EVENT REPORT (LER) (SeePage3forrequirednumberofdigitslcharactersforeachblock) (SeeNUREG-1022 R.3forinstructionandgsidanceforcompetingthisform hltps.n’.-.wnrc ov/readrng-riVdrx-co(lectons/nure0s.slafflsr1022/r31) 15. ExpectedSubmission Date No Yes (Ifyes.complete 15. ExpectedSubmission Date) N/A N/A N/A 16, Abstract(Limitto1560spaces.i.e..approoimately15single-spacedtypewrittenlines) On June 17, 2021, with River Bend Station (RBS) operating at 100 percent power, Entergy received a letterfrom GE Hitachi issuing SC 21-04, Revision 1, Fuel Support Side Entry Orifice Meta-Stable Flow for 2 Beam Locations in the BWR/6 Reactors,’ identifying that the Global Nuclear Fuels (GNF) model forfuel affected by the Side Entry Orifices did not accurately account forthe loss coefficients at those core locations causing a local overprediction in Minimum Critical Power Ratio (MCPR) margin. This resulted in the determination by Entergythat a condition prohibited by Technical Specifications (TSs) had existed at RBS and this report being made in accordance with 10 CFR 50.73(a)(2)O)(B). The causeofthe eventwasGNF had not accurately accounted for the loss coefficients at applicable core locations causing a local overprediction in MCPR margin resulting in exceeding the MCPR TS limit. Corrective actions include implementing a penalty to Operating Limit MCPR (OLMCPR) in the core monitoring system via an update to the databank to include all penalties associated with GEH letter SC 21-04, Revision 1, and an update to the current Core Operating Limits Report (COLR). There were no consequences to the general safety of the public, nuclear safety, industrial safety, nor radiological safety. NRC FORM 366A U.S. NUCLEARREGULATORYCOMMISSION APPROVEDBY0MB: NO.3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimatedburden perresponsetocomplywith this mandatorycollectionrequest 80hours Reported / r LICENSEE EVENT REPORT (LER) lessonslearned are incorporated intothelicensingprocess and fed backtoindustry Send comments /1 regardng burden est’nale to the FOIA. Library. and tn!ormato.n Collection Branch (T.6 Al0M. US Nuclear Regulatory Comm:ss’sn. Wasflirgton. DC 20555-0001. or by e-mail to ‘- - ‘ and the0MB reviewe’ at: 0MB OfticeofIntarmatonand Reguatory Altars. (3l5O0l04i. Attn Desk Officerforthe Nuclear Regulatory Commission, 725 17th Street NW. (SeeNUREG-1022, R.3forinstructionandguidanceforcompletingthisform Washington, DC 20503, e-mail: pyqsubni]ssiu oiyrbeny.qov The NRC may not conduct or ht(ps//www.nrc.gov/reading-rrn/c(oc-collections/nuregs/stafl/srlQ22!r3/) sponsor. anda person isnot requiredtorespondto. acolteclionofinformation unless thedocument requestingorreqoiringthecollectiondisplaysacurrentlyvalid0MBcontrolnumber, 1. FACILITYNAME , 2. DOCKETNUMBER 3. LERNUMBER River Bend Station, Unit 1 05000 - 458 YEAR SE N Q U U M EN BE T R IAL R N E O V . 2021 004 00 - - NARRATIVE PlantConditions: River Bend Station (RBS) Unit 1 was operating at 100 percent power in MODE 1. There were no Structures, Systems, or Components thatwere inoperable that contributed to this event. Event Description: On June 17, 2021, with RBS operating at 100 percent power, Entergy received a letterfrom GE Hitachi (GEH) concerning a Part 21 Report. This Part 21 Report was transmitted to Entergy and the NRC documenting an update on the issue related to an underprediction of the Side Entry Orifice (SEO) loss coefficients in core analyses, resulting in a local overprediction in MCPR margin. Specifically, Global Nuclear Fuels (GNF) identified the SEQ loss coefficients forfuel bundle locations adjacent to 2-beam (corner) locations may potentially be higher than the current design basis value that is applied. The MCPR impact on potentially affected bundles that are near limits can potentially reduce this margin by greater than 0.01 in Critical Power Ratio. GEH has completed the evaluation of the condition to determine reportability under 10 CFR Part 21 and is a reportable condition under 10 CFR Part 21.21(a)(2) and a transfer of information under 10 CFR 21.21(b). The basis for reportability is that the change in MCPR associated with this issue could contribute to the exceeding ofa Safety Limit, as defined in the RBS TSs. The history of variable Maximum Fraction of Limiting Core Power Ratio (MFLCPR) for the last 3 years was reviewed. The objective was to identify any period where the MFLCPR (corrected for SC 21-04) exceeded 1.0 for more than 6 hours. During Cycle 20 (May 2018 through March 2019) and Cycle 21 (May 2019 through February 2021) there were multiple periods where MFLCPR was greater than 1.0 for longer than 6 hours. During these instances, the requirements ofTS 3.2.2 were not met; however, during this time period there were no limiting transients that would be a challenge to the Safety Limit and there were no Safety Limit violations. RBS previously performed an Operability Evaluation for SC 21-04 Revision 0 in CR-RBS-2021-3221 CA-Cl, which resulted in the implementation of a compensatory measure for tracking CR-RBS-202l-03221. To ensure compliance until the new COLR is approved, the site issued a standing order to implement the reduced administrative MFLCPR. The site’s review of SC 21-04 Revision 1 was performed and based on that review; the standing order was updated to add additional conservatism. The BWR/6 plant design has supporting cross beams that form a grid structure underneath the core plate. The orientation of SEO’s relative to the beams produces different losses due to the difference in upstream flow areas. These variations influence the SEQ flow patterns and the potential for a meta-stable pressure loss. Because the frequency at which meta-stable losses may occur has not been determined, RBS was evaluated using a bounding loss coefficient (1.9 times the current loss value) at the 2-beam locations. Results show the potential MCPR impact at limiting locations can be greater than 0.01 and will vary by plant and power/flow condition. The MCPR impact is greater than the 0.01 criterion that GEH has historically applied for reporting that a TS Safety Limit (as found in TS 2.1) could have been exceeded as defined under 10 CFR Part 21. Ifthe MCPR impact is greaterthan 0.01 due to possible meta-stable losses atthe 2-beam locations, and if not addressed, the condition could occur at a limiting bundle location and reduce transient margin. This could have resulted in exceeding the Safety Limit Minimum Critical Power Ratio (SLMCPR) if a limiting transient were to have occurred. NRCFORM366A (08-2020) Page2of3 NRC FORM 366A U.S.NUCLEARREGULATORYCOMMISSION APPROVEDBY0MB: NO.3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden perresponsetocomplyw/hthis mandatorycollection request 80 hours Reported ,,.. lessons(earned are nrporated intothe licensing press andfnd backtoindustry. Send comments regarding burden estimate to the FOIA Library, and Information Collection 8ranch (1.6 AIOMI US / COMTINUATION SUET Nuclear Regulatory Commission, Wsshingtor DC 20555-000) or by e-mail to i —Rn e ard he OUB re eue at 0 B Office f inomat n arc Regulatory Affairs, (3t50-0t041, Attn Desk Officerforthe Nuclear RegulatoryCommisssn. 725 17thStreet NW. (SeeNUREG-1022,R.3forinstructionand guidanceforcompletingthisform Washingtcn. DC 20503: e-mail: cra s.c’ ns.p3moeon Toe NRC may not conduct or hops/iwwwnrc.govlieadlng rrn/doc collecfions/nureguissaffisr1022ii3/) sponsor and a person is not required to respond to acollectionofinformation unlessthedocumest requestingorrequiringthecollectiondisplaysacurrentlyvalid0MBcontrolnumber. 1. FACILITYNAME 2. DOCKETNUMBER 3. LERNUMBER River Bend Station, Unit 1 05000 458 YEAR SE N Q U U M EN B T ER IAL R N E O V . - 2021 004 00 - - SafetyAssessment: Therewere no actual consequences forthis event. The RBS Operating Limit MCPR(OLMCPR) is set such that if the plant is operating within this limit, the most limiting operational transient forthe cycle will not result in violation of the SLMCPR. The site reviewed the unit operating history for limiting transients and other analyzed transients that are close to being limiting in the Supplemental Reload Licensing Reports. This review concluded that, for the period reviewed, the limiting transients were turbine trip without bypass, feedwater controllerfailure, generator load reject without bypass, rod withdrawal error, and loss of feedwater heating. Because these limiting transients were not identified in the period reviewed, the margin between the SLMCPR and OLMCPR was adequate for continued SLMCPR protection. The SLMCPR was not exceeded in previous analyzed cycles and the margin between SLMCPR and OLMCPR was sufficient to accommodate the penalty evaluated in SC 21-04, Revision 1. As a result, there was no impact to the health and safety ofthe public or plant personnel from this condition. In addition, this event does not meetthe criteria for a Safety System Functional Failure. Event Cause(s): Based on the Entergy internal review, it was determined that the cause ofthis event was: GNF did not accurately account for loss coefficients atthose core locations causing a local overprediction in MCPR margin resulting in exceeding the MCPR TS limit. These occurrences ofexceeding the MCPR TS limit were beyond the control of Entergy to predict or prevent because it is a legacy design calculation error. Entergy does not have the capability to check these calculations, nor does Entergy have the resources to perform an independent review of all GNF calculations. The methodology used in the reload process has been accepted by Entergy and we do not check underlying calculations that have existed unchanged for multiple cycles. Entergy will credit actions taken by GNF as part ofthe Part 21 notification, including actions they are taking for extent of condition in their calculations. This would include the results of any technical audit they are performing. Entergy Supplier Quality Assurance was notified ofthis Part 21 forfollow-up on the GNF corrective action. CorrectiveActions: To ensure compliance with the MCPR TS, RBS issued the standing order as described above. Complete. RBS will implement a penalty to OLMCPR in the core monitoring system through an update to the databank to include all penalties associated with GEH letter SC 21-04, Revision 1. Completion tracked by Corrective Action Program. RBS will update the current COLR and associated documents to account for all penalties associated with GEH letter SC 21-04, Revision 1. Completion tracked by Corrective Action Program. Entergy’s Supplier QA has added CR-HQN-2021-01048 and SC 21-04 Ri tothe Qualified Supplier List comments sections for GEH/GNF Fuels forfollow-up in the next audit. Complete. Previous SimilarEvents: None. NRCFORM366A (08-2020) Page3of3 | 08-16-2021 | 12. Licensee ContactforthisLER LicenseeContact Tim Schenk, ManagerRegulatoiy Assurance - . - P (2 ho 2 n 5 e ) N -3 um 8 b 1 e - r 4 t 1 nc 7 lu 7 deAreaCode( . , 13.CompleteOneLineforeachComponentFailureDescnbedinthisReport Cause System Component Masufactarer ReportableToIRIS Cause System Component Manufacturer ReportableToIRIS N/A N/A N/A N/A N/A N/A N/A N/A N/A N/A . 14. Supplemental ReportExpected Month Day Year ‘ NRC FORM366 U.S. NUCLEAR REGULATORYCOMMISSION 108-2020) LICENSEE EVENT REPORT (LER) (SeePage3forrequirednumberofdigitslcharactersforeachblock) (SeeNUREG-1022 R.3forinstructionandgsidanceforcompetingthisform hltps.n’.-.wnrc ov/readrng-riVdrx-co(lectons/nure0s.slafflsr1022/r31) 15. ExpectedSubmission Date No Yes (Ifyes.complete 15. ExpectedSubmission Date) N/A N/A N/A 16, Abstract(Limitto1560spaces.i.e..approoimately15single-spacedtypewrittenlines) On June 17, 2021, with River Bend Station (RBS) operating at 100 percent power, Entergy received a letterfrom GE Hitachi issuing SC 21-04, Revision 1, Fuel Support Side Entry Orifice Meta-Stable Flow for 2 Beam Locations in the BWR/6 Reactors,’ identifying that the Global Nuclear Fuels (GNF) model forfuel affected by the Side Entry Orifices did not accurately account forthe loss coefficients at those core locations causing a local overprediction in Minimum Critical Power Ratio (MCPR) margin. This resulted in the determination by Entergythat a condition prohibited by Technical Specifications (TSs) had existed at RBS and this report being made in accordance with 10 CFR 50.73(a)(2)O)(B). The causeofthe eventwasGNF had not accurately accounted for the loss coefficients at applicable core locations causing a local overprediction in MCPR margin resulting in exceeding the MCPR TS limit. Corrective actions include implementing a penalty to Operating Limit MCPR (OLMCPR) in the core monitoring system via an update to the databank to include all penalties associated with GEH letter SC 21-04, Revision 1, and an update to the current Core Operating Limits Report (COLR). There were no consequences to the general safety of the public, nuclear safety, industrial safety, nor radiological safety. NRC FORM 366A U.S. NUCLEARREGULATORYCOMMISSION APPROVEDBY0MB: NO.3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimatedburden perresponsetocomplywith this mandatorycollectionrequest 80hours Reported / r LICENSEE EVENT REPORT (LER) lessonslearned are incorporated intothelicensingprocess and fed backtoindustry Send comments /1 regardng burden est’nale to the FOIA. Library. and tn!ormato.n Collection Branch (T.6 Al0M. US Nuclear Regulatory Comm:ss’sn. Wasflirgton. DC 20555-0001. or by e-mail to ‘- - ‘ and the0MB reviewe’ at: 0MB OfticeofIntarmatonand Reguatory Altars. (3l5O0l04i. Attn Desk Officerforthe Nuclear Regulatory Commission, 725 17th Street NW. (SeeNUREG-1022, R.3forinstructionandguidanceforcompletingthisform Washington, DC 20503, e-mail: pyqsubni]ssiu oiyrbeny.qov The NRC may not conduct or ht(ps//www.nrc.gov/reading-rrn/c(oc-collections/nuregs/stafl/srlQ22!r3/) sponsor. anda person isnot requiredtorespondto. acolteclionofinformation unless thedocument requestingorreqoiringthecollectiondisplaysacurrentlyvalid0MBcontrolnumber, 1. FACILITYNAME , 2. DOCKETNUMBER 3. LERNUMBER River Bend Station, Unit 1 05000 - 458 YEAR SE N Q U U M EN BE T R IAL R N E O V . 2021 004 00 - - | PlantConditions: River Bend Station (RBS) Unit 1 was operating at 100 percent power in MODE 1. There were no Structures, Systems, or Components thatwere inoperable that contributed to this event. Event Description: On June 17, 2021, with RBS operating at 100 percent power, Entergy received a letterfrom GE Hitachi (GEH) concerning a Part 21 Report. This Part 21 Report was transmitted to Entergy and the NRC documenting an update on the issue related to an underprediction of the Side Entry Orifice (SEO) loss coefficients in core analyses, resulting in a local overprediction in MCPR margin. Specifically, Global Nuclear Fuels (GNF) identified the SEQ loss coefficients forfuel bundle locations adjacent to 2-beam (corner) locations may potentially be higher than the current design basis value that is applied. The MCPR impact on potentially affected bundles that are near limits can potentially reduce this margin by greater than 0.01 in Critical Power Ratio. GEH has completed the evaluation of the condition to determine reportability under 10 CFR Part 21 and is a reportable condition under 10 CFR Part 21.21(a)(2) and a transfer of information under 10 CFR 21.21(b). The basis for reportability is that the change in MCPR associated with this issue could contribute to the exceeding ofa Safety Limit, as defined in the RBS TSs. The history of variable Maximum Fraction of Limiting Core Power Ratio (MFLCPR) for the last 3 years was reviewed. The objective was to identify any period where the MFLCPR (corrected for SC 21-04) exceeded 1.0 for more than 6 hours. During Cycle 20 (May 2018 through March 2019) and Cycle 21 (May 2019 through February 2021) there were multiple periods where MFLCPR was greater than 1.0 for longer than 6 hours. During these instances, the requirements ofTS 3.2.2 were not met; however, during this time period there were no limiting transients that would be a challenge to the Safety Limit and there were no Safety Limit violations. RBS previously performed an Operability Evaluation for SC 21-04 Revision 0 in CR-RBS-2021-3221 CA-Cl, which resulted in the implementation of a compensatory measure for tracking CR-RBS-202l-03221. To ensure compliance until the new COLR is approved, the site issued a standing order to implement the reduced administrative MFLCPR. The site’s review of SC 21-04 Revision 1 was performed and based on that review; the standing order was updated to add additional conservatism. The BWR/6 plant design has supporting cross beams that form a grid structure underneath the core plate. The orientation of SEO’s relative to the beams produces different losses due to the difference in upstream flow areas. These variations influence the SEQ flow patterns and the potential for a meta-stable pressure loss. Because the frequency at which meta-stable losses may occur has not been determined, RBS was evaluated using a bounding loss coefficient (1.9 times the current loss value) at the 2-beam locations. Results show the potential MCPR impact at limiting locations can be greater than 0.01 and will vary by plant and power/flow condition. The MCPR impact is greater than the 0.01 criterion that GEH has historically applied for reporting that a TS Safety Limit (as found in TS 2.1) could have been exceeded as defined under 10 CFR Part 21. Ifthe MCPR impact is greaterthan 0.01 due to possible meta-stable losses atthe 2-beam locations, and if not addressed, the condition could occur at a limiting bundle location and reduce transient margin. This could have resulted in exceeding the Safety Limit Minimum Critical Power Ratio (SLMCPR) if a limiting transient were to have occurred. NRCFORM366A (08-2020) Page2of3 | ML21228A240
Grand Gulf Nuclear Station | Unit 1 | Core Monitoring System Software Modeling Error Resulted in Conditions Prohibited by Technical Specifications | 08-31-2023 | On June 17, 2021, with Grand Gulf Nuclear Station (GGNS) operating at 100 percent power, Entergy received a letter from GE Hitachi issuing SC 21-04, Revision1, “Fuel Support Side Entry Orifice Meta-Stable Flow for 2 Beam Locations in the BWR/6 Reactors,” identifying that the Global Nuclear Fuels (GNF) model for fuel affected by the Side Entry Orifices did not accurately account for the loss coefficients at those core locations causing a local overprediction in Minimum Critical Power Ratio (MCPR) margin. This resulted in the determination by Entergy that a condition prohibited by Technical Specifications (TSs) had existed at GGNS and this report being made in accordance with 10 CFR 50.73(a)(2)(i)(B). The cause of the event was GNF had not accurately accounted for the loss coefficients at applicable core locations causing a local overprediction in MCPR margin resulting in exceeding the MCPR TS limit. Corrective actions include implementing a penalty to Operating Limit MCPR (OLMCPR) in the core monitoring system via an update to the databank to include all penalties associated with GEH letter SC 21-04, Revision 1, and an update to the current Core Operating Limits Report (COLR). There were no consequences to the general safety of the public, nuclear safety, industrial safety, nor radiological safety. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 05000 - 416 NUMBER NO. 2021 - 002 - 00 | Plant Conditions: Grand Gulf Nuclear Station (GGNS) Unit 1 was operating at 100 percent power in MODE 1. There were no Structures, Systems, or Components that were inoperable that contributed to this event. Event Description: On June 17, 2021, with GGNS operating at 100 percent power, Entergy received a letter from GE Hitachi (GEH) concerning a Part 21 Report. This Part 21 Report was transmitted to Entergy and the NRC documenting an update on the issue related to an underprediction of the Side Entry Orifice (SEO) loss coefficients in core analyses, resulting in a local overprediction in MCPR margin. Specifically, Global Nuclear Fuels (GNF) identified the SEO loss coefficients for fuel bundle locations adjacent to 2-beam (corner) locations may potentially be higher than the current design basis value that is applied. The MCPR impact on potentially affected bundles that are near limits can potentially reduce this margin by greater than 0.01 in Critical Power Ratio. GEH has completed the evaluation of the condition to determine reportability under 10 CFR Part 21 and is a reportable condition under 10 CFR Part 21.21(a)(2) and a transfer of information under 10 CFR 21.21(b). The basis for reportability is that the change in MCPR associated with this issue could contribute to the exceeding of a Safety Limit, as defined in the GGNS TSs. The history of variable Maximum Fraction of Limiting Core Power Ratio (MFLCPR) for the last 3 years was reviewed. The objective was to identify any period where the MFLCPR (corrected for SC 21-04) exceeded 1.0 for more than 6 hours. During Cycle 22 (August 2018 through January 2020) and Cycle 23 (2020 – Present) there were multiple periods where MFLCPR was greater than 1.0 for longer than 6 hours. During these instances, the requirements of TS 3.2.2 were not met; however, during this time period there were no limiting transients that would be a challenge to the Safety Limit and there were no Safety Limit violations. GGNS previously performed an Op Eval for SC 21-04 Revision 0 in CR-GGN-2021-3024 CA-01, which resulted in the implementation of a compensatory measure for tracking CR-GGN-2021-04909. To ensure compliance until the new COLR is approved, the site issued a standing order for reduced administrative MFLCPR as the compensatory measure. The site’s review of SC 21-04 Revision 1 was performed and based on that review; the standing order was updated to add additional conservatism. The BWR/6 plant design is that it has supporting cross beams that form a grid structure underneath the core plate. The orientation of SEO’s relative to the beams produces the different losses due to difference in upstream flow areas. These variations influence the SEO flow patterns and the potential for a meta-stable pressure loss. Because the frequency at which meta-stable losses may occur has not been determined, GGNS was evaluated using a bounding loss coefficient (1.9 times the current loss value) at the 2-beam location. Results show the potential MCPR impact at limiting locations can be greater than 0.01 and will vary by plant and power/flow condition. The MCPR impact is greater than the 0.01 criterion that GEH has historically applied for reporting that a TS Safety Limit (as found in TS 2.1) could have been exceeded as defined under 10 CFR Part 21. If the MCPR impact is greater than 0.01 due to possible meta-stable losses at the 2-beam locations, and if not addressed, the condition could occur at a limiting bundle location and reduce transient margin. This could have resulted in exceeding the Safety Limit Minimum Critical Power Ratio (SLMCPR) if a limiting transient were to have occurred. | ML21228A259
Grand Gulf Nuclear Station | Unit 1 | Reactor Scram Due to Main Turbine Trio | 08-31-2023 | At 0433 CT on Monday, May 25, 2020, while operating in MODE 1 at approximately 66 percent power, Grand Gulf Nuclear Station (GGNS) experienced an automatic Reactor SCRAM due to a Main Turbine Trip. All systems responded as designed. The plant was stabilized in MODE 3. The Root Cause of the event is that Entergy Engineering Leadership (Corporate Projects and Site Engineering) did not ensure critical assumptions in EC 72780, Turbine Control Protection System - Non-Safety, were documented or validated for turbine shaft movement during operation where a reduction in margin was present in accordance with EN-DC-115, Engineering Change Process roles and responsibilities were not well communicated across organizations, and leadership behaviors were lacking to promote sufficient challenge to achieve an acceptable result to prevent an unplanned Scram. The corrective actions to preclude repetition was to revise EN-HU-104, Technical Task Risk & Rigor, to require creation of a detailed table listing generation risk parameters (setpoints, settings, dimensions) for engineering changes with high generation risk. There were no consequences to the general safety of the public, nuclear safety, industrial safety and radiological safety. This report is made in accordance with 10 CFR 50.73(a)(2)(iv)(A), for any event or condition that resulted in manual or automatic actuation of the Reactor Protection System (RPS). NRG FORM 366 (0B-2020) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) / ...... Estimated burden per response to comply with this mandatory collection request: 80 ~l¼I: , ' LICENSEE EVENT REPORT (LER) hours. Reported lessons learned are incorporated into the licensing process and fed li¥1i back to industry. Send comments regarding burden estimate to the FOIA, Library, ..... CONTINUATION SHEET and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information (See NUREG-1022, R.3 for instruction and guidance for completing this form and Regulatory Affairs, {3150-0104), Attn: Desk Officer for the Nuclear Regulatory http:f/www .nrc.qov/reading-rm/doc-colleclions/nuregs/staff/sr1022/r3/) Commission, 725 17th Street NW, Washington, DC 20503; e-mail: 01ra subm1ss1on@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 05000-416 NUMBER NO. 2020 -002 -02 | Plant Conditions: Grand Gulf Nuclear Station (GGNS) Unit 1 was operating at approximately 66 percent power in MODE 1. There were no Structures, Systems, or Components that were inoperable that contributed to this event. Event Description: At 0433 CT on Monday, May 25, 2020, while operating in MODE 1 at approximately 66 percent power, GGNS experienced an automatic Reactor SCRAM due to a Main Turbine [TA] Trip at a power level beyond the capability of the Turbine Bypass valves. The unit was shutdown without complication using pressure control through the main condenser. The unit tripped during valve testing in the initial power ascension following implementation of a Digital Turbine Control System upgrade during RF22. All systems responded as designed. No loss of offsite power or Engineered Safety Feature actuation occurred. No Emergency Core Cooling System or Emergency Diesel Generator initiations occurred. Main Steam Isolation valves remained open and no radioactive release occurred due to this event. The plant was stabilized in MODE 3. This event was reported under 10 CFR 50.72(b)(2)(iv)(B), for any event that results in tt:ie actuation of the Reactor Protection System (RPS), when the reactor is critical. Event Notification EN54725. This report is made pursuant to 10 CFR 50.73(a)(2)(iv)(A), as any event or condition that results in manual or automatic actuation of the RPS. Event Cause(s): The direct cause of the trip was determined to be inadvertent overspeed signals from two (2) Active Speed Probes which contacted the speed wheel installed on the turbine shaft. The contact resulted from movement of the shaft during operation of the turbine_ The contact occurred when one of four steam lines to the High-Pressure turbine was being isolated during valve stroke testing. The speed sensing probes, and speed sensing wheel had been modified via installation of new equipment during RF22 with a smaller air gap which reduced operating margin. The Root Cause of the event is that Entergy Engineering Leadership (Corporate Projects and Site Engineering) did not ensure critical assumptions in EC 72780, Turbine Control Protection System - Non-Safety, were documented or validated for turbine shaft movement during operation where a reduction in margin was present. In accordance with EN-DC-115, Engineering Change Process roles and responsibilities were not well communicated across organizations, and leadership behaviors were lacking to promote sufficient challenge to achieve an acceptable result to prevent an unplanned Scram. Safety Assessment: The Reactor Scram due to the Main Turbine Trip did not result in actual consequences to safety of the general public, nuclear safety, industrial safety or radiological safety. The safety significance of this event is determined to be low. The response to the Scram was performed in accordance with plant procedures. Plant parameters (reactor level, pressure) were maintained within procedure and safety limits. There were no actual nuclear safety consequences or radiological consequences during the event. | ML21231A135
Grand Gulf Nuclear Station | Unit 1 | Manual Reactor Scram Due To Turbine Hiah Pressure Control Valve Malfunction And Automatic Reactor Water Level Scram | 08-31-2023 | At 0127 CT on August 8, 2020, while operating in MODE 1 at approximately 86 percent power, Grand Gulf Nuclear Station Control Room staff inserted a manual reactor Scram in response to main turbine high pressure control valve oscillations >5% peak to peak and Average Power Range Monitor power swings 7% peak to peak. All systems responded as designed and the plant was stabilized in MODE 3. Subsequently, at 0159 CT on August 8, 2020, reactor water level reached level 3, resulting in initiation of the Reactor Protection System, and an automatic reactor Scram due to a malfunction of the Feedwater Startup Level Control Valve. The Root Causes for this event were: 1) Entergy Engineering Leadership did not ensure the actuator assembly design was fully evaluated and the effects of vibration on the equipment in the Engineering Change were fully evaluated and 2) Entergy Engineering Leadership did not ensure full implementation of Entergy processes as intended to verify Vendor Quality of the valve actuator assembly. The cause of reactor water level reaching level 3 was caused by a malfunction of the Feedwater Startup Level Control Valve. There were no consequences to the general safety of the public, nuclear safety, industrial safety or radiological safety. This report is made in accordance with to 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of the Reactor Protection System. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-202,0,,1, , ....... Estimated burden per response to comply with this mandatory collection request: BO , hours. Reported lessons learned are incorporated into the licensing process and fed ,:~'\ LICENSEE EVENT REPORT (LEA) back to industry. Send comments regarding burden estimate to the FOIA, Library, \~...../ j and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information (See NUREG· 1022, R.3 for instruction and guidance for completing this form and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: http://www.nrc.gov/readinq-rm/doc-collections/nuregs/staff/sr1022/r3/) oira subm1ssion@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 05000-416 NUMBER NO. 2020 -003 -01 | Plant Conditions: Grand Gulf Nuclear Station (GGNS) Unit 1 was operating at approximately 86 percent power in MODE 1. Plant conditions prior to inserting the manual Scram were as follows: pressure control valve oscillations greater than five (5) percent peak-to-peak with Average Power Range Monitor (APRM) power swings seven (7) percent peak-to-peak and 80 Megawatt electric (MWE) swings peak-to-peak on generator output. There were no other structures, systems, or components that were inoperable that contributed to this event. Event Description: At 0127 CT on August 8, 2020, while operating in MODE 1 at approximately 86 percent power, GGNS Control Room staff inserted a manual reactor Scram in response to pressure control valve oscillations greater than five (5) percent. The manual shutdown was due to a Main Turbine [TA] High Pressure Control Valve actuator malfunction. Reactor pressure was controlled with bypass control valves to the main condenser. Reactor level was maintained with condensate and feedwater through Startup Level Control. All control rods fully inserted and there were no complications associated with the Scram. All systems responded as designed and the plant was stable in MODE 3. This event was reported in accordance with 10 CFR 50.72(b)(2)(iv)(B), as any event or condition that results in actuation of the Reactor Protection System (RPS) when the reactor is critical. (Event number 54824.) At approximately 0159 CT on August 8, 2020, reactor water level reached level 3, resulted in initiation of the RPS and an automatic reactor Scram due to a malfunction of the Feedwater [SJ] Startup Level Control Valve. This event was reported in accordance with 10 CFR 50.72(b)(3)(iv)(A), as any event or condition that results in a valid actuation of any of the systems listed in 10 CFR 50.72(b)(3)(iv)(B). (Event number 54824.) This report is made in accordance with 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of the Reactor Protection System. Safety Assessment: The Reactor Scram did not result in actual consequences to safety of the general public, nuclear safety, industrial safety, or radiological safety. The safety significance of this event is determined to be low. The response to the Scram was performed in accordance with plant procedures. Event Cause(s): The direct cause of the pressure control valve oscillations was a loose threaded connection for the LVRT driver plate on the hydraulic actuator for Main Turbine Control Valve 1N 11 F026D. The first Root Cause of the event is that Entergy Engineering Leadership (Corporate Projects and Site Engineering) did not ensure the actuator assembly design was fully evaluated and the effects of vibration on the equipment in EC 72780, Turbine Control Protection System - Non-Safety, were fully evaluated. Vibration on equipment was determined to cause equipment issues with alignment, assembly fasteners to loosen, and assembly parts critical to the function of the actuator assembly NRG FORM 366A (08-2020) Page 2 of 3 | ML21231A136
Grand Gulf Nuclear Station | Unit 1 | A, "' ,.;,., ;, RP.;:ir.tnr ~ccarn Due Io Beactor FP.P.rl Pt Jmn Trin | 08-31-2023 | 12. Licensee Contact for this LER Licensee Contact rrephone Number (Include Area Code) I J eff Hardy, Manager Regulatory Assurance I ( so1 l 437-2103 13. Complete One Line for each Component Failure Described in this Report Cause System Component Manufacturer Reportable To ICES Cause System Component Manufacturer Reportable To ICES X SJ V ABB/Bailey y N/A N/A N/A N/A N/A 14. Supplemental Report Expected Month Day Year 15. Expected Submission Date □ Yes (If yes, complete 15. Expected Submission Date) [8J No NIA N/A N/A ~bstract (Limit to 1400 spaces, i.e., approximately 14 single-spaced typewritten lines) At 2305 CT on August 24, 2020, while operating in MODE 1 at approximately 14 percent power, Grand Gulf Nuclear Station experienced an automatic Reactor scram after a trip of Reactor Feed Pump (RFP) B and subsequent lowering of reactor water level to 11.4 inches Narrow Range. The root cause of the event was that the Reactor Feed Pump "B" Minimum Flow Valve positioner installed during Preventive Maintenance activities failed due to infant mortality within approximately 29 hours of service. This caused the minimum flow valve to close and tripped the pump on low suction flow. Immediate action was replacement and satisfactory testing of the positioner for RFP B prior to unit restart. Additionally, the positioner for the RFP A Minimum Flow Valve was replaced as part of the initial extent of condition review. The corrective action for the root cause is to develop work instructions for those Air Operated Valves (AOV) using ABB/Bailey AV1 or AV2 series positioners to inspect the positioners prior to installation. There were no consequences to the safety of the public, nuclear safety, industrial safety, or radiological safety. This report was made in accordance with 10 CFR 50.73(a)(2)(iv)(A), as any event or condition that results in actuation of the Reactor Protection System. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed LICENSEE EVENT REPORT (LER) back to industry. Send comments regarding burden estimate to the Information Services Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC CONTINUATION SHEET 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer (See NUREG-1022, R.3 for instruction and guidance for completing this form for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or http://www.nrc.qov/reading-rm/doc-collections/nuregs/staff/sr1022/@/) sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 05000-416 NUMBER NO. 2020 -004 -01 | Plant Conditions: Grand Gulf Nuclear Station (GGNS) Unit 1 was operating at approximately 14 percent power in MODE 1 following forced outage FO-23-02. Reactor Feed Pump (RFP) B was in service through the startup level control valve with RFP A in standby. The main generator was offline at the time of the event. There were no structures, systems or components that were inoperable that contributed to this event. Event Description: At 2305 CT on August 24, 2020, while operating in MODE 1 at approximately 14 percent power, GGNS experienced an automatic Reactor scram after a trip of Reactor Feed [SJ] Pump B, reactor water level subsequently lowered to the scram setpoint of 11.4 inches Narrow Range. Reactor feedwater was being supplied by the RFP B through the Startup Level Control Valve. The RFP A was in standby as only one feed pump was required to maintain sufficient inventory for this power level. At 2304, RFP B tripped due to a low suction flow condition. Operations personnel initiated immediate actions to place RFP A in service. However, before RFP A could be placed in service, an automatic reactor scram occurred on low water level. Follow-up investigation revealed that the low feed pump suction flow condition occurred as a result of the RFP B minimum flow valve (1 N21 F503B) failing closed. During troubleshooting, an attempt was made to drive the valve locally, but the valve was unresponsive. The cover of the valve's positioner (1 N21 R0B5B) was removed, and it was discovered that the positioner's pilot valve was stuck. Technicians were able to exercise the pilot valve which allowed the positioner to control the valve. The positioner was subsequently replaced, and the failed positioner was sent to a vendor for failure analysis. All control rods fully inserted and there were no complications. All systems responded as designed. Main Steam Isolation Valves were manually closed to control reactor cooldown rate. Reactor water level was being maintained with the condensate system. This event was reported under 10 CFR 50.72(b)(2)(iv)(B), as any event or condition that results in actuation of the Reactor Protection System when the reactor is crttical. (EN 54855.) This report is made in accordance with 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of the Reactor Protection System. Safety Assessment: The Reactor scram due to the reactor feed pump trip did not result in actual consequences to safety of the general public, nuclear safety, industrial safety, or radiological safety. The safety significance of this event is determined to be low. There were no actual nuclear safety consequences or radiological consequences during the event. Event Cause(s): The direct cause of the condition was that the pilot valve for the Reactor Feed Pump "B" Minimum Flow Valve's positioner stuck in a position that resulted in the minimum flow valve going closed. This directly resulted in the RFP low suction flow condition that triooed RFP B. NRG FORM 3668 (08-2020) Page 2 of 3 | ML21231A137
Grand Gulf Nuclear Station | Unit 1 | Primarv Water Svstem Flow Lowered Causinc Turbine Trio and Subseauent Reactor Scram | 08-19-2021 | 12. Licensee Contact for this LEA L,censee Contact lelephone Number (Include Area Code) I I Jeff Hardv, Manaqer Requlatorv Assurance (269)-764-2011 13. Complete One Line for each ComPOnent Failure Described in this Report Cause System Component Manufacturer Reportable To IRIS Cause System Component Manufacturer Reportable To IRIS NIA NIA NIA NIA NIA NIA NIA NIA NIA NIA 14. Supplemental Report Expected Month Day Year D 1:8] 15. Expected Submission Date NIA NIA NIA Yes (If yes, complete 15. Expected Submission Date) No !Abstract (Limit to 1560 spaces, i.e., approximately 15 single-spaced typewritten lines) On November 6, 2020 at 0239 CT, while operating in MODE 1 at approximately 84 percent power, Grand Gutt Nuclear Station received a signal for low Primary Water system flow to generator bushing C, which resulted in an automatic turbine trip and reactor Scram. All control rods fully inserted and there were no complications associated with the Scram. All systems responded as designed and the plant was stabilized in MODE 3. Primary water is non-radioactive ultra-purified water circulated to and from the generator to cool the generator stator, bushings, and rotor. The root cause of the event is that Entergy Engineering Leadership (Corporate Projects and Site Engineering) made changes to the design of the primary water bushing flow instrumentation loop without fully evaluating the impacts of the changes to the instrumentation feedback quality and existing operating margins to a generator trip. The corrective actions to preclude repetition was to revise EN-HU-104, Technical Task Risk & Rigor, to require creation of a detailed table listing generation risk parameters (setpoints, settings, dimensions) for engineering changes with high generation risk. Corrective action to preclude repetition included modifying the sensing lines for all primary water flow transmitters to obtain the proper slope and to allow back filling the flow instruments. Addrrionally, the margin between the low flow alarm and low flow trip setpoint was increased. There were no consequences to the general safety of the public, nuclear safety, industrial safety, or radiological safety. No radiological release occurred due to this event. This report is made in accordance with 10 CFR 50.73(a)(2)(iv)(A), any event or condrrion that resulted in manual or automatic actuation of the Reactor Protection System. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 /'. ..... \ hours. Reported lessons learned are incorporated into the licensing process and fed LICENSEE EVENT REPORT (LER) back to industry. Send comments regarding burden estimate to the Information \~ ...... ) Services Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC CONTINUATION SHEET 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Ottice of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer (See NUREG-1022, R.3 for instruction and guidance for completing this form for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRG may not conduct or http://www.nrc.gov/reading-rm/doc-colleclions/nuregs/stafflsr1022/r3/) sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 05000-416 NUMBER NO. 2020 -005 -02 | Plant Conditions: Grand Gulf Nuclear Station (GGNS) Unit 1 was operating at 84 percent power in MODE 1. There were no Structures, Systems, or Components that were inoperable that contributed to this event. Event Description: Primary water is non-radioactive ultra-purified water circulated to and from the generator to cool the generator stator, bushings, and rotor. On November 6, 2020 at 0132 CT, during normal steady state operation, the control room received and alarm for low Primary Water (PW) system flow to main generator bushing Phase C. One of the three channels for bushing C flow caused the alarm and then cleared. Indication for all nine flow transmitters in Phases A, B, and C had drifted down in a slow trend over the course of 2-3 hours, with C phase having a steeper rate of degradation. Overall flow indications degraded slightly and the instrument noise level increased significantly the combination of which eventually led to the low flow trip. An actual low flow condition (overall bushing flow below trip setpoint) did not exist in any of the Primary Water flow paths. Alarms continued to come in with increasing frequency. On November 6, 2020 at 0239 CT, while operating in MODE 1 at 84 percent power, GGNS received a signal for primary water system flow to generator bushing C, which lowered below its trip setpoint resulting in an automatic generator and turbine (TA) trip and subsequent automatic reactor Scram. All control rods fully inserted and there were no complications associated with the Scram. All system responded as designed and the plant was stabilized in MODE 3. No radiological releases occurred due to this event. This event was reported under 10 CFR 50.72(b)(2)(iv)(B), as any event or condition that results in actuation of the Reactor Protection System when the reactor is critical. (EN 54986) This report is made in accordance with 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of the Reactor Protection System. Safety Assessment: The reactor Scram due to the turbine trip did not result in actual consequences to safety of the general public, nuclear safety, industrial safety, or radiological safety. The safety significance of this event is determined to be low. Event Cause(s): The direct cause of the generator and turbine trip was gas voids in the primary water system, which degraded generator bushing primary water flow and increased instrument noise in the bushing primary water flow transmitters. This resulted in the bushing flow indication dropping and then reaching its trip setpoint. The root cause of the event is that Entergy Engineering Leadership (Corporate Projects and Site Engineering) made changes to the design of the primary water bushing flow instrumentation loop without fully evaluating the impacts of the changes to the instrumentation feedback quality and existing operating margins to a generator trip. | ML21231A138
Grand Gulf Nuclear Station | Unit 1 | Primarv Water Tank Low Level Causina Turbine Trio and Subseauent Reactor Scram | 08-19-2021 | 12. Licensee Contact for this LEA Licensee Contact relephone Number (Include Area Code) I I Jeff Hardy, Manager Regulatory Assurance (269)-764-2011 13. Complete One Line for each Component Failure Described in this Report Cause System Component Manufacturer Reportable To IRIS Cause System Component Manufacturer Reportable To IRIS N/A N/A N/A N/A N/A N/A N/A N/A N/A N/A 14. Supplemental Report Expected Month Day Year D 15. Expected Submission Date N/A N/A N/A [8J Yes (If yes, complete 15. Expected Submission Date) No ~bstract (Limit to 1560 spaces, i.e., approximately 15 single-spaced typewritten lines) On December 11, 2020, at 1204 CT, while operating in MODE 1 at 100 percent power, Grand Gulf Nuclear Station experienced an Automatic Reactor Scram after a main turbine and generator trip. All Control Rods fully inserted and there were no complications associated with the Scram. All systems responded as designed and the plant was stabilized in MODE 3. The direct cause of the generator and turbine trip was while adding makeup water to the primary water system, the Operator misdiagnosed the response of the Leakage Water Return Valve and closed the valve manually. This led to a trip of the main turbine when primary water system tank level lowered to the trip setpoint of 78 percent. Primary water is non-radioactive, ultra- purified water circulated to and from the generator to cool the generator stator, bushings and rotor. The root causes for this event were: 1) Entergy Engineering Leadership established a design for the Leakage Water Return Valve control logic which was not fully understood and 2) the operating crew lacked adequate knowledge of the Primary Water System to control and stabilize the leakage water standpipe level. To preclude repetition, continuing training on the Primary Water system will be provided to GGNS License Operator and Non-License Operator. Entergy's procedure EN-HU-104, Technical Task Risk and Rigor, was revised requiring a detailed table listing generation risk parameters being revised for engineering changes with high generation risk. Corrective actions included revising the primary water system operating procedure with specific instructions for local manual standpipe level control. There were no consequences to the general safety of the public, nuclear safety, industrial safety, or radiological safety. No radiological releases occurred due to this event. -~, NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 /''\ hours. Reported lessons learned are incorporated into the licensing process and fed LICENSEE EVENT REPORT (LER) back to industry. Send comments regarding burden estimate to the FOIA, Library, \~.....l j and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information (See NUREG-1022, R.3 for instruction and guidance for completing this form and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/@ Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 05000-416 NUMBER NO 2020 -006 -02 | Plant Conditions: Grand Gulf Nuclear Station (GGNS) Unit 1 was operating at 100 percent power in MODE 1. There were no Structures, Systems, or Components that were inoperable that contributed to this event. Event Description: On December 11, 2020 at 1204 CT, while operating in MODE 1 at 100 percent power, GGNS received a signal for low primary water tank level resulting in an automatic generator and turbine [TA] trip and subsequent automatic reactor Scram. Primary water is non-radioactive ultra-purified water circulated to and from the generator to cool the generator stator, bushings, and rotor. All Control Rods fully inserted and there were no complications associated with the Scram. All systems responded as designed and the plant was stabilized in MODE 3. No radiological releases occurred due to this event. This event was reported under 10 CFR 50.72(b)(2)(iv)(B), as any event or condition that results in actuation of the Reactor Protection System when the reactor is critical. (EN 55030) This report is made pursuant to 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of the Reactor Protection System. Safety Assessment: The automatic turbine trip and subsequent reactor Scram did not result in actual consequences to safety of the general public, nuclear safety, industrial safety, or radiological safety. The safety significance of this event is determined to be low. Event Cause(s): The direct cause of the generator and turbine trip was while adding makeup water to the primary water system, the Turbine Building Operator misdiagnosed the response of the Leakage Water Return Valve and closed the valve manually. • This prevented transfer of makeup water from the standpipe to the Primary Water tank. • This action initiated a sequence of events which led to a Main Turbine/Generator trip and Reactor Scram. The first root cause of the event was that Entergy Engineering Leadership (Corporate Projects and Site Engineering) established a design for the Leakage Water Return Valve control logic which was not fully understood and had impacts that changed the operation which were not desired in Engineering Change, EC 72780, Turbine Control Protection System - Non-Safety, resulting in an automatic plant trip. This ultimately reduced the operational margin causing a plant trip. The second root cause of the event was that the operating crew lacked adequate knowledge of the Primary Water System to control and stabilize the leakage water standpipe level. NRG FORM 366A (08-2020) Page 2 of 3 | ML21231A139
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | High Pressure Coolant Injection Inoperable due to Oil Leak | 09-08-2021 | On April 10, 2020 at 0300, an oil leak from 23PCV-12, HPCI Trip System Pressure Control Valve (PCV) resulted in the system being declared inoperable. This condition is being reported as a condition that could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident per 10 CFR 50.73(a)(2)(v)(D) and for a period longer than allowed by Technical Specification 3.5.1 per 10 CFR 50.73(a)(2)(i)(B). Corrective action to replace valve 23PCV-12 was completed and system was restored to service at time 2015 on April 10, 2020. NRC FORM 366 (08-2020) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments CONTINUATION SHEET regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 – 333 NUMBER N0. 2020 – 003 – 01 | Background The High Pressure Coolant Injection (HPCI) System [EIIS Identifier: BJ] is part of the Emergency Core Cooling System (ECCS); HPCI provides and maintains an adequate coolant inventory inside the Reactor Pressure Vessel [RPV] to prevent damage to the reactor core under postulated accident scenarios. The system is comprised of various components which include a turbine, pumps, valves, piping, and instrumentation. The HPCI System may be initiated by automatic or manual means. The HPCI turbine oil system provides for lubrication and cooling of the equipment bearings and other accessories. The oil system also provides control and hydraulic oil to the turbine governor system. Loss of oil pressure to the turbine governor system will cause the steam supply stop valve and turbine control valve to go shut, securing steam to the turbine. The HPCI oil system is not normally pressurized, the system is only pressurized during operational checks of the system and during actual system operation. Event Description While conducting a HPCI monthly operability test (ST-4B), a control oil leak was observed from 23PCV-12. The oil leak is only visible when the oil system is pressurized. Initial leakage rate was estimated at approximately 0.1 gallons per minute. To confirm leak location and validate leak rate, the auxiliary oil pump was restarted. With system oil pressure reestablished, the leak rate was determined to have degraded such that the capability of the HPCI system to meet mission time would be challenged. Event Analysis Level in the HPCI Oil Tank provides net positive suction head (NPSH) to the suctions of the oil pumps for the duration of HPCI mission time. Loss of NPSH to the suction of HPCI Main Lube Oil Pump (23P-1MO) and the HPCI Turbine Aux. Lube Oil Pump (23P-150) will result in a loss of oil pressure to the system bearings and system control valves. Oil pressure is required for operation of the HPCI Turbine Steam Supply Stop Valve (23HOV-1) and HPCI Turbine Control Valve (23HOV-2). Loss of bearing cooling and oil pressure for the stop and control valves would have limited HPCI operation and challenged the capability of the HPCI system to meet its mission time. 23PCV-12 was installed on December 16, 2017. It was identified that this PCV had a vulnerability associated with the HPCI system oil PCV actuator diaphragm due to a manufacturing error, as reported by General Electric-Hitachi MFN 10-192. This error resulted in inadequate fabric reinforcement that is critical to ensure durability and reliability of the diaphragm, preventing tearing of the diaphragm. The failure of 23PCV-12 diaphragm would result in a loss of HPCI system turbine lubricating and control oil through the failed diaphragm. This condition is reportable under 10 CFR 50.73(a)(2)(v)(D), Event or Condition that Could Have Prevented Fulfillment of a Safety Function. Due to the cyclic failure mechanism of the diaphragm, HPCI was inoperable longer than allowed by Technical Specifications (TS) 3.5.1, ECCS Operating. TS 3.5.1 Condition C requires HPCI System be restored to Operable within 14 days or, Condition G, be in Mode 3 and reduce reactor steam dome pressure to ≤ 150 psig within 12 hours. This represents a condition prohibited by Tech Spec and reportable in accordance with 10 CFR 50.73(a)(2)(i)(B). Cause The cause was determined to be a tear in the 23PCV-12 control valve diaphragm, allowing a loss of control oil from the system. Page 2 of 3 | ML21251A585
Edwin I. Hatch Nuclear Plant | Unit 1 | Automatic Reactor Scram And Containment Isolation On Low Reactor Water Level Due To Trip Of Both Reactor Feed Pumps | 10-01-2021 | On 08/03/2021 at 1026 EDT, Unit 1 experienced an automatic reactor SCRAM and containment isolation due to low reactor water level. A spurious trip of a Turbine Building 600V breaker caused a loss of control power and immediate trip of both 1A and 1B reactor feed pumps. Due to loss of reactor feedwater, the reactor water level lowered to the setpoints for the following automatic actuations: reactor SCRAM, High Pressure Coolant Injection (HPCI) start, Reactor Core Isolation Cooling (RCIC) start, and both primary and secondary containment isolation. All safety-related actuations occurred as designed. Reactor operators responded to stabilize the plant and control reactor water level. Unit 2 was not affected. The initial notification to the NRG was documented in Event Notification 55394. Corrective action was completed to replace the failed breaker with a more reliable breaker. This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to actuations of systems listed in 10 CFR 50.73(a)(2)(iv)(B). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and lnfonmation Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555--0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resourre@n1c.gov, and the 0MB reviewer at: 0MB Office of lnfonmation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira submission@omb.eop.gov- The NRG may not conduct or sponsor, and a person is not required lo respond to, a collection of infonmation unless the document http://www.nrc.gov/reading-rm/doc-collections/nureqs/staff/sr1022/r3/} requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 05000-1 DYEA R SEQUENTIAL REV ~-I NUMBER 1-NO~. Edwin I. Hatch Nuclear Plan - Unit 1 321 I 001 | EVENT DESCRIPTION: Prior to the event on 08/03/2021, Unit 1 was operating at 100% power. There were no inoperable structures, systems, or components that contributed to the event. At approximately 1025 EDT, the 1 B Turbine Building 600V breaker 1 R23S002FR6T tripped, due to a spurious trip of its Digitrip 610 trip unit. 1R23S002FR6T is the normal supply breaker to 1A 120/208V Station Service Switchgear 1R23S021. The loss of power to 1 R23S021 resulted in both 1A and 1 B reactor feed pump turbines losing power to their Mark Vie control panels, resulting in a dual reactor feed pump trips. The loss of both reactor feed pumps resulted in a loss of feedwater and lowering of reactor water level. At 1026 EDT, automatic reactor SCRAM and primary containment isolation occurred at the Reactor Pressure Vessel (RPV) Low Water Level setpoint. All control rods fully inserted. After the SCRAM, the actuation setpoint was reached for automatic start of the High Pressure Coolant Injection (HPCI) [EIIS BJ] and Reactor Core Isolation Cooling (RCIC) [EIIS BN] systems and for secondary containment isolation. All safety-related actuations occurred as designed. Reactor operators responded to stabilize the plant and control reactor water level within band. EVENT CAUSE ANALYSIS: The event was determined to be caused by a spurious trip of the Digitrip 610 trip unit on the 1B Turbine Building 600V breaker 1R 23S002FR6T. REPORTABILITY AND SAFETY ASSESSMENT: This event is reportable pursuant to 10 CFR 50. 73(a)(2)(iv)(A) due to the following system actuations: Reactor Protection System (RPS), general containment isolation signals affecting containment isolation valves in more than one system, or Emergency Core Cooling System (ECCS) for Boiling Water Reactors (BWRs) including HPCI and RCIC. There were no safety consequences as a result of this event. There were no safety-related systems that failed during this event. The operating crew responded correctly to the event. The applicable abnormal/emergency operating procedures were entered. The event was within the analysis of the Updated Final Safety Analysis Report (UFSAR) Chapter 15. No radiological release occurred due to this event. CORRECTIVE ACTIONS: The corrective action replaced the Digitrip 610 trip unit on the 1B Turbine Building 600V breaker 1R23S002FR6Twith a General Electric Microversa Trip Plus (MVT+ ) trip unit, which is proven to be more reliable. PREVIOUS SIMILAR EVENTS: Plant Hatch had two previous events caused by spurious trips of Digitrip 610 trip units. These events occurred in 2008 and 2014. In both cases, power was lost to 1 F Control Building 600V bus 1 R24S030. Loss of power to 1R 24S030 did not result in a total loss of a significant plant system, a transient, or a down power of the unit. | ML21274A418
Edwin I. Hatch Nuclear Plant | Unit 1 | Low Pressure Coolant Injection Inoperable Longer Than The Allowed Technical Specification Completion Time | 10-01-2021 | On 08/03/2021 at 11 :50 EDT, while Unit 1 was at 0% power and in MODE 3 following an unplanned reactor SCRAM, the 'B' reactor recirculation discharge isolation valve failed to initially close when required to do so during the restart of the 'A' reactor recirculation pump. The safety function of the reactor recirculation discharge isolation valve is to ensure that Low Pressure Coolant Injection (LPCI) flow does not bypass the core when it injects into the recirculation lines as described in Technical Specification (TS) Bases 3.3.5.1. Further investigation revealed that a loose fuse connection caused intermittent contact within the control power circuitry, resulting in the valve being unable to reliably function. Because the same intermittent position indication of the 'B' reactor recirculation discharge isolation valve was identified on 07/05/2021, it is likely that the reactor recirculation discharge isolation valve and subsequently the 'B' LPCI loop was inoperable for longer than allowed by TS 3.5.1. The corrective action to replace the loose bayonet connectors for the fuse holders has been completed. This condition is reportable per 10 CFR 50.73(a)(2)(i)(B). u_s_ NRC FORM 366A NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request 80 hours. Reported lessons learned are incorporated into the licensing process and fed back lo industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch [T-6 A10M), U.S. Nuclear Regulatory Commission, Washington. DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at 0MB Office of Information and Regulatory Affairs, (3150--0104). Attn: Desk Officer for the Nuclear Regulatory Commission. 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to. a collection of in1ormation unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currenUy vatid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER DYEA R SEQUENTIAL REV Edwin I. Hatch Nuclear Plant - Unit 1 05000- 1 321 ~-I NUMBER 1-NO0. I 002 | EVENT DESCRIPTION: At approximately 11 :50 EDT on 08/03/2021, while Unit 1 was at 0% power and in MODE 3 following an unplanned SCRAM, the 'B' reactor recirculation pump discharge valve (1B31-F031B) [EIIS Code: AD, ISV] was taken to the closed position per procedure during the restart of the 'A' reactor recirculation pump. Light indication immediately extinguished as soon as the 1B 31-F031 B switch was taken to the closed position. Maintenance was dispatched and reported that neither the breaker or overloads were tripped. A few seconds later the light indication came on and the 1B 31-F031 B valve was successfully closed. EVENT CAUSE ANALYSIS: The site's investigation into the brief loss of control power indication revealed that the continuity issues were the result of a loose bayonet connector in the fuse holder for fuse 1 B31-F239. The loose bayonet connector was most likely caused by the maintenance troubleshooting activities performed on 07/05/2021 for a failed MOV motor. The prior troubleshooting activities included the removal and re-installation of both control fuses for the 1B31-F031B valve, which likely loosened the bayonet connectors. A loose bayonet connector would have caused the power supply to the control circuit of the 1B 31-F031 B valve to become intermittent, and would have ultimately prevented stroking the 1B31-F031B valve when the switch was placed in the closed position. REPORTABILITY AND SAFETY ASSESSMENT: The normal position for the 1B31-F031 B valve is open with an active safety function to close. This safety function ensures that Low Pressure Coolant Injection (LPCI) [EIIS Code: BO] flow does not bypass the core when it injects into the recirculation lines as described in Technical Specification (TS) Bases 3.3.5.1, and provides for core cooling and reactor coolant pressure boundary integrity. With unreliable control circuitry continuity, the closure of valve 1B31-F031B could not be guaranteed during a Loss of Coolant Accident (LOCA). and thus provided reasonable assurance that operability could not be maintained. Because the operation of valve 1B31-F031B was unreliable from at least 07/05/2021 through 08/05/2021, the 'B' LPCI loop would have been inoperable for a period of time longer than allowed by Condition B of TS Limiting Condition of Operation (LCO) 3.5.1. The were no safety consequences as a result of this event. The other low pressure Emergency Core Cooling Systems, the 'A' loop of LPCI and both Core Spray pumps [EIIS Code: BM], remained operable through the event. CORRECTIVE ACTIONS: The 'B' LPCI loop was declared inoperable, and the loose bayonet connectors for the fuse holders were replaced (control fuses 1B31-F239 and 1B31-F240) on 08/05/2021. PREVIOUS SIMILAR EVENTS: None NRG FORM 366A (08-2020) Page 2 of 2 | ML21274A738
Sequoyah Nuclear Plant | Unit 1 | Exceeded Breach Margin Renders Both Trains of the Auxiliary Building Gas Treatment System Inoperable | 10-19-2021 | On August 20, 2021, at 0905 eastern daylight time main control room operators were notified that auxiliary building secondary containment enclosure (ABSCE) boundary Door A118 was open. This was discovered by Fix-it-now personnel that were in the process of establishing compensatory measures associated with an active breach permit for Door A118. A past operability evaluation determined that ABSCE Door A118 had been left open without compensatory measures in place on four occasions between August 18 and August 20, 2021. The open door created a breach of the ABSCE boundary that exceeded the allowed breach margin and rendered both trains of the Auxiliary Building Gas Treatment System (ABGTS) inoperable. Additionally, the POE determined that due to the unknown inoperability of the ABGTS, the requirements of Limiting Condition for Operation 3.7.12 Condition E were not met. The cause of the event was miscommunication between the Work Control Center Senior Reactor Operator and Maintenance Services personnel on the requirements of the ABSCE breaching procedure, related to the work being performed, resulting in a breach permit not being issued when required. Corrective actions included revising the ABSCE breaching procedure to clarify exception requirements and require a breach permit if an ABSCE door will be left open greater than the allowable time and briefings with Operations personnel concerning the requirements of the ABSCE breaching procedure. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Sequoyah Nuclear Plant Unit 1 05000-327 NUMBER NO. 2021 - 003 - 00 | I. Plant Operating Conditions Before the Event At the time of the event, Sequoyah Nuclear Plant (SQN) Units 1 and 2 were in Mode 1 at 100 percent rated thermal power. II. Description of Event A. Event Summary: On August 20, 2021, at 0905 eastern daylight time (EDT), main control room (MCR) operators were notified that auxiliary building [EIIS: NF] secondary containment enclosure (ABSCE) boundary Door [EIIS: DR] A118 was open. This was discovered by Fix-it-now (FIN) personnel that were in the process of establishing compensatory measures associated with an active breach permit for Door A118. The arrival of FIN personnel, with a breach permit and appropriate compensatory actions to close the door as required, allowed operators to determine the ABSCE was operable at the time of discovery. Investigation revealed Maintenance Services personnel had been taking equipment through the door as part of ongoing work associated with a glycol chiller replacement project. The work order had instructions to obtain an ABSCE breach permit; however, when Maintenance Services personnel reported to the Work Control Center (WCC) to obtain the permit, the WCC senior reactor operator (SRO) incorrectly determined an ABSCE breach permit was not required. As a result, ABSCE Door A118 was left open without a breach permit and required compensatory measures until FIN personnel discovered the issue at 0905. A past operability evaluation (POE) determined that ABSCE Door A118 had been left open without compensatory measures in place on four occasions between August 18 and August 20, 2021 (the longest period the door was open without compensatory measures in place was approximately 21 minutes). The open door created a breach of the ABSCE boundary that exceeded the allowed breach margin. The four occasions should have caused entry into Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.12, Condition B for two trains of the Auxiliary Building Gas Treatment System (ABGTS) [EIIS: VF] inoperable due to an inoperable ABSCE boundary in Mode 1, 2, 3, or 4 and Condition E for a required train of ABGTS inoperable with fuel stored in the spent fuel pool. The inoperability of two trains of the ABGTS during the required mode of applicability constitutes an event or condition that could have prevented fulfillment of a safety function of structures or systems that are needed to: (C) control the release of radioactive material and (D) mitigate the consequences of an accident. This LER documents the reportable event under 10 CFR 50.73(a)(2)(v)(C) and 10 CFR 50.73(a)(2)(v)(D). Additionally, the POE determined that due to the unknown inoperability of the ABGTS, the requirements of LCO 3.7.12 Condition E were not met. Condition E requires immediately suspending all crane operations with loads over the spent fuel pool. Contrary to this | ML21292A181
Edwin t. Hatch Nuclear Plant | Unit 1 | Unit 1 High Pressure Coolant Injection System discharge valve failure to open 5. Event Data 8. LER Number 7. Report Date 8. Other Facllltlff Involved Monlh Day Yur Year Sequential Revlalon Month Day Yor Facility Name Docket Number Number No. 05000 - - 09 08 2021 2021 003 00 11 01 2021 Fac!Hty Name Docllet Number 05000 rO. 9. Operating Mode Power Level 1 100 11. This Report Is Submitted Pursuantto the Requirements of 10 CFR §: (Check all that apply) 10 CFR Part 20 □ 20.2203(a)(2)(vl) □ 50.36(c)(2) □ 50. 73(a)(2)(1v)(A) □ 50. 73(a)(2)(x) □ 20.2201(b) □ 20.2203(a)(3)(1) □ 50.48(a)(3)(11) □ 50. 73(a)(2)(v)(A) 10 OfRPart73 □ 20.2201(d) □ 20.2203(a)(3)(11) □ 50.89(g) □ 50. 73(a)(2)(v)(B) □ 73. 71.(a)(4) □ 20.2203(a)(1) □ 20.2203(a)(4) □ 50,73(a)(2)(1)(A) □ SO. 73(a)(2)(v){C) □ 73.71(a)(5) D 20.2203(a)(2)(1) 10 OF-R Part 21 □ 50.73(a)(2)(I)(B) ~ 50. 73(a)(2)(v)(D) □ 73.77(8)(1)(1) D □ 20.2203{a){2){H) 21.2(c) □ 50. 73(a)(2)(1)(C) □ so. 73(a)(2)(vll) □ 73. 77(a)(2)(I) D □ 20.2203(a){2)(iil) 10 CFR Part 50 □ 50.73(a)(2)(11)(A) 50.73(a)(2)Mlll(A) □ 73.77(a)(2)(11) □ 20.2203(a)(2}(1v) □ 50.36(c)(1)(1)(A) □ 50.73(8)(2)(11)(8) □ 50. 73(a)(2)(vlll)(B) □ 20.2203(a)(2)(v) □ 50.36(c)(1 )(ll)(A) □ 50.7 3(a)(2}(111) □ 50. 73(a)(2)(Ix)(A) □ OTHER (Specify here, in abstract, .or NRC 366A). 12. Licensee Contact for this LER LicenaNContact Phone Number (!nol!lclt IIWI IIOC!1) Edwin I. Hatch / Jimmy Collins - Licensing Manger 912-453e2342 13. Complete One Line for each Component Failure Described In this Report Cauae System ComJ)Oflent Manufacturer Reportable to IRIS Cause System Component Msnufai;turvr Rtportl»lt to IRl!I A BJ ISV L200 y 14. Supplemental Report Expected YHr Ill ID 15. Expected Submlaalon Date No Yes (If yes, ~mplete 15. Expected Submission Date) 16. Abstract (Limit lO 1560 spaces. Le., approximately 15 single-spaced typewritten lines) On September 8, 2021, while Unit 1 was at 100% rated thermal power, the High Pressure Coolant Injection (HPCI) pump discharge isolation valve was stroked closed as a part of a valve surveillance activity. Up to this point, HPCI was operable, When the valve was given an open signal, the valve did not return to the open position. Without the ability to open this valve, HPCI is inoperable. Systematic troubleshooting determined that the pinion gear key in the valve actuator had not been properly staked during previous maintenance activities in 2006, leading to the key moving and the pinion gear disengaging from the actuator motor shaft. This caused the valve to become inoperable, not allowing it to stroke to the open position. As a corrective action, the pinion gear key was properly staked per procedure to the actuator motor shaft and the pinion gear reinstalled. .• NQC F,O..R-M. .3,6 6A U.S, NUCLl;AR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/3112023 j00,2020) Estimated burden per response lo comply 111th this m3!!(falofy collection request: 80 houis. Reported lessons lllamed ~ incorporalaQ inlQ the llcensk1g ~ and !81! b;lc!t lo inl!lll!~, Send comments ' '. ..... '\ .! LICEN C S O E N E T I E N V U E A N T T IO R N E P S O HE R E T T ( LER) l N ll u g c a l r e d a in r g b R w e d g e u n la e to s r t y im ale C o to m t m he is s F i O on IA , , U W br a a s ly h , i n a g n t d o n I , n for D m C at ion 2 C 0 o 5 l 5 le 5 c -0 tio 0 n 0 s 1 . B ra o n r d l (T by -6 A1 e 0 -m M a }. i l u. s to . \, "./ lnfocollec1S.Resouroe@nrc.gov, and the 0MB reviewef at QMB Office ot lnlon!tation and Regulatoly Affairs, (315(}0104), Attn: Desk Officer~ the Nuclear Regulaloly Commlssi>n, 725171h Straet NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington. DC 20503; e-mail: ~~t!la.®i· The NRC may not conduct or t'lltP~!lwww,nrc.govJce.agJ119.~--couecuonwnur.ea1/Jtafff111m/mJ sponsor, and a PMOO is not required to l9Sj)Olld to, a ootleclion of infonnatiQn 1&1less the docurpent requesting or requiring the collection displays a cumintly vaid 0MB conbot null!ber. 1. FACILITYNAME 2. DOCKET NUMBER 3. LER NUMBER r:Y:E:A7R SEQUENTIAL REV 05000-1 Edwin I. Hatch Nuclear Plant Unit 1 321 I~ -I NUMBER 1-NO0. 003 NARRATIVE EVENT DESCRIPTION: On September 8, 2021 at 0159, while Unit 1 was in MODE 1 at 100% rated thermal power, the High Pressure Coolant Injection (HPCI) pump [EIIS BJ} discharge isolation valve [EIIS ISV] was stroked closed as a part of a valve surveillance activity. Up to this point, HPCI was operable. When the valve was given an open signal, the valve did not return to the open position. Without the ability to open this valve, HPCI is inoperable. There was no other safety related equipment inoperable that contributed to this event. HPCI was returned to operable status on September 9, 2021 at 1444. EVENT CAUSE ANALYSIS: Systematic troubleshooting determined that the pinion gear key in the valve actuator had not been properly staked during previous maintenance activities in 2006, leading to the key moving and the pinion gear disengaging from the actuator motor shaft. This caused the valve to become inoperable, not allowing it to stroke to the open position. The cause of the incorrect staking was the SNC maintenance electrician performing the activity in 2006 did not peen enough metal to retain the key as was required in the guidance/procedure. REPORTABILITY ANO SAFETY ASSESSMENT: HPCI does not have a redundant system; therefore, this condition is being reported as an event or condition that at the time of discovery could have prevented the fulfillment of the safety function per 10 CFR 50.73{a)(2)(v)(D). While the HPCI system was inoperable, the Reactor Core Isolation Cooling (RCIC) system and low pressure emergency core cooling systems were operable. Therefore, there were no safety consequences due to this event. The operating crew responded correctly to the event. The event was within the analysis of the UFSAR Chapter 15. There was not a release of radioactivity during this event. CORRECTIVE ACTIONS: As a correc.tive action, the pinion gear key was properly staked per procedure to the actuator motor shaft and the pinion gear reinstalled. PREVIOUS SIMILAR EVENTS: None NRC FORM 366A {06-2020) Page 2 of 2 | 11-01-2021 | On September 8, 2021, while Unit 1 was at 100% rated thermal power, the High Pressure Coolant Injection (HPCI) pump discharge isolation valve was stroked closed as a part of a valve surveillance activity. Up to this point, HPCI was operable, When the valve was given an open signal, the valve did not return to the open position. Without the ability to open this valve, HPCI is inoperable. Systematic troubleshooting determined that the pinion gear key in the valve actuator had not been properly staked during previous maintenance activities in 2006, leading to the key moving and the pinion gear disengaging from the actuator motor shaft. This caused the valve to become inoperable, not allowing it to stroke to the open position. As a corrective action, the pinion gear key was properly staked per procedure to the actuator motor shaft and the pinion gear reinstalled. .• NQC F,O..R-M. .3,6 6A U.S, NUCLl;AR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/3112023 j00,2020) Estimated burden per response lo comply 111th this m3!!(falofy collection request: 80 houis. Reported lessons lllamed ~ incorporalaQ inlQ the llcensk1g ~ and !81! b;lc!t lo inl!lll!~, Send comments ' '. ..... '\ .! LICEN C S O E N E T I E N V U E A N T T IO R N E P S O HE R E T T ( LER) l N ll u g c a l r e d a in r g b R w e d g e u n la e to s r t y im ale C o to m t m he is s F i O on IA , , U W br a a s ly h , i n a g n t d o n I , n for D m C at ion 2 C 0 o 5 l 5 le 5 c -0 tio 0 n 0 s 1 . B ra o n r d l (T by -6 A1 e 0 -m M a }. i l u. s to . \, "./ lnfocollec1S.Resouroe@nrc.gov, and the 0MB reviewef at QMB Office ot lnlon!tation and Regulatoly Affairs, (315(}0104), Attn: Desk Officer~ the Nuclear Regulaloly Commlssi>n, 725171h Straet NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington. DC 20503; e-mail: ~~t!la.®i· The NRC may not conduct or t'lltP~!lwww,nrc.govJce.agJ119.~--couecuonwnur.ea1/Jtafff111m/mJ sponsor, and a PMOO is not required to l9Sj)Olld to, a ootleclion of infonnatiQn 1&1less the docurpent requesting or requiring the collection displays a cumintly vaid 0MB conbot null!ber. 1. FACILITYNAME 2. DOCKET NUMBER 3. LER NUMBER r:Y:E:A7R SEQUENTIAL REV 05000-1 Edwin I. Hatch Nuclear Plant Unit 1 321 I~ -I NUMBER 1-NO0. 003 | EVENT DESCRIPTION: On September 8, 2021 at 0159, while Unit 1 was in MODE 1 at 100% rated thermal power, the High Pressure Coolant Injection (HPCI) pump [EIIS BJ} discharge isolation valve [EIIS ISV] was stroked closed as a part of a valve surveillance activity. Up to this point, HPCI was operable. When the valve was given an open signal, the valve did not return to the open position. Without the ability to open this valve, HPCI is inoperable. There was no other safety related equipment inoperable that contributed to this event. HPCI was returned to operable status on September 9, 2021 at 1444. EVENT CAUSE ANALYSIS: Systematic troubleshooting determined that the pinion gear key in the valve actuator had not been properly staked during previous maintenance activities in 2006, leading to the key moving and the pinion gear disengaging from the actuator motor shaft. This caused the valve to become inoperable, not allowing it to stroke to the open position. The cause of the incorrect staking was the SNC maintenance electrician performing the activity in 2006 did not peen enough metal to retain the key as was required in the guidance/procedure. REPORTABILITY ANO SAFETY ASSESSMENT: HPCI does not have a redundant system; therefore, this condition is being reported as an event or condition that at the time of discovery could have prevented the fulfillment of the safety function per 10 CFR 50.73{a)(2)(v)(D). While the HPCI system was inoperable, the Reactor Core Isolation Cooling (RCIC) system and low pressure emergency core cooling systems were operable. Therefore, there were no safety consequences due to this event. The operating crew responded correctly to the event. The event was within the analysis of the UFSAR Chapter 15. There was not a release of radioactivity during this event. CORRECTIVE ACTIONS: As a correc.tive action, the pinion gear key was properly staked per procedure to the actuator motor shaft and the pinion gear reinstalled. PREVIOUS SIMILAR EVENTS: None | ML21305A874
Grand Gulf Nuclear Station | Unit 1 | Hiah Pressure Core Sorav Declared lnooerable | 11-04-2021 | 12. Licensee Contact for this LER Licensee Contact relephone Number (Include Area Code) I Jeff Hardy, Manager Regulatory Assurance I (802)-380-s 124 13. Complete One Line for each Component Failure Described in this Report Cause System Component Manufacturer Reportable To IRIS Cause System Component Manufacturer Reportable To IRIS X BJ RLY GE N N/A N/A N/A N/A N/A 14. Supplemental Report Expected Month Day Year D 15. Expected Submission Date N/A N/A N/A Yes (If yes, complete 15. Expected Submission Date) ~ No ~bstract (Limit to 1560 spaces, i.e., approximately 15 single-spaced typewritten lines) On September 9, 2021, at 0033 CT, while Grand Gulf Nuclear Station was operating in MODE 1 at 70 percent power, the control room received the following alarms: High Pressure Core Spray System (HPCS) Out of Service, along with HPCS Motor Operated Valve/Overload Power loss status light. Additionally, the HPCS Min Flow to Suppression Pool light indication was lost. An operator and electrician were dispatched to the HPCS Min Flow to Suppression Pool Breaker, reporting back that the breaker was in the closed position. Troubleshooting identified the following: HPCS MIN FLO TO SUPP POOL, control circuit alarm relay, shorted causing the control transformer fuse to fail. The direct cause of equipment failure was the alarm relay, associated with breaker HPCS Min Flow to Suppression Pool Breaker, failed due to the coil shorting. This caused the control circuit fuse to blow resulting in the inability to open the High Pressure Core Spray min flow valve to the suppression pool. Immediate action taken was to replace the damaged relay and associated control fuse. There were no consequences to the general safety of the public, nuclear safety, industrial safety or radiological safety. No radiological releases occurred due to this event. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (0B-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed LICENSEE EVENT REPORT (LER) back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects. Resource@nrc.gov. and the 0MB reviewer at: 0MB Office of Information and (See NUREG-1022, R.3 for instruction and guidance for completing this form Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr10221r3/) Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 05000-416 NUMBER NO. 2021 -003 -00 | Plant Conditions: Grand Gulf Nuclear Station (GGNS) Unit 1 was operating at 70 percent power in MODE 1. There were no Structures, Systems, or Components that were inoperable that contributed to this event. Event Description: On September 9, 2021, at 0033 CT, the control room received the following alarms: High Pressure Core Spray System (HPCS) [BJ] Out of Service, 1H13-P601-16A-H5 along with HPCS Motor Operated Valve/Overload Power loss status light. Additionally, the HPCS Min Flow to Suppression Pool light indication was lost. An operator and electrician were dispatched to the HPCS Min Flow to Suppression Pool Breaker [BKR] (52-170109) and reported back that breaker was in the closed position. Troubleshooting the cause of the event identified that the HPCS MIN FLO TO SUPP POOL, control circuit alarm relay [RL Y] device shorted causing the control transformer fuse to fail. This caused the hand switch for the Min Flow Valve to be non-functional. Loss of the control fuse caused the Min Flow Valve to be inoperable and resulted in declaring HPCS inoperable. The inability to open the Min Flow Valve adversely affects overall system injection response time to inject and provide containment isolation by closing. This event was reported under 10 CFR 50.72(b)(3)(v)(D), any event or condition which could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident. (EN 55451) This report is made in accordance with 10 CFR 50.73(a)(2)(v)(D), any event or condition that could have prevented the fulfillment of the safety function needed to mitigate the consequences of an accident. Safety Assessment: There were no actual consequences for this event. The event posed no threat to the health and safety of the general public or to nuclear safety as HPCS was inoperable but available. Industrial safety was not challenged, and there was no potential or actual radiological release during the event. Event Cause(s): The direct cause of equipment failure was the alarm relay, associated with breaker 52-170109, failed due to the coil shorting. This caused the control circuit fuse to blow resulting in the inability to open the High Pressure Core Spray min flow valve to the suppression pool. Corrective Actions: Work Order 567580 replaced the shorted control circuit alarm relay and blown control circuit fuse. Completed. Generate Preventive Maintenance to replace General Electric (GE) alarm relay on the same 10-year frequency as the associated circuit breakers. AR 21010831 Previous Similar Events: None. | ML21308A491
Surry Power Station | Unit 1 | Unanalyzed Condition Due to Appendix R Concern Identified With Cable Separation | 11-11-2021 | On September 13, 2021, at 1822 EDT, an apparent non-compliance with 10 CFR 50, Appendix R, Section III.G.2 (separation of redundant fire safe shutdown equipment) was identified based on Operating Experience (OE) from North Anna Power Station (LER 2021-002-00). A review of the affected control circuits for the Unit 1 and Unit 2 Emergency Diesel Generator (EDG) output breakers and Emergency Bus feeder breakers identified a concern that damage to the control power circuits during a fire may affect the ability to provide emergency power on both units. An 8-hour non-emergency report was made per 10 CFR 50.72(b)(3)(ii)(B) for an unanalyzed condition. Fire watches were established in the affected areas. The cause of this condition is the station’s original post-fire safe shutdown analysis did not accurately assess the impact on the equipment from associated cable damage due to fire for the select cables. Risk mitigating actions have been developed, implemented, and will continue to be performed until appropriate permanent corrective actions are in place to mitigate this condition. This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(B) for “Any event or condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety.” NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000- NUMBER NO. Surry Power Station, Unit 1 280 2021 - 001 - 00 | Plant Operating Conditions Prior to the Event Unit 1 - 100 Percent Power Unit 2 - 100 Percent Power 1.0 Description of Event On September 13, 2021, at 1822 EDT, an apparent non-compliance with 10 CFR 50, Appendix R, Section III.G.2 (separation of redundant fire safe shutdown equipment) was identified based on Operating Experience (OE) from North Anna Power Station (LER 2021-002-00). A review of the affected control circuits for the Unit 1 and Unit 2 Emergency Diesel Generator (EDG) output breakers (EIIS Component BKR, System EK) and Emergency Bus feeder breakers (EIIS Component BKR, System EK) identified a concern that damage to the control power circuits during a fire may affect the ability to provide emergency power on both units. An 8-hour non-emergency report was made per 10 CFR 50.72(b)(3)(ii)(B) for an unanalyzed condition (EN #55459). This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(B) for “Any event or condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety.” Several control cables were identified within common fire areas that, if fire damaged, could prevent the availability of both trains of Emergency Diesel Generators (EDGs) (EIIS Component DG, System EK) to start and power their respective emergency buses (EIIS Component BU, System EB) required by the station's current Appendix R analysis. The following issues were found: 1. Fire damage to control power cables for normal supply breakers may result in loss of control power and inability to power the emergency bus without manual operator actions outside of the main control room. 2. Hot shorts on the normal supply breakers (EIIS Component BKR, System EK) could result in spurious breaker operations that may prevent EDGs and/or emergency buses from performing its Appendix R function. 2.0 Significant Safety Consequences and Implications No significant safety consequences resulted from this event. Surry Appendix R analysis assumes all equipment within the fire area or zone is damaged; however, it is expected that damage would be minimized due to the defense in depth strategy for fire protection. Installed fire protection features are provided within the areas of concern to ensure fire damage to the impacted control cabling is minimized. All affected fire areas have installed area-wide fire detection and installed suppression systems. During this timeframe, Surry Units 1 and 2 operated at 100% power. The health and safety of the public were not affected by this event. 3.0 Cause of the Event The cause of this condition is the station's original post-fire safe shutdown analysis did not accurately assess the impact on the equipment from associated cable damage due to fire for the select cables. In addition, the original Multiple Spurious Operations review effort failed to recognize applicability of EDG/Emergency Power scenarios for some areas for the plant. | ML21315A001
Susquehanna Steam Electric Station | Unit 1 | Automatic Reactor Scram Due to Main Turbine Trip Caused by a ‘C’ Isophase Bus Ground Fault | 11-11-2021 | On July 21, 2021, at approximately 18:26, Susquehanna Steam Electric Station Unit 1 reactor automatically scrammed due to a main turbine trip. Both divisions of the Reactor Protection System (RPS) actuated and all control rods inserted. This event was reported by Event Notification 55370 in accordance with 10 CFR 50.72(b)(2)(iv)(B) and (b)(3)(iv)(A). This event is also reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of a system listed in 10 CFR 50.73(a)(2)(iv)(B). The cause of the event was a dislodged de-ionizing baffle plate that contacted the ‘C’ isophase bus causing a ground fault. The root cause was determined to be accelerated wear of the de-ionizing baffle tack welds due to increased isophase bus forced air. Corrective actions included replacement and tack welding the dislodged and loose baffle plates and implementing an Engineering Change to modify the Unit 1 Main Generator-end ‘A’ and ‘C’ isophase bus de-ionizer baffle plates to install an aluminum retaining rod to secure the baffle plates together. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366 (08-2020) NRC FORM 366A U. S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station Unit 1 05000-387 NUMBER NO. 2021 - 003 - 01 | CONDITIONS PRIOR TO EVENT Unit 1 – Mode 1, approximately 100 percent Rated Thermal Power Unit 2 – Mode 1, approximately 100 percent Rated Thermal Power There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. EVENT DESCRIPTION On July 21, 2021, at approximately 18:26, Susquehanna Steam Electric Station Unit 1 reactor automatically scrammed due to a main turbine [EIIS System/Component Code: TA/TRB] trip. The Unit 1 Control Room received indication of a main turbine trip with both divisions of the Reactor Protection System (RPS) [EIIS System Code: JC] actuated and all control rods inserted. The Reactor Recirculation Pumps [EIIS System/Component Code: AD/P] tripped on End of Cycle Recirculation Pump Trip. Operations subsequently maintained reactor water level at the normal operating band using the Reactor Feedwater system [EIIS System Code: SJ]. This event was reported by Event Notification 55370 in accordance with 10 CFR 50.72(b)(2)(iv)(B) and (b)(3)(iv)(A). This event is also reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of a system listed in 10 CFR 50.73(a)(2)(iv)(B). CAUSE OF EVENT The cause of the event was a dislodged de-ionizing baffle plate that contacted the ‘C’ isophase bus [EIIS System/Component Code: EL/IPBU] causing a ground fault. The root cause was determined to be accelerated wear of the de-ionizing baffle tack welds due to increased isophase bus forced air. Contributing causal factors included: 1) industry isophase bus events were not effectively reviewed to identify and implement station learnings for prevention of isophase bus failures and 2) visual inspection guidelines used to inspect the isophase de-ionizer grids for fatigue were inadequate. ANALYSIS/SAFETY SIGNIFICANCE The scram did not require or result in the actuation of any Emergency Core Cooling System or the Reactor Core Isolation Cooling system [EIIS System Code: BN] and no main steam relief valves [EIIS System/ Component Code: SB/RV] opened. All safety systems responded properly during the event. There were no actual consequences to the health and safety of the public as a result of this event. Page 2 of 3 . | ML21315A010
Limerick Generating Station | Unit 1 | Unit 1 HPCI Inoperable Due to Remote Shutdown Panel Switch Failure | 11-22-2021 | During the testing of the High Pressure Coolant Injection (HPCI) System, the HPCI pump failed to obtain the Technical Specification required pressure and flow as a result of high contact resistance in the HPCI Emergency Shutdown Switch. The high resistance was attributed to mechanical switch degradation that was introduced by cycling the switch during the logic system functional Surveillance Test, which was completed 1 hour and 32 minutes prior to the HPCI Pump Valve and Flow Surveillance Test. The switch was replaced, and testing is being developed to verify the switch is functioning after the switch is operated. This event is being reported because it resulted in an unplanned inoperability of a single train safety system that could have prevented fulfillment of a safety function. An eight (8) hour ENS notification was completed on September 23, 2021 at 18:46 hours. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments ~¥' LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. ; i CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to ..... Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory <--+_, ~o' Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER •YEAR SEQUENTIAL REV 05000- NUMBER NO. Limerick Generating Station Unit 1 352 D 2021 - I 001 - 00 I I I I I | Unit Condition Prior to the Event Unit 1 was in Operational Condition (OPCON) 1 (Power Operation) at approximately 100% power. There were no structures, systems, or components out of service that contributed to this event. Description of the Event On September 23, 2021, two Unit 1 High Pressure Coolant Injection (HPCI) System [BJ] testing activities were scheduled: the HPCI Logic System Functional Isolation Logic Test and the HPCI Pump Valve and Flow Test. At 09:25 the HPCI system was declared inoperable for the performance of the HPCI Logic System Functional Isolation Logic Test. At 13:09 the HPCI System was declared Operable after the completion of the test. At 14:43 the HPCI System was declared inoperable for the performance of the HPCI Pump Valve and Flow Test. During the initial start of the turbine during the HPCI Pump Valve and Flow Test the indicated turbine speed on the plant computer point and Main Control Room tachometer was downscale. The pump flow and discharge pressure indications were used to establish an acceptable test return valve position while the speed indication issue was investigated. The test was aborted when the HPCI Pump was not able to meet the Technical Specification requirements for rated flow and discharge pressure. An eight (8) hour ENS notification was completed on September 23, 2021 at 18:46 hours. Troubleshooting determined high contact resistance existed in the HPCI Emergency Shutdown Switch located on the Remote Shutdown Panel. The purpose of this switch is to terminate or prevent HPCI injection from the Remote Shutdown Panel under various Fire Safe Shutdown events. The HPCI Emergency Shutdown Switch is installed in the 48Vdc power supply to the HPCI EG-M module but includes additional contacts in the external wiring connections to the Woodward governor components including the flow controller demand signal to the Ramp Generator and Signal Converter (RGSC) module. Analysis of the Event The HPCI Emergency Shutdown Switch high resistance was attributed to mechanical switch degradation that was introduced by cycling the switch during the HPCI Logic System Functional Isolation Logic Test, which was performed 1 hour and 32 minutes prior to the HPCI Pump Valve and Flow Surveillance Test. With the unplanned loss of a single train system this condition is being reported per 10 CFR 50.73(a)(2)(v)(D), as a condition that could have prevented the fulfillment of the safety function of structures or systems required to mitigate the consequences of an accident. Safety Consequence There were no actual safety consequences associated with this event. The potential safety consequences of this event were minimal. The Reactor Core Isolation Cooling (RCIC), Automatic Depressurization System (ADS), Residual Heat Removal (RHR), and Core Spray (CS) systems remained operable during the period that HPCI was inoperable. Corrective Actions Completed The Unit 1 HPCI Emergency Shutdown Switch was replaced. A review of the completed Unit 2 testing verified the HPCI Emergency Shutdown Switch is operable. | ML21326A008
Nine Mile Point | Unit 1 | Isolation of both Emergency Condensers due to loss of UPS 162A | 11-19-2021 | On Saturday September 25, 2021, at approximately 0341 hours with power level at approximately 100 percent, Nine Mile Point Unit 1 (NMP1) experienced a loss of Uninterruptible Power Supply (UPS) 162Awhich resulted in the loss of Reactor Protection System (RPS) Bus 11. The loss of RPS Bus #11 resulted in a half scram, Reactor Water Cleanup isolation, and isolation of both #11 and #12 Emergency Condensers. The cause of this event was the premature failure of the oscillator board (X2) and/or the sync board (X5) in UPS 162A. Corrective actions include replacement of faulted sync and oscillator boards. This event is reportable under 10 CFR50.73(a)(2)(v)(B). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons teamed are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document htlp%www.nrc.goJ!}reading-rmJdQc~collections/nurn_g_s/s1aJf/SJJ022/r3/) requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER cY:E:A-R1 SEQUENTIAL REV I I NUMBER 1-NO~. Nine Mile Point Unit 1 05000-1 220 □ -1 I 002 | I. DESCRIPTION OF EVENT A. PRE-EVENT PLANT CONDITIONS: Unit 1 was in Run, operating at approximately 100% rated thermal power when the event occurred. There were no structures, systems, or components out of service that contributed to this event. B. EVENT: On September 25, 2021, at approximately 0341 hours, the NMP Unit 1 control room received multiple annunciators concurrent with a loss and subsequent restoration of RPS Bus #11 on UPS 162A. This resulted in a half scram, Reactor Water Cleanup isolation, and isolation of both #11 and #12 Emergency Condensers. The Emergency Condenser System was declared inoperable, and the appropriate Technical Specification Action was entered. The condition was reported to the NRC on September 25, 2021 at approximately 0916 hours pursuant to the requirements of 10 CFR 50.72(b)(3)(v)(B) (Event Notification #55492). After consultation with the vendor Ametek, the oscillator board (X2) and the sync board (X5) were replaced simultaneously. This was done based on advisement from Ametek that these cards should be replaced in pairs. Following replacement of these circuit boards, UPS-162A was restarted and exhibited no signs of frequency or voltage oscillations. Additionally, the UPS-162A was energized and the output monitored for several days to ensure consistent output performance while unloaded with no anomalies noted. Nine Mile Point Unit 2 (NMP2) was unaffected. The event has been entered into the plant's corrective action program as IR 04448532. C. INOPERABLE STRUCTURES, COMPONENTS, OR SYSTEMS THAT CONTRIBUTED TO THE EVENT: No other systems, structures, or components contributed to this event. | ML21327A024
Prairie Island Nuclear Generating Plant | Unit 1 | Loss of Electrical Bus Results in 121 Motor Driven Cooling Water Pump Auto Start | 12-13-2021 | On October 17, 2021, the Prairie Island Nuclear Generating Plant (PINGP) 2RY Transformer was de-energized when operations personnel opened the 2RSY Reserve Auxiliary Transformer 34.5KV B Disconnect Switch instead of closing the 2RSX Reserve Auxiliary Transformer 34.5KV B Disconnect Switch during restoration of the 2RX Transformer in the substation. The de-energization of 2RY caused a loss of power to the Unit 2 4.16 KV Bus 23. This led to an auto-start of 121 Motor Driven Cooling Water Pump on a sensed low header pressure. This event is reportable under 10CFR 50.73(a)(2)(iv)(A) due to a valid Emergency Service Water system actuation. Outage Shutdown Safety Assessment and Probability Risk Assessment remained green during the event and recovery actions. The cause of the de-energization of 2RY was individual errors during hard match and concurrent verification. The corrective action implemented required all substation switching to be identified as high risk with field supervisor oversight required. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Prairie Island Nuclear Generating Plant, 05000282 NUMBER NO. Unit 1 2021 - 002 - 00 | EVENT DESCRIPTION On October 17, 2021, the Prairie Island Nuclear Generating Plant (PINGP), Unit 1 was in Mode 1 (Power Operation) at 100 percent power and Unit 2 was in Mode 6 (Refueling) at 0 percent power. The 2RY Reserve Auxiliary Transformer was supplying Safety Related 4.16 KV Bus 25 and the Non-Safety Related 4.16 KV Buses 23 and 24. At 1601 CDT, the 2RY Reserve Auxiliary Transformer was de-energized when operations personnel opened the 2RSY Reserve Auxiliary Transformer 34.5KV B Disconnect Switch instead of closing the 2RSX Reserve Auxiliary Transformer 34.5KV B Disconnect Switch during restoration of the 2RX Reserve Auxiliary Transformer in the substation. The de-energization of 2RY caused a loss of power to the Unit 2 Buses 23, 24, and 25. Automatic reenergization of Bus 25 via CT12 Transformer, the other offsite power source, occurred. Bus 23 supplies power to Non-Safety Related 21 Cooling Water (CL) pump, which was supporting all the CL system loads. Following the trip of 21 CL Pump, 121 Motor Driven Cooling Water Pump (MDCLP) auto started on a sensed low header pressure. The 121 MDCLP is designed to start automatically if CL header pressure drops to 80 pounds per square inch gauge (psig). EVENT ANALYSIS 121 MDCLP The 121 MDCLP is a part of the PINGP CL System (EIIS CODE: BI). The CL system is a ring header which is shared by Units 1 and 2 that provides a heat sink for the removal of process and operational heat from safety-related components during a design basis accident or transient. During normal and shutdown operation, the CL system also provides this function for various safety-related and non-safety related components. The CL system consists of a common CL pump discharge header for five CL pumps: two non-safety related pumps, two safety related Diesel Driven Cooling Water Pumps (DDCLP), and 121 MDCLP that can be aligned as replacement for either DDCLP by realigning its power supply and administratively disabling the CL pump discharge header valves to direct flow to the appropriate train. The total Cooling Water (CL) system operating flow rates were in the range that operation of only one CL pump for both Units was desired. The ring header valves were open and 121 MDCLP was not aligned as a replacement for either DDCLP. The trip of 21 CL Pump resulted in a reduction in header pressure to the 121 MDCLP auto start setpoint. This event is reportable per 10CFR 50.73(a)(2)(iv)(A) due to a valid Emergency Service Water system actuation. Human Performance PINGP Non-Licensed Operators (NLOs) were performing their first-time evolution of the tasks of restoring the 2RX Reserve Auxiliary Transformer in the switchyard during the Unit 2 Refueling Outage. After successful closure of the 2RSX Reserve Auxiliary Transformer 34.5KV A Disconnect Switch, the NLOs opened the 2RSY Reserve Auxiliary Transformer 34.5KV B Disconnect Switch instead of closing the 2RSX Reserve Auxiliary Transformer 34.5KV B Disconnect Switch. ASSESSMENT OF SAFETY CONSEQUENCES Outage Shutdown Safety Assessment (SSA) and Probability Risk Assessment (PRA) remained green during the event and subsequent recovery actions. The auto start of 121 MDCLP did not challenge nuclear safety as the Cooling Water system responded as designed. This event does not represent a safety system functional failure for Unit 1 or Unit 2. CAUSE OF THE EVENT The cause of the de-energization of 2RY was individual errors during hard match and concurrent verification. | ML21347A972
River Bend Station | Unit 1 | Potential Loss of Safety Function due to Inoperable Reactor Core Isolation Cooling Steam Flow Transmitter | 12-16-2021 | On October 19, 2021 at 13:40 Central Time (CT) with the unit in Mode 1 at 100% power, wire insulation inside one of the Reactor Core Isolation Cooling (RCIC) Steam Flow Transmitters was found in a degraded condition. The degraded wire insulation could have caused a fault which would have prevented one of the redundant RCIC steam supply line isolations from occurring. The issue was determined to be reportable in accordance with 10 CFR 50.73(a)(2)(v)(C) as any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material and 10 CFR 50.73(a)(2)(i)(B) as an operation prohibited by Technical Specifications. The degraded wire insulation was corrected on October 21, 2021 at 08:38 CT by repair with qualified material. The most probable cause of the wire insulation degradation is moisture intrusion. NRC _ F , O RM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) ..... .._ .. Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported ~ l).!.,f ~ _ ~~ '; LICENSEE EVENT REPORT (LEA) r le e s g s a o r n d s in g le a b r u n r e d d e n a r e e s t in im c a o t r e p o t r o a t t e h d e in F t O o IA th , e l i l b ic r e a n ry si , n g a n p d r o ln ce fo s n s n a a n ti d o n f e C d o b ll a e c c k ti o t n o i B n r d a u n s c t h ry . ( T S - e 6 n d A 1 c 0 o M m ) m , e U n .S ts . "'-....~ .// CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to ,.. lnlocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: rnra subm1ss1on@omb eop.gov. The NRC may not conduct or https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV River Bend Station - Unit 1 05000- 458 NUMBER NO. 2021 005 00 | EVENT DESCRIPTION Surveillance test STP-207-4249 performs a channel calibration of the Reactor Core Isolation Cooling (RCIC) [BN] Steam Flow Transmitter [PDT] E31-PDTN084B as required by Technical Specification Surveillance Requirement 3.3.6.1.5-3.i. This Surveillance Test is performed on a 2-year frequency with the last completion documented on 04/21/2019. On 10/19/2021 transmitter E31-PDTN084B was calibrated, and its performance was determined to be satisfactory by the performance of STP-207-4249. During the performance of the Surveillance Test, Maintenance Technicians identified insulation falling off of the negative wire terminated in the transmitter. The insulation on the positive wire was intact; however, it was discolored. These wires are terminated inside the transmitter and routed through a conduit seal mounted on the transmitter. This condition could have prevented fulfilment of one of the RCIC steam supply high flow isolation functions. The specified safety function of the transmitter is to detect a break in the common RCIC / Residual Heat Removal (AHR) steam supply line and initiate inboard isolation valve closure. The transmitter provides a 4-20 mA signal to its associated trip unit. The isolation occurs on high steam flow. The degraded insulation did not affect the 4-20 mA signal; however, the transmitter was considered inoperable based on the potential for the bare wire to contact the transmitter housing (ground) during a seismic event. This could result in the signal failing downscale which would prevent the detection of a line break. A gross failure alarm is received if the signal from the transmitter fails downscale. There were no documented gross failures of E31-PDTN084B over the past three years. There is no work history listed against the transmitter over the past three years other than the surveillance test STP-207-4249 performed on 04/21/2019. Therefore, the only opportunity to observe the wire insulation over the past three years was during the field portion of STP-207-4249 performed on 04/21/2019. STP-207-4249 was satisfactorily completed on 04/21/2019 without any documented degradation of the wiring insulation. The redundant isolation function, as triggered from RCIC Steam Flow Transmitter E31-PDTN084A, was rendered inoperable for planned surveillance testing on 09/1/2020 from 13:20 to 15:00 CT and again from 15:20 to 16:25 CT. Therefore, this condition could have prevented fulfillment of the safety function for the for the duration of the time the redundant isolation function was rendered inoperable for testing on 09/1/2020. This issue is reportable in accordance with 10 CFR 50.73(a)(2)(v)(C) as any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. The degraded wiring insulation on the negative wire was corrected with qualified material on 10/21/2021 08:38 CT. After the time of discovery, one of the RCIC steam supply high flow isolation functions was determined to be inoperable for 43 hours. The Technical Specifications allow 37 hours of operation in this condition. Therefore, this condition is also reported as an operation prohibited by Technical Specifications in accordance with 10 CFR 50.73(a)(2)(i)(B). Although this event could have prevented the fulfillment of a safety function, engineering analysis has shown that this condition did not actually prevent fulfillment of a safety function. Therefore, this event is not reportable as a Safety System Functional Failure (SSFF) under the Regulator Assessment Performance Indicator Guideline, NEI 99-02. | ML21350A425
Clinton Power Station | Unit 1 | Core Monitoring System Software Modeling Error Results in Condition Prohibited by Technical Specifications | 08-31-2023 | On 07/20/21, with Clinton Power Station (CPS) operating at 98 percent power, it was determined CPS had operated in conditions prohibited by Technical Specifications (TS). This determination was based on a review of operational history and General Electric - Hitachi (GEH) Safety Communication SC 21-04, Revision 1, "Fuel Support Side Entry Orifice Meta-Stable Flow for 2 Beam Locations in the BWR/6 Reactors." The review concluded there were periods on 5/25/19, and between 6/22/19 to 8/3/19, when TS 3.2.2, "Power Distribution Limits - Minimum Critical Power Ratio (MCPR)" was not met due to a Core Monitoring System software modeling error. The error was identified by GEH and was caused by underprediction of Side Entry Orifice (SEO) loss coefficient for some fuel bundle locations which impacted the Maximum Fraction of the Limiting Critical Power Ratio (MFLCPR). The current MFLCPR value was verified within the recommended limit. Operations Standing Orders were issued to capture recommended actions from SC 21-04. The Core Operating Limit Report and Databank Design Analysis were revised and the core monitoring system was updated to address SC 21-04. This condition is reportable under 10 CFR 50.73(a)(2)(i)(B), any operation or condition which was prohibited by the plant's TSs. There was no impact to the health and safety of the public or plant personnel because the Safety Limit MCPR was not exceeded in previous cycles and the available margin was sufficient to accommodate the penalty evaluated in SC 21-04. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2( (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours Reported lessons learned are incorporated into the licensing process and led back to industry LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by ..... CONTINUATION SHEET e-mail to lnfocollects.Resource@nrc gov, and the 0MB reviewer at: 0MB Office of Informal.on and Regulatory Affairs. (3150-0104). Attn: Desk Officer for the Nuclear Regulatory Commission, (See NUREG-1022, R.3 for instruction and guidance for completing this form 725 17th Street NW, Washrnglon, DC 20503. e-mail: o-a ,.er,; crccr~ :eo ~c ,. The NRC http Jlwww nrc qovrreading-rrn/doc-collect1ons/nureqs/staft srl 022/r3I) i m nf a o y r m n a o ti l o n c o u n n d le u s c s t o lh r e s d p o o c n u s m or e , nt a n re d q u a e s p t e in r g so o n r r i e s q u n i o ri l n g re l q h u e i re c d o lle lo c tio re n s p d o is n p d la y lo s , a a c u c r o re lle n c tl t y io n va li o c 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Clinton Power Station, Unit 1 05000461 NUMBER NO. 2021 - 001 00 | PLANT AND SYSTEM IDENTIFICATION General Electric -- Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in text as [XX]. EVENT IDENTIFICATION Core Monitoring System Software Modeling Error Results in Condition Prohibited by Technical Specifications A Plant Operating Conditions Before the Event Unit: 1 Event Date: July 20, 2021 Event Time: NIA Mode: 1 Mode Name: Power Operation Reactor Power: 098 8. Description of Event Minimum Critical Power Ratio (MCPR) is a ratio of the fuel assembly power that would result in the onset of boiling transition to the actual fuel assembly power. The Operating Limit MCPR (OLMCPR) is established to ensure that no fuel damage results during anticipated operational occurrences, and that 99.9% of the fuel rods avoid boiling transition if the limit is not violated. Although fuel damage does not necessarily occur if a fuel rod experiences boiling transition, the critical power at which boiling transition is calculated to occur has been adopted as a fuel design criterion. The core monitoring system applies the appropriate OLMCPR limits incorporating the appropriate flow dependent MCPR (MCPRF) or the power dependent MCPR (MCPRP) limits; maximum of the two off-rated limits is applied for added conservatism. When this OLMCPR is divided by the calculated actual MCPR, this returns the Maximum Fraction of the Limiting Critical Power Ratio (MFLCPR). With MFLCPR <1.000, the Core Operating Limits Report (COLR) limits are met such that Technical Specification (TS) 3.2.2, Power Distribution Limits - Minimum Critical Power Ratio (MCPR), is satisfied. With MFLCPR > 1.000, TS 3.2.2 requires MFLCPR to be restored within 2 hours or power reduced to below 21.6% Rated Thermal Power within the next 4 hours. On July 20, 2021, it was determined that a core monitoring system software modeling error resulted in multiple entries into a condition prohibited by TS. This determination was reached after detailed review of plant operational history and information provided in General Electric - Hitachi (GEH) Safety Communication (SC) 21-04, "Fuel Support Side Entry Orifice Meta-Stable Flow for 2 Beam Locations in the BWR/6 Reactors," Revision 1, issued on June 17, 2021. SC 21-04, Revision 0, issued on April 19, 2021, identified a flow pattern that may periodically form under certain core conditions in which fuel bundle bypass flow is not accurately modeled by the core monitoring system. This condition is applicable to BWR/6 stations utilizing GEH core | ML21351A167
Cooper Nuclear Station 05000 298 1 OF 4 | Unknown Unit | Failure of High Pressure Coolant Injection Flow Indicating Switch Results in Condition Prohibited by Technical Specifications | 12-27-2021 | On October 28, 2021, the High Pressure Coolant Injection (HPCI) Flow Indicating Switch (FIS) (HPCI-FIS-78) failed to trip prior to exceeding the Technical Specification Limiting Condition for Operation 3.3.5.1 (Emergency Core Cooling System (ECCS) Instrumentation) Function 3.f (HPCI Pump Discharge Flow-Low (Bypass)) during the performance of the surveillance procedure. The cause of the failure was determined to be a shift in setpoint due to the initial over-range conditions experienced on September 14, 2021, by a new FIS that had been installed on July 27, 2021. The initial shift in setpoint due to over-range operation is a previously unpublished characteristic of Barton 289A switches, not identified in any Vendor literature or Industry Operating Experience. The As Found trip value would not have prevented the HPCI pump from performing its required functions. There was not an impact on nuclear safety, plant reliability, radiological safety, or industrial safety. Corrective actions completed were HPCI-FIS-78 was calibrated within As Left Tolerance (ALT), followed by the application of an over-range pressure equivalent to HPCI full flow for 45 minutes, and then tested once again and found to be within ALT. The remaining corrective actions are to revise the associated Vendor Manual and Maintenance procedure with respect to initial set-up for switches used in over-range applications. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A1 0M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or https://www.nrc.gov/readinq-rm/doc-collections/nureqs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITYNAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Cooper Nuclear Station 05000- 298 NUMBER NO. 2021 - 003 00 | PLANT STATUS Cooper Nuclear Station (CNS) was in Mode 1, Power Operation, at 100 percent power, when the event was discovered; i.e., October 28, 2021. No other equipment was inoperable or non-functional that contributed to this event. BACKGROUND Technical Specifications Bases for Limiting Condition for Operation (LCO) 3.3.5.1 (Emergency Core Cooling System (ECCS) Instrumentation), Function 3.f (High Pressure Coolant Injection (HPCI) Pump Discharge Flow-Low (Bypass)) states that the HPCI [EIIS: BJ] minimum flow instrument [EIIS: PDS] is provided to protect the HPCI pump [EIIS: P] from overheating when the pump is operated at reduced flow. The HPCI minimum flow line valve [EIIS: V] is opened when low flow is sensed and either 1) the pump is on, or 2) the system has initiated; and the valve is automatically closed when the flow rate is adequate to protect the pump. One Flow Switch (i.e., HPCI-FIS-78) [EIIS: BJ, PDS] is used to detect the HPCI Pump flow rate. HPCI-FIS-78 contains two internal switches that provide open and close permissive signals to the HPCI minimum flow (bypass) valve. On low system flow, HPCI-FIS-78 Switch #1 provides the low flow permissive signal to open the HPCI minimum flow (bypass) valve to protect the HPCI pump from overheating (Function 3.f: Allowable Value (AV) >/= 490 gpm). The AV is established high enough to ensure that the HPCI pump flow rate is sufficient to protect the pump. Once system flow is adequate to protect the pump, HPCI-FIS-78 Switch #2 provides a permissive signal to close the HPCI minimum flow (bypass) valve. The HPCI minimum flow (bypass) valve is required to close to achieve the Technical Specification required ECCS injection flow for HPCI (>/= 4250 gpm), but is not required to close to achieve the ECCS flow assumed [EIIS: BJ] in the analyzed transients that require HPCI injection (>/= 3825 gpm). Therefore, this instrument does not have a Technical Specifications AV associated with the HPCI minimum flow (bypass) valve closure. EVENT DESCRIPTION HPCI-FIS-78 was replaced on July 27, 2021, with a new Barton 289A Flow Indicating Switch (FIS) and was satisfactorily calibrated using station procedures. Then, on September 14, 2021, a surveillance procedure was performed to test the HPCI pump to ensure that it can produce its Technical Specifications required flow of>/= 4250 gpm. However, the surveillance procedure did not functionally test HPCI-FIS-78. On October 28, 2021, at 12:08 Central Time, with the plant operating at 100% Power in Mode 1, the HPCI-FIS-78 Switch #1 failed to trip prior to exceeding the Technical Specifications LCO 3.3.5.1 Function 3.f, AV of>/= 490 gpm during the performance of the calibration procedure for HPCI-FIS-78. HPCI-FIS-78 Switch #1 tripped at 473.5 gpm decreasing. | ML21361A084
Fermi 2 | Unknown Unit | High Pressure Coolant Injection Inoperable due to Contact Oxidation | 12-29-2021 | On 6/3/2021 at 0313 a condition was encountered during performance of the HPCI Condensate Storage Tank Level Channel Functional Test when the HPCI Pump Suction Isolation Valve from the Suppression Pool was slow to open. The Channel Functional Test was successfully completed; however, the valve took approximately 5 minutes to open on the simulated low Condensate Storage Tank (CST) level signal. Technical Specification (TS) 3.3.5.1 Action D.2.1 and D.2.2 were entered on 6/3/2021 at 0241 (surveillance start) which allows 24 hours to place the channel in trip or to align HPCI pump suction to the suppression pool. Troubleshooting of the condition identified an oxidated relay contact was the cause of the slow opening of the suction isolation valve. After relay repair and a repeat performance of the HPCI CST Level Channel Functional Test the Limiting Condition of Operation was exited on 6/4/2021 at 1451. It was later determined that the condition impacted both channels of the CST low level suction transfer logic, and during the condition TS 3.3.5.1 Action D.1 should have been entered resulting in declaring the HPCI system inoperable. HPCI suction was transferred to the suppression pool on 6/3/2021 at 1817 completing required actions for D.2.2 also making condition D.1 not applicable. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV 05000- NUMBER NO. Fermi 2 341 2021 - 003 - 0 | INITIAL PLANT CONDITIONS Mode – 1 Reactor Power – 100% There were no structures, systems, or components that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT On 6/3/2021 at 0313 while performing the HPCI [BJ] Condensate Storage Tank Level Channel Functional Test, the E4150-F042, HPCI Pump Suction Isolation Valve [ISV] from the Suppression Pool [BT], was slow to open. The isolation valve took approximately 5 minutes to open on the simulated signal low CST level. Technical Specification (TS) 3.3.5.1 Action D.2.1 and D.2.2 were entered which allows 24 hours to place the channel in trip or to align HPCI pump suction to the suppression pool. During the LCO period of time it was believed HPCI remained operable and available as there are two channels within this logic and the subsequent channel was verified to be working satisfactorily following the slow response time of the first channel. The first channel tested operates the logic and transfers the suction from the CST to the suppression pool. The valves are not repositioned to test the second channel, only the logic is tested. Further investigation identified that an oxidated contact on a common relay [RLY] was the cause of the delayed opening of the E4150-F042 isolation valve. This condition impacted both channels of the CST low level suction transfer logic. Technical Specification 3.3.5.1 Action D.1 should have been entered declaring the HPCI system inoperable or HPCI suction transferred to the Suppression Pool within 1 hour upon the discovery of the impact to both channels. During the event HPCI was available and functional. During the HPCI condition between 0313 on 6/3/2021 and 1451 on 6/4/2021 Reactor Core Isolation Cooling (RCIC) was declared inoperable twice for performance of surveillances. The first instance was from 0944 to 1236 on 6/3/2021. At 1236 the Division 1 Emergency Equipment Cooling Water (EECW) Pump and Valve Operability Test was satisfactorily completed restoring RCIC operability. The second instance was from 1515 to 1750 on 6/3/2021. At 1750 the Division 1 EECW Check Valve Operability Test was completed satisfactorily restoring RCIC operability. During performance of these surveillances entry into TS 3.5.1 Condition I with a completion time of 12 hours to be in Mode 3 was required due to the HPCI condition but was not recognized or entered. When RCIC is restored to Operable status TS 3.5.1 Condition I is exited. During performance of the EECW pump and valve operability tests HPCI was verified operable by administrative means; however, it was not recognized that HPCI was inoperable due to the common relay. HPCI suction was transferred to the suppression pool on 6/3/2021 at 1817 completing required actions for TS 3.3.5.1 D.2.2 also making Action D.1 not applicable. After relay repair and a repeat performance of the HPCI CST Level Channel Functional Test the LCO was exited on 6/4/2021 at 1451. After CST level logic was repaired and restored to operable it was discovered that HPCI should have been declared inoperable and an eight-hour NRC report was required per 10CFR50.72 and an LER per 10CFR50.73(a)(2)(v)(D) Mitigate the consequences of an accident. The 8 Hour NRC Event Notification for Unplanned HPCI Inoperability for the relay E41A-K17 condition was identified on 11/3/2021 at 0900 and completed on 11/3/2021 at 1345. A Technical Evaluation was completed that determined HPCI was available to perform its function during this event. | ML21363A084
Peach Bottom Atomic Power Station | Unit 2 | Manual Reactor Scram due to Degrading Condenser Vacuum | 01-12-2022 | On 11/14/2021 at 05:25 EST, a manual reactor scram was inserted on Unit 2 from 79 percent power due to degrading Main Condenser (EIIS: SG) vacuum. The loss of vacuum occurred due to an isolation of the Offgas System (EIIS: WF) on high Steam Jet Air Ejector discharge pressure and high Jet Compressor suction pressure. The manual reactor scram occurred with no complications and plant systems responded as expected. Unit 3 was unaffected. The scram resulted in an automatic Primary Containment Isolation System (PCIS)(EIIS: JM) Group II/III isolation. Upon initial investigation, it was identified that the valve positioner for the Jet Compressor Bypass Valve (EIIS: PCV) had a significant air leak which prevented the valve from closing. The root cause of the positioner failure was determined to be the use of low temperature soft parts in a high temperature environment. The soft parts within the failed positioner were replaced with higher-temperature rated components. Actions are in place to replace other low temperature soft parts within the Offgas System. There were no safety consequences as a result of the event. This report is made pursuant to 10CFR50.73(a)(2)(iv)(A) for manual actuation of the Reactor Protection System (scram) (EIIS: JC) and automatic actuation of the PCIS which affected containment isolation valves in more than one system. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Peach Bottom Atomic Power Station, Unit YEAR NUMBER NO. 05000- 277 2 2021 - 003 - 00 | Plant Operating Conditions Before the Event Peach Bottom Atomic Power Station Unit 2 (PB2) was operating at approximately 100 percent power in MODE 1 at the beginning of the event. Reactor power was reduced to 79 percent prior to inserting the manual scram. There were no structures, systems or components (SSC) that were inoperable at the start of the event that contributed to the event. Failed Component Information Model Number: Design ES Type Description: 2” Design ES control valve, 657 Actuator, 3582 Positioner Manufacturer: Fisher Controls International Type: Pressure Control Valve Event Description On 11/12/2021, an alarm was received in the Main Control Room for high pressure in the Unit 2 Offgas Jet Compressor suction. Adjustments to the pressure controller for the Jet Compressor Bypass Valve were made, but were unsuccessful in lowering pressure, and the pressure setpoint for Offgas System isolation was reached. Operator actions to restore the Offgas System were unsuccessful and reactor power was lowered to control Main Condenser vacuum. In response to continued degradation of Main Condenser vacuum, a manual Reactor scram was inserted from 79 percent power on 11/14/2021 at 05:25 EST. The manual scram occurred with no complications and plant systems responded as expected. The scram resulted in an automatic PCIS Group II/III isolation, reactor water level was maintained with the Feedwater system (EIIS: SJ), and reactor pressure was maintained with the Electrohydraulic Control system (EIIS: JJ), with the Main Condenser available as the primary heat sink. Unit 3 was unaffected. This event was reported by Notification EN 55575 in accordance with 10CFR50.72(b)(2)(iv)(B). Upon initial investigation, it was identified that the valve positioner for the ‘A’ train Jet Compressor Bypass Valve had a significant air leak which prevented the valve from closing. This air operated valve is designed to close with air pressure and to fail open. The purpose of the valve is to maintain Jet Compressor suction pressure by controlling bypass steam supply to the suction of the Jet Compressors. After the reactor scram, the valve positioner was replaced and post maintenance testing was completed satisfactorily. The plant entered start-up on 11/15/2021 and reached 100% power on 11/16/2021. The root cause of the failure of the positioner was determined to be the use of low temperature soft parts in a high temperature environment. Analysis identified that the positioner failure was due to a degraded bellows o-ring and subsequent air leakage. The elastomer became embrittled to the point of failure, likely caused by heat/temperature aging. A high temperature environment existed when a steam leak occurred near the failed part in 2019. | ML22012A400
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Automatic High Pressure Coolant Injection (HPCI) System Function Prevented by Control Circuit Relay Failure | 01-14-2022 | On November 18, 2021, during a simulated actuation test of High Pressure Coolant Injection (HPCI), 23MOV-19, HPCI Pump Discharge to Reactor Inboard Isolation Valve, failed to open. This was caused by a failure of the valve’s control logic circuit relay 23A-K54 to actuate. An investigation identified contacts 3-7 were intermittently not closing. The failure of the contacts to close was due to binding between the associated spring leave and the contact carrier channel sidewall. The binding was due to dimensional issues that caused chaffing on the sidewall of the contact carrier channel. This chaffing worsened over time until binding started to occur intermittently within 23A-K54. The condition of this relay could have prevented the automatic actuation of HPCI and is reportable per 10 CFR 50.73(a)(2)(v)(D). Manual actuation of HPCI remained unaffected by this condition; therefore, the system remained available. Relay 23A-K54 was replaced and HPCI was restored to Operable on November 19, 2021. NRC FORM 366 (08-2020) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments CONTINUATION SHEET regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 – 333 NUMBER N0. 2021 – 002 – 00 | Background The High Pressure Coolant Injection (HPCI) System [EIIS Identifier: BJ] at James A. FitzPatrick Nuclear Power Plant (JAF) is a part of the Emergency Core Cooling System (ECCS); HPCI provides and maintains an adequate coolant inventory inside the Reactor Pressure Vessel [RPV] to prevent damage to the reactor core under postulated accident scenarios. The system is comprised of various components which include pumps, valves, piping, and instrumentation. The HPCI System is required to actuate automatically to perform their design functions but it may be initiated manually. Automatic initiation occurs for conditions of Reactor Vessel Water Level – “Low Low” (Level 2) or Drywell Pressure – “High” (Level 8). The Technical Specification (TS) Surveillance Requirement (SR) 3.5.1.10 ensures HPCI actuates on an actual or simulated automatic initiation signal by verifying initiation logic will cause the system to operate as designed, including actuation of the system throughout its emergency operating sequence, automatic pump startup and actuation of all automatic valves to their required positions. This Surveillance also verifies that the HPCI System will automatically restart on an RPV low water level signal received subsequent to an RPV high water level trip. HPCI Pump Discharge to Reactor Inboard Isolation Valve 23MOV-19 is one of the valves that is required to open in order for the system to perform its function. Event Description On November 18, 2021, planned testing was performed in accordance with ST-4E, HPCI and SGT Logic System Functional and Simulated Automatic Actuation Test, for SR 3.5.1.10. During the high drywell pressure operation test 23MOV-19 was confirmed to open satisfactorily. During the subsequent RPV low water level operation test 23MOV-19 failed to open. It was determined that the valve failed to change position due to the valve’s control logic circuit relay, 23A-K54. Troubleshooting determined a high resistance connection between contacts 3-7. Manual cycling of the contacts showed that the contacts were intermittently not closing with a visible air gap. The intermittent failure of 23A-K54 to actuate is a condition which could have prevented fulfillment of the safety function for the HPCI system. This condition was reported in accordance with 10 CFR 50.72(b)(3)(v)(D) via ENS 55593. Event Analysis A failure analysis of 23A-K54 was performed. All contact surfaces appeared to be in very good condition. There was no evidence of arcing, pitting, contamination, corrosion, or tarnishing. The condition observed during the event was able to be duplicated on 4 of 20 trials. Contacts 3-7 resistance were measured high and an air gap was visible between the mating surfaces. Contacts 3-7 are typically open because the relay is normally energized (fail safe) and closes to open injection valve 23MOV-19. When the contacts did not close the valve did not open. On the instances when Contacts 3-7 was open when expected to be closed the associated spring leave moved during relay pickup and bound in a position that caused the intermittent issue. The spring leave channels were examined and dimensions were collected for the channel associated with contacts 3-7 and compared to the neighboring channel.The channel for contacts 3-7 is approximately 2.5 to Page 2 of 3 | ML22014A173
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | LER: 2021-003, Air Solenoid Valve Condition Results in Main Steam Isolation Valve (MSIV) Fast Closure Test Failure | 01-14-2022 | On September 14, 2020, at the beginning of James A. FitzPatrick (JAF) refueling outage (RO24), stroke time tests for Main Steam Isolation Valves (MSIV) 29AOV-86C and 29AOV-86D were outside the required time limit of 3 to 5 seconds per Surveillance Requirement (SR) 3.6.1.3.6. All other MSIVs were tested satisfactorily. A failure analysis was completed on November 18, 2021, the most probable failure mechanism is a sticking solenoid combined with vendor overhaul practices. This condition is common between two independent channels of a system used to control the release of radioactive material to become inoperable. Therefore, this LER is reportable per 10 CFR 50.73(a)(2)(vii). Corrective actions to replace the air solenoid valves were completed and both were tested satisfactorily on September 26, 2020. In the next refuel outage six MSIV air solenoid valves are planned to be replaced and sent for additional investigation. NRC FORM 366 (08-2020) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments CONTINUATION SHEET regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 – 333 NUMBER N0. 2021 – 003 – 00 | Background James A. FitzPatrick Nuclear Power Plant (JAF) has four main steam lines [EIIS identifier: SB] between the reactor and the main turbine [TA]. These lines are designed to isolate in the event of design basis accidents. In the event of a main steam line break, the isolation prevents further radiological release. In the event of a loss of coolant (LOCA) accident, they isolate to maintain coolant inside of containment. Two isolation valves are provided in series in a horizontal run of each main steam line, as close as practical to the primary containment. One inside (inboard) and the other outside (outboard) together form part of the primary containment barrier for Reactor Coolant System breaks inside the containment and part of the Reactor Coolant Pressure Boundary for main steam line breaks outside the primary containment. Event Description On September 14, 2020, during the performance of ST-1B, Main Steam Isolation Valve (MSIV) Fast Closure Test, the isolation times for 29AOV-86C and 29AOV-86D were not in compliance with the Technical Specification Surveillance Requirement 3.6.1.3.6. The acceptable isolation time is 3 to 5 seconds. Observed times from control switch manipulation to indication of full closure for 29AOV-86C and 29AOV-86D were 10.69 seconds and 24.97 seconds respectively. Event Analysis The MSIV components did not have any internal issues that would cause it to stick or bind while closing. From the MSIV position indicator data, the valves closed within the expected 3-5 seconds once the valves started to move. The delay in valve closure was caused by a delay in the venting of air from the valve’s solenoid air valves associated with MSIV operators 29AOV-86C(OP) and 29AOV-86D(OP). The excessive stroke of the main valve was due to response time of the solenoid to a control signal indicating an internal issue with the air solenoid valve. The air operator solenoid manifold assemblies were in fair physical condition when inspected, with proper alignment and assembly of the subcomponents. As found testing and inspection revealed unexpected leakage around the solenoids, areas of wear and corrosion, and foreign material. At no time during the inspection and testing of this assembly did the air control valves and solenoid valves fail to shift completely or exhibit any significant delay. While the wear/corrosion has been identified as the potential source of leakage noted during test, it does not provide an adequate source for the extended stroke time. The inspection and testing did not provide any conclusive example or replication of delayed stroke time, however the testing revealed abnormal solenoid leakage. It should be noted that while the leaking solenoid is abnormal, it still shifted fully during the as-found functional test and continued to function within specification under a continued air supply. During disassembly, the 4-way solenoid valve air manifold and air valves were inspected and found to have traces of contamination. The lead piston had an undetermined contamination on the surfaces. The contamination could result in a delay in the solenoid valve and therefore a delay in the MSIV stroke time. This is a condition which caused two independent channels of a system used to control the release of radioactive material to become inoperable reportable per 10 CFR 50.73(a)(2)(vii). Page 2 of 3 | ML22014A174
Grand Gulf Nuclear Station | Unit 1 | Procedure inadequacy resulted in Core Monitoring System miscalibration and violation of technical specification | 01-19-2022 | On November 18, 2021, a Past Operability Evaluation determined that an issue associated with jet pump summer miscalibration was a reportable event. Specifically, while performing, 17-S-02-5, Post Refueling Recirculation System Flow Instrumentation Calibration (site procedure), it was discovered that multiple conversion calculations in the procedure were incorrect and the procedural guidance for which data points to use in the calculation was unclear. This affects the transmitter and computer point calibration data used by Instrumentation and Control (l&C) personnel. This caused an incorrect core flow indication to the control room panel indication and the Core Monitoring System. Resulting in a violation of Technical Specification (TS) 3.2.2 for Minimum Critical Power Ratio (MCPR). There were no actual safety consequences for this event. Reactor Engineering and Operations had agreed to a Compensatory Measure and issued Standing Order 21-05 (Administrative Limit for Maximum Fraction of Limiting Core Power Ratio MFLCPR) to establish an administrative reduction in MFLCPR limit to 0.970. Standing Order 21-018 (Total Core Flow Indication) was issued to provide operators the ability to calculate total core flow using reactor recirculation drive flow indications that were not impacted by the calibration of the jet pump instrumentation. There were no consequences to the general safety of the public, nuclear safety, industrial safety, or radiological safety. No radiological releases occurred due to this event. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported '¥' lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) : I regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. ~ ...... r; CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocol!ecrs Resource@nrc gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: 011a subrni,,,e-~,;cmb.eo□ uov. The NRC may not conduct or https://www.nrc.gov/readinq-1 m/doc-collections/nuregs staff sr1022/r3) sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 05000 - 416 NUMBER NO. 2021 - 004 - 00 | Plant Conditions: Grand Gulf Nuclear Station (GGNS) Unit 1 was operating at 100 percent power in MODE 1. There were no Structures, Systems, or Components that were inoperable that contributed to this event. Event Description: On January 29, 2021, due to errors in the site procedure, Reactor Engineering provided l&C personnel incorrect voltage inputs that resulted in the miscalibration of the Jet Pump Loop Flow Summers for Loop A and Loop B. This miscalibration caused an incorrect core flow indication to the control room panel indication and the Core Monitoring System, resulting in a violation of Technical Specification (TS) 3.2.2 MCPR. On July 29, 2021, it was determined that multiple conversion calculations in the procedure were incorrect, and the procedural guidance was unclear. This resulted in the wrong data for jet pump flow being used to calibrate Jet Pump Loop Flow Summers for Loop A and Loop B. Additionally, it was determined that the core flow signal from the jet pump summers to the core monitoring software was 1.95 [Mlbm/hr] higher than actual core flow (a difference of approximately two percent of rated flow) and there was an adverse effect on thermal limits generated by the core monitoring software to satisfy technical specification Limiting Condition for Operation 3.2.2. In response to this issue, an administrative reduction in MFLCPR limit to 0.970 was applied. This was put in place via Standing Order 21-015. On November 18, 2021, a Past Operability Evaluation determined that an issue associated with jet pump summer miscalibration was a reportable event. Specifically, while performing the site procedure, it was discovered that multiple conversion calculations in the procedure were incorrect and the procedural guidance for which data points to use in the calculation was unclear. This affects the transmitter and computer point calibration data used by l&C personnel. This caused an incorrect core flow indication to the control room panel indication and the Core Monitoring System Resulting in a violation of Technical Specification (TS) 3.2.2 for MCPR. The Human Performance Evaluation identified two factors that contributed to the condition. First, the procedure used for performing the core flow instrumentation calibration, contains gaps in process as well as confusing and vague steps for calculations. The other factor identified was gaps in knowledge of the core flow calibration process, including gaps in knowledge of the methodology used in the jet pump calibration spreadsheet used with the site procedure to perform the calculations. The Organizational and Programmatic (O&P) process identified two factors that contributed to the condition - process weaknesses and organizational problems with program execution. Procedure contains errors and there are inconsistencies between it and the spreadsheet used to perform the calculations. The procedure also contains gaps in the core flow calibration process compared to the standard method from the General Electric Station Nuclear Engineering Manual, and it is unclear and vague on certain steps performing calculations. There are also inconsistencies between the procedure and the spreadsheet used to perform the calculations. The responsibility to implement the Software Quality Assurance (SQA) program is not well understood for utilizing spreadsheets in the reactor engineering group. NRG FORM 366A (08-2020) Page 2 of 3 | ML22019A270
Brunswick Steam Electric Plant (BSEP) | Unit 1 | Automatic Specified System Actuation due to Loss of Power to Emergency Bus E3 | 01-20-2022 | At 11:25 Eastern Standard Time (EST) on December 6, 2021, during a planned Emergency Diesel Generator (EDG) 3 maintenance outage, with Unit 1 and 2 in Mode 1 at approximately 100% power, electrical power was lost to 4160V emergency bus E-3. By design this resulted in automatic isolation of various Unit 2 Primary Containment Isolation System (PCIS) Group 2, 3, 6, and 10 isolation valves, and Unit 1 PCIS Group 6 isolation valves. EDG 3 received an automatic start signal by design but was under clearance for planned maintenance and therefore did not start. Electrical power to emergency bus E-3 was lost due to an inadvertent undervoltage signal generated during a planned relay replacement as part of the EDG 3 maintenance outage. During removal of a support bar to facilitate relay replacement, a washer was released contacting terminals directly below the bolt being removed causing control power fuses to blow. This resulted in an undervoltage signal and the loss of electrical power to emergency bus E-3. The washer that was released was not on any design drawings and its location, behind the support bar, precluded viewing and establishment of preventative measures. Emergency bus E-3 was re-energized on December 6, 2021, at 13:12 EST via its normal power source (i.e., Unit Auxiliary Transformer). There was no impact on the health and safety of the public or plant personnel. The safety significance of this event is minimal. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) due to actuation of the PCIS and EDG 3. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant (BSEP), 05000- 325 YEAR NUMBER NO. Unit 1 2021 - 001 - 00 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. Background Initial Conditions At the time of the event, Unit 1 was in Mode 1 (i.e., Power Operation), at approximately 100 percent rated thermal power. Unit 2 was in Mode 1 (i.e., Power Operation), at approximately 100 percent rated thermal power. Reportability Criteria This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) because it involved actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B). Specifically, the Unit 1 and 2 Primary Containment Isolation System (PCIS) [JM], and Emergency Diesel Generator (EDG) [EK] 3 actuated during this event. The NRC was notified of this event per 10 CFR 50.72(b)(3)(iv)(A) via Event Notification 55627 at 18:14 Eastern Standard Time (EST) on December 6, 2021. An update was provided on December 6, 2021, at 20:28 EST. Event Description At 11:25 EST on December 6, 2021, during a planned maintenance outage on EDG 3, with Unit 1 and 2 in Mode 1 at approximately 100% power, electrical power was lost to 4160V emergency bus [EB] E-3. EDG 3 received an automatic start signal by design but was under clearance for planned maintenance and therefore did not start. By design the loss of power to emergency bus E-3 and corresponding loads resulted in automatic isolation signals to various Unit 2 PCIS Group 2 (i.e., Drywell Equipment and Floor Drain, Residual Heat Removal (RHR) Discharge to Radwaste, RHR Process Sample, and Traversing Incore Probe), Group 3 (i.e., Reactor Water Cleanup), Group 6 (i.e., Containment Atmosphere Control/Dilution, Containment Atmosphere Monitoring, and Post Accident Sampling Systems), and Group 10 (i.e., Drywell Pneumatics) isolation valves. In addition, automatic isolation of the Unit 1 PCIS Group 6 isolation valves occurred due to the resulting loss of power to the Main Stack High Radiation logic which is powered from Unit 2. Appropriate primary containment isolation valves closed as expected. Other Unit 1 and 2 actuations included Reactor Building Ventilation System [VA] isolation (i.e., Secondary Containment isolation) and automatic start signals to the Standby Gas Treatment System [BH] and Control Room Emergency Ventilation System [VI]. The affected equipment responded as designed. Event Cause As part of the planned EDG 3 maintenance outage, the EDG 3 Synchronization (Sync) Check Relay was being replaced. Inside the associated electrical compartment, a metal support bar connects the Sync Check Relay, the Over/Undervoltage Relay, and the Undervoltage Relay. Installation of the new Sync Check Relay required removal of the metal support bar to facilitate modification of the support bar to accommodate the slightly different bolting configuration of the new Sync Check Relay. During removal of the support bar, a washer was released contacting the Undervoltage Relay terminals directly below the bolt being removed causing control power fuses to blow. This resulted in an undervoltage signal to the protective relay logic which tripped the incoming breaker resulting in the loss of electrical power to emergency bus E-3. The washer that was released was not on any design drawings and its location, behind the support bar, precluded viewing and establishing measures to prevent the event. Work history was reviewed following the event and no work has been performed on these relays which would have disturbed the relay cases or the associated support bar, indicating that this washer configuration was part of original plant construction. | ML22020A402
Quad Cities Nuclear Power Station | Unit 1 | High Pressure Coolant Injection System Inoperable due to Gland Seal System Malfunction | 01-26-2022 | On December 1, 2021, Unit 1 was at 100% power with a High Pressure Coolant Injection (HPCI) surveillance in progress. HPCI was declared inoperable at 1809 per the surveillance instructions. With HPCI running at rated speed, Main Control Room alarms were received for the HPCI Gland Exhauster at 1843. At 1847, Operators in the plant reported smoke and acrid odors from cubicles at a Motor Control Center (MCC) associated with Unit 1 HPCI and the Gland Exhauster. Operations aborted the surveillance and placed HPCI in Trip/Latch, and subsequently closed steam supply isolation valves to HPCI making it unavailable for automatic operation. The causes of this event are the failure of a level switch in the HPCI Gland Seal Condenser (GSC) Hotwell and a failed thermal overload for the HPCI Gland Exhauster motor. Immediate corrective actions were to electrically isolate the faulted Gland Exhauster and to restore the system to a normal standby line up. Subsequent actions included replacement of the level switch and thermal overload. This report is being submitted in accordance with 10 CFR 50.73(a)(2)(v)(D) for an event or condition that could have prevented the fulfillment of a safety system needed to mitigate the consequences of an accident. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of lnfonnation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of infonnation unless the document http://www. nrc. gov/readinq-rm/doc-col lections/nuregs/staff/sr1 022/r3/) requesting or requiring the collection displays a currently valid 0MB control number, 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Quad Cities Nuclear Power Station Unit 1 05000- 254 YEAR SE N Q U U M E B N E T R IA L R N E O V . 2021 - 001 00 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. EVENT IDENTIFICATION High Pressure Coolant Injection System Inoperable due to Gland Seal System Malfunction CONDITION PRIOR TO EVENT Unit: 1 Event Date: December 1, 2021 Event Time: 1847 CST Reactor Mode: 1 Mode Name: Run Power Level: 100% No structures, systems or components were inoperable at the start of this event that contributed to the event. A. DESCRIPTION OF EVENT On December 1, 2021, Unit 1 was operating at 100% power. Unit 1 High Pressure Coolant Injection (HPCl)[BJ] quarterly operability testing was in progress and had progressed to the point where Unit 1 HPCI was declared INOPERABLE at 1809. At 1843, the Main Control Room (MCR) received a HPCI MOTOR OVERLOAD alarm, indicating a motor overload condition for the Unit 1 HPCI Gland Exhauster. At 1847, Operators in the plant reported smoke and acrid odor coming from multiple cubicles at 250VDC MCC [EJ] 1A. (This Motor Control Center (MCC) is the power supply for the Unit 1 HPCI Gland Exhauster.) Concurrently, Operators in the Unit 1 HPCI Room reported acrid odor and smoke coming from the vicinity of the Unit 1 HPCI Front Standard. Unit 1 operators aborted the surveillance, and the Unit Supervisor directed Unit 1 HPCI taken to 'Trip/Latch' at 1847 hours. By placing Unit 1 HPCI in 'Trip/Latch', the system was in a condition that could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident; therefore, this condition is reportable per 10 CFR 50.72(b)(3)(v)(D). An Event Notification Sheet (ENS) #55619 was transmitted to the NRC at 2358. Steam supply to HPCI was also isolated at 1853. The Gland Exhauster was electrically isolated, supply steam was reestablished and the HPCI stand-by lineup was completed by 2110. HPCI was declared operable at 2110. HPCI was unavailable for automatic initiation for 1 hour 27 minutes. NRG FORM 366A (08-2020) Page_2_ of _4_ | ML22026A288
Oconee Nuclear Station | Unit 2 | Actuation of the Keowee Hydroelectric Station Due to Loss of AC Power to the Unit 2 Main Feeder Buses | 01-26-2022 | On November 27, 2021 at 0519 EST, with Unit 2 in MODE 5 with the Unit 2 Start-up transformer (CT-2) carrying the unit’s power loads, a CT-2 Lockout occurred. As a result, Unit 2 experienced a loss of alternating current (AC) power to the Main Feeder Buses (MFBs) resulting in the automatic start of both Keowee Hydroelectric Station (KHS) Units, initiated by the MFB Monitor Panel. Power was automatically restored to the Unit 2 MFBs from the CT-5 Transformer via the MFB Monitor Panel. During the power transfer, the operating Unit 2 Decay Heat Removal (DHR) pump stopped and then automatically restarted, as designed, with the restoration of power to the MFBs. The direct cause of this event was an inaccurate procedure step that resulted in Start-up Bus Differential Relay Control Switches being out of the required alignment. Because of the switch lineup that existed at the time, the Unit 1 Start-up Transformer (CT-1) also locked out at the same time as CT-2, however Unit 1 loads were being supplied by the Unit 1 Auxiliary Transformer (1T) and not by CT-1, therefore Unit 1 did not experience a loss of AC power and did not initiate any actuation signal to the KHS Units. This event was reported to the NRC on November 27, 2021, in Event Notification (EN) number 55612, as an 8-hour notification under 10 CFR 50.72(b)(3)(iv)(A) – Emergency AC Electrical Power System Actuation. It is also reportable as a 60-day written report under 10 CFR 50.73(a)(2)(iv)(A). NRC FORM 366 (08-2020) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported l¥~1'.11(,11~\. .. LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the Information Services Branch (T-6 A10M), U.S. Nuclear Regulatory \,, ~l CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB ?.,. ...... reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection displays http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Oconee Nuclear Station Unit 2 0500000270 NUMBER NO. 2021 002 00 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. BACKGROUND During start-ups, shutdowns, and outage periods where the Auxiliary Transformer (2T on Unit 2) [XFMR] is not available, offsite power [EA] is supplied to the Unit’s Main Feeder Busses (MFB) [EB] from the 230 kV Switchyard through the Start-up Transformer (CT-2 on Unit2)[XFMR] or from Central Switchyard through Transformer CT-5 [XFMR] via one or both Standby Buses[EB]. Emergency power [EB] can be provided to any or all three Oconee Nuclear Station (ONS) Units MFB from the Keowee Hydroelectric Station (KHS) [EK] from either of two emergency power paths: 1. The Overhead Path, that includes the Unit’s Start-up Transformer (CT-1, CT-2, or CT-3) [XFMR] on each ONS unit 2. The Underground Path, through Transformer CT-4 [XFMR] and one or both Standby Buses. Emergency onsite power may also be provided to any or all three ONS Units MFB from a Lee Combustion Turbine (LCT) [EK] on a dedicated 100kV transmission line through Transformer CT-5 via one or both Standby Buses. The Main Feeder Bus Monitor Panel (MFBMP) [P] provides an automatic method of establishing safe and reliable power to the MFBs during non-Engineered Safeguards events. MFBMP detects low voltage on a Unit’s MFB and initiates load shed logic, an emergency start of both KHS units, and permissive signals to permit automatically aligning the Unit’s MFB to either the Unit’s Startup Transformer energized from the Overhead Path or the Standby Buses energized by either Transformer CT-4 or Transformer CT-5. EVENT DESCRIPTION On November 27, 2021, Unit 1 was in MODE 1 operating at 100% reactor power with its MFB powered from the Unit 1 Auxiliary Transformer (1T) [XFMR] . Unit 2 was in MODE 5 with the Unit 2 Start-up transformer (CT-2) powering the unit’s MFB. The Unit 2 Low Pressure Injection (LPI)[BP] system was providing Decay Heat Removal (DHR). Standby Buses were energized from Central Switchyard via CT-5 to provide an additional offsite power source for Unit 2 for outage defense in depth. At 0519 EST, Unit 2 was starting the 2B2 Reactor Coolant [AB] Pump (RCP) Motor [MO] for an uncoupled run. When the 2B RCP switch was placed to the Start position, CT-1 and CT-2 lock out [86] occurred. Unit 1 was operating with the unit being powered from 1T and therefore did not lose power when CT-1 locked out. The CT-2 lockout, however, did result in a loss of AC power to the Unit 2 and MFBMP initiated an automatic start of both KHS Units. KHS emergency start completed and CT-4 was energized by KHS. However, since CT-5 was already energizing the Standby Buses, power was automatically restored to the Unit 2 MFBs from CT-5 by MFBMP. During the MFBMP power transfer, the operating Unit 2 DHR pump stopped and then automatically restarted, as designed, with the restoration of power to the Unit 2 MFBs. Reportability This event was reported to the NRC on November 27, 2021, in Event Notification (EN) number 55612, as an 8-hour notification under 10 CFR 50.72(b)(3)(iv)(A) – Emergency AC Electrical Power System Actuation. It is also reportable as a 60-day written report under 10 CFR 50.73(a)(2)(iv)(A). EN 55612 also reported a loss of safety function of the DHR system. After additional review, it has been determined that a loss of safety function did not occur as both DHR trains were capable of being powered via the automatic power switching logic and all the associated equipment to support cooling was available. Incoming power source swapping is part of the design of the system. As such, this event is not reportable per 10 CFR 50.72(b)(3)(v) or 10 CFR 50.73(a)(2)(v). | ML22026A530
Grand Gulf Nuclear Station | Unit 1 | Oscillation Power Range Monitors (OPRMs) Setpoint Error Causes Technical Specification Noncompliance | 02-02-2022 | On June 21, 2021, while operating in MODE 1 at approximately 100 percent power, Grand Gulf Nuclear Station identified that the Detect and Suppress Solution - Confirmation Density (DSS-CD) settings for the Oscillation Power Range Monitors (OPRM) had not been updated to the current licensing basis as required per NEDC-33075P Rev 7 Licensing Topical Report General Electric Hitachi (GEH) Boiling Water Reactor Detect and suppress Solution - Confirmation Density. As a result, the Oscillation Power Range Monitors (OPRM) upscale setting requirements specified in Technical Specification (TS) Table 3.3.1.1-1, Reactor Protection System Instrumentation, function 2, Average Power Range Monitors (APRM), Sub-Function "f' OPRM upscale limits were not fully met. This event is reportable under 10 CFR 50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications. The direct cause of this event was that the setpoints were not implemented correctly during Maximum Extended Load Line Limit Analysis Plus (MELLLA+) implementation. The direct cause was corrected by changing the Maximum Oscillation · Period, T max setpoint to 4.0 seconds on all four (APRM) channels. This corrected the OPRM setpoints for DSS-CD. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch {T-6 A10M}, U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or httos://www .nrc.qov/readinq-rm/doc-collections/nureqs/staff/sr1022/r3D sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 05000-416 NUMBER NO. 2021 - 005 - 00 | Plant Conditions: Grand Gulf Nuclear Station (GGNS) Unit 1 was operating at 100 percent power in MODE 1. There were no Structures, Systems, or Components that were inoperable that contributed to this event. Event Description: On June 21, 2021, while performing analysis for a future fuel load, GGNS identified that the Detect and Suppress Solution - Confirmation Density (DSS-CD) settings had not been updated to the current version of the General Electric Hitachi (GEH) recommended report. Additionally, the Instrument and Control (l&C) Calibration procedures were not updated for the Average Power Range Monitor (APRM) channels. Specifically, the Maximum Oscillation Period, maximum time period (T max), setpoint was set at 3.5 seconds instead of 4.0 seconds as required in the licensing basis per NEDC- 33075P, Rev 7 Licensing Topical Report GEH Boiling Water Reactor DSS-CD. The settings for the maximum period installed in the plant were non-conservative with respect to the licensing basis. The Oscillation Power Range Monitors (OPRM) Upscale setting requirements specified in the Technical Specifications (TS) 3.3.1.1, Reactor Protection System (RPS) Instrumentation, Table 3.3.1.1-1, Reactor Protection System Instrumentation, function 2, Average Power Range Monitors, Sub-Function "f', OPRM Upscale limits were not fully met. This event is reportable under 10 CFR 50. 73(a)(2)(i)(B), as any operation or condition prohibited by the plant's Technical Specifications. Safety Assessment: The actual consequences for this event were very low. There was no radiological release from the primary containment as a result of this calibration error. There were no other actual consequences to safety of the general public, nuclear safety, industrial safety, or radiological safety. No Technical Specification Safety Limits were violated. Event Cause(s): The direct cause of this event was that the setpoints were not implemented correctly during Maximum Extended Load Line Limit Analysis Plus (MELLLA+) implementation. Causal Factors 1 - The technical basis for the change in OPRM settings was not clearly communicated such that consequences of not executing the work were well understood. Causal Factors 2 - GGNS-NE-16-00007, the engineering report for the June 17, 2016, OPRM SCRAM, was inappropriately revised in a way that contradicted the Power Range Neutron Monitor (PRNM) DSS-CD Settings Report causing confusion regarding the actual licensing basis. The report was also inappropriately used to state T max = 3.5 seconds was acceptable, also contradicting the PRNM DSS-CD Settings Report. . . Corrective Actions: The direct cause was corrected by changing the T max setpoint to 4.0 seconds on all four APRM channels. This corrected the OPRM setpoints for DSS-CD. Reperform an extent of condition on MELLLA+ Implementation for settings/setpoint changes. Tracked by the Corrective Action Program. | ML22033A065
North Anna Power Station | Unknown Unit | Unanalyzed Condition Due to App R Concern Identified With Cable Separation | 09-17-2021 | On July 20, 2021 at 1707 hours, an apparent non-compliance with 10 CFR50, Appendix R, Section 111.G.2 (separation of redundant fire safe shutdown equipment) was identified. On July 22, 2021 at 1751 hours, a further review of the affected control circuits for the Unit 1 and Unit 2 Emergency Diesel Generator (EOG) output breakers and Emergency Bus feeder breakers identified a concern that breaker position interlocks routed to or through non-safety related components or spaces may affect the ability to provide emergency power on the affected unit due to impacts on the control power circuits during an Appendix R fire associated with a loss of offsite power. An 8-hour non-emergency report was made per 10 CFR 50.72(b)(3)(ii)(B) for an unanalyzed condition. Hourly fire watches were established in the affected areas. The cause of this condition is the station's original post-fire safe shutdown analysis did not accurately assess the impact on the equipment from associated cable damage due to fire for the select cables. Risk mitigating actions have been developed, implemented, and will continue to be performed until appropriate permanent corrective actions are in place to mitigate this condition. This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(B) for "Any event or condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety." U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A1 0M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: 011a submisslon(cvorniJ eoo.qov. The NRC may not conduct or sponsor, http// www. n rc.q<21£Lr_~9_ctLQQ~:J!Dl9_9._g::_gol lections/n u reqs/staff/ sr1022/r:3/l and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. North Anna Power Station, Units 1 and 2 05000-338 2021 ... 002 00 | Plant Operating Conditions Prior to the Event Unit 1 - Mode 1, 100 percent Rated Thermal Power Unit 2 - Mode 1, 100 percent Rated Thermal Power 1.0 Description of Event On July 20, 2021 at 1707 hours, an apparent non-compliance with 10 CFR50, Appendix R, Section 11I.G.2 (separation of redundant fire safe shutdown equipment) was identified during the development of the North Anna Fire Probabilistic Risk Assessment. On July 22, 2021 at 1751 hours, a further review of the affected control circuits for the Unit 1 and Unit 2 Emergency Diesel Generator (EOG) output breakers (EIIS Component BKR, System EK) and Emergency Bus feeder breakers (EIIS Component BKR, System EK) identified a concern that breaker position interlocks routed to or through non-safety related components or spaces may affect the ability to provide emergency power on the affected unit due to impacts on the control power circuits during an Appendix R fire associated with a loss of offsite power. An 8-hour non emergency report was made per 10 CFR 50. 72(b)(3)(ii)(B) for an unanalyzed condition. This event is reportable in accordance with 10 CFR 50. 73(a)(2)(ii)(B) for "Any event or condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety." Several control cables were identified within common fire areas that, if fire damaged, could prevent the availability of both trains of Emergency Diesel Generators (EDGs) (EIIS Component DG, System EK) to start and power their respective emergency buses (EIIS Component BU, System EB) required by the station's current Appendix R analysis. The following issues were found: 1. Fire damage to control power cables for EOG output breakers may result in loss of control power and inability to power the emergency bus without manual operator actions outside of the main control room. 2. Hot shorts on the normal/alternate supply breakers (EIIS Component BKR, System EK) could result in spurious breaker operations that may prevent EDGs and/or emergency buses from performing its Appendix R function. 2.0 Significant Safety Consequences and Implications No significant safety consequences resulted from this event. During this timeframe, North Anna Units 1 and 2 operated at 100% power. The health and safety of the public were not affected by this event. 3.0 Cause of the Event The cause of this condition is the station's original post-fire safe shutdown analysis did not accurately assess the impact on the equipment from associated cable damage due to fire for the select cables. In addition, the Multiple Spurious Operations review effort failed to recognize applicability of EOG/Emergency Power scenarios for some areas for the plant. 4.0 Immediate Corrective Action Hourly fire watches were established in the Unit 1 and Unit 2 Turbine Buildings, Unit 1 and Unit 2 Cable Spreading Rooms, and Unit 1 and Unit 2 Normal Switchgear Rooms to mitigate the risk of fire and aid in early detection of fire. Risk mitigating actions have been developed, implemented, and will continue to be performed until appropriate permanent corrective actions are in place to mitigate this condition. Page 2, of J | ML22035A167
Susquehanna Steam Electric Station 05000388 1 of 3 | Unknown Unit | Loss of Secondary Containment due to Failed Differential Pressure Transmitter | 02-08-2022 | On August 30, 2021, at 09:55, operators at the Susquehanna Steam Electric Station (SSES), Unit 2, identified that Reactor Building Zone II Pressure Differential Indicator (PDI), PDI-27581, was stuck at a reading of 0.32” water column vacuum. Operators also reported difficulties opening doors in the SSES Unit 2 Reactor Building, indicating a positive secondary containment differential pressure (D/P). At this time, operators determined that a loss of the secondary containment had occurred and entered the off-normal procedure for the condition. Review of alternate indication documented from earlier that day, identified the condition likely existed longer than allowed by the Technical Specification Surveillance Requirement 3.6.4.1.1 associated Note. This condition is being reported under 10 CFR 50.73(a)(2)(v)(C) as a loss of safety function. Secondary containment was restored to an operable status at 10:30 on August 30. The cause of the event was determined to be an age-related failure of Pressure Differential Transmitter (PDT) PDT-27581. Corrective actions included replacing PDT-27581. There were no actual safety consequences associated with the described condition. NRC FORM 366A U. S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station, 05000-388 NUMBER NO. Unit 2 2021 - 002 - 01 | CONDITIONS PRIOR TO EVENT Unit 1 – Mode 1, approximately 100 percent Rated Thermal Power (RTP) Unit 2 – Mode 1, approximately 100 percent RTP At 04:00 on August 30, 2021, operators at the Susquehanna Steam Electric Station (SSES), Unit 2, identified that both the A and B Standby Gas Treatment (SGT) System Zone 2 Outside Delta Pressure Indicators, pressure differential indicators (PDIs) PDI-07554A2 and PDI-07554B2 [EIIS System/Component Codes BH/PDI], respectively, were indicating below downscale on the associated meters while the digital display was reading -0.25” water column (wc) vacuum. This is indicative of a positive differential pressure (D/P) in the secondary containment. At the time of discovery, this was believed to be an “indication-only” issue. EVENT DESCRIPTION At 09:55 on August 30, 2021, while investigating the downscale indication on the A and B SGT System Zone 2 Outside Delta Pressure Indicators, PDI-07554A2 and PDI-07554B2, operators at SSES, Unit 2, identified that the SGT System Zone 2 Exhaust System Circulating Space/Outside D/P Indicator, PDI-27581 [VA/PDI], was stuck at a reading of 0.32” wc vacuum. Operators also reported difficulties opening doors in the SSES Unit 2 Reactor Building, indicating a positive secondary containment D/P. At this time, operators determined that a loss of the secondary containment had occurred and entered the off-normal procedure for the condition. Entry into Technical Specification Limiting Condition for Operation (LCO) 3.6.4.1, Condition A was evaluated and determined to be unnecessary at the time of discovery based on no known breach in secondary containment and the SGT subsystem was determined to be capable of drawing down secondary containment to 0.25” wc vacuum. This allowance is defined within the associated Note for Surveillance Requirement (SR) 3.6.4.1.1. Subsequently, when reviewing the stuck indication on PDI-27581 in aggregate with the downscale readings on PDI-07554A2 and PDI-07554B2, it was determined firm evidence exists that secondary containment D/P was likely lost at 04:00 when PDI-07554A2 and PDI-07554B2 were identified as reading downscale. As a result, the four-hour allowance of the Note modifying SR 3.6.4.1.1 would result in the SR not met at approximately 08:00 and LCO 3.6.4.1, Condition A being entered. Because there is no redundant system to secondary containment, this event requires reporting under 10 CFR 50.73(a)(2)(v)(C) as a condition that could have prevented the fulfillment of a safety function needed to control the release of radioactive material. CAUSE OF EVENT The cause of the event was determined to be an age-related failure of Pressure Differential Transmitter (PDT) PDT-27581 [VA/PDT]. The output of PDT-27581 was failed and providing incorrect inputs to the indicators and controllers, which resulted in the loss of Zone 2 D/P. | ML22039A022
Fermi 2 | Unknown Unit | Unplanned lnoperability of High Pressure Coolant Injection System Due to an Inverter Circuit Failure | 03-15-2022 | At 0529 Eastern Daylight Savings Time (EDT) on August 22, 2021, while in Mode 1 at 100% power, alarms occurred for the Division 2 emergency diesel generator (EOG) load sequencer and the High Pressure Coolant Injection (HPCI) inverter circuit. These issues led to Division 2 EDGs and HPCI being declared inoperable per Technical Specification (TS) 3.8.1 and TS 3.5.1, respectively. Subsequent failures of the Division 2 battery charger and inoperability of the Division 2 direct current (DC) electrical power distribution subsystem were identified under TS 3.8.4 and TS 3.8.7, respectively. The cause of the event was a voltage spike of unknown origin. However, the spare battery charger was placed in service for Division 2 and the replacement of the power supplies for the load sequencer and HPCI inverter eliminated the problem and allowed for all the systems to be returned to service with no further issues by (or before) 0956 EDT on August 24, 2021. Other safety systems such as the Reactor Core Isolation Cooling (RCIC) system and Division 1 EDGs remained operable throughout the event. Although no violations of TS occurred, the unplanned inoperability of HPCI is a reportable condition. The safety significance of this event was determined to be very low and there were no radiological releases. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response lo comply with this mandatory collection request 80 hours. Reported lessons learned are irKDp003ted ilto the licensing process and fed back lo indushy. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate lo the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Coomission, Washington, DC 20555--0001, or by e-mail lo CONTINUATION SHEET lnfooolleds.Resource@nrc.gov, and the 0MB reviewer at 0MB Office of Information and Regulatory Affairs, (3150-0104). Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e--mai: oira submission@omb.eop.gov. The NRG may not conduct or sponsor, and a person is not required to respond to, a collection of i,forrnation unless the document http://www.nrc.gov/readinq-rm/doc-collections/nureqs/staff/sr1022/r3/) requesting or requiring the oolection displays a currentiy valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV IFermi 2 I 05000- 1 341 ~□ -I NUMBER 1-CN2O. J 002 | INITIAL PLANT CONDITIONS Mode-1 Reactor Power - 100% There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT At 0529 Eastern Daylight Savings Time (EDT) on August 22, 2021, alarms [ALM] occurred for the Division 2 emergency diesel generator (EOG) [DG] load sequencer [34] and the High Pressure Coolant Injection (HPCI) [BJ] inverter circuit. These issues led to Division 2 EDGs and HPCI being declared inoperable per TS 3.8.1, "Alternating Current (AC) Sources -Operating," Required Action 8.4 and TS 3.5.1, "Emergency Core Cooling Systems (ECCS) - Operating," Condition E.1, respectively. Offsite power circuits and Division 1 EDGs were verified to be operable in accordance with TS 3.8.1 Required Actions 8.1 and 8.3.1, respectively. The Reactor Core Isolation Cooling (RCIC) [BN] system was verified operable in accordance with TS 3.5.1 Required Action E.1. The HPCI system and the EDG load sequencer are powered by the Division 2 battery. The initial investigation identified blown fuses associated with the power supplies of both the Division 2 EOG load sequencer and HPCI. The fuses were replaced but blew again. The blown replacement fuses were removed and additional troubleshooting activities were performed. During the subsequent troubleshooting activities, fluctuations were identified in the Division 2 battery charger [BYC] in the direct current (DC) electrical power subsystem [El]. The Division 2 battery charger was declared inoperable at 2233 EDT on August 22, 2021, and TS 3.8.4, "DC Sources - Operating," Condition A was entered. Shortly thereafter, at 2331 EDT, the Division 2 DC electrical power distribution subsystem was also declared inoperable due to low voltage and TS 3.8.7, "Distribution Systems- Operating," Condition B was entered. The spare battery charger was placed in service for Division 2. Using the spare, the Division 2 battery charger was restored to an operable status at 0046 EDT on August 23, 2021 and TS 3.8.4 Condition A was exited. Placement of the spare battery charger also stabilized voltage on the Division 2 DC electrical power distribution subsystem such that TS 3.8. 7 Condition B was exited at 0055 EDT on August 23, 2021. The durations of the inoperability's of the Division 2 battery charger and DC electrical power distribution subsystem were approximately 2 hours and 1 hour, respectively which were both within the TS allowable durations of 4 hours and 2 hours, respectively. No other safety-related systems were out of service during the event. Following transfer to the Division 2 spare battery charger, the aux transformer was replaced in the original battery charger, the power supplies for the Division 2 EOG load sequencer and HPCI Inverter were replaced. The Division 2 EDG load sequencer was restored to service and the EDGs were declared operable at 2132 EDT on August 23, 2021. The duration of the Division 2 EOG load sequencer inoperability was approximately 40 hours which was within the TS 3.8.1 Condition B NRG FORM 366A (08-2020) Page 2 of 5 | ML22075A087
Susquehanna Steam Electric Station | Unit 2 | Condition Prohibited by Technical Specifications Due to Drift of Reactor Pressure Switch | 03-21-2022 | On July 6, 2021, the Unit 2 “D” Reactor Steam Dome Pressure – Low permissive pressure switch, Microswitch 2, was found outside of the Technical Specification (TS) 3.3.5.1 allowable value. The switch drifted outside of the lower allowable value which is intended to ensure that the Emergency Core Cooling System (ECCS) injection prevents the fuel peak cladding temperature from exceeding the limits of 10 CFR 50.46. Based on the information available, the condition likely existed for longer than allowed by TS 3.3.5.1, TS 3.5.1, and TS 3.0.3. As such, this is a condition prohibited by TS and is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B). In addition, since the “C” channel (PIS-B21-2N021C) was surveillance tested just prior to identification of the drift of the “D” channel (PS-B21-2N021D), redundant channels were inoperable at the same time impacting both Core Spray and LPCI functions; therefore, this is also considered a condition that could have prevented fulfillment of a safety function (10 CFR 50.73(a)(2)(v)(D)) and a common cause inoperability of independent trains or channels (10 CFR 50.73(a)(2)(vii)). The cause of the event was determined to be instrument setpoint drift due to temperature/humidity changes and mechanical hysteresis as a result of the original design inputs not accounting for temperature and humidity effects on the switch. The switch was replaced with an unmodified pressure indicating switch. Final corrective action will revise the allowable value for TS 3.3.5.1, Functions 1.c, 1.d, 2.c, and 2.d. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366 (08-2020) NRC FORM 366A (08-2020) Page 2 of 3 . NRC FORM 366A (08-2020) U. S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 LICENSEE EVENT REPORT (LER) CONTINUATION SHEET Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. (See NUREG-1022, R.3 for instruction and guidance for completing this form https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Susquehanna Steam Electric Station Unit 2 05000-388 YEAR SEQUENTIAL NUMBER REV NO. 2021 - 001 - 01 | CONDITIONS PRIOR TO EVENT Unit 1 – Mode 1, approximately 100 percent Rated Thermal Power Unit 2 – Mode 1, approximately 100 percent Rated Thermal Power There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. EVENT DESCRIPTION Prior to September 2017, Susquehanna Steam Electric Station (SSES) had been utilizing International Telephone and Telegraph (ITT)-Barton 288A pressure switches in the Reactor Steam Dome Pressure – Low channels [EIIS System/Component Identifier: JE/PS] that provide the injection permissive for the Core Spray system [EIIS System Identifier: BM] (Technical Specification (TS) 3.3.5.1, Function 1d) and the Residual Heat Removal (RHR)/Low Pressure Coolant Injection system (LPCI) [EIIS System Identifier: BO] (TS 3.3.5.1, Function 2d). Due to instrument drift concerns, all eight obsolete ITT-Barton 288A pressure switches were replaced with General Electric (GE) recommended Cameron-Barton 288A pressure switches between September 6, 2017 and November 15, 2017. Following replacement, instrument drift continued to be an issue, and additional corrective action was determined necessary to resolve the drift concerns. The additional corrective action included procuring and installing Cameron- Barton 288A instruments that had been modified to remove an over-range condition and the movement assembly/associated linkages that were determined to be affecting instrument drift. The first of these modified instruments was installed and calibrated on July 8, 2020 in the Unit 2 “D” channel (pressure switch for PS-B21-2N021D). On August 10, 2020, the new, modified PS-B21-2N021D switch, Microswitch 2, was tested for its first surveillance interval and found to be outside of TS acceptance criteria. The switch drifted 1.2 psig outside of the upper allowable value which is intended to ensure that the reactor dome pressure has fallen to a value below the Core Spray and RHR/LPCI maximum design pressures to preclude over-pressurization of the low pressure systems prior to low pressure injection initiation. This event was reported in LER 50-388/2020-002-01, dated July 1, 2021. On July 6, 2021, the Unit 2 “D” Reactor Steam Dome Pressure – Low permissive pressure switch, Microswitch 2, was found outside of the TS 3.3.5.1 allowable value. The switch drifted outside of the lower allowable value which is intended to ensure that the Emergency Core Cooling System (ECCS) injection prevents the fuel peak cladding temperature from exceeding the limits of 10 CFR 50.46. Based on the information available, the condition likely existed for longer than allowed by TS 3.3.5.1, “Emergency Core Cooling System (ECCS) Instrumentation,” TS 3.5.1, “ECCS-Operating,” and TS 3.0.3. As such, this is a condition prohibited by TS and is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B). In addition, since the “C” channel (PIS-B21-2N021C) was surveillance tested just prior to identification of the drift of the “D” channel (PS-B21-2N021D), redundant channels were inoperable at the same time impacting both Core Spray and LPCI functions; therefore, this is also considered a condition that could have prevented fulfillment of a safety function (10 CFR 50.73(a)(2)(v)(D)) and a common cause inoperability of independent trains or channels (10 CFR 50.73(a)(2)(vii)). | ML22080A215
Susquehanna Steam Electric Station | Unit 1 | Loss of 1B RHRSW Pump due to Cable Damage During Excavation Activities | 03-21-2022 | At approximately 15:19 on October 7, 2021, operators at the Susquehanna Steam Electric Station, Unit 1 observed current oscillations during a run of the Unit 1 ‘B’ Residual Heat Removal Service Water (RHRSW) Pump (“1B RHRSW Pump”). Following shutdown of the pump, operators entered Technical Specification (TS) 3.7.1, Condition B for an inoperable RHRSW subsystem. Troubleshooting identified the cause of the current oscillations to be a ground on the B-phase power cable for the pump, which was likely damaged on September 23, 2021 during excavation activities, thereby rendering the pump inoperable at the time. The power cable was replaced, and the RHRSW System was declared operable at 07:33 on October 11, 2021. Therefore, this event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. The Unit 1, ‘A’ RHRSW subsystem was determined to be concurrently inoperable on September 29. Therefore, this event is also being reported in accordance with 10 CFR 50.73(a)(2)(v)(B) as a condition that could have prevented fulfillment of a safety function. The event was caused by an inadvertent puncture of conduit during excavation activities and the use of a flawed damage assessment method. Corrective actions include repairing and replacing the cable and conduit and updating plant documents. There were no actual safety consequences associated with the described condition. NRC FORM 366A (08-2020) Page 2 of 3 . NRC FORM 366A (08-2020) U. S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 LICENSEE EVENT REPORT (LER) CONTINUATION SHEET Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. (See NUREG-1022, R.3 for instruction and guidance for completing this form https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Susquehanna Steam Electric Station, Unit 1 05000-387 YEAR SEQUENTIAL NUMBER REV NO. 2021 - 004 - 01 | CONDITIONS PRIOR TO EVENT Unit 1 – Mode 1, approximately 100 percent Rated Thermal Power (RTP) Unit 2 – Mode 1, approximately 100 percent RTP On September 23, 2021, during excavation activities to support future unrelated piping replacement work, personnel at the Susquehanna Steam Electric Station (SSES) punctured a 4” conduit line. Work was immediately stopped, and an investigation commenced. On October 7, the damaged conduit was positively identified as F1F104 [EIIS System/Component Code: BI/CND]. F1F104 contains cable FF1S0601A [BI/CBL], which is the power cable for Pump 1P506B [BI/P], the Unit 1, ‘B’, Residual Heat Removal Service Water (RHRSW) Pump (hereafter referred to as the “1B RHRSW Pump”). EVENT DESCRIPTION At approximately 15:19 on October 7, 2021, operators at the Susquehanna Steam Electric Station, Unit 1 observed current oscillations during a run of the 1B RHRSW Pump. The operators shut down the 1B RHRSW Pump entered Technical Specification (TS) 3.7.1, “Residual Heat Removal Service Water (RHRSW) System and the Ultimate Heat Sink (UHS),” Condition B, for the inoperable Unit 1 ‘B’ RHRSW subsystem. Troubleshooting identified the cause of the current oscillations to be a ground on the B-phase of cable FF1S0601A. Troubleshooting also determined that the likely cause of the ground on cable FF1S0601A was damage to the cable when conduit F1F104 was punctured on September 23. Therefore, the 1B RHRSW Pump is considered to have been inoperable from the time of cable damage on September 23, 2021. Cable FF1S0601A was replaced, conduit F1F104 was repaired, and the 1B RHRSW pump was returned to service at 07:33 on October 11. Therefore, this event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. Further, on September 29, the Unit 1 ‘A’ RHRSW subsystem was declared inoperable due to UHS spray array and bypass valve alignments to support UHS nozzle cleaning. Thus, both subsystems of the Unit 1 RHRSW System were concurrently inoperable. Therefore, this event is also being reported in accordance with 10 CFR 50.73(a)(2)(v)(B) as condition that could have prevented the fulfillment of the safety function of structures, systems, or components that are needed to remove residual heat. CAUSE OF EVENT The direct cause of the event was determined to be that Cable FF1S0601A was struck through an inadvertent puncture of unidentified conduit F1F104 during excavation activities. The apparent cause of the failure was that methods for reviewing the condition of Cable FF1S0601A following damage were flawed, resulting in an inaccurate assessment and non-conservative decisions. ANALYSIS/SAFETY SIGNIFICANCE An Engineering Evaluation was performed for the time period for which the Unit 1 ‘B’ RHRSW subsystem was inoperable. On September 29, the Unit 1 ‘A’ RHRSW subsystem was declared inoperable due to spray array and bypass valve alignments to support spray array inspection and nozzle cleaning. The associated | ML22080A216
Susquehanna Steam Electric Station | Unit 2 | Automatic Reactor Scram Due to Main Turbine Trip Caused by Inadvertent Trip of the Main Generator Output Breakers | 03-24-2022 | On October 11, 2021, at approximately 13:21, Susquehanna Steam Electric Station Unit 2 reactor automatically scrammed due to a main turbine trip. Both divisions of the Reactor Protection System (RPS) actuated and all control rods inserted. This event was reported by Event Notification 55514 in accordance with 10 CFR 50.72(b)(2)(iv)(A), (b)(2)(iv)(B) and (b)(3)(iv)(A). This event is also reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of a system listed in 10 CFR 50.73(a)(2)(iv)(B). The event was caused by the 500kV switchyard primary plant interface relay inadvertently tripping open the main generator output breakers due to a transient voltage resulting from a ground applied on the primary switchyard battery system. This led to a load reject trip of the main turbine that resulted in an automatic scram. Key corrective actions included removing the ground from the 125 VDC primary switchyard battery system, implementing an increased time delay for trip signals to the primary plant interface relay, and lifting redundant shield grounds on the station side of the relay. Additionally, primary plant interface inputs will be hardened, as appropriate. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366 (08-2020) <)P~ REc11~ /~ {Ko~ :; _2l_ i ~~~-Ir', ; ~,.,-:;-•'71 +01 •it-•~· I I I I I I I I I I I I I I I I I I I I I I I I I I I NRC FORM 366A (08-2020) Page 2 of 3 . NRC FORM 366A (08-2020) U. S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 LICENSEE EVENT REPORT (LER) CONTINUATION SHEET Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. (See NUREG-1022, R.3 for instruction and guidance for completing this form https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Susquehanna Steam Electric Station Unit 2 05000-388 YEAR SEQUENTIAL NUMBER REV NO. 2021 - 003 - 01 | CONDITIONS PRIOR TO EVENT Unit 1 – Mode 1, approximately 100 percent Rated Thermal Power Unit 2 – Mode 1, approximately 95 percent Rated Thermal Power There were no structures, systems, or components that were inoperable at the start of the event that contributed to the event. EVENT DESCRIPTION On October 11, 2021, at approximately 13:21, Susquehanna Steam Electric Station Unit 2 reactor automatically scrammed due to a main turbine [EIIS System/Component Code: TA/TRB] trip. The Unit 2 Control Room received indication of a main turbine trip with both divisions of the Reactor Protection System (RPS) [EIIS System Code: JC] actuated and all control rods inserted. The turbine bypass valves [EIIS System/Component Code: JI/PCV] opened automatically to control reactor pressure and subsequently remained open causing the reactor to depressurize; this event is reported in Licensee Event Report 50-388/2021-004. Operations manually closed the Main Steam Isolation Valves (MSIVs) [EIIS System/Component: SB/ISV] to stop reactor depressurization. The High Pressure Coolant Injection (HPCI) [EIIS System Code: BJ] and Reactor Core Isolation Cooling (RCIC) [EIIS System Code: BN] systems were manually initiated to control reactor water level. Operations subsequently maintained reactor water at the normal operating band using RCIC and reactor pressure was controlled with HPCI in pressure control mode and the main steam line drains. The Reactor Recirculation Pumps [EIIS System/Component Code: AD/P] tripped on End of Cycle Recirculation Pump Trip. This event was reported by Event Notification 55514 in accordance with 10 CFR 50.72(b)(2)(iv)(A), (b)(2)(iv)(B) and (b)(3)(iv)(A). This event is also reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of a system listed in 10 CFR 50.73(a)(2)(iv)(B). CAUSE OF EVENT The direct cause of the event was an applied ground by the switchyard [EIIS System: FK] owner contractor on the primary switchyard battery system which caused transient voltage at the relay [EIIS Component: RLY] input. The apparent cause was the switchyard owner interface relay design and settings were not in alignment with the vendor / original equipment manufacturer best practices leading to inadequate margin to prevent transient voltages from unintentionally causing a trip signal. ANALYSIS/SAFETY SIGNIFICANCE During the reactor scram off-site power remained available to power all safety related shutdown equipment. All control rods inserted as designed and all safety related equipment operated as designed. There was no loss of function that prevented the safe shutdown of the reactor and to maintain it in a safe shutdown condition. All safety systems were available to mitigate the consequences of an accident. The condition described herein did not result in a safety system functional failure. Accordingly, this event will not be counted as a safety system functional failure in the Reactor Oversight Process Performance Indicators There were no actual consequences to the health and safety of the public as a result of this event. | ML22083A168
Susquehanna Steam Electric Station | Unit 1 | Automatic Reactor Scram due to Turbine Control Valve Fast Closure | 03-30-2022 | At approximately 12:54 on November 30, 2021, Susquehanna Steam Electric Station, Unit 1, experienced an automatic reactor scram during Turbine Valve Cycling surveillance testing. During the fast closure portion of the surveillance test on Main Stop Valve 4 (MSV-4), a closure of Turbine Control Valve 4 (CV-4) occurred, resulting in a Division II Reactor Protection System (RPS) actuation. While the Division II half scram signal was actuated, a Division I RPS actuation occurred, resulting in a full reactor scram. All control rods inserted and operators placed mode switch to shut down. Event Notification 55616 reported this event in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72{b)(3)(iv)(A). This event is also reportable in accordance with 10 CFR 50.73(a)(2){iv)(A) as an event that resulted in automatic actuation of a system in 10 CFR 50.73(a)(2)(iv)(B). The CV-4 fast closed due to transient voltage from a ground fault on the CV-4 Fast Acting Solenoid (FASV) field wiring. The previous single point vulnerability review for the system failed to identify and mitigate this failure mechanism. The Electro-hydraulic Control fluid pressure perturbation from the simultaneous closure of MSV-4 and CV-4 resulted in the Division II RPS actuation. Further review identified a recommended modification to dampen pressure in the system was never installed based on vendor recommendation. Key corrective actions include, in part, replacement of the CV-4 FASV wire and installation of orifices in accordance with the General Electric Technical Information Letter 1212-2 guidance. There were no actual consequences to the health and safety of the public as a result of this event. U. 5. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT RE Po RT (LE R) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A1 0M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory f , h' f Affairs, (3150-0104), Attn: Desk all: oira submission@ornb.eop.gov. The NRG may not conduct or (See NUREG-1022, R.3 for _inStruction and gu_idance or completing t IS arm sponsor, and a person is not required to respond to, a collection of infonmation unless the document https://www.nrc.gov/read1ng-rm/doc-collect1ons/nuregs/staff/sr1022/r31) requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LERNUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station, 05000-387 NUMBER NO, Unit 1 2021 - 005 - 01 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, approximately 80 percent Rated Thermal Power (RTP) Unit 2 - Mode 1, approximately 100 percent RTP Unit 1 Turbine Valve Cycling surveillance testing was in progress at the time of the event. EVENT DESCRIPTION At approximately 12:54 on November 30, 2021, Susquehanna Steam Electric Station, Unit 1, experienced an automatic scram due to a Reactor Protection System (RPS) [EIIS System Code: JC] actuation during Turbine Valve Cycling surveillance testing. During the fast closure portion of the surveillance test on Main Stop Valve 4 (MSV-4) [EIIS System/Component Codes: TA/SHV], Control Valve 4 (CV-4) [TA/FCV] unexpectedly fast closed, thereby generating a Turbine Control Valve fast closure on Division II RPS. Fast closure of CV-4 and MSV-4 caused an Emergency Trip System (ETS) pressure perturbation in the Electro-hydraulic Control (EHC) [TG] system which actuated one of the two Division I RPS low pressure switches. The Division I signal combined with the Division II signal resulted in a full scram. All control rods inserted, and operators placed mode switch to shut down. Reactor water level was maintained at the normal operating band using the Reactor Feed Water system [SJ]. All safety systems responded properly during the event. Event Notification 55616 reported this event in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). This event is also reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of a system listed in 10 CFR 50.73(a)(2)(iv)(B). CAUSE OF EVENT Transient voltage from a ground fault on the CV-4 Fast Acting Solenoid, SV10150D, field wiring energized the solenoid causing CV-4 to unexpectedly fast close. The EHC Single Point Vulnerability Assessment did not identify failure modes necessary to develop bridging and mitigation strategies on a passive component (i.e., wiring) located in a severe service environment and ultimately contributed to a reactor scram. ETS header pressure drop from simultaneous fast closure of CV-4 and MSV-4 actuated one of the two Division I RPS control valve ETS low pressure switches (PSLC721 N005A/C) [JJ/PS]. Operating Experience General Electric Technical Information Letter (TIL) 1212-2, which provided recommendations for controlling ETS pressure/flow via installation of orifices [OR], was previously evaluated with an inadequate conclusion resulting in the orifices not being installed as recommended. , ANALYSIS/SAFETY SIGNIFICANCE The actual consequence of this event was a Unit 1 Reactor scram. The scram did not require or result in the actuation of Emergency Core Cooling System and no main steam relief valves [SB/RV] opened. Reactor Core Isolation Cooling system [BN] initiated as designed. All safety systems responded properly during the event. The condition described herein did not result in a safety system functional failure. Accordingly, this | ML22089A238
YEAR SEQUENTIAL REV | Unknown Unit | Condition Prohibited by Technical Specification Due to Setpoint Drift Attributed to Age Related Degradation | 04-11-2022 | 12.Licensee Contact for this LER Licensee Contact Phone Number (Include Area Code) Peggy Kramer, Regulatory Affairs Engineer I( 570) 542-3131 13.Complete One Line for each Component Failure Described in this Report Cause I System Component I Manufacturer I Reportable to IRIS I Cause I System I Component I Manufacturer I Reportable to IRIS I X I JC LIS I B080 I Y I I I I 14.Supplemental Report Expected I I Month I Day I Year 15.Expected Submission Date ☒ No I☐ Yes (If yes, complete 15. Expected Submission Date) I I I I 16.Abstract (Limit to 1560 spaces, i.e., approximately 15 single-spaced typewritten lines) At approximately 13:50 on December 15, 2021, during surveillance testing, personnel at the Susquehanna Steam Electric Station, Unit 2, found the setpoint for the Unit 2 ‘B’ Reactor Vessel Water Level Narrow Range Indicator, LISB212N024B, had drifted outside of its Technical Specification (TS) Allowable Value (AV). Operators declared the Reactor Protection System and the Primary Containment Isolation System inoperable, and entered TS 3.3.1.1, Condition A, and TS 3.3.6.1, Condition A. The level indicator’s setpoint was adjusted to within the TS AV, and TS 3.3.1.1, Condition A, and TS 3.3.6.1, Condition A, were exited at 15:42 on December 15. Based on the information available, the condition is considered to have existed for longer than allowed by TS 3.3.1.1 and TS 3.3.6.1. Therefore, the condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant’s TS. The cause of the event was determined to be an increase in instrument drift due to age related degradation of LISB212N024B internal micro switch 1A. Contributing to this was that a work order was previously generated to replace the switch but not scheduled. Corrective actions included replacement of LISB212N024B, which included internal micro switches 1A and 1B. There were no actual safety consequences associated with the described condition. NRC FORM 366A U. S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station, 05000-388 NUMBER NO. Unit 2 2021 - 005 - 01 | CONDITIONS PRIOR TO EVENT Unit 1 – Mode 1, approximately 98 percent Rated Thermal Power (RTP) Unit 2 – Mode 1, approximately 100 percent RTP EVENT DESCRIPTION At approximately 13:50 on December 15, 2021, during surveillance testing, personnel at the Susquehanna Steam Electric Station, Unit 2, found the setpoint for the Unit 2 ‘B’ Reactor Vessel Water Level Narrow Range Indicator LISB212N024B [EIIS System/Component Code: JC/LIS] had drifted outside of its Technical Specification (TS) Allowable Value (AV). Operators declared the Reactor Protection System and the Primary Containment Isolation System [JM] inoperable, and entered TS 3.3.1.1, “Reactor Protection System (RPS) Instrumentation,” Condition A, and TS 3.3.6.1, “Primary Containment Isolation Instrumentation,” Condition A. LISB212N024B was adjusted to within the TS AV, and TS 3.3.1.1, Condition A, and TS 3.3.6.1, Condition A, were exited at 15:42 on December 15. Based on the information available, the condition is considered to have existed for longer than allowed by TS 3.3.1.1 and TS 3.3.6.1. Therefore, the condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant’s TS. CAUSE OF EVENT The cause of the event was determined to be an increase in instrument drift due to age related degradation of LISB212N024B internal micro switch 1A. Contributing to this was that a work order was previously generated to replace the switch but not scheduled. ANALYSIS/SAFETY SIGNIFICANCE While LISB212N024B was outside of the TS 3.3.1.1 and TS 3.3.6.1 allowable value, the other trip system channel was available with the exception of a 6.5-hour window when its indicators were out of service for surveillance. Excessive drift of LISB212N024B would not have occurred in the approximate 6.5 hours taken to satisfactorily surveil the other trip system which immediately followed surveillance of LISB212N024B. Therefore, RPS and Primary Containment Isolation System would have performed within their safety functions and the condition described herein did not result in a safety system functional failure. Accordingly, this event will not be counted as a safety system functional failure in the Reactor Oversight Process Performance Indicators. There were no actual consequences to the health and safety of the public as a result of this event. CORRECTIVE ACTIONS The switch was returned to within TS allowable values. Corrective actions included replacement of LISB212N024B, which included internal micro switches 1A and 1B. Page 2 of 3 | ML22101A186
River Bend Station | Unit 1 | Condition Prohibited by Technical Specifications due to Residual Heat Removal B Pump Motor Bearing Oil Leak | 05-17-2022 | On March 29, 2022, at 19:00 Central Time (CT) with River Bend Station, Unit 1 operating at 100% power, Residual Heat Removal Pump B was declared inoperable due to an oil leak from the motor lower bearing sight glass that would have prevented the motor from fulfilling its mission time. The Residual Heat Removal Pump B motor lower bearing sight glass oil leak was caused by improper installation of the sight glass O-ring on March 14, 2022, when the sight glass O-ring was replaced during the performance of a preventative maintenance work order. The leak was discovered on March 18, 2022. The oil leak was corrected by replacing the sight glass assembly and O-ring on March 30, 2022. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or httpsJ/www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV River Bend Station, Unit 1 05000-458 NUMBER NO. 2022 001 00 | EVENT DESCRIPTION On 03/29/2022, at 1900 Central Time (CT) with River Bend Station, Unit 1 operating at 100% power, Residual Heat Removal Pump 8 (RHR 8) [BO] was declared inoperable when it was confirmed that the leakage rate from the motor lower bearing oil reservoir would prevent RHR 8 from meeting its mission time. The oil leak began following sight glass O-ring replacement performed on 03/14/2022. An oil leak was identified in condition reports on 03/18/2022 and 03/26/2022. In both cases, the oil level was low, but above the minimum required level and oil additions were made to bring the level up to the standstill mark. An analysis performed on 03/29/2022 determined that the identified leakage would not have supported the mission time of RHR 8. On 03/30/2022, a new sight glass assembly and O-ring were installed. Engineering verified that the installation and post maintenance test were both satisfactory. RHR 8 was determined to be inoperable from the time of the original sight glass O-ring replacement on 03/14/2022 until the sight glass assembly and O-ring was replaced and re-tested satisfactorily on 03/30/2022. This resulted in inoperability for a time longer than allowed by Technical Specifications. There is no record of an oil leak prior to maintenance performed on 03/14/2022. This condition is being reported as an operation or condition prohibited by Technical Specifications in accordance with 10 CFR 50. 73(a)(2)(i)(B). SAFETY ASSESSMENT The actual consequence of this event was the potential inability of RHR B to fulfill its mission time following a Design Basis Accident. Residual Heat Removal Pump A (RHR A) [BO] was Operable for the duration of this event; therefore, this event was of minimal significance to the health and safety of the public. EVENT CAUSE The direct cause of this event was improper installation of the sight glass O-ring during the performance of preventative maintenance. CORRECTIVE ACTIONS Complete: The condition was corrected by replacing the sight glass assembly and O-ring on 03/30/2022. Planned Actions tracked in the Corrective Action Program: • Update all affected ECCS model work orders for sight glass and O-ring replacement to include further guidance to prevent future occurrences. • Adjust the scope of the preventative maintenance work orders for sight glass and O-ring replacement to reflect the manufacturer recommendations. Timeliness of identification, evaluation, and resolution of this condition are being driven to resolution by individual condition reports within the Corrective Action Process. PREVIOUS SIMILAR EVENTS None NRG FORM 366A (08-2020) Page 2 of 2 | ML22137A035
Quad Cities Nuclear Power Station | Unit 2 | Electromatic Relief Valve 38 Did Not Actuate Due to Incorrectly Oriented Plunger Well Plastic Guides | 05-20-2022 | On March 21, 2022, with Unit 2 in shutdown, Electromatic Relief Valve (ERV) 2-O2O3-3B, 2B Main Steam Line Relief Valve, did not stroke in accordance with work package instructions. The valve was being tested to satisfy Technical Specification Surveillance Requirement (TS SR) 3.5.1.10, verify each Automatic Depressurizing System (ADS) valve actuator strokes when manually actuated. All other Unit 2 ADS valves were found to stroke satisfactorily. The cause of the failure was unclear vendor guidance and insufficient procedural guidance regarding the orientation for the installation of the internal plunger well plastic guides. The guides were incorrectly installed during rebuild which caused actuator binding. The failure will be prevented by revising the site maintenance rebuild procedure with input from the manufacturer. This event is being reported in accordance with 10 CFR 50. 73(a)(2)(i)(B), an operation or condition which was prohibited by the plant's Technical Specification. TS 3.5.1 Condition Hallows one ADS valve to be inoperable for a period of 14 days. This ADS valve was found to be inoperable for the entire cycle. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EX.PIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104). Attn: Desk Officer for the Nuclear Regulatory Commission, 72517th Street NW, Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-cbllections/nureqs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Quad Cities Nuclear Power Station 05000- 254 YEAR NUMBER NO. 2022 - 001 00 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Electromatic Relief Valve 38 Did Not Actuate Due to Incorrectly Orientated Plunger Well Plastic Guides CONDITION PRIOR TO EVENT Unit: 2 Event Date: March 21, 2022 Event Time: 1030 CDT Reactor Mode: 4 Mode Name: Cold Shutdown Power Level: 0% No structures, systems or components were inoperable at the start of this event that contributed to the event. A. DESCRIPTION OF EVENT On March 21, 2022, with Unit 2 in shutdown for refueling outage Q2R26, and during performance of the Technical Specification (TS) Surveillance Requirement (SR) 3.5.1.10, the 2-0203-38 Electromatic Relief Valve (ERV)[SB] failed to actuate. TS SR 3.5.1.1 O requires each Automatic Depressurizing System (ADS)[SB] valve actuator stroke when manually actuated. All other Unit 2 ADS valves were found to stroke successfully. The 2-0203-38 actuator was replaced and stroked successfully prior to completion of refueling outage Q2R26, restoring the system to operable. The 2-0203-38 ERV failed actuator was originally installed in March 2020 after having been rebuilt earlier in the month in preparation for refue.ling outage Q2R25. The actuator had been rebuilt in accordance with revision 10 of site maintenance rebuild procedure. In the April 2020, all the Unit 2 ADS ERVs were successfully stroked multiple times prior to unit startup from Q2R25, confirming no actuator binding was observed on any of the Unit 2 ERVs. Revision 11 of the site maintenance rebuild procedure, which included corrective actions from the 2-0203-3D ERV failure, was implemented in August 2020 after startup from the Q2R25 refuel outage. Initial assessment of the removed 2-0203-38 ERV was that solenoid actuator was burnt out and there was significant binding of the actuator. The actuator was sent to Constellation Powerlabs for further evaluation and cause determination, which was completed prior to startup from the Q2R26 refueling outage. An extent of condition review, including inspection of the other Unit 2 ERVs was performed as well as a review of the rebuild work instructions for the Unit 1 ERVs. No significant or similar issues with either unit's ERVs were found during the extent of condition review. | ML22140A128
i | Unknown Unit | Turbine Stop Valve Limit Switch Failure due to Lubricant Degradation | 05-27-2022 | 12. Licensee Contact for this LER Licensee Contact Phone Number (Include area code) CJ Smith, Operations Director (815) 415-2200 13. Complete One Line for each Component Failure Described in this Report Cause System Component Manufacturer Reportable to IRIS I•• .. Cause System Component Manufacturer Reportable to IRIS B TA 33 N007 y ~:•.: NA NA NA NA NA 14. Supplemental Report Expected Month Day Year 181 No I D Yes (If yes, complete 15. Expected Submission Date) 15. Expected Submission Date 6. Abstract (Limit to 1560 spaces, i.e., approximately 15 single-spaced typewritten lines) On 12/4/21 during suNeillances of the turbine stop valves (TSV), limit switch 1 C71-N006C failed. The component was sent offsite for failure analysis. Component failure analysis was complete on 2/4/2022 and determined that the cause was attributed to degradation of switch lubricant which established firm evidence that a past inoperability condition existed. The component 1C71-N006C is the TSV-3 Closure Reactor Protection System (RPS) channel A2 scram limit switch. This device is required by technical specifications to support LCO 3.3.1.1 function 8 (RPS) and LCO 3.3.4.1 (End of Cycle - Recirculation Pump Trip or EOC-RPT). Each TSV position is monitored by two limit switches (for TSV-3, A2 and 81 channels). This condition results in the TSV-3 input to RPS A2 as well as one channel of the EOC-RPT trip being INOPERABLE. The appropriate LCO Conditions and Required Actions were entered and tracked. The RPS and EOC- RPT functions were maintained due to the redundant channels remaining OPERABLE. There were no reportability thresholds applicable to this issue at the time of the event, and there was no loss of safety function. The condition is reportable in accordance with 10 CFR 50. 73(a)(2)(i)(B) for operation or condition prohibited by Technical Specifications. Immediate corrective actions were taken to replace the component and restore the associated channel to OPERABLE. NRC FORM 366A (08-2020) Page_2_ of _5_ NRC FORM 366A (08-2020) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 ,,,,. ...... lt~;t.1.,l.\ LICENSEE EVENT REPORT (LER) \~~ ; CONTINUATION SHEET /) ..... (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www. nrc.g ov/reading-rm/doc-collections/nuregs/staff/sr1 022/r31) Estimated burden per response lo comply with lhis mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and led back to industry. Send comments regarding burden estimate to lhe FOIA, library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required lo respond lo, a collection of infonnation unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR LaSalle County Station, Unit 1 05000- 373 SEQUENTIAL NUMBER REV NO. 2022 - 001 | Plant and System Identification LaSalle Country Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the main turbine system. The affected component was the turbine stop valve (TSV) limit switch 1C71- N006C. This is the limit switch for the TSV number 3 Closure Reactor Protection System (RPS) A2. channel. Condition Prior to Event Unit(s): 1 Reactor Mode(s): 1 Description Date: Mode(s) Name: Feb 4, 2022 Power Operation Time: 00:00 CDT Power Level: 100 percent On 12/4/21 the limit switch on unit 1 TSV-3 failed to actuate during surveillance testing. The limit switch is normally held in the actuated position during unit operation and only allowed to return to the relaxed, shelf state position, once per 6 months. The component (1 C71-N006C) was replaced and sent offsite for component testing and failure analysis. The component failure analysis (documented in report dated Feb 4, 2022) verified the limit switch malfunction and determined the cause was attributed to degradation of switch lubricant. Cause The failure analysis functional testing verified the limit switch malfunction. The switch cam would rotate but no electrical switching occurred and no audible "clicking" sound was heard. Based on internal component inspection, the failure mode was attributed to the slide and base plate having considerable corrosion products. The internal components were covered with a black, sticky material of dried-out grease and steel corrosion products. Reportabllity and Safety Analysis The component 1C71-N006C is the TSV-3 Closure RPS channel A2 scram limit switch. This device is required to be OPERABLE per LCO 3.3.1 .1 function 8 (RPS) and LCO 3.3.4.1 (EOC-RPT). TSV-3 was fully closed during the surveillance, which should have resulted in the 1 C71-N006C switch being open. Each TSV position is monitored by two limit switches (for TSV-3, A2 and B1 channels). This condition results in the TSV-3 input to RPS A2 as well as one channel of the EOC-RPT trip being INOPERABLE. The appropriate LCO Conditions and Required Actions were entered and tracked. The RPS and EOC-RPT functions were maintained due to the redundant channels remaining OPERABLE. There were no reportability thresholds applicable to this issue at the time of the event, and there was no loss of safety function. 00 Upon receipt of the failure analysis on February 4, 2022, the station was made aware that a past inoperability period existed from the test failure that occurred on December 4, 2021. The inoperability period was greater than allowed by TS LCO 3.3.1.1 and 3.3.4.1, as indicated below. This event is reportable in accordance with 10 CFR 50. 73(a)(2)(i)(B) as a condition prohibited by the plant's TS. • LCO 3.3.1.1 requires that the RPS instrumentation for each function is OPERABLE, and Condition A applies to one or more required channels being inoperable requires that the channel or its associated trip system is placed in trip within 12 hours. In this case, the station had exceeded the completion time of 12 hours, when the | ML22147A131
Browns Ferry Nuclear Plant | Unit 1 | Pressure Boundary Leak on Residual Heat Removal System Low Pressure Coolant Injection Test Line | 05-31-2022 | On January 15, 2022, at 2320 Central Standard Time (CST), during a drywell entry for leak identification, BFN Engineering personnel discovered a through-wall piping leak on a test line upstream of the Residual Heat Removal and Shutdown Cooling test shut-off valve. This test line is classified as American Society of Mechanical Engineers Code Class 1 piping and constitutes part of the Unit 1 Reactor Coolant System pressure boundary. Operations personnel declared the Unit 1 Low Pressure Coolant Injection system (LPCI) Loop I inoperable and maintained Unit 1 in Mode 4 or 5 until the leak was repaired. On January 16, 2022, at 0541 CST, eight-hour Event Notification 55706 was made to the NRC. The test line was cut and capped pending permanent repairs, and on January 20, 2022, at 1520 CST, Unit 1 LPCI Loop I was declared operable. The root cause of this event was small bore piping which was not specifically analyzed for fatigue failure vulnerability due to operational or resonance vibration. The corrective action for this event is to implement Engineering Change Packages for all small bore piping with vulnerability to fatigue failure due to exceeding the endurance limit due to operational vibration. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 1 05000-259 NUMBER NO. 2022 - 001 - 01 | I. Plant Operating Conditions Before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN) Unit 1 was in Mode 4 at approximately zero percent power. II. Description of Event A. Event Summary On January 15, 2022, at 2320 Central Standard Time (CST), during a drywell (DW) entry for leak identification, BFN Engineering personnel discovered a through-wall piping leak on a test line [PSF] upstream of the Residual Heat Removal (RHR) [BO] and Shutdown Cooling test shut-off valve [SHV]. This test line is classified as American Society of Mechanical Engineers (ASME) Code Class 1 piping and constitutes part of the Unit 1 Reactor Coolant System (RCS) [AC] pressure boundary. Operations personnel declared the Unit 1 Low Pressure Coolant Injection system (LPCI) Loop I inoperable and maintained Unit 1 in Mode 4 or 5 until the leak was repaired. On January 16, 2022, at 0541 CST, eight-hour Event Notification (EN) 55706 was made to the NRC. The test line was cut and capped pending permanent repairs, and on January 20, 2022, at 1520 CST, Unit 1 LPCI Loop I was declared operable. The TVA is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant’s Technical Specifications (TS); and 10 CFR 50.73(a)(2)(ii)(A), as any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML22151A327
Palo Verde Nuclear Generating Station (PVNGS) | Unit 1 | Unit 1 and Unit 3 Emergency Diesel Generator Actuation on Loss of Offsite Power to Class 4.16 kV Buses | 06-03-2022 | On October 20, 2021, at approximately 1446 Mountain Standard Time, a valid actuation of the emergency diesel generators (EDGs) for Palo Verde Nuclear Generating Station Unit 1 train ‘B’ and Unit 3 train ‘A’ occurred due to an undervoltage condition on their respective 4.16 kilovolt (kV) safety buses. Both EDGs started and loaded as designed, including associated train essential spray pond pumps and the Unit 1 B-train auxiliary feedwater pump. The loss of power to the Unit 1 and Unit 3 safety buses and resulting component actuations were the result of an unintended personnel contact with an energized portion of the Unit 2 S06 intermediate bus during maintenance. Unit 1 and Unit 3 entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1, Condition A, for one required offsite circuit inoperable, which was exited after off-site power was restored to the units’ respective safety buses. The root cause of the event was attributed to overconfidence of the work team during validation activities. The team incorrectly assumed the work planning and clearance processes had established conditions for conducting work activities safely. Corrective actions to address the cause of the event include developing and implementing a plan to reinforce the belief and value that, "I am responsible for my own protection". Additional actions include monitoring worker behaviors, developing and delivering training on electrical safe work practices, increased oversight and engagement by station leaders and evaluating and increasing knowledge and proficiency of electrical workers. No similar events have been reported by PVNGS in the last three years. NRC FORM 366A (08-2020) Page 2 of 4 NRC FORM 366A (08-2020) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Palo Verde Nuclear Generating Station 05000-528 YEAR SEQUENTIAL NUMBER REV NO. 2021 001 01 | All times are Mountain Standard Time and approximate unless otherwise indicated. 1. REPORTING REQUIREMENT(S): This Licensee Event Report (LER) is being submitted pursuant to 10 CFR 50.73 (a)(2)(iv)(A) to report a valid automatic actuation of the circuitry that starts the emergency diesel generator (EDG) (EIIS: EK) for Unit 1 and Unit 3 following an undervoltage condition on the affected safety bus for each unit on October 20, 2021. The event included actuations of the associated essential spray pond (SP) pumps (EIIS: BS) and the Unit 1 B auxiliary feedwater (AF) pump (EIIS: BA). This event was reported to the NRC on October 20, 2021, via the event notification system (ENS 55534) and was updated on December 3, 2021. 2. DESCRIPTION OF STRUCTURE(S), SYSTEM(S) AND COMPONENT(S): The safety related equipment for each Palo Verde Nuclear Generating Station (PVNGS) unit is powered by one of two load groups (A-train and B-train). Either of the associated trains can provide power for safe plant shutdown. Each alternating current (AC) train includes one Class 1E 4.16 kilovolt (kV) bus (EIIS: EB). The preferred and alternate power sources for each load group is offsite 525 kV AC power (EIIS: EK) and is supplied via the 13.8 kV secondary windings of two of the three startup transformers (EIIS: EA) to six 13.8 kV intermediate buses; Each unit receives 13.8 kV power from two of the intermediate buses. Class 1E 4.16 kV safety load group power is provided from the associated intermediate bus engineered safety feature (ESF) transformers. The standby power supply for each safety load group consists of one EDG (EIIS: EK), including its auxiliary and fuel systems. The standby power supply functions as a source of AC power for safe plant shutdown in the event of loss of preferred power and for post-accident operation of ESF loads. 3. INITIAL PLANT CONDITIONS: On October 20, 2021, Palo Verde Unit 1 and Unit 3 were in Mode 1 (Power Operation) at 100 percent power, normal operating temperature and normal operating pressure. There were no inoperable structures, systems, or components at the time that contributed to this event. Unit 2 was defueled for a refueling outage. 4. EVENT DESCRIPTION: On October 20, 2021, at 1446, a valid loss of power (LOP) actuation occurred due to an undervoltage condition on the Unit 1 train ‘B’ and Unit 3 train ‘A’ safety buses which resulted in an automatic actuation of the circuitry that starts the Unit 1 B-train EDG and Unit 3 A-train EDG. Both EDGs started and loaded as designed. The EDG actuations were accompanied by the start of associated train essential SP pumps in both units. The Unit 1 B-train EDG actuation was also accompanied by the start of the Unit 1 B-train essential auxiliary feedwater pump, as required for the undervoltage condition. By design, actuation of the Unit 3 A-train steam-driven auxiliary feedwater pump was not required in response to the EDG actuation. The undervoltage condition on the Unit 1 and Unit 3 Class 1E 4.16 kV buses resulted from an electrical fault that occurred when a worker (utility, non-licensed) contacted an energized 13.8 kV element in the back side the “B” cubicle of Unit 2 S06 switchgear, which opened 525 kV breakers supplying the startup transformer AE- NAN-X02. This de-energized the startup transformer which was powering the Unit 1 13.8 kV intermediate bus S06 and the Unit 3 13.8 kV intermediate bus S05, which fed the respective Unit 1 B-train and Unit 3 A-train | ML22154A554
Nine Mile Point | Unit 2 | Automatic Reactor Scram due to Low Reactor Water Level During Maintenance | 06-03-2022 | On Thursday, April 5, 2022, at approximately 0222 hours with power level at approximately 100 percent, Nine Mile Point Unit 2 (NMP2) experienced a feedwater level control transient during maintenance on the Feedwater Flow Control Valve (LV1 OB), which resulted in a low reactor water level scram. This event is reportable per 10 CFR 50.7 3(a)(2)(iv)(A) as any event or condition that resulted in a manual or automatic actuation of any of the systems listed in 10 CFR50.7 3(a)(2)(iv)(B). Following the reactor scram, all plant systems responded per design. The root cause of this event was incorrect procedure guidance for nulling the demand and position signal in N2-SOP-06, "Feedwater Failures, Attachment 1, Restoration of 2FWS-LV10 Control". Corrective actions included revising N2-SOP-06, Attachment 1 to correctly null the demand signal to the potentiometer intended for control. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555,()001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document http://www. n rc.gov/reading-rm/doc-collections/n uregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid 0MB control number. I1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER I DYEA R SEQUENTIAL REV Nine Mile Point Unit 2 05000-1 410 I ~-I NUMBER 1-NO0. 001 | I. DESCRIPTION OF EVENT A. PRE-EVENT PLANT CONDITIONS: Prior to the event, NMP2 was in Mode 1, operating at approximately 100 percent rated thermal power. Feedwater level control was controlling in automatic with Feedwater Level Control Valve LV1 0A controlling in AUTO on the backup position sensor due to the primary position sensor being non-functional. Feedwater Level Control Valve LV1 OB was controlling in MANUAL with both primary and backup position sensors non-functional. Feedwater flow control is provided by a flow control valve in the discharge line of each reactor feed pump. The feedwater flow control valves may be controlled either in automatic or manual. Each feedwater flow control valve is provided with a primary and a secondary sensor that provides position feedback to the feedwater level control system. B. EVENT: On Thursday, April 5, 2022, at appr9ximately 0222 hours, NMP2 experienced a reactor scram due to reactor water low level while performing maintenance on Feedwater Level Control Valve LV10B. The potentiometer of the primary position sensor was being replaced on Feedwater Level Control Valve LV1 OB. Feedwater Level Control Valve LV1 OB was placed in a lock-up condition to support replacement of the potentiometer primary position sensor to allow Operations to regain automatic valve functionality. After the potentiometer was insta'lled, Operations attempted to restore Feedwater Level Control Valve LV1 OB to the primary position using N2-SOP-06, Feedwater Failures, Attachment 1. Upon restoring Feedwater Level Control Valve LV1 OB primary positioner, the position feedback signal was mismatched (80% open and demanded position was 43%), causing Feedwater Level Control Valve LV10B to rapidly close which subsequently caused reactor water level to lower. Feedwater Level Control Valve LV10A attempted to open to maintain reactor water level but was unsuccessful, resulting in a low reactor water level scram. High Pressure Core Spray and Reactor Core Isolation Cooling systems actuated as designed to maintain level, and plant personnel successfully recovered feedwater level control. The condition was reported to the NRC on April 5, 2022 at approximately 0608 hours pursuant to the requirements.of 10 CFR50. 72(b )(2)(iv)(A), 50. 72(b )(2)(iv)(B), and 50. 72(b)(3)(iv)(A) (Event Notification #55821) Nine Mile Point Unit 1 (NMP1) was unaffected. The event has been entered into the plant's corrective action program as IR 04490223. C. INOPERABLE STRUCTURES, COMPONENTS, OR SYSTEMS THAT CONTRIBUTED TO THE EVENT: No other systems, structures, or components contributed to this event. | ML22159A196
Dresden Nuclear Power Station | Unit 3 | Unit 3 Reactor Scram due to Main Power Transformer Failure | 06-14-2022 | On October 16, 2021, at 0428 CDT, an automatic reactor protection system actuation occurred due to failure of the main power transformer. The safety significance of this event was minimal. All control rods inserted to their full-in position. Following the reactor scram, all systems operated as expected. The cause of this event was due to a sudden, unanticipated, catastrophic failure of the main power transformer high voltage oil impregnated paper bushing. Corrective actions included replacement of the failed main power transformer and restricting use and/or procurement of the specific type of bushing that failed. This event is being reported in accordance with 10 CFR 50.7 3(a)(2)(iv)(A), an event that resulted in automatic actuation of a system listed in paragraph 10 CFR 50.7 3(a)(2)(iv)(B), specifically the reactor protection system including reactor scram. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Esumated burden per response to comply with this mandatory collection request: 80 hour... Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, library, and Information Collections Branch (T-6 A1 0M), U.S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfooollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affair.. (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira submiss1on@omb eoo.qov. The NRC may not conduct or (See NUREG-1022, R,3 for instruction and guidance for completing this form sponsor, and a per..on is not required to respond to, a collection of informaUon unless the document http //www nrc gov/read1ng-rm/doc-collect1ons/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Dresden Nuclear Power Station, Unit 3 05000- 249 2021 - 001 01 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 megawatts thermal rated core power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. A. CONDITIONS PRIOR TO EVENT Unit: 3 Event Date: October 16, 2021 Event Time: 0428 CDT Reactor Mode: 1 Mode Name: Power Operation Power Level: 100% B. DESCRIPTION OF EVENT On October 16, 2021, at 0428 CDT, an automatic reactor protection system [JC] actuation occurred due to failure of the main power transformer (MPT) [EL]. All control rods [AA] inserted to their full-in position. Following the reactor scram, all systems operated as expected. The MPT experienced a phase-to-ground fault. There is no evidence of a plant event or grid event as the initiator. There were no alarms indicative of a transformer failure as a precursor to the failure. Additionally, a dissolved gas analysis of the transformer oil sample performed two hours prior to the event revealed no alert nor degrading trend. The MPT "A" phase high voltage bushing, lightning arrester, and control cabinet suffered catastrophic damage. Ancillary components and equipment of the transformer suffered various degrees of damage. As a result of a fire associated with the MPT failure, an Unusual Event was declared due to a fire in the protected area not extinguished in less than 60 minutes. The Unusual Event was terminated at 0709 CDT. The transformer was replaced with a transformer of a different design and a different manufacturer. This event is being reported in accordance with 10 CFR 50. 73(a)(2)(iv)(A), an event that resulted in automatic actuation of a system listed in paragraph 10 CFR 50.73(a)(2)(iv)(B), specifically the reactor protection system including reactor scram. C. CAUSE OF EVENT The cause of the event was due to a sudden, unanticipated, catastrophic failure of the MPT high voltage oil impregnated paper bushing. This conclusion is based on the failure history associated with Trench Condenser Oil Transformer ANSI High Voltage Oil-Impregnated Paper (COTA HV OIP) bushings, the physical characteristics of the catastrophic failure, and the various analyses performed. | ML22165A204
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | LER: 2022-001, Exhaust Drain Pot Line Filled with Water up to HPCI Turbine due to Relay Failure | 06-28-2022 | At 1251 EDT on April 29, 2022, while troubleshooting the failure of the High Pressure Coolant Injection (HPCI) Exhaust Drain Pot High Level Alarm to clear, it was discovered that the High Pressure Coolant Injection exhaust line condensate drain system was not functioning as designed to support removal of condensate from the turbine exhaust. Troubleshooting determined that a logic relay failed to start the HPCI Gland Seal Condensate pump. This resulted in some water accumulation in the turbine casing. Subsequently, the High Pressure Coolant Injection System was declared inoperable. The turbine casing was manually drained and the failed relay was replaced. The system was restored to Operable. As a result, this condition is being reported under 10 CFR 50.72(b)(3)(v)(D) as a condition that could have prevented fulfillment of the safety function at the time of discovery. NRC FORM 366 (08-2020) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments CONTINUATION SHEET regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 – 333 NUMBER N0. 2022 – 001 – 00 | Background The High Pressure Coolant Injection (HPCI) System [EIIS Identifier: BJ] at James A. FitzPatrick Nuclear Power Plant (JAF) is a part of the Emergency Core Cooling System (ECCS); HPCI provides and maintains an adequate coolant inventory inside the Reactor Pressure Vessel [RPV] to prevent damage to the reactor core under postulated accident scenarios. The system is comprised of various components which include pumps, valves, piping, and instrumentation. The HPCI system is powered by a steam turbine using steam from the reactor. Steam is pressurized up to the admission valve 23MOV-14 which will open to admit steam to the HPCI turbine on a system initiation signal. HPCI has a Gland Exhaust System to collect steam leakage from the turbine shaft seals, turbine control & stop valve stems, and turbine exhaust casing drains. The system works with the HPCI exhaust Drain Pot to collect condensation from the bonnets of several valves and the HPCI turbine casing. The condensation is collected in the Gland Seal Condenser, and then pumped to Radwaste while in a standby lineup. 23LS-98 senses level in the Exhaust Drain Pot, causes Annunciator ARP-09-3-3-18 (HPCI Exhaust Drain Pot Level High) and opens a valve to allow the Drain Pot to drain to the Gland Seal Condenser. 23LS-100 senses level in the Gland Seal Condenser, energizes 23A-K31, and auto starts the 23P-141 (HPCI Gland Seal Condensate Pump) to pump the Gland Seal Condenser to Radwaste. Event Description On April 28, 2022, at 2245, control room annunciator ARP-09-3-3-18, HPCI drain pot water level alarm was received. Troubleshooting determined that HPCI logic relay 23A K31 failed to activate the HPCI Gland Seal Condensate pump to remove condensate from the turbine exhaust. As a result, water from 23MOV-14 steam leakby had accumulated in the HPCI turbine casing. The crew placed the HPCI auxiliary oil pump in Pull to Lock to mitigate any potential impact to personnel while draining the HPCI exhaust. The Pull to Lock switch position prevents the HPCI turbine from starting. The HPCI Exhaust Drain Pot was manually drained by Operations. Following draining, the HPCI system was declared operable. The condition was reported as a condition which could have prevented fulfillment of a safety function to mitigate the consequences of an accident per 10 CFR 50.72(b)(3)(v)(D), as submitted by ENS 55871. Event Analysis Level switch 23LS-100 senses water level in the HPCI gland seal condenser. On a high level, the level switch actuates relay 23A-K31 which alarms in the control room and starts the HPCI gland seal condenser pump (23P-141). The pump removes the condensate by pumping the water to the radwaste system. Troubleshooting determined that 23A-K31 had failed, preventing the auto start of 23P-141. This caused the HPCI exhaust drain pot to fill with condensate and subsequently a volume of condensate also accumulated in the HPCI turbine casing. The potential effects of water in the HPCI turbine casing is that a slug of water could cause a HPCI exhaust rupture disk diaphragm to be damaged upon HPCI initiation. Another potential effect of water in the turbine Page 2 of 3 | ML22179A366
Palo Verde Nuclear Generating Station (PVNGS) | Unit 2 | Units 2 and Unit 3 Emergency Diesel Generator Actuation on Loss of Offsite Power to Class 4.16 kV Buses | 07-01-2022 | On May 4, 2022, at approximately 1955 Mountain Standard Time, a valid actuation of the emergency diesel generators (EDGs) for Palo Verde Nuclear Generating Station Unit 2 A-train and Unit 3 B-train occurred due to an undervoltage condition on their respective 4.16 kilovolt (kV) safety buses. Both EDGs started and loaded as designed, including associated train essential spray pond pumps and the Unit 3 B-train auxiliary feedwater pump. The loss of power to the Unit 2 and Unit 3 safety buses and resulting component actuations were the result of startup transformer NAN-X01 tripping offline. Unit 2 and Unit 3 both entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1, Condition A, for one required offsite circuit inoperable. In addition, both units also entered TS 3.8.9, Condition A, for the loss of the Class 1E bus, which was exited when the EDGs started and restored power to their respective Class 1E buses. LCO 3.8.1, Condition A, was exited by both units on May 5, 2022. The direct cause of the undervoltage condition and the EDG and pump actuations was startup transformer NAN-X01 tripping offline. The direct cause of the event was attributed a grounded shield wire at the start-up transformer NAN-X01 W cabinet for the NAN-S06E cubicle differential relay current transformer (CT) from what should have been an unrelated billing and metering CT landed at a common terminal board location, resulting in circulating ground current. No similar events have been reported by PVNGS in the last three years due to the same initial cause. NRC FORM 366A (08-2020) Page 2 of 5 NRC FORM 366A (08-2020) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Palo Verde Nuclear Generating Station 05000-529 YEAR SEQUENTIAL NUMBER REV NO. 2022 001 00 | All times are Mountain Standard Time and approximate unless otherwise indicated. 1. REPORTING REQUIREMENT(S): This Licensee Event Report (LER) is being submitted pursuant to 10 CFR 50.73 (a)(2)(iv)(A) to report a valid automatic actuation of the circuitry that starts the emergency diesel generator (EDG) (EIIS: EK) for Unit 2 and Unit 3 following an undervoltage condition on the affected safety bus for each unit on May 4, 2022. The event included actuations of the associated essential spray pond (SP) pumps (EIIS: BS) and the Unit 3 B auxiliary feedwater (AF) pump (EIIS: BA). This event was reported to the NRC on May 5, 2022, via the event notification system (ENS 55878). 2. DESCRIPTION OF STRUCTURE(S), SYSTEM(S) AND COMPONENT(S): The safety related equipment for each Palo Verde Nuclear Generating Station (PVNGS) unit is powered by one of two load groups (A-train and B-train). Either of the associated trains can provide power for safe plant shutdown. Each alternating current (AC) train includes one Class 1E 4.16 kilovolt (kV) bus (EIIS: EB). The preferred and alternate power sources for each load group is offsite 525 kV AC power (EIIS: EK) and is supplied via the 13.8 kV secondary windings of two of the three startup transformers (EIIS: EA) to six 13.8 kV intermediate buses; Each unit receives 13.8 kV power from two of the intermediate buses. Class 1E 4.16 kV safety load group power is provided from the associated intermediate bus engineered safety feature (ESF) transformers. The standby power supply for each safety load group consists of one EDG (EIIS: EK), including its auxiliary and fuel systems. The standby power supply functions as a source of AC power for safe plant shutdown in the event of loss of preferred power and for post-accident operation of ESF loads. 3. INITIAL PLANT CONDITIONS: On May 4, 2022, Palo Verde Units 2 and 3 were in Mode 1 (Power Operation) at 100 percent power, normal operating temperature and normal operating pressure. There were no inoperable structures, systems or components at the time that contributed to this event. Unit 1 was in Mode 5 (Cold Shutdown) for a refueling outage. 4. EVENT DESCRIPTION: On May 4, 2022, at 1955, a valid loss of power (LOP) actuation occurred due to an undervoltage condition on the Unit 2 A-train and Unit 3 B-train safety buses which resulted in an automatic actuation of the circuitry that starts the Unit 2 A-train EDG and Unit 3 B-train EDG. The undervoltage condition on the Units 2 and 3 Class 1E 4.16 KV buses resulted from the startup transformer NAN-X01 tripping offline. Both EDGs started and loaded as designed. The EDG actuations were accompanied by the start of associated train essential SP pumps in both units. The Unit 3 B-train EDG actuation was also accompanied by the start of the Unit 3 B-train auxiliary feedwater pump, as required for the undervoltage condition. By design, actuation of the Unit 2 A-train steam-driven auxiliary feedwater pump was not required in response to the EDG actuation. At 1955 on May 4, both Units 2 and 3 entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1, Condition A for one required offsite circuit inoperable and LCO 3.8.9, Condition A for the loss of the Class 1E bus. Both units exited LCO 3.8.9, Condition A within one minute, after the Unit 2 A-train and Unit 3 B-train EDGs | ML22182A500
Fermi 2 | Unknown Unit | Unexpected HPCI Turbine Trip | 07-06-2022 | On May 11, 2022, the High Pressure Coolant Injection (HPCI) turbine unexpectedly experienced an overspeed trip during performance of surveillance 24.202.01 "HPCI Pump and Valve Operability Test At 1025 PSI". The cause was the HPCI Turbine Magnetic Pick-Up Speed Element (E41N212) was found shorted, breaking the speed feedback circuit to the HPCI Speed Controller. The HPCI Turbine Magnetic Pick-Up Speed Element (E41 N212) was replaced on 05/12/2022 and HPCI 24.202.01 surveillance was completed satisfactorily on 05/16/2022. An 8 hour Event Notification 55894 was reported to the NRC operations center per 10 CFR 50.72(b)(3)(v)(D). This report is submitted per 10 CFR 50.73(a)(2)(v)(D). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response lo oo~ly with this mandatory collection request 80 hours. Reported lessons learned are inro,porated into the licensing process and fed back to industry. Send cooiments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A1 0M), U. S. Nuclear Regulatory Coovnission, Washington, DC 20555--0001. or by e--ma~ lo CONTINUATION SHEET lnfocolleds.Resource@nrc.gov, and the 0MB reviewer at 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e--rnai: oira submission@omb.00!).00V. The NRG may not conduct or http:/lwww.nrc.gov/reading-nn/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond lo, a collection of information unless the document requesting or requiring the ooDection displays a currenHy valid 0MB conlrol number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER I I IFermi 2 05000- 341 | INITIAL PLANT CONDITIONS Mode- 1 Reactor Power - 10 Percent There were no structures, systems, or components (SSCs} that were inoperable at the start of this event that contributed to this event. Automatic Depressurization System (ADS} [RV] and Reactor Core Isolation Cooling (RCIC}[BN] were operable during the event. DESCRIPTION OF THE EVENT On May 11, 2022 at 1814 the plant was in Mode 1 performing start up activities. A High Pressure Coolant Injection (HPCI) [BJ] surveillance was in progress via surveillance 24.202.01 "HPCI Pump and Valve Operability Test at 1025 PSI." The HPCI turbine tripped on a mechanical overspeed due to failure of the HPCI Turbine Magnetic Pick-Up Speed Element (E41N212}. Operations noted the HPCI Turbine Steam Isolation Valve (E4100F067} and the HPCI/RCIC Test Pressure Control Valve (E41 00F011} were opening and closing unexpectedly. HPCI is designed to automatically restart when turbine speed drops below the mechanical over speed trip setpoint. Troubleshooting of the system shows the system restarted twice following the initial overspeed trip before HPCI was manually tripped. Troubleshooting determined that the HPCI Turbine Magnetic Pick-Up Speed Element (E4100N212} was shorted, breaking the speed feedback circuit to the HPCI Speed Controller. Troubleshooting also identified the HPCI Pump Discharge Pressure Switch (E41 00N027}, which controls the HPCI Minimum Flow Valve (E4150F012) was found to be out of tolerance low, causing the HPCI minimum flow valve (E4150F012) to cycle open and closed. There is no evidence the condition of the shorted HPCI Turbine Magnetic Pick-Up Speed Element (E4100N212) or the HPCI Pump Discharge Pressure Switch (E410 0N027) low out of tolerance conditions existed prior to the overspeed trip event on 05/11/2022. This is based on the fact the HPCI system performed as expected during surveillance testing 24.202.02 HPCI Flow Rate Test At 165 PSI Reactor Steam Pressure on 05/09/2022 and HPCI did not exhibit abnormal behavior prior to the start of 24.202.01 "HPCI Pump and Valve Operability Test at 1025 PSI" on 05/11/2022. The HPCI Turbine Magnetic Pick-Up Speed Element (E4100N212) was replaced and the HPCI Pump Discharge Pressure Switch (E41 00N027) was successfully calibrated into tolerance and HPCI was restored to operable status following satisfactorily performance of 24.202.01 HPCI Pump and Valve Operability at 1025 Rx PSIG" on 05/16/2022. Prior to the event, during the refueling outage, the HPCI turbine internal inspection was performed; which, included removing HPCI Turbine Magnetic Pick-Up Speed Element (E4100N212). The Post Maintenance Test for this work included performing both 24.202.02 "HPCI Flow Rate Test At 165 PSI Reactor Steam Pressure" and 24.202.01 "HPCI Pump and Valve Operability at 1025 Rx PSIG". Procedure 24.202.02 was satisfactorily completed on 05/09/2022. On 05/11/2022, the HPCI turbine unexpectedly experienced an overspeed trip during performance of surveillance 24.202.01. Troubleshooting determined the HPCI Turbine Magnetic Pick-Up Speed Element (E41 N212) had failed. The failed speed element was replaced and HPCI 24.202.01 surveillance was completed satisfactorily on 05/16/2022. An 8 hour Event Notification 55894 was reported to the NRC operations center per 10 CFR 50.72(b}(3)(v)(D). This report is submitted per 10 CFR 50.73(a)(2)(v)(D). | ML22187A109
Quad Cities Nuclear Power Station | Unit 1 | Low Pressure Coolant Injection Manually Isolated Due To Valve Test Equipment Issue | 07-08-2022 | On May 10, 2022, with Unit 1 operating at 100% power, motor operated valve (MOV) thrust testing was being performed on Residual Heat Removal (RHR) Low Pressure Coolant Injection (LPCI) valve 1-1001-28B, 1B LPCI Loop Upstream Stop Valve. Inadequate thrust conditions were discovered on this valve, which also serves as a Primary Containment Isolation Valve (PCIV). Technical Specification (TS) 3.6.1.3 Condition A requires that a containment penetration with a degraded valve be manually isolated within 4 hours. Manual closure of the companion PCIV valve 1-1001-29B, 1B LPCI Loop Downstream Stop Valve, including opening of the electrical breaker MCC 18/19-5 Cubicle F1 to the valve, rendered both loops of LPCI incapable of either manual or automatic injection as described in TS 3.5.1 Condition E for two LPCI Subsystems inoperable. The cause of the low MOV thrust value was found to be insufficient installation bond between the valve stem and the thrust sensor instrument. Thrust was eventually found to be sufficient, but this was not identified prior to the 4 hour TS action requirement. A new sensor was installed, and the valve thrust results were found to be satisfactory. This report is being submitted in accordance with 10 CFR 50.73(a)(2)(v)(B) and 10 CFR 50.73(a)(2)(v)(D) for an event or condition that could have prevented the fulfillment of a safety function needed to (B) remove residual heat and (D) mitigate the consequences of an accident. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 72517th Street NW, Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of infonmation unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Quad Cities Nuclear Power Station Unit 1 05000- 254 YEAR NUMBER NO. 2022 - 002 00 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Low Pressure Coolant Injection Manually Isolated Due To Valve Test Equipment Issue CONDITION PRIOR TO EVENT Unit: 1 Event Date: May 10, 2022 Event Time: 17 46 CST Reactor Mode: 1 Mode Name: Run Power Level: 100% No structures, systems or components were inoperable at the start of this event that contributed to the event. A. DESCRIPTION OF EVENT On May 10, 2022, Unit 1 was operating at 100% power. Motor Operated Valve (MOV) [VJ diagnostic testing was being performed on Residual Heat Removal (RHR) Low Pressure Coolant Injection (LPCI) [BO] valve 1-1001-288, 1B LPCI Loop Upstream Stop Valve, when a low thrust was measured at 1359 hours causing the valve to be declared inoperable. Inadequate grease volume was also identified in one chamber of the MOV actuator, which was considered an initial contributor to the insufficient thrust measurement. The grease was later eliminated as a cause or a contributor to this event. This valve is also a Primary Containment Isolation (PCIV) [BD] valve for containment penetration X-0138, resulting in TS 3.6.1.3 Condition A to be entered for a penetration flow path with one PCIV inoperable. TS 3.6.1.3 Condition A requires that the affected flow path be isolated within 4 hours by use of one closed and de-activated valve. Engineering review of thrust data and grease quantities did not reach a conclusion during the 4 hour window to provide confidence in valve performance. Operations de-activated the affected penetration at 1746 hours by closing the 1-1001-298, 18 LPCI Loop Downstream Stop Valve, and electrically isolating it by opening breaker [BKR] MCC 18/19-5 Cubicle F1. LPCI Loop Select Logic will determine if LPCI flow is injected into the A or B loop of the Reactor Recirculation (RR) [AD] System depending upon the appropriate accident's line break location. The isolated penetration is part of the injection flow path into the B loop of the RR system with either the A or B loop of LPCI providing injection. Because the LPCI injection path cannot be predicted ahead of an event, this penetration isolation renders both the A and B LPCI loops inoperable, causing entry into TS 3.5.1 Condition E for two LPCI subsystems inoperable. | ML22189A029
Monticello Nuclear Generating Plant | Unknown Unit | Loss of Control Room Envelope Operability | 07-07-2022 | On May 13, 2022, the Monticello Nuclear Generating Plant was operating in Mode 1 at 100% power. Following an inspection in the Steam Jet Air Ejector room, it was identified that the steam leakage from two valves exceeded the assumptions in the Alternate Source Term dose analysis calculation. As a result, the Control Room Envelope (CRE) was declared inoperable and LCO 3.7.4, "Control Room Emergency Filtration (CREF) System," Condition B was entered. The leaks were mitigated such that the CRE was declared operable on May 20, 2022. This report is being submitted as an "event or condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety" per 10 CFR 50.73(a)(2)(ii)(B); as an "event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident" per 10 CFR 50.73(a)(2)(v)(D); and as "any event where a single cause or condition caused at least one independent train or channel to become inoperable in multiple systems or two independent trains or channels to become inoperable in a single system designed to mitigate the consequences of an accident" per 10 CFR 50.73(a)(2)(vii). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 3. LER NUMBER 1.FACILITY NAME 2.DOCKET NUMBER YEAR SEQUENTIAL REV 05000- NUMBER NO. Monticello Nuclear Generating Plant -263 2022 - 001 - 00 | EVENT DESCRIPTION On May 13, 2022, the Monticello Nuclear Generating Plant was operating in Mode 1 at 100% power. Following an inspection in the Steam Jet Air Ejector (SJAE) room, it was identified that the steam leakage from two valves exceeded the assumptions in the Alternate Source Term (AST) dose analysis calculation. As a result, the Control Room Envelope (CRE) was declared inoperable and LCO 3.7.4, "Control Room Emergency Filtration (CREF) System," Condition B was entered. The leaks were mitigated such that the CRE was declared operable on May 20, 2022. EVENT ANALYSIS Steam leakage from the 12 SJAE Pressure Control outlet valve [PCV], MS-23-2, was originally identified on May 5, 2022. As part of an investigation into the leakage, Operators opened the 12 SJAE Pressure Control bypass valve [PCV], MS-24-2, to allow maintenance to remove insulation from MS-23-2. Upon entry into the SJAE room to remove the insulation from MS-23-2 it was discovered that the valve packing from MS-24-2 had failed and was also leaking steam. After removal of the insulation from MS-23-2, it was determined that the leakage from MS-23-2 and MS-24-2 both exceeded the leakage rate assumptions of the AST dose analysis calculation and evaluation. As a result, the Control Room CRE was declared inoperable. The CRE was inoperable from May 5, 2022 until May 20, 2022 when the leakage sources were mitigated. This condition was determined to be reportable in accordance with 10 CFR 50.73(a)(2)(ii)(B) as an "event or condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety,” 10 CFR 50.73(a)(2)(v)(D), as an "event or condition that could have prevented fulfillment of a safety function to mitigate the consequences of an accident," and 10 CFR 50.73(a)(2)(vii) as "any event where a single cause or condition caused at least one independent train or channel to become inoperable in multiple systems or two independent trains or channels to become inoperable in a single system designed to mitigate the consequences of an accident." This event will be reported as a Safety System Functional Failure in accordance with Nuclear Energy Institute 99-02, "Regulatory Assessment Performance Indicator Guideline". SAFETY SIGNIFICANCE There was no actual safety consequence from this condition. During the time the CRE was inoperable radiation levels in the Turbine Building and on the Wide Range Gas Monitors remained stable. Compensatory measures were put in place, including assigning a dedicated operator to promptly isolate the portion of the SJAE system that was leaking in the event of a design basis event. In addition, the control room operators were directed to don a self-contained breathing apparatus (SCBA) on breathing air if a design basis event were to occur. An engineering analysis determined that donning SCBAs would ensure control room operator doses remained below 5 Rem Total Effective Dose Equivalent (TEDE). Prior to the implementation of the compensatory measures described above on May 13, 2022, it is estimated the post-accident dose limit for the control room operators could have been exceeded. During the time the steam leakage in the SJAE Room exceeded the assumptions of the AST analysis both CREF subsystems were otherwise available. | ML22189A111
Browns Ferry Nuclear Plant | Unit 3 | Main Steam Relief Valves Lift Settings Outside of Technical Specifications Required Setpoints | 07-11-2022 | On May 10, 2022, the Tennessee Valley Authority was notified of As-Found testing results that four Main Steam Relief Valves (MSRVs) from Browns Ferry Nuclear Pant (BFN), Unit 3 were outside the +/- 3 percent set-point band required for operability. More than the one allowed MSRV was considered to be inoperable during the entire operating cycle and longer than permitted by Technical Specifications. During this time, BFN Unit 3 made entries into Modes of Operation that were not allowed under this condition. The affected valves remained capable of maintaining reactor pressure within the American Society of Mechanical Engineers code limits. It was determined that the MSRVs failed due to corrosion bonding to the valve seats and non-quantifiable leakage known as simmering. All thirteen of the MSRV pilot valves were replaced during the Unit 3 spring 2022 refueling outage. The Boiling Water Reactor Owners' Group is continuing to work toward a solution to improve the quality and adhesion of the platinum coating on the discs. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 3 05000-296 NUMBER NO. 2022 - 001 - 00 | I. Plant Operating Conditions before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN) Unit 3 was in Mode 1 at approximately 100 percent power. II. Description of Event A. Event Summary On May 10, 2022, NWS Technologies notified the Tennessee Valley Authority (TVA) with the as found testing results of the thirteen Main Steam Relief Valves (MSRVs) [RV], which were removed during the spring 2022 Unit 3 Refueling Outage 20 (U3R20). Four MSRVs (BFN-3-PCV-001-0004, BFN-3-PCV-001-0022, BFN-3-PCV-001-0034, and BFN-3-PCV-001-0041) had as found lift settings which were outside of the +/- 3 percent band of their setpoints required for operability. Technical Specification (TS) 3.4.3, Safety/Relief Valves (S/RVs), requires twelve of the thirteen S/RVs to be operable for S/RV system [SB] operability. The four MSRVs were found to have been inoperable for an indeterminate period of time during the entire operating cycle between March 25, 2020, and February 26, 2022, and longer than permitted by TS 3.4.3. Throughout this event, the two stage MSRV pilot valves remained capable of maintaining the reactor pressure below 1375 pounds per square inch gauge (psig), which is the American Society of Mechanical Engineers (ASME) code limit of 110 percent of the vessel design pressure. The valves remained capable of performing their required safety function. The TVA is submitting this report in accordance with Title 10 of the Code of Federal Regulations 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant’s TS. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML22192A036
Peach Bottom Atomic Power Station | Unit 2 | Automatic Reactor Scram due to Loss of Power to Both RPS Buses | 07-15-2022 | On 5/16/22 at 1537 hours, the Unit 2A reactor protection system motor generator set (RPS MG set) tripped in response to grid perturbations, causing a half scram condition as expected. At 1552 hours, Unit 2 experienced an automatic scram and Group 1 isolation. The scram was the result of a self-revealing technical human performance event during the execution of a procedure to return 2A RPS to service. The loss of both RPS buses resulted in a reactor scram, Primary Containment Isolation System Group 1 Isolation (main steam isolation valve closure), safety relief valve actuation, and loss of the normal heat sink. Emergency Core Cooling Systems were utilized to maintain reactor pressure vessel level and pressure. At no time was there a public safety risk and there were no safety consequences as a result of the event. All control rods inserted, and all safety systems performed as expected. Operations safely stabilized Unit 2 and brought it to a cold shutdown condition. The root cause of this event was a breakdown in technical human performance, which led to directing the wrong procedure steps and resulted in a reactor scram. Immediate corrective actions included increased oversight and reinforced stop work criteria. Longer term corrective actions include procedure and training enhancements. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Peach Bottom Atomic Power Station, YEAR NUMBER NO. 05000- 277 Unit 2 2022 - 001 - 00 | Plant Operating Conditions Before the Event Prior to the event Peach Bottom Atomic Power Station Unit 2 was operating at approximately 100% power in MODE 1. All 4kV (EIIS: EB) buses were aligned to one source due to a planned offsite source outage window. Because of this alignment, the Unit 2 B bus of the Reactor Protection System (RPS)(EIIS: JC) was being powered by an alternate feed. The 4kV and RPS power supply alignment had been in this configuration for four weeks prior to the event. There were no other structures, systems or components (SSC) that were inoperable at the start of the event that contributed to the event. Event Description At 1532 hours on 5/16/22, an offsite electrical transient(s) occurred which caused a main generator perturbation and multiple control room alarms for both units. The 2A Recirculation (EIIS: AD) pump speed lowered slightly (10 RPM). The operations crew entered the procedure for unexpected change in core flow. The Unit 2 Reactor Water Cleanup (EIIS: CE) system also tripped as a result of the event. At 1537 hours on 5/16/22, another offsite electrical transient occurred with a large main generator perturbation, and the 2A RPS motor generator set output breaker tripped which caused a loss of power to the 2A RPS bus, a half scram, and Unit 2 Primary Containment Isolation System Group II/III inboard isolations (EIIS: JM). Loss of RPS power also caused a trip of Unit 2 Reactor Building Ventilation (EIIS: VA). One of two main generator output breaker (EIIS: EL) for each unit opened and there was a <1K Ohm ground indicated on the 2A/C and 2B/D batteries (EIIS: EJ). In response to the 2A RPS trip, operations supervision directed performance of procedures to restore the tripped 2A RPS motor generator set to service. During this evolution, a self-revealing technical human performance event occurred when an operator was directed by shift management to utilize a version of the procedure that was not annotated to account for the abnormal electrical alignment. The operator opened the breakers from the alternate electrical feed to the 2B RPS bus which was powering the B RPS at the time. At 1552 hours on 5/16/22, the loss of power to the second RPS bus resulted in a Reactor scram and Primary Containment Isolation System (EIIS:JM) Group I isolation which closed all main steam isolation valves (MSIVs). All safety systems performed as expected in response to the scram. Reactor pressure increased as a result of MSIV closure. Safety relief valves (EIIS: SB) initially lifted within their setpoints to control pressure, then the valves were utilized manually for pressure control. Closure of the MSIVs isolated the normal heat sink (condenser, EIIS: SG) and the steam supply to the feedwater (EIIS: SJ) pumps, so emergency systems were utilized for injection. High Pressure Coolant Injection (EIIS: BJ) was manually used for injection into the reactor pressure vessel and was used for pressure control. Reactor Core Isolation Cooling (RCIC)(EIIS:BN) was manually utilized for reactor pressure vessel level control. Operations safely stabilized Unit 2 and brought it to a cold shutdown condition. Unit 3 was affected by the grid transient, with both Unit 3 Recirculation pump speeds lowering and entering speed hold, but was unaffected by the Unit 2 scram. This event is reportable under 10CFR50.73(a)(2)(iv)(A) due to manual or automatic actuation of systems listed in 10CFR50.73(a)(2)(iv)(B) including RPS, containment isolation signals, actuation of an emergency core cooling system and RCIC. An ENS notification was made within 4 hours of the event, reference ENS 55899. | ML22196A020
McGuire Nuclear Station | Unit 1 | Both Control Room Area Chilled Water System Trains Inoperable Due to Human Error | 08-18-2022 | At 2240 [EST] on June 21, 2022, with Unit 1 and Unit 2 operating at approximately 100 percent power and the A train of the Control Room Area Chilled Water System (CRACWS) inoperable for planned maintenance, a loss of safety function occurred when the B train CRACWS chiller tripped. A clearance required for maintenance on the A train was being performed when a non-licensed auxiliary operator (AO) opened the breaker feeding the oil pump associated with the running and operable B train. This resulted in an inadvertent trip of the B Chiller. With both CRACWS trains inoperable, Operations entered Abnormal Procedure AP-39 (Control Room High Temperature) and restored the B train within thirty-five minutes. The cause of this event is attributed to a human performance error in which the AO did not effectively use human performance tools to ensure the correct component was identified prior to operation. In addition to prompt restoration of the B Train of CRACWS and the system's safety function, corrective actions were initiated to improve accountability of the operator associated with this event, and implementation of additional layers of defense when placing clearances. This event had no impact on the health and safety of the public. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Repcrted lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICE NS EE EVE NT REPORT ( LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira submission@omb.eop.gov. The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form spcnsor, and a person is not required to respond to, a collection of information unless the document https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LERNUMBER YEAR SEQUENTIAL REV McGuire Nuclear Station, Unit 1 05000-369 NUMBER NO. 2022 - 001 - 00 | BACKGROUND The following information is provided to assist readers in understanding the event described in this LER. Applicable Energy Industry Identification [EIIS] system and component codes are enclosed within brackets. Control Room Area Chilled Water System [KM] The purpose of the Control Room Area Chilled Water System (CRACWS) [KM] is to provide chilled water to the Control Room and Control Room Area Ventilation (CRAV S) [VI] equipment to maintain temperature within Technical Specification limits. The CRACWS system has two redundant trains (A and B) serving the CRAV S air handling units providing cooling of recirculated control room air. The CRACWS operates in conjunction with the CRAV S and are shared between both McGuire units. These trains are normally not cross-connected. Each CRACWS train consists of a compression tank to provide water surge protection, a chilled water pump and a control area chiller. Chilled water circulates in a closed loop. Each chiller has its own separate refrigeration system. The CRACWS water exchanges heat with the refrigerant in the evaporator to be chilled to a desired temperature. The CRACWS is an emergency system which also operates during normal unit operations. A single train will provide the required temperature control to maintain the control room at approximately 75°F. The control room is shared between units. NRC FORM 3666 (08-2020) Page 2 of 5 | ML22230C557
Fermi 2 05000 341 1 OF 4 | Unknown Unit | Turbine trip and subsequent reactor trip due to Mayflies | 08-23-2022 | At 2338 EDT on June 24, 2022, while in Mode 1, 100 percent power, Fermi 2 experienced a turbine trip followed by a reactor SCRAM, due to differential relaying sensing a generator output fault. The generator output fault occurred when a swarm of mayflies caused an arc from a 345 kV bus bar to the bottom of the insulator during a hatch. The National Weather Service data indicated the Mayfly hatch that occurred near Fermi 2 site on June 24, 2022 was significant, and compensatory actions were taken, however, additional subsequent actions were taken to minimize the potential for future switchyard operations being impacted from mayflies. Area and building lighting has been reduced further to limit attracting mayflies to sensitive plant equipment and the mayfly infestation buildup and forecast will be closely monitored as part of the mayfly mitigation plan. The seasonal mayfly control procedure has been updated to reflect these changes. A 4-hour event notification (EN 55964) was made to the NRC pursuant to Title 10 Code of Federal Regulations (10 CFR) 50.72(b)(2)(iv)(B) for RPS Actuation (Reactor Scram) and 10 CFR 50.72(b)(3)(iv)(A) as an event or condition that resulted in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Fermi 2 341 YEAR SEQUENTIAL REV 05000- NUMBER NO. 2022 - 003 - 00 | INITIAL PLANT CONDITIONS Mode – 1 Reactor Power – 100 Percent There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT At 2338, on June 24th, 2022 with the unit in Mode 1 at 100 percent power, the reactor automatically scrammed due to a Reactor Protection System (RPS) actuation on a Main Turbine Trip. Concurrent with the Turbine Trip and Reactor Scram, Security reported a flash from an intermediate switchyard between the generator output transformers and the 345kV switchyard. Additionally, operators noted the main control room lights dimmed; and field operators reported a large sound in the vicinity of the 345 kV switchyard. A large mayfly hatch was in progress at the time of the scram. During the investigation, it was identified that the reported flash from the switchyard was due to arcing from a conductor (bus bar) to ground. This arc damaged the base of the insulator and the bus bar. The scram occurred with no surveillances or activities in progress. As a result of the scram, an expected low reactor water level (Level 3) occurred resulting in isolation of Primary Containment Groups 4, 13, and 15, as expected. Group 4, RHR Shutdown Cooling and Head Spray, was already isolated, Group 13, Drywell Sumps, isolated and Group 15, Traversing In-Core Probe System was already isolated. A 4-hour event notification (EN 55964) was made to the NRC pursuant to Title 10 Code of Federal Regulations (10 CFR) 50.72(b)(2)(iv)(B) for RPS Actuation (Reactor Scram) and 10 CFR 50.72(b)(3)(iv) (A)as an event or condition that resulted in valid actuation of any of the systems listed in paragraph (b)(3)(iv)(B). Additionally, Div. 2 CCHVAC (Control Center [Main Control Room] Heating Ventilation and Air Conditioning) shifted to recirculation mode at the time of the scram, when the trouble annunciators associated with CCHVAC Radiation Monitors (3D39/3D38) were received. This was determined to be from the voltage transient from the generator fault. Following verification of proper recirculation mode lineup, Div. 2 CCHVAC was returned to normal mode. Offsite power supplied to the plant was not affected by the scram, thus all ECCS equipment remained operable and available. The cause is a large hatch of mayflies flew or landed in close proximity to the equipment, creating a conductive path from the bus (conductor) to ground at the bottom of the insulator. The mayfly infestation was substantial enough to create an arc across the insulator, damaging the insulator and bus bar. Indications were identified on the insulator consistent with a tracking arc strike through the conducting material (Mayflies) and not indicative of an insulator failure. Mayfly infestation is a natural phenomenon in the Great Lakes occurring during late spring and early summer months. Fermi 2 has seasonal procedural measures to reduce the potential impact on the plant and switchyard operations from mayfly accumulation. These measures were confirmed to be in place at the time of the event. A review of the National Weather Service data indicated a significant hatch of mayflies occurred near Fermi 2 site at the time of the event. | ML22235A106
River Bend Station | Unit 1 | Division 1 Standby Diesel Generator Speed Sensor Power Supply Failure | 09-01-2022 | On July 04, 2022, at 2115 Central Time, while River Bend Station, Unit 1 was operating in Mode 1 at 100 percent power, the Division 1 Standby Diesel Generator was declared Inoperable due to failure of redundant power supplies in the speed control circuitry. This was discovered during monthly surveillance testing. The failedpower supplies provide power to the exciter flash circuitry and ramp governor control. This condition would have prevented the Division 1 Standby Diesel Generator from providing power to Division 1 Emergency Loads. The issue was determined to be reportable in accordance with 10 CFR 50.73(a)(2)(v)(A), (B), (C), and (D) as any event or condition that could have prevented the fulfillment of the safety function of structures or systems. This event was not reportable in accordance with 10 CFR 50. 72 because the Division 2 Standby Diesel Generator was operable and available at the time of discovery. The condition was corrected by replacing the power supplies on July 07, 2022. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/l sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITYNAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV River Bend Station, Unit 1 05000-458 NUMBER NO. 2022 003 00 | EVENT DESCRIPTION On July 04, 2022, at 2115 Central Time, River Bend Station, Unit 1 (RBS) was operating in Mode 1 at 100 percent power. There were no other structures, systems, or components (SSCs) that were inoperable that contributed to this event. A failure was identified in the speed control circuitry of the Division 1 Standby Diesel Generator (EGS-EG1A) [EK] [DG] during monthly surveillance testing per STP-309-0201, Division I Diesel Generator Operability Test. EGS-EG1A was,declared inoperable due to the speed control circuitry failure and documented in the RBS Corrective Action Program in CR-RBS-2022-03801. EGS-EG1A speed control circuit contains redundant Dynalco SDC-2000, 125 VDC to 24 VDC power supply converters (EGS-E/EX43A and EGS-E/EY4 3A) [CNV]. These components supply power to individual speed switches and tachometers. EGS-E/EY43A also supplies power to Emergency Response Information System (ERIS) [ID] computer point (EGSEY009) [SI]. The speed control circuit is designed such that either one of the power supplies is sufficient to allow field flash and loading of the diesel genetator. These power supplies were refurbished by Paragon and installed in December 2020. The failures occurred after approximately 1.5 years with an expected replacement frequency of 8 years. Timeline of events: 06/01/22 - STP-309-0201, Division 1 Diesel Generator Operability Test completed. This was the last known successful operability run for EGS-EG1A. This verified that both EGS-E/EX43A and EGS-E/EY4 3A were functioning properly on 06/01/22 because the local tachometers and EGSEY009 provided proper indication. 06/08/22 - ERIS computer point, EGSEY009 "flatlined" starting on 06/08/22, which is most likely when EGS-E/EY43A lost power. This was not a normally monitored component and went undetected until troubleshooting identified the condition on 07/05/22. 06/12-13/22-Performed STP-309-0202, Division 2 Diesel Generator Operability Test.The normal requirements of this test resulted in 0.63 hours of Unavailability for the Division 2 Standby Diesel Generator (EGS-EG 1B ) [EK] [DG]. 07/04/22-EGS-EG1A, Division 1 Emergency Diesel Generator was declared inoperable. 07/05/22 - Trouble shooting determined the failure of both power supplies EGS-E/EX43A and EGSE/EY43A. 07 /05/22 - Trouble shooting determined that both power supplies had blown fuses. 07 /05/22 - Common Mode Failure evaluation determined that EGS-EG 1B utilizes the same exact design and manufacturer for these components. However, voltage readings for EGS-E/EX43B and EGS-E/EY4 3B were satisfactory leading to the conclusion that the failure was not currently present in EGS-EG 1B . 07 /05/22 - Common Mode Failure evaluation excluded the Division 3 High Pressure Core Spray Diesel Generator due to differing designs. 07/06/22 - RBS function testing to determine the cause of the blown fuses was inconclusive. 07/07/22-Completed installation of EGS-E/EX43A and EGS-E/EY43A power supplies per Engineering Change (EC-87792). The new Phoenix power supplies are designed with external lights to provide positive indication of power status. 07/07/22 - Completed post maintenance testing and declared EGS-EG1A operable. 08/04/22 - The failed Dynalco SDC-2000 power supplies were shipped to an outside vendor, Engine Systems Inc., to perform a detailed failure analysis. Preliminary results are expected in September 2022. As stated in the timeline above, monthly surveillance testing rendered EGS-EG1 B unavailable for a total of 0.63 hours during June 12-13, 2022. The discovery of EGSEY009 "flatlined" starting on June 08, 2022, means that EGS-E/EY 43A most likely lost power at that time. Although either EGS-E/EY 43A or EGS-E/EX43A functioning properly would allow EGS-EG1A to load, the timing of EGS E/EX43A power loss is unknown. Therefore, this condition is being reported in accordance with 10 CFR 50.73(a)(2)(v) as "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: (A) Shut down the reactor and maintain it in a safe shutdown condition; (B) Remove residual heat; (C) Control the release of radioactive material; or (D) Mitigate the consequences of an accident." This event was not an ENS notification because EGS-EG1 B was operable and available at the time of discovery. | ML22244A098
LICENSEE EVENT REPORT (LER) | Unknown Unit | Estimated burden per response to comply with this mandatory conecoori request 80 hours. Repor1e<f lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollec1s.Resource@nrc.gov, and 1he 0MB reviewer at 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currentiy valid 0MB control number. 2. Docket Number· 3. Page . 05000 - 254 1 OF 5 Both Trains of Standby Gas Treatment Inoperable Due to Blockage in the Common Discharge Line | 09-01-2022 | On 7/4/22 at 0104, Unit 2 experienced a reactor scram. As a result, the 1/2 B Standby Gas Treatment (SGT) train.auto started and was found to have lower than Technical Specification (TS) required flow. The 1/2 B SGT train was secured and the 1/2 A SGT train was manually started and found to have the same low flow condition. On 7/4/22 at 0130, both units entered TS 3.6.4.3 Condition D for having both SGT trains inoperable. On 7/4/22 at 0230 TS 3.6.4.3 Condition E was entered. SGT flow slowly increased with the running of the train and on 7/4/22 at 1122 the 1/2 B SGT train was declared operable, and TS 3.6.4.3 Condition E was exited. The cause of the SGT low flow condition was water in the common SGT discharge line. This event is being reported under 10 CFR 50.73(a)(2)(v)(C) and (D) - "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are n_eeded to: (C) control the release of radioactive material, and (D) mitigate the consequences of an accident." This event is also reportable under 10 CFR 50.73(a)(2)(i)(B) - "Any operation or condition which was prohibited by the plant's Technical Specifications." NRC FORM 366A (08-2020) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (;-•'" """,,,o\ 'l, .,,'41 *"'*•"" .,.o' LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www. nrc. g ov/readi ng-rm/d oc-col lections/nu reqs/staff/sr1 022/r3/) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A 10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 72517th Street NW, Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER· Quad Cities Nuclear Power Station Unit 1 05000- 254 YEAR SEQUENTIAL NUMBER REV NO. 2022 - | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. EVENT IDENTIFICATION 003 Both Trains of Standby Gas Treatment Inoperable Due to Blockage in the Common Discharge line CONDITION PRIOR TO EVENT Unit: 1 Event Date: July 4, 2022 Reactor Mode: 1 Mode Name: Power Operation Event Time: 0130 CST Power Level: 100% No structures, systems or components were inoperable at the start of this event that contributed to the event. A. DESCRIPTION OF EVENT 00 On July 4, 2022, at 0104, Unit 2 experienced a manual scram. As a result of the reactor scram, the 1/2 B train of Standby Gas Treatment (SGT)[BH] auto started; however, the train was running with degraded and oscillating flow between 2400-2600 scfm. Technical Specification 5.5.7 requires a SGT flow of 4000 cfm +/- 10%. TS 3.6.4.3 Condition A was entered on July 4, 2022, at 0127 for one SGT subsystem being inoperable. TS 3.6.4.1 Condition A was also entered for inoperable Secondary Containment because Secondary Containment vacuum was found to be less than 0.25 inches water gauge vacuum required by TS surveillance requirement (SR) 3.6.4.1.3. On July 4, 2022, at 0130, Operations manually secured the 1/2 B SGT train and started the 1/2 A SGT train and it also indicated degraded and oscillating flow of a similar flowrate and signature to the 1/2 B SGT train. TS 3.6.4.3 Condition D was entered on July 4, 2022, at 0130 for two SGT subsystems being inoperable. Operations initiated troubleshooting efforts that identified a partial blockage in the 24 inch common discharge line [PSX] from both trains of SGT to the main chimney. The SGT flow control valves (FCV)[FCV] were also observed as being fully open, when during normal operation the FCV is partially open and controlling the flow through the train. As the SGT system continued to operate, the flowrate through the train slowly increased. On July 4, 2022, at 0230, TS 3.6.4.3 Condition E was entered for not having restored one SGT subsystem within 1 hour. · Condition E requires both Unit 1 and Unit 2 to be in Mode 3 within 12 hours. Unit 2 was already in Mode 3 due to the earlier manual scram. On July 4, 2022, at 0853 (CT), Event Notification System (ENS) notification #55976 was completed for the immediate reportability required under 10 CFR 50.72(b)(3)(v)(C) and (D) - "Any event or condition | ML22244A134
LICENSEE EVENT REPORT (LER) | Unknown Unit | Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of lnfonmation and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira submission@omb.eop.gov. The NRG may not conductor sponsor, and a person is not required to respond to, a collection of infonmation unless the document requesting or requiring the collection displays a currently valid 0MB control number. 2. Docket Number 3.Page 05000 - 265 1 OF 4 Manual Scram Due To Feedwater Regulator Valve Failure Decreasing Reactor Water Level | 09-01-2022 | On July 4, 2022, Unit 2 was at 100% power with no surveillance activities in progress that contributed to the event. At 0103 hours the 2A Feedwater Regulating Valve (FRV) failed in the closed position and locked up, causing a decrease in reactor vessel water level. Attempts at manual control of the feedwater system to increase level were not successful. At 0104, a manual scram was inserted in accordance with operating procedures. All control rods inserted, and the scram was uncomplicated. The cause of this event is foreign material partially or completely blocking hydraulic oil flow internal to a servo valve in the 2A FRV that caused it to move rapidly from the half open position to the full closed position. This caused Unit 2 reactor vessel water level to rapidly lower until it reached the established scram criteria of +11 inches, at which time a manual scram was inserted. This report is being submitted in accordance with 10 CFR 50.73(a)(2)(iv)(A) for an event or condition that resulted in manual or automatic actuation of the reactor protection system including a reactor scram. NRC FORM 366A (08-2020) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 0!!/31/2023 LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.govlreading-rmldoc-collectionslnuregslstafflsr1022/r31) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Quad Cities Nuclear Power Station Unit 2 05000- 265 YEAR SEQUENTIAL NUMBER REV NO. 2022 - | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. EVENT IDENTIFICATION 002 Manual Scram Due To Feedwater Regulator Valve Failure Decreasing Reactor Water Level CONDITION PRIOR TO EVENT Unit: 2 Event Date: July 4, 2022 Reactor Mode: 1 Mode Name: Power Operation Event Time: 0104 CDT Power Level: 100% No structures, systems or components were inoperable at the start of this event that contributed to the event. A. DESCRIPTION OF EVENT On July 4, 2022, Unit 2 was operating at 100% power. There were no surveillances in progress that contributed to the event. At 0103 hours, main control room (MCR) alarms indicated the 2A Feedwater (FW) [JB] Regulating Valve (FRV) [FCV] failed in a manner that drove it to a closed position and caused the valve to lock up. As a result, reactor vessel water level began to decrease. MCR Operators took manual control of the FW system in an effort to increase water level prior to reaching the scram threshold. The 2A FRV was locked up in the closed position. The 2B FRV rapidly opened to maintain level, but the single FRV was incapable of passing sufficient flow to maintain vessel level at full reactor power. Manual control of the FRVwas not successful at maintaining level. It is noted that there was a potential missed opportunity to perform an emergency power reduction which could have reduced reactor power, allowing the single FRV to maintain sufficient vessel level. At 0104 hours, the decreasing water level reached the +11 inches threshold at which a manual scram was ordered. All control rods inserted, and the scram was not complicated. The NRC was notified via ENS Report 55975 at 0557 EDT. Following replacement of the 2A FRV, Unit 2 returned to power operations on July 6, 2022. 00 NRG FORM 366A (08-2020) Page_2_. of _4_ | ML22244A135
byron station | Unknown Unit | OB Control Room Ventilation Supply Fan Failed to Start due to Erroneous Position Indication from the Closed Limit Switch for Charcoal Deluge Valve Interlock | 09-09-2022 | 12. Licensee Contact for this LER Licensee Contact Phone Number (Include area code) Zoe Cox, Regulatory Assurance Manager (815) 406-2800 13. Complete One Line for each Component Failure Described in this Report Cause System Component Manufacturer Reportable to IRIS Cause System Component Manufacturer Reportable to IRIS B VI ZIS N007 y NIA NIA NIA NIA NIA 14. Supplemental Report Expected Month Day Year I 15, Expected Submission Date D ~ No Yes (If yes, complete 15. Expected Submission Date) NA NA NA 16, Abstract (Limit to 1560 spaces, ie., approximately 15 single-spaced typewritten lines) On July 12, 2022, the OB Control Room Ventilation (VC)[VI] supply fan (0VC01 CB) failed to start when commanded due to an erroneous position indication from the closed limit switch (0ZS-FP432B-A) for the OB VC recirculation charcoal deluge valve (0FP432B). The deluge valve was closed but the limit switch operating lever had rolled under the limit switch finger, causing the operating lever to be in the same position as if the deluge valve were in the "intermediate" or "open" position. This resulted in the OB train of VC not being operable for 48 days. Once identified, the actuator arm and limit switch were adjusted to properly make up the closed limit and the fan was started, restoring the OB train of VC to operable. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) for any operation or condition which was prohibited by the plant's Technical Specifications. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 72517th Street NW, Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www. nrc. gov/ read i nq-rm/d oc-collection sin u reg s/staff/sr1 0 2 2/ r3/) requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Byron Station, Unit 1 05000454 NUMBER NO. 2022 - 001 00 | A. Plant Operating Conditions Before the Event: Event Date: July 12, 2022 Unit 1 - Mode 1 - Power Operations, Reactor Power 100 percent Unit 2 - Mode 1 - Power Operations, Reactor Power 100 percent Reactor Coolant System (RCS) [AB): Normal Operating Temperature and Pressure No structures, systems or components were inoperable at the start of this event that contributed to the event B. Description of Event: On July 12, 2022, at 03:24 CDT, the OB Control Room (VC)[VI) supply fan (0VC01 CB) failed to start when commanded due to an erroneous position indication from the closed limit switch (0ZS-FP432B-A) for the OB VC recirculation charcoal deluge valve (0FP432B). The deluge valve was in the closed position; however, the limit switch operating lever had rolled under the limit switch finger, resulting in the operating lever being in the same position as if the deluge valve was in the intermediate or open position. In accordance with the OB VC Supply Fan control logic drawing (6E-0-4030VC02), if the 0FP432B valve limit switch is in the intermediate or open position (i.e., not closed), the supply fan shunt trip coil is energized, preventing the supply fan breaker from remaining closed after a start command, causing the fan to trip immediately. A review was completed to determine the last time the 0FP432B valve was manipulated. On May 23, 2022, the OB VC System makeup filter and recirculation charcoal adsorber were placed in service for OB VC chiller performance verification testing. This was the last documented run of 0VC01 CB supply fan prior to July 12, 2022. On May 25, 2022, 0FP432B, recirculation charcoal deluge valve was manually cycled to support performance of a Fire Protection (FP) surveillance. On July 12, 2022, at 03:24 CDT, the attempted start of the 0VC01 CB supply fan resulted in it immediately tripping. The 0A VC train was restarted 1 hour and 13 minutes later in accordance with procedural guidance. On July 12, 2022, at 14:05 CDT, the OB VC train was started after the actuator arm and limit switch were adjusted to properly make up the closed limit interlock. On July 12, 2022, at 19:48, after completion of post-maintenance testing, Limiting Condition for Operation (LCO) Condition A for Technical Specifications 3. 7.10, "Control Room Ventilation (VC) Filtration System" and LCO Condition A for TS 3.7.11, "Control Room Ventilation (VC) Temperature Control System" were exited, and operability of the OB train of VC was restored. C. Cause of Event The cause of the OB VC supply fan to not start was the limit switch operating lever had rolled under the limit switch finger which made the 0FP432B valve appear to be in the intermediate or open position causing the supply fan shunt trip coil to remain energized, thereby preventing the fan breaker from remaining closed after the start command. There were inadequate margins in the length of the limit switch operating levers to be made up with the limit switch finger. D. Safety Consequences: This condition had no actual safety consequences impacting plant or public safety. This event is not considered an event or condition that could have prevented fulfillment of a safety function. The VC system has two full capacity, redundant equipment trains that perform the same function. The VC HVAC system is designed to ensure control of environmental conditions within specified maximum and minimum | ML22252A138
Brunswick Steam Electric Plant (BSEP) | Unit 1 | High Pressure Coolant Injection (HPCI) Inoperable | 09-12-2022 | At 20:20 Eastern Daylight Time (EDT) on July 15, 2022, with Unit 1 in Mode 1 at approximately 96% power for planned maintenance on the ‘1A’ Condensate Deep-bed Demineralizer (unrelated to this event), the High Pressure Coolant Injection (HPCI) system was declared inoperable upon discovering the HPCI flow controller without power. The HPCI flow controller lost power as a result of an intermittent connection in the flow controller fuse holder. The fuse was secured in the fuse holder and HPCI was declared operable on July 16, 2022, at 12:10 EDT following associated post maintenance testing. The Reactor Core Isolation Cooling (RCIC) System and Automatic Depressurization System (ADS) remained operable during this event. There was no impact on the health and safety of the public or plant personnel. The safety significance of this event is minimal. This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Brunswick Steam Electric Plant (BSEP), 05000- 325 YEAR NUMBER NO. Unit 1 2022 - 001 - 00 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. Background Initial Conditions At the time of the event, Unit 1 was in Mode 1 (i.e., Power Operation), at approximately 96 percent rated thermal power for planned maintenance on the ‘1A’ Condensate Deep-bed Demineralizer (unrelated to this event). There was no inoperable equipment that contributed to the event. Reportability Criteria The High Pressure Coolant Injection (HPCI) [BJ] inoperability is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented fulfillment of the safety function needed to mitigate the consequences of an accident. The NRC was notified of this event per 10 CFR 50.72(b)(3)(v)(D) via Event Notification 55997 at 23:41 Eastern Daylight Time (EDT) on July 15, 2022. Event Description At 20:20 EDT on July 15, 2022, with Unit 1 in Mode 1 at approximately 96% power for planned maintenance on the ‘1A’ Condensate Deep-bed Demineralizer (unrelated to this event), the HPCI system was declared inoperable upon discovering the HPCI flow controller without power during Reactor Operator control board walkdowns. Event Cause Upon initial investigation into the issue, a loose lead to the HPCI flow controller was discovered. Upon tightening the loose lead power returned to the HPCI flow controller, and availability of the HPCI system was restored at 20:23 EDT on July 15, 2022. However, the HPCI system remained inoperable at this time while additional troubleshooting and testing were performed. Additional troubleshooting determined that the identified loose lead could not have caused loss of power to the device and some other intermittent connection was present. While performing a calibration check on the device, a loose fuse holder connection was identified on the backside of the flow controller. The fuse was secured in the fuse holder and HPCI was declared operable on July 16, 2022, at 12:10 EDT following associated post maintenance testing. The HPCI flow controllers are refurbished and replaced on a 10-year frequency. This flow controller had been replaced in the May 2022 timeframe. However, fuse replacement is not part of the refurbishment instructions, and checking fuse holder tightness is not included in the installation instructions. This allowed the fuse holder to work its way loose over time due to normal handling/inspection/maintenance. Therefore, the cause of this event was determined to be inadequate procedural guidance associated with ensuring tightness of the fuse holder. Safety Assessment There was no impact on the health and safety of the public or plant personnel as a result of this event. HPCI system availability was restored at 20:23 EDT on July 15, 2022, following power restoration to the HPCI flow controller. Therefore, the system was available to perform its safety function of injecting the required flow rate into the Reactor Pressure Vessel at this time. In addition, the Reactor Core Isolation Cooling (RCIC) [BN] System and Automatic Depressurization System (ADS) remained operable during this event. | ML22255A164
Surry Power Station | Unit 1 | Failure of Unit 1 Emergency Diesel Generator Results in an Operation or Condition Prohibited by Technical Specifications | 09-19-2022 | On July 25, 2022, with both Surry Power Station Units 1 and 2 at 100% power, the 7-day Technical Specification (TS) Allowed Outage Time (AOT) for an emergency diesel generator (EDG) was exceeded due to a partial loss of load during monthly surveillance testing for the Unit 1 emergency diesel generator (EDG-1 ), requiring repair and restoration. To complete the EDG-1 repair, balancing, testing, and return to service, a request for enforcement discretion was submitted and approved that extended the TS AOT by two days (for a total of nine days). During event troubleshooting, it was revealed that the cause was corrosion between the lugs of the field lead causing a hard ground on one pole of the generator rotor. The risk analysis performed for this event concluded that the increase in core damage and large early release probability remained within the NRC Enforcement Manual, Appendix F limits. Completed corrective actions included the replacement of the EDG-1 generator and verification of operability of the EDG-2 and EDG-3. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document http://www.n rc.g ov /reading-rm/doc-co Il ections/n ur egs/staff/ sr 10 22/r3/} requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER DYEA R SEQUENTIAL REV Surry Power Station, Unit 1 05000- , 280 ~-I NUMBER 1-NGO. I 002 | PLANT OPERAT ING CONDITIONS BEFORE THE EVENT Surry Power Station (SPS) Unit 1 and Unit 2 were at 100% power. 1.0 DESCRIPTION OF THE EVENT The SPS emergency diesel generator (EDG) [EIIS: DG] for Unit 1 (EDG-1) and Unit 2 EOG (EDG-2) are dedicated to emergency buses 1H and 2H [EIIS: BU], respectively. A third diesel generator (EDG-3) is provided as a "swing diesel" and is shared by both units (the "J" bus). Each EDG has 100% capacity and is connected to an independent 4160 V emergency bus. EDG-1 provides emergency power to certain equipment and systems common to Units 1 and 2, including the Auxiliary Feedwater system (AFW) [EIIS: BA] cross-tie between Units 1 and 2, the Auxiliary building [EIIS: NF] filter exhaust fan [EIIS: FAN], Main Control Room (MCR) [EIIS: NA] chiller [EIIS: CHU], and MGR/Emergency Switchgear Room [EIIS: EK] filtered supply fans [EIIS: FAN]. At 0956 on July 18, 2022, the SPS EDG-1 for Unit 1 was removed from service to perform the monthly surveillance test. Approximately 20 minutes after reaching full load, EDG-1 experienced a partial loss of load. The MCR operators noted that the generator load had lowered and the generator output current indication was above the normal amps for fully loaded. Local field operators noted a change in engine sound normally associated with decreasing load; subsequently, EDG-1 was unloaded and ran unloaded for 30 minutes before being secured in accordance with the normal shutdown sequence. Following shutdown, EDG-1 was removed from service for investigation. Troubleshooting was performed, and it was discovered that a lead to the generator exciter [EIIS: EXC] was grounded. A physical inspection of this lead revealed a failure between the generator brush rigging and the panel wiring at the bolted connection point. A bridge and megger check on the generator stator was satisfactory. Further troubleshooting of the generator rotor indicated a hard ground on one out of eight (8) rotor poles. It was concluded that repairs to EDG-1 were necessary, including replacement of the generator. During the return-to service testing portion of the repair effort, activities required to complete the repair, perform post-maintenance testing, and return the SPS Unit 1 EDG-1 to service would not be accomplished within the 7-day Allowed Outage Time (AOT) (reference: TS 3.16.B.1.a.3 for an inoperable EOG), and as such, a request for enforcement discretion was requested and verbally approved on July 24, 2022, at 14:27. This enforcement discretion allowed a 2-day extension to the 7-day AOT to complete the EDG-1 return to service activities. TS 3.16.B.1.a.3 requires an inoperable EDG to be restored to service within seven (7) days or action be initiated to place the appropriate unit in a shutdown condition. In addition, TS 3.0.2 states that TS action statements associated with any individual systems, subsystems, trains, components, and devices that EDG-1 supports also would be governed by the 7- day EOG AOT. Since EDG-1 provides emergency power to certain equipment and systems common to Units 1 and 2, the shutdown of Unit 2 also would be required upon the expiration of the EDG-1, 7-day AOT. During final return-to-service testing, at 0956 on July 25, 2022, with both Surry Power Station (SPS) Unit 1 and Unit 2 at 100% power, the AOT for TS 3.16.B.1.a.3 was exceeded for Unit 1. Additionally, TS 3.0.2 for Unit 2 was not satisfied due to the inoperability of EDG-1 beyond that allowed by TS 3.16.B.1.a.3. Both units remained at 100% power throughout the restoration of EDG-1 that was declared operable at 1705 on July 26, 2022. | ML22263A429
Palo Verde Nuclear Generating Station (PVNGS) | Unit 1 | Units 1 and 3 Emergency Diesel Generator Actuation on Loss of Offsite Power to Class 4.16 kV Buses | 10-11-2022 | On August 14, 2022, at 1702 Mountain Standard Time, a valid actuation of the emergency diesel generators (EDGs) for Palo Verde Nuclear Generating Station (PVNGS) Unit 1 B-train and Unit 3 A-train occurred due to an undervoltage condition on their respective 4.16 kilovolt (kV) Class 1E buses. Both EDGs started and loaded as designed, including associated train essential spray pond pumps and the Unit 1 B-train auxiliary feedwater pump. The loss of power to the Unit 1 and Unit 3 Class 1E buses and resulting component actuations were the result of startup transformer NAN-X02 tripping offline. Unit 1 and Unit 3 both entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1, Condition A, for one required offsite circuit inoperable. In addition, both units also entered TS LCO 3.8.9, Condition A, for the loss of the Class 1E bus, which was exited when the EDGs started and restored power to their respective Class 1E buses. TS LCO 3.8.1, Condition A, was exited by both units on August 15, 2022. The direct cause of the undervoltage condition and the EDG and pump actuations was startup transformer NAN-X02 tripping offline due to the opening of the NAN-X02 startup transformer 525 kV breakers and 13.8 kV breakers due to protective relay actuation. The apparent cause of the event was attributed to water intrusion into the 2E-NAN-S05A cubicle as the result of a heavy rainstorm and high winds, in combination with degraded weatherstripping and conductor insulating boots that are not waterproof. No similar events have been reported by PVNGS in the last three years due to the same initial cause. NRC FORM 366A (08-2020) Page 2 of 5 NRC FORM 366A (08-2020) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Palo Verde Nuclear Generating Station 05000-528 YEAR SEQUENTIAL NUMBER REV NO. 2022 001 00 | All times are Mountain Standard Time and approximate unless otherwise indicated. 1. REPORTING REQUIREMENT(S): This Licensee Event Report (LER) is being submitted pursuant to 10 CFR 50.73 (a)(2)(iv)(A) to report a valid automatic actuation of the circuitry that starts the emergency diesel generator (EDG) (EIIS: EK) for Unit 1 and Unit 3 following an undervoltage condition on the affected Class 1E bus for each unit on August 14, 2022. The event included actuations of the associated essential spray pond (SP) pumps (EIIS: BS) and the Unit 1 B auxiliary feedwater (AF) pump (EIIS: BA). This event was reported to the NRC on August 14, 2022 via the event notification system (ENS 56044). 2. DESCRIPTION OF STRUCTURE(S), SYSTEM(S) AND COMPONENT(S): The safety related equipment for each Palo Verde Nuclear Generating Station (PVNGS) unit is powered by one of two load groups (A-train and B-train). Either of the associated trains can provide power for safe plant shutdown. Each alternating current (AC) train includes one Class 1E 4.16 kilovolt (kV) bus (EIIS: EB). The preferred and alternate power sources for each load group is offsite 525 kV AC power (EIIS: EK) and is supplied via the 13.8 kV secondary windings from two of the three startup transformers (EIIS: EA) to six 13.8 kV intermediate buses. Each unit receives 13.8 kV power from two of the intermediate buses. Class 1E 4.16 kV safety load group power is provided from the associated intermediate bus engineered safety feature (ESF) transformers. The standby power supply for each safety load group consists of one EDG (EIIS: EK), including its auxiliary and fuel systems. The standby power supply functions as a source of AC power for safe plant shutdown in the event of loss of preferred power and for post-accident operation of ESF loads. 3. INITIAL PLANT CONDITIONS: On August 14, 2022, PVNGS Units 1, 2 and 3 were in Mode 1 (Power Operation) at 100 percent power, normal operating temperature and normal operating pressure. There were no inoperable structures, systems or components at the time that contributed to this event. 4. EVENT DESCRIPTION: On August 14, 2022, at 1702, a valid loss of power (LOP) actuation occurred due to an undervoltage condition on the Unit 1 B-train and Unit 3 A-train Class 1E buses which resulted in an automatic actuation of the circuitry that starts the Unit 1 B-train EDG and Unit 3 A-train EDG. The undervoltage condition on the Units 1 and 3 Class 1E 4.16 KV buses resulted from startup transformer NAN-X02 tripping offline. Both EDGs started and loaded as designed. The EDG actuations were accompanied by the start of associated train essential SP pumps in both units. The Unit 1 B-train EDG actuation was also accompanied by the start of the Unit 1 B-train auxiliary feedwater pump, as required for the undervoltage condition. By design, actuation of the Unit 3 A-train steam-driven auxiliary feedwater pump was not required in response to the EDG actuation. | ML22285A000
Fermi 2 05000 341 1 OF 4 | Unknown Unit | Containment Isolation Valve Actuator Found Disconnected from its Bonnet Resulting in Condition Prohibited by Technical ~n..c.r-ifir-~+innc | 10-31-2022 | On 06/27/2022 during start up walkdowns for Forced Outage 22-01, engineering personnel discovered the B2103F019 (Main Steam Outboard Drain Isolation valve) motor operator separated from the valve bonnet yoke arm flange. The motor operator was energized (motor and gear train freely running) and agitating on the end of the vertically oriented valve stem. The inboard isolation valve (B2103F016) was capable to isolate during the entire time the B2103F019 was inoperable. Upon identification, the Containment Isolation Valve was declared inoperable per Technical Specification 3.6.1.3. The cause was determined to be improper thread engagement, due to personnel error of installing the incorrect bolts following testing using an installed testing device. B2103F019 was secured and is planned to be reworked during the next availability (refueling outage). The cycle schedule was reviewed for the impact of B2103F016 and 82103F019 isolated with no issues identified. An extent of condition was performed on the other motor operated valves tested during the previous refueling outage. This event is being reported under 10 CFR 50.73(a)(2)(i)(B) for operation or condition prohibited by TS. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to co~ly with this mandatory collection request 80 hows. Reported lessons learned are incorporated ilto the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A1 0M), U. S. Nuclear Regulatory Comnission, Washington, DC 20555--0001, or by e-mail to CONTINUATION SHEET lnfocolleds.Resource@nrc.gov, and the 0MB reviewer at 0MB Office of Information and Regulatory Affairs, (3150--0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, {See NUREG-1022, R3 for instruction and guidance for completing this form Washington, DC 20503; e-mai: oira submission@omb.eop.gov. The NRG may not conduct or http://www.nrc.gov/readinq-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a petson is not required to respond to, a oolleclion of ilformation unless the document requesting or requiring the colection displays a currentiy valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV I 05000- 1 341 a□ -I NUMBER 1-0 N O. 004 | INITIAL PLANT CONDITIONS Mode-1 Reactor Power - 9 Percent There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to his event. DESCRIPTION OF THE EVENT On 06/27/2022 during start up walkdowns for Forced Outage 22-01, engineering personnel discovered the B2103F019 (Main Steam Outboard Drain Isolation valve) [SBJ[ISV] motor operator [84] separated from the valve bonnet yoke arm flange [V]. The motor operator was energized (motor and gear train freely running) and agitating on the end of the vertically oriented valve stem. Having run out of stem threads, the actuator was being restrained on the end of the valve stem by the unthreaded portion of the stem nut counterbore and by the electrical conduit that serves the motor operated valve (MOV). The MOV was de-energized by shutting off the actuator power supply at the Motor Control Center. During the initial investigation, the (4) actuator mounting bolts had pulled out of the actuator housing, with visible damage to he threaded actuator mounting holes. After inspection it was identified that the removed bolts were 1 in long 5/16 inch cap bolts that, when fully tightened, only had 2 or 3 threads of engagement into the actuator. Based on the sequence of events, as noted per plant computer data, during the 06/27/2022 closing stroke the actuator-to-bonnet yoke flange-threaded connections failed. This allowed the unrestrained actuator to traverse up the valve stem as the stem nut rotated about the valve-stem threads. SIGNIFICANT SAFETY CONSEQUENCES AND IMPLICATIONS There were no safety consequences or radiological releases associated with this event. At no time during this event was here a potential for endangering the public health and safety. B2103F019 is a normally closed Primary Containment Isolation Valve (PCIV) [JM] and has a safety function to automatically close on a Reactor Vessel Low Level 1, and on Accident Isolation Signals E-Main Steam Line High Flow, F-Main Steam Line Tunnel High Temperature, G- Main Steam Line Low Pressure, J- Low Condenser Vacuum, P-Turbine Building High Temperatures to provide primary containment isolation of penetration, X-8. B2103F019 does not have a safety function in he open position. It is opened to provide a drain path for Main Steam line moisture to the turbine drain system during plant start-up or similar conditions. It is an 1ST Appendix Ill (formerly NRC GL 96-05) MOV with an active safety function to close within a design basis stroke time of 23 seconds per TRM 3.6.3 Table TR3.6.3-1 Group 1 Main Steam Automatic Isolation Valves. It is Type C Leak Tested and Bypass Leakage Tested under the Appendix J program. It is classified as Seismic Class I. NRG FORM 366A (08-2020) Page 2 of 4 | ML22304A009
Dresden Nuclear Power Station | Unit 2 | Ultimate Heat Sink Declared Inoperable due to River Grass Accumulation | 10-28-2022 | On July 29, 2022, at 2217 CDT, Technical Specification (TS} 3.7.3, "Ultimate Heat Sink (UHS}" Limiting Conditions for Operation (LCO} was not met, and Condition A, UHS inoperable, was entered since UHS water level was determined to be below 501.5 feet. On July 30, 2022, at 0135 CDT, UHS water level was restored to be>/= 501.5 feet. On July 30, 2022, at 1116 CDT, TS 3.7.3 LCO was not met, and Condition A was entered for water level identified to be less than 501.5 feet. At 1800 CDT, UHS water level was restored to be>/= 501.5 feet. The cause of low water level was due to accumulation of river vegetation and grass on the Unit 2/3 Intake Bay 13 bar racks. The root cause was procedures and processes were not aligned with industry excellence standards to prevent intake blockage events. Corrective actions included clearing river vegetation from the Unit 2/3 Intake Bay 13 bar racks, securing one Circulating Water pump, and transitioning to closed cycle to restore UHS water level. Additional corrective actions included implementing tools and management model process changes to monitor and prevent future fouling of the intake. This event is being reported in accordance with 10 CFR 50. 73(a}(2}(v}(B}, "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat." NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response lo comply with this mandatory collection request 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A1 0M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollecls.Resource@nrc.gov. and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 72517th Street NW, Washington, DC 20503; e-mail: oira subm1ss1on@omb eop gov. The NRC may not conduct or (See NUREG-1022, R3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV Dresden Nuclear Power Station, Unit 2 05000237 YEAR NUMBER NO. 2022 - 002 01 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 megawatts thermal rated core power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. A. CONDITIONS PRIOR TO EVENT Unit: 2 Event Date: July 29, 2022 Event Time: 2217 CDT Reactor Mode: 1 Mode Name: Power Operation Power Level: 100% B. DESCRIPTION OF EVENT The Ultimate Heat Sink (UHS) [BS] provides a suction pathway for the cooling water associated with Containment Cooling Service Water (CCSW) [Bl) and Diesel Generator Cooling Water (DGCW) [LBJ systems. The Technical Specification (TS) Surveillance Requirement (SR) verifies water level in the suction bays is sufficient for proper operation of the CCSW and DGCW pumps [P]. The CCSW pumps take suction from intake Bay 13. On July 29, 2022, at approx. 1000 CDT, station Operators performed routine rounds in the Unit 2/3 Cribhouse [NN], which included review of traveling screen [SCN] differential pressure recorders [PDR], observing intake suction Bay 13 water level, and general condition of the Unit 2/3 Cribhouse. Station Operations recorded the intake bar racks were free of debris, the traveling screen differential pressure recorders were satisfactory, and the Cribhouse intake suction Bay water levels were satisfactory. On July 29, 2022, at 2217 CDT, an equipment operator identified the Unit 2/3 intake suction Bay 13 water level was less than the TS SR value of>/= 501.5 feet. This condition did not meet TS 3.7.3, "Ultimate Heat Sink (UHS)," and required entering Condition A, UHS inoperable. The associated Required Actions and Completion Times were A.1, be in Mode 3 in 12 hours, and A.2, be in Mode 4 in 36 hours. Actions were taken to clear river vegetation and grass from the intake bar racks, troughs and traveling screens. On July 30, 2022, at 0135 CDT, Bay 13 water level was restored to>/= 501.5 feet and TS 3.7.3 Condition A was exited. On July 30, 2022, at 1116 CDT, accumulation of river vegetation and grass occurred and the TS 3. 7 .3 Condition A, UHS inoperable, was entered due to UHS water level in Bay 13 being less than 501.5 feet. The station continued clearing debris, secured a Circulating Water [KE] pump, and transitioned the plant to closed cycle (see Safety Analysis section below for further explanation) to restore intake suction Bay 13 water level. At 1800 CDT, intake suction Bay 13 water level was restored to>/= 501.5 feet and TS 3.7.3 Condition A was exited. | ML22304A225
Dresden Nuclear Power Station | Unit 2 | Unit 2 Reactor Scram due to Turbine Trip on High Reactor Water Level caused by Feedwater Regulating Valve Failure | 10-28-2022 | On July 12, 2022, at 0803 CDT, an automatic reactor protection system actuation occurred following a main turbine trip due to high reactor water level. The safety significance of this event was minimal. All control rods inserted to their full- in position. Following the reactor scram, all systems operated as expected. The cause of high reactor water level is due to a feedwater regulating valve unexpectedly failing full-open. The root cause of the feedwater regulating valve failing full-open was due to the feedwater regulating valve pilot valve assembly not operating due to a manufacturing byproduct inside the pilot valve introduced during the manufacturing process. Corrective actions included replacement of the respective air solenoid valve. Additional corrective actions include inspecting and certifying these incoming valves are free of foreign material. Also, the solenoid valves for the feedwater regulating valves were reclassified as single point vulnerabilities. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), an event that resulted in automatic actuation of a system listed in paragraph 10 CFR 50. 73(a)(2)(iv)(B}, specifically the reactor protection system including reactor scram. NRC FORM 366A (08-2020) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 c.,.t.~1111111rou,1> +" o,. f r,~-.. B ~ LICENSEE EVENT REPORT (LER) \~''i!!!';t:/ CONTINUATION SHEET ., ...... (See NUREG-1022, R.3 for instruction and guidance for completing this form http·/twww.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collecbons Branch (T-6 A 10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Oesk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira subm,ss,on@omb eoo gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR Dresden Nuclear Power Station, Unit 2 05000- 237 2022 - | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 megawatts thermal rated core power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. A. CONDITIONS PRIOR TO EVENT Unit: 2 Reactor Mode: 1 Event Date: July 12, 2022 Mode Name: Power Operation 8. DESCRIPTION OF EVENT Event Time: 0803 CDT Power Level: 100% SEQUENTIAL NUMBER 001 REV NO. 01 On July 12, 2022, at 0759 CDT, one of two Feedwater [JB] regulating valves (FWRV) [FCV]. which are used to control feedwater flow to the reactor vessel, unexpectedly failed to the full-open position from its initial position of 42% open, resulting in a Reactor Feedwater [SK] Pump [P] trip on low suction pressure and an automatic Reactor Recirculation [AD] runback. This condition resulted in reactor water level rising due to the inability of the Feedwater system to regulate flow. At 0803 CDT, an automatic reactor protection system [JC] actuation occurred following a main turbine [TA] trip due to high reactor water level. Plant systems operated as expected in response to the automatic scram. All control rods [AA] inserted to their full-in position and the scram was not complicated. Reactor pressure was maintained in the normal control band. Reactor water level was restored and maintained in the normal control band. The NRC was notified via ENS Report 55988 at 1147 EDT. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), an event that resulted in automatic actuation of a system listed in paragraph 10 CFR 50.73(a)(2)(iv)(B), specifically the reactor protection system including reactor scram. C. CAUSE OF EVENT The cause of the FWRV failure was due to failure of the respective air solenoid valve [SOL], which is used to control FWRV position. The solenoid valve failure prevented the FWRV from repositioning. Failure analysis and root cause of the air solenoid valve failure was due to a manufacturing byproduct on the pilot valve plunger, which prevented the pilot valve from seating. A small piece of plastic was found on the internal seat surface. The plastic is the same material as the valve body construction. This material is not consistent with any other component in the instrument air system. Evidence supports the conclusion that the material was present when the valve was assembled at the factory. | ML22304A228
Susquehanna Steam Electric Station | Unit 2 | Unit 2 Main Turbine Pressure Regulator Inoperable for Longer Than Allowed by Technical Specifications due to Inadequate Valve Modification | 11-03-2022 | At approximately 13:21 on October 11, 2021, the Susquehanna Steam Electric Station, Unit 2, experienced an automatic reactor scram due to a main turbine trip. All turbine bypass valves (TBVs) opened, as expected, to control reactor pressure but did not subsequently re-close. Troubleshooting identified Pressure Transmitter PT-20101B as the cause of the TBVs failure to re-close. To control reactor pressure, operators manually closed the four main steam isolation valves and utilized the main steam line drains and the High Pressure Coolant Injection System. Further analyses showed the Pressure Transmitter PT-20101B failure was caused by failure of the pressure transmitter root valve resulting from main steam line vibrations created by the scram. The root valve was previously modified; however, station personnel did not validate that the modification would perform properly in all plant operating conditions. To correct the condition, the failed valve was replaced and applicable procedures were updated. Based on failure information, it is likely that Pressure Transmitter PT-20101B was inoperable for longer than allowed by Technical Specification (TS) 3.7.8. Therefore, this event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. There were no actual safety consequences associated with the described condition. NRC FORM 366A U. S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, a collection of information unles s the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station, 05000-388 NUMBER NO. Unit 2 2021 - 004 - 01 | CONDITIONS PRIOR TO EVENT Unit 1 – Mode 1, approximately 100 percent Rated Thermal Power (RTP) Unit 2 – Mode 1, approximately 95 percent RTP At approximately 13:21 on October 11, 2021, the Susquehanna Steam Electric Station (SSES), Unit 2, experienced an automatic reactor scram due to a main turbine trip. Subsequently, all turbine bypass valves (TBVs) [EIIS System/Component Codes: JI/PCV] immediately opened as expected. EVENT DESCRIPTION On October 11, 2021, at approximately 13:21, the Susquehanna Steam Electric Station Unit 2 reactor automatically scrammed due to a main turbine [TA/TRB] trip. The scram event is reported under LER-2021- 003. The Unit 2 Control Room received indication of a main turbine trip with both divisions of the Reactor Protection System (RPS) [EIIS System Code: JC] actuated and all control rods inserted. The TBVs opened automatically, as expected, to control reactor pressure but subsequently remained open. Reactor pressure was initially stabilized through manual closure of the Main Steam Isolation Valves (MSIVs) [SB/ISV] and maintained using the main steam line drains [SB/DRN] and the High Pressure Coolant Injection (HPCI) [BJ] System. Based on failure information, it is likely that Pressure Transmitter PT-20101B was inoperable for longer than allowed by Technical Specification (TS) 3.7.8, “Main Turbine Pressure Regulation System.” Therefore, this event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. CAUSE OF EVENT Previous to the scram, the root valve (2RV-PT20101B) [RTV] for the ‘B’ Mains Steam Pressure Secondary Transmitter, PT-20101B, experienced a steam leak on the valve packing. A temporary repair was installed to seal the leak using 2X sealant. During the Unit 2 scram vibrations from the main steam lines caused the 2X sealant to crack and separate from the valve stem. The valve subsequently closed resulting in sustained pressure indication to the TBVs, which remained open longer than required. In preparation of the temporary repair, the station did not validate that 2X sealant would perform properly under all plant operating conditions. ANALYSIS/SAFETY SIGNIFICANCE While failure of the pressure transmitter is a potential transient initiator when operating at full power, it is not credited in the mitigation of any accident. The TBVs are credited in multiple Updated Final Safety Analysis Report Chapter 15 analyses, all of which assume the bypass valves will open to mitigate the pressure transient from the event. As noted in the event summary, the failure of the pressure transmitter did not prevent the bypass valves from opening nor was there any other impact to components credited with mitigation. The condition described herein did not result in a safety system functional failure. Accordingly, this event will not be counted as a safety system functional failure under the Reactor Oversight Process Performance Indicators. There were no actual consequences to the health and safety of the public as a result of this event. Page 2 of 3 | ML22307A260
Susquehanna Steam Electric Station | Unit 2 | Inadequate Performance of Loss of Safety Determination Resulting in Both Divisions of Core Spray Being Inoperable | 11-23-2022 | On September 26, 2022, operators at the Susquehanna Steam Electric Station performed quarterly stroke time testing of Unit 2 Emergency Service Water (ESW) to Turbine Building Closed Cooling Water and ESW to Reactor Building Closed Cooling Water isolation valves. Performance of this surveillance results in the inoperability of Unit 2, Division 2 of the Core Spray system. This surveillance was performed while Unit 2, Division 1 of the Core Spray system was out of service for planned maintenance, resulting in both divisions of the Core Spray system being inoperable and a loss of safety function. The condition was identified during the subsequent shift while performing routine review of operator logs. The condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented fulfillment of a safety function. The cause of the event was determined to be inadequate performance of a loss of safety function determination, which failed to identify a loss of safety function resulting from concurrent inoperability of both divisions of Core Spray. This cause was attributed to human performance. There were no actual consequences to the health and safety of the public as a result of this event. <)P~ REc11~ /~ {Ko~ :; _2l_ i ~~~-Ir', ; ~,.,-:;-•'71 +01 •it-•~· I I I I I I I I I I I I I I I I I I I I I I I I I I I NRC FORM 366A (08-2020) Page 2 of 3 . NRC FORM 366A (08-2020) U. S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 LICENSEE EVENT REPORT (LER) CONTINUATION SHEET Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. (See NUREG-1022, R.3 for instruction and guidance for completing this form https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Susquehanna Steam Electric Station, Unit 2 05000-388 YEAR SEQUENTIAL NUMBER REV NO. 2022 - 001 - 00 | CONDITIONS PRIOR TO EVENT Unit 1 – Mode 1, approximately 100 percent Rated Thermal Power (RTP) Unit 2 – Mode 1, approximately 100 percent RTP EVENT DESCRIPTION On September 26, 2022, operators at the Susquehanna Steam Electric Station performed quarterly stroke time testing of the Unit 2 Emergency Service Water (ESW) [EIIS System Code: BI] to Turbine Building Closed Cooling Water (TBCCW) [EIIS System Code: CC] and ESW to Reactor Building Closed Cooling Water (RBCCW) [EIIS System Code: CC] isolation valves [EIIS Component Code: ISV]. Performance of this surveillance results in the inoperability of Unit 2, Division 2 of the Core Spray system [EIIS System Code: BG]. This surveillance was performed while Unit 2, Division 1 of the Core Spray system was out of service for planned maintenance, resulting in both divisions of the Core Spray system being inoperable and a loss of safety function. The condition was identified during the subsequent shift while performing routine review of operator logs. The following timeline demonstrates the sequence of events: 09/25/2022 ~ 09:00: The quarterly surveillance original start time is postponed due to conflicting work on the Unit 2 RBCCW heat exchangers [EIIS Component Code: HX]. A condition report is generated for the surveillance to be rescheduled after the completion of the Unit 2, Division 1 Core Spray planned maintenance. 09/25/2022 ~ 19:45: Unit 2, Division 1 Core Spray planned maintenance begins. Limited Condition of Operation (LCO) 3.5.1, “Emergency Core Cooling Systems (ECCS), Reactor Pressure Vessel (RPV) Water Inventory Control, and Reactor Core Isolation Cooling (RCIC) System,” Condition A is entered to support this work. 09/26/2022 ~ 05:00: During operations shift turnover, the need to track the postponed surveillance was discussed. However, the oncoming Unit Supervisor completed turnover with the misunderstanding that the surveillance needed to be completed during the Unit 2 RBCCW heat exchanger restoration. 09/26/2022 ~ 09:00: The surveillance is rescheduled for 09/27/2022, after the Unit 2, Division 1 Core Spray planned maintenance was scheduled to be complete. 09/26/2022 ~ 14:00: Unit 2 RBCCW heat exchanger work is reported completed. Operations begins preparation for performance of the quarterly surveillance. During this process, operations inadequately performed a loss of safety function determination using a previously completed copy of the station procedure, which did not identify the Unit 2, Division 1 Core Spray ongoing planned maintenance. 09/26/2022 ~ 14:08: Operations entered Condition C of LCO 3.7.2, “Emergency Service Water (ESW) System,” due to Division 2 ESW being inoperable for performance of the surveillance. A peer check for entry into the LCO condition was not received as required by station procedures. Investigation identified this as the time the loss of safety function occurred. 09/26/2022 ~ 14:17: The surveillance on Division 2 ESW is completed. Operations exited Condition C of LCO 3.7.2. | ML22327A176
Grand Gulf Nuclear Station | Unit 1 | Primarv Containment Outer Airlock Door lnooerable Due To Unaccer table Leak Rate | 11-30-2022 | On February 22, 2021, Grand Gulf Nuclear Station's Primary Containment Outer Airlock located on 208' elevation exceeded the Technical Specification (TS) Surveillance Requirements 3.6.1.2.1 leakage rate during the pre- maintenance barrel test due to gross leakage of the equalizing valve associated with the outer airlock door. Analysis determined that the inner and outer airlock equalizing valves were leaking - caused by lack of lubrication during valve installation. This event is reportable under 10 CFR 50.73(a)(2)(i)(B), as an operation or condition which was prohibited by the plant's Technical Specifications. The event is also being reported under 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented the fulfillment of a safety function. This supplement expands the original Licensee Event Report to include applicability of 1O CFR 21.2(c). Actions taken were the lubrication and replacement of the equalizing valve on the outer door. The equalizing valve on the inner door was rebuilt with new O-rings and lubricated prior to reinstallation. Following replacement of the outer door and rebuild of the inner door, the local leak rate test (LLRT) was tested satisfactorily. There were no consequences to the general safety of the public, nuclear safety, industrial safety or radiological safety. No radiological releases occurred due to this event. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 ,,,. (O!l-2020) Estimated burden per response to comply with this mandatory collection request: 80 ....... hours. Reported lessons learned are incorporated into the licensing process and led "¥,' LICENSEE EVENT REPORT (LER) back to industry. Send comments regarding burden estimate to the FOIA, Library, !\ 11 and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory ...... CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects . Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and (See NUREG-1022, R.3 for instruction and guidance for completing this form Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1 o 221r3D Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira subm1ssion@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document reauesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 05000-416 NUMBER NO. 2021 -001 -01 | Plant Conditions: Grand Gulf Nuclear Station (GGNS) Unit 1 was operating at 100 percent power in MODE 1. There were no Structures, Systems, or Components that were inoperable that contributed to this event. Event Description: On February 22, 2021, GGNS's Primary Containment [NH] Airlock [AL] outer door located on 208' elevation exceeded the Technical Specification (TS) Surveillance Requirements (SR) 3.6.1.2.1 leakage rate during the pre-maintenance barrel test due to gross leakage of the 1 M23F018D equalizing valve [V] associated with the outer airlock door, resulting in a condition that could have prevented the fulfillment of a safety function during times when the inner airlock door was open. A maintenance work window for the 208' Containment Personnel Airlock outer door was scheduled for February 22, 2021. As part of the maintenance evolution, the airlock barrel local leak rate test (LLRT) was performed to identify any leaking components needing to be repaired during the maintenance window. Technical Specification 3.6.1.2, Primary Containment Airlocks, was entered on February 22, 2021, at 0530 hrs. for the maintenance window. Per calculation MC-O1 M23-16001, the maximum allowable primary containment leakage rate (La) for the calculated maximum peak containment pressure (Pa) 12.1 psig is 337,617 SCCM. Per SR 3.6.1.2.1 overall airlock leakage rate is less than or equal to 0.05 times La which is 16,880 SCCM. Analysis determined that the equalizing valves had failed prior to February 22 due to lack of lubrication during installation. The Containment Airlock outer door was declared inoperable due to excessive leakage. In accordance with TS 3.6.1.2 Condition (One or more primary containment airlocks with one primary containment airlock door inoperable), the OPERABLE door should be closed and locked in the affected airlock. The required actions were not met in the required completion time. This event is reportable under 10 CFR 50.73(a)(2)(i)(B), any operation or condition which was prohibited by the plant's Technical Specifications. This also resulted in a condition that could have prevented the fulfillment of a safety function to mitigate the consequences of an accident, during times when the inner airlock door was open, and is reportable under 10 CFR 50.73(a)(2)(v)(D). Subsequent investigation led to the determination that the equalizing valves had been dedicated by a vendor and that lubrication was to have been performed during the dedication process. Lubrication was not performed, leading to the failure of the leakage test. As a result, this event is reportable under 10 CFR 21.2(c). The site formally completed its 10 CFR 21 Evaluation on October 17, 2022. During the periods when the outer airlock door was inoperable, the inner airlock door either remained closed (Operable) or was opened for passage and under the control of site personnel. As a result, Entergy has determined that it did not result in a safety system functional failure. Therefore, in accordance with the guidance provided in NEI 99-02, Revision 7, Regulatory Assessment Performance Indicator Guideline, Section 2.2, Mitigating Systems Cornerstone, Sub-Section, Safety System Functional Failures, Page 30, Lines 27 through 30; this condition will not be counted as a safety system functional failure against Performance Indicator MS05, Safety System Functional Failures. | ML22334A222
i | Unknown Unit | Steam Bypass Valve Demand Limited on the 'B' Train due to a Degraded Signal in the Max Combined Flow Limit Circuit | 12-05-2022 | On October 7, 2022 at 174 0, it was identified that the Maximum Combined Flow Limiter In Control light was lit with the Steam Bypass and Pressure Regulating system on the "B" channel. This light being lit indicates that the max combined flow limiter is in control, which limits steam flow to the main turbine and condenser hrough the control valves and bypass valves. This indication appeared to be an erroneous indication as reactor power and pressure remained stable. The system contains two channels of pressure regulation, an "A" and "B" channel. A failure in either channel could cause the light to illuminate. A troubleshooting earn was developed to determine the potential failure modes. On October 13, 2022 during problem solving for the Maximum Combined Flow Limiter In Control light, the problem solving team detennined the "A" channel was operating normally and that the "B" channel would prevent the bypass valves from responding to a pressure perturbation with the steam bypass and regulating system operating on the "B" channel. The control room shifted off the "B" channel to the "A" channel and declared the "B" channel inoperable. The direct cause of the Maximum Combined Flow Limiter Light was the failure of "B" Flow Demand circuit card based on the indications obtained and observable damage found on the card during replacement. Corrective action was taken to replace the failed card. The safety significance of this event is considered to be very low. This condition is reportable under 50. 73(a)(2)(i)(B) as an operation or condition prohibited by the plant's technical specifications. Technical Specification (TS) 3.7.6 requires the main turbine bypass system to be operable with rated power greater than 23.8 percent, when the "B" channel was in control it was determined that the system was not operable. TS 3.7.6 requires that bypass valve operability be restored within 2 hours, otherwise be less than 23.8 percent power within 4 hours. Vllith firm evidence that the issue had existed on October 7 and with the inoperable "B" channel in control until October 13 the required actions of TS 3.7.6 were not taken, and a condition prohibited by TS resulted. NRC FORM 366A U.S. NUCLEAR REGULA TORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this miw,datory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A1 0M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at 0MB Office of Information and Regulatory Affairs, (3150.0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting http:/lwww.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3Q or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER ;J. Lt:K numos;" YEAR SEQUENTIAL REV Perry Nuclear Power Plant 05000-1 00440 -I NUMBER 1-G NO. 20221 002 I | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. EVENT DESCRIPTION On October 7, 2022 at 1740 and with the reactor at mode 1 and 100% rated thermal power, it was identified that the Maximum Combined Flow Limiter In Control (MCFLC) light was lit with the Steam Bypass and Pressure Regulating system [JI] on the "B" channel, this light being lit indicates that the maximum combined flow limiter is in control, which results in a limitation of steam flow to the main turbine [TG] and condenser through the control valves and bypass valves. While observing plant parameters this appeared to be an erroneous indication as reactor power and pressure remained stable. The system contains two channels of pressure regulation, an "A" and "B" channel. A failure in either channel could cause the light to illuminate. A troubleshooting team was developed to determine the potential failure modes. On October 13, 2022 during problem solving on the MCFLC light, the problem solving team determined the "A" channel was operating normally while the "B" channel contained a degradation in the circuitry resulting in the illumination of the MCFLC light. The data also indicated the MCFLC signal could be limiting the "B" channel, which would prevent the bypass valves from responding to a pressure perturbation while operating on the "B" channel. At that time operations placed the "A" channel in operation and declared the "B" channel inoperable. During a maintenance outage on October 30, 2022, the "B" flow demand circuit card [CBD] was replaced. Following the card replacement, testing on the "B" channel determined the channel to bein proper working condition. CAUSE OF EVENT The direct cause of the failure of the MCFLC Light was the "B" flow demand circuit card based on the voltage readings and observable damage found on the card during replacement. The likely cause of failure of the circuit card is age-related failure of the components as they are plant original parts. The removed flow demand card had observable charring at several resistors on the circuit card, and it had degraded output voltage. Based on the voltage reading and the observed charred components on the card, the "B" flow demand circuit card is the direct cause of the MCFLC light illuminating. EVENT ANALYSIS A Probabilistic Risk Assessment (PRA) bounding evaluation was performed for this event. Fire and other external hazards were qualitatively addressed to be of low risk. The analysis of this event results in delta CDF and delta LERF values that are below the acceptable thresholds of 1.0E-06/yr an d 1.0E-07/yr, as discussed in Regulatory Guide 1.174 . Sensitivities performed that increased the frequency of a general transient initiating event did not change these conclusions. The risk of this event is therefore considered to be of very low safety significance in accordance with the Regulatory Guidance. | ML22339A029
Susquehanna Steam Electric Station | Unit 1 | Automatic Reactor Scram Due to Reactor Protection System Actuation on High Reactor Vessel Pressure Signal Following Inadvertent Closure of Inboard Main Steam Isolation Valve | 12-05-2022 | At approximately 17:16 on May 23, 2022, Susquehanna Steam Electric Station, Unit 1, experienced an automatic reactor scram. Reactor Protection System (RPS) was actuated on a high reactor vessel pressure signal due to inadvertent closure of an inboard Main Steam Isolation Valve (MSIV) (HV141F022D). All control rods inserted, and operators placed the mode switch to shut down. All safety systems responded as designed during this event. Event Notification 55909 reported this event in accordance with 10 CFR 50.72(b)(2)(iv)(A), 10 CFR 50.72(b)(2)(iv)(B), and 10 CFR 50.72(b)(3)(iv)(A). This event is also reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of a system listed in 10 CFR 50.73(a)(2)(iv)(B). The cause of the scram was due to a loss of pneumatic pressure resulting in closure of an inboard MSIV (HV141F022D) which resulted in a high reactor vessel pressure signal and valid RPS actuation. The loss of pneumatic pressure occurred due to high cycle fatigue induced failure, most likely from vibration, of the 3/8” Containment Instrument Gas tubing. Affected tubing was replaced and the weld on 3/8” tubing to HV141F022D was repaired. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366A U. S. NUCLEAR REGULATORY COMMISSIONAPPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station, 05000-387 NUMBER NO. Unit 1 2022 - 002 - 01 | CONDITIONS PRIOR TO EVENT Unit 1 – Mode 1, approximately 100 percent Rated Thermal Power (RTP) Unit 2 – Mode 1, approximately 100 percent RTP EVENT DESCRIPTION At approximately 17:16 on May 23, 2022, Susquehanna Steam Electric Station, Unit 1, experienced an automatic reactor scram. Reactor Protection System (RPS) [EIIS System Code: JC] was actuated on a high reactor vessel pressure signal due to inadvertent closure of an inboard Main Steam Isolation Valve (MSIV) (HV141F022D) [EIIS System/Component Codes: SB/ISV] following loss of pneumatic pressure. All control rods inserted, and operators placed the mode switch to shut down. Containment isolations [JM] and both Reactor Recirculation Pump [AD/P] trips occurred as reactor water level dropped below the Anticipated Transient Without Scram – Reactor Pump Trip logic setpoint. High Pressure Coolant Injection [BJ] and Reactor Core Isolation Cooling [BN] initiated as designed when the reactor water level lowered. Subsequently, operators maintained reactor water level within normal band using Reactor Feedwater [SJ]. All other safety systems responded as designed. Event Notification 55909 reported this event in accordance with 10 CFR 50.72(b)(2)(iv)(A), 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). This event is also reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of a system listed in 10 CFR 50.73(a)(2)(iv)(B). CAUSE OF EVENT The cause of the scram was due to a loss of pneumatic pressure resulting in inadvertent closure of an inboard MSIV (HV141F022D) which resulted in a high reactor vessel pressure signal and valid RPS actuation. The loss of pneumatic pressure occurred due to high cycle fatigue induced failure, most likely from vibration, of the 3/8” Containment Instrument Gas [LK] tubing [TBG]. ANALYSIS/SAFETY SIGNIFICANCE The actual consequence of this event was an automatic reactor scram. All safety systems responded as designed during this event. Residual Heat Removal [BO] and Residual Heat Removal Service Water [BI] remained available to remove residual heat. No fuel or clad damage occurred during the scram, as evidenced by Main Steam Line and Off-Gas radiation levels decreasing post-scram. All applicable systems were available to control the release of any radioactive material. All safety systems were available to mitigate the consequences of an accident. The condition described herein did not result in a safety system functional failure. Accordingly, this event will not be counted as a safety system functional failure in the Reactor Oversight Process Performance Indicator. There were no actual consequences to the health and safety of the public as a result of this event. Page 2 of 3 | ML22339A095
Limerick Generating Station | Unit 1 | Unit 1 HPCI Inoperable Due to Inadvertent Isolation Signal | 12-13-2022 | On October 14, 2022, during planned testing of the High Pressure Coolant Injection (HPCI) System, a spurious HPCI Division 2 isolation occurred due to a fault in an electrical connector associated with the HPCI Division 2 isolation reset circuit. The affected electrical connector carries signals for the control circuits of the outboard HPCI Turbine Exhaust Line Vacuum Breaker isolation valve and HPCI Test Line Flush isolation valve and the HPCI Division 2 isolation reset circuit. Closing the outboard HPCI Turbine Exhaust Line Vacuum Breaker isolation valve energized degraded pins within the electrical connector resulting in a fault that initiated the HPCI Division 2 isolation signal. The defective electrical connector was removed, and the affected cable spliced in accordance with an approved design change. This event is being reported as a condition that, at the time of discovery, could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident. An eight (8) hour ENS notification was completed on October 14, 2022, at 18:03 hours. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments ~¥' LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. ; i CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to ..... Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory <--+_, ~o' Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER •YEAR SEQUENTIAL REV 05000- NUMBER NO. Limerick Generating Station Unit 1 352 D 2022 - I 001 - 00 I I I I I | Unit Condition Prior to the Event Unit 1 was in Operational Condition (OPCON) 1 (Power Operation) at approximately 100% power. There were no structures, systems, or components out of service that contributed to this event. Description of the Event On October 14, 2022, a Unit 1 High Pressure Coolant Injection (HPCI) System [BJ] surveillance test was conducted on the HPCI Turbine Exhaust Vacuum Breakers. The purpose of this test is to ensure that the HPCI turbine exhaust line vacuum breakers function properly in both the forward and reverse flow directions. The HPCI turbine exhaust line vacuum breaker isolation valves, HV-055-1F093 and HV-055-1F095 must be closed to establish the required alignment to test the vacuum breaker check valves. The HPCI System is inoperable, but available in this test alignment. At 09:15 the HPCI turbine exhaust line vacuum breaker isolation valves were closed to establish the required alignment to perform the surveillance test. At 09:23, a Unit 1 Division 2 Safeguard Battery ground alarm was received, and all DC related testing was stopped to investigate the alarm. At 10:07, a HPCI Division 2 isolation signal was received accompanied by auto closure of the outboard HPCI Steam line isolation valve and the inboard HPCI Pump Suppression Pool suction valve. An eight (8) hour ENS notification (56163) was completed on October 14, 2022, at 18:03 hours. Troubleshooting and failure analysis of the removed electrical connector concluded that degradation of several of the pin connections within the affected electrical connector resulted in a fault that propagated to the HPCI Division 2 isolation reset circuit. The fault within the electrical connector was initiated when the degraded pin connections were energized by closure of the outboard HPCI turbine exhaust line vacuum breaker isolation valve, HV-055-1F093, for the planned surveillance test. The defective electrical connector was removed, and the affected cable spliced in accordance with an approved design change. The HPCI system was returned to service on October 17, 2022, at 21:15. (cid:3025) Analysis of the Event The inadvertent HPCI isolation that occurred during a planned surveillance test was attributed to a degraded electrical connector that was energized when closing one of the motor operated valves required to establish the alignment for the surveillance test. Failure analysis of the electrical connector identified that a fault propagated to the HPCI Division 2 isolation reset circuit when the outboard HPCI turbine exhaust vacuum breaker isolation valve, HV-055-1F093, was closed to establish the required alignment to perform the planned surveillance test. Additionally, due to the degradation on other pin connectors of the affected electrical connector, the failure analysis could not conclusively eliminate the possibility of a fault occurring through a different mechanism. With the unplanned loss of a single train system this condition is being reported per 10 CFR 50.73(a)(2)(v)(D), any condition that could have prevented the fulfillment of the safety function of structures or systems required to mitigate the consequences of an accident. | ML22347A286
Peach Bottom Atomic Power Station | Unit 2 | Automatic Depressurization System Safety Relief Valve Actuator Diaphragm Degraded | 12-15-2022 | On October 17, 2022, with the unit in a refueling outage. Water was identified leaking from a fastener on the PB2 RV- 71B Main Steam Safety/Relief Valve (S/RV) body. The water leak was a small steady stream. The leakage was due to a degraded gasket and steam cut fastener threads. Subsequent laboratory analysis of the leaking valve identified the Automatic Depressurization System, (ADS) function performed by the pneumatic operator was non-functional. The pneumatic operator resilient components (diaphragm) were discovered to be embrittled and lost pressure retaining integrity. The timeframe for the degraded ADS capability cannot be reasonably determined at this time. The relief valve overpressure function was evaluated to be not impacted by the leak or the loss of ADS function. Therefore, Peach Bottom is submitting this report in accordance with 10 CFR 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant’s Technical Specifications, having exceeded the required 14 day action time or maximum Risk Informed Completion Time (RICT) to restore an ADS valve to OPERABLE status. There were no other systems which were inoperable during this identified condition that contributed to this event. There were no actual safety consequences as a result of this event. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Peach Bottom Atomic Power Station, Unit 2 05000- 277 NUMBER NO. 2022 - 002 - 00 | Plant Operating Conditions before the Event: Unit 2 was in Mode 4, Cold Shutdown, with the Main Steam Lines water solid, operating at 0% of rated thermal power on October 17, 2022. Unit 2 was shut down for its 24th Refueling Outage (P2R24) on October 16, 2022. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event: There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. The Energy Industry Identification System component function identifier and name of each component or system: EIIS: Safety Relief Valves [SB], RV-2-02-071B, B SAFETY RELIEF VALVE (RV-71B) Target Rock Model 67F pilot operated safety/relief valve Serial Number 024 Description of Event: On October 17, 2022, at 1337 hours, station personnel identified a small steady stream of water, approximately 0.2 gallons per minute leaking from the insulation around the ‘71B’ Main Steam/Relief Valve (S/RV). Subsequent investigation revealed that the leakage was from the relief valve pilot filter plug threaded connection. There was no through-wall leakage of any Reactor Coolant System (RCS) pressure boundary component. The RV-71B was emergently replaced in the scope of the planned outage, quarantined, and shipped to an off-site vendor for analysis and repair. As part of vendor testing the relief valve, the pneumatic operator is functionally tested with air. The pneumatic operator failed to actuate and air leakage was audible during testing, indicating potential resilient parts degradation. Disassembly and examination of the pneumatic operator revealed the actuator diaphragm elastomer had embrittled and delaminated, enabling gross leakage that inhibited the S/RV manual operation capability. This as-found condition represents a loss of the valve’s Automatic Depressurization System (ADS) function. Technical Specification (TS) 3.5.1 Limiting Condition of Operation (LCO) requires each Emergency Core Cooling System (ECCS) injection/spray subsystem and the Automatic Depressurization System (ADS) function of five (5) S/RVs to be OPERABLE in operating modes 1, 2 and 3. The remaining four (4) S/RVs that support ADS capability were verified to be operable for this function. Peach Bottom TS Limiting Condition for Operation 3.5.1, Condition E for one (1) ADS valve inoperable, has a Completion Time of 14 days or in accordance with the Risk Informed Completion Time Program. The event start time for the loss of ADS function of the RV-71B is indeterminate. The S/RV ADS function is considered inoperable for a period greater than permitted by TS since the start of the degradation cannot be reasonably determined. Therefore, the condition is reportable under criterion 10CFR 50.73(a)(2)(i)(B) as any operation or condition which was prohibited by the plant’s Technical Specifications. The RV-71B was installed as part of the planned preventive maintenance relief valve outage work scope in October of 2018 (P2R22). The valve was in-service approximately four (4) years at the time of discovery. The RV-71B ADS Safety Relief Valve was not actuated during Cycle 24 operations (October 2018 – October 2020). The RV-71B was used for manual pressure control during Cycle 25 (October 2020 – October 2022) as part of post U2 SCRAM actions on May 15, 2022 (ML22196A020). Control room operators manually operated the valve from the main control room and observed the expected response. | ML22349A084
YEAR SEQUENTIAL REV | Unknown Unit | Inoperable 13.8kV Startup Transformer due to Misaligned Load Tap Charger Local/Remote Control Switch | 12-19-2022 | 12.Licensee Contact for this LER Licensee Contact Phone Number (Include Area Code) Derek R. Smith, Senior Engineer – Nuclear Regulatory Affairs I( 570)542-1377 13.Complete One Line for each Component Failure Described in this Report Cause I System Component I Manufacturer I Reportable to IRIS I Cause I System I Component I Manufacturer I Reportable to IRIS I I I I I I I I 14.Supplemental Report Expected I I Month I Day I Year 15.Expected Submission Date ☒ No I☐ Yes (If yes, complete 15. Expected Submission Date) I I I I 16.Abstract (Limit to 1560 spaces, i.e., approximately 15 single-spaced typewritten lines) On October 22, 2022, operators at the Susquehanna Steam Electric Station identified the load tap changer (LTC) local/remote control switch on one of the two 13.8 kV startup transformers was in the remote position, as opposed to the required local position. Upon identification of the condition, operators entered Technical Specification (TS) 3.8.1, “AC Sources-Operating,” Condition A for one offsite circuit inoperable. The switch was restored to the local position and the transformer was declared operable at 21:00 on October 22, 2022. Based on investigation and cause, the condition is likely to have existed since October 12, 2022, and is, therefore, being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. The cause of the event was determined to be inadvertent bumping of the LTC local/remote control switch during opening and closing of the transformer cabinet doors by maintenance personnel. This cause was attributed to a human performance error. Corrective actions include planned procedure revisions to verify the LTC control switches are properly positioned during transformer restoration. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366A U. S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Susquehanna Steam Electric Station Unit 2 05000-388 NUMBER NO. 2022 - 003 - 00 | CONDITIONS PRIOR TO EVENT Unit 1 – Mode 1, approximately 85 percent Rated Thermal Power (RTP) Unit 2 – Mode 1, approximately 100 percent RTP There were no structures, systems, or components that were inoperable at the start of the event and contributed to the event. One of the two 13.8kV startup transformers was inoperable for planned maintenance. EVENT DESCRIPTION On October 22, 2022, operators at the Susquehanna Steam Electric Station identified the load tap changer (LTC) local/remote control switch [EIIS Component Code: 33] on one of the two 13.8kV startup transformers [EIIS System/Component Code: E/XFMR] was in the remote position, as opposed to the required local position. Upon identification of the condition, operators entered Technical Specification (TS) 3.8.1, “AC Sources-Operating,” Condition A for one offsite circuit inoperable. Investigation determined the control switch was most likely inadvertently manipulated while restoring the transformer to operable from planned maintenance on October 12, 2022. The switch was restored to the local position and the transformer was declared operable at 21:00 on October 22, 2022. The following timeline demonstrates the sequence of events: 10/10/2022 ~ 22:10: TS 3.8.1, Condition A is entered to support planned maintenance on one of the two 13.8 kV startup transformers. 10/11/2022 ~ 06:00: Routine preventative maintenance activities begin to inspect and change the oil in the transformer LTC. The LTC local/remote control switch is not manipulated per the work instructions. 10/11/2022 ~ 14:00: While removing the clearance order from the 480 V normal and alternate control cabinet [EIIS Component Code: CAB], the transformer cooling fans [EIIS Component Code: FAN] started unexpectedly, requiring troubleshooting to restore the transformer to operable. 10/11/2022 ~ 18:15: Maintenance of the LTC is completed and post maintenance testing (PMT) is completed successfully. 10/11/2022 through 10/12/2022 ~20:00: Troubleshooting on the unexpected fan start continued. Troubleshooting activities require access in the cabinet where the LTC local/remote control switch is located. Investigation determined this to be the most probable timeframe the switch was inadvertently bumped. 10/12/2022 ~ 20:00: The transformer is restored to service and declared Operable. TS 3.8.1, Condition A is exited. 10/22/2022 ~ 15:13: The control room received a report that the transformer LTC local/remote control switch was found in the remote position, as opposed to the expected local position. The transformer is declared inoperable and TS 3.8.1, Condition A is entered. 10/22/2022 ~ 21:00: The LTC local/remote control switch is placed in the correct position and the transformer is declared operable. TS 3.8.1, Condition A is exited. Based on the timeline above, the transformer was inoperable for longer than allowed by TS. Therefore, this condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. Page 2 of 3 | ML22353A082
Grand Gulf Nuclear Station | Unit 1 | Loss of Secondary Containment during Standby Gas Treatment System Testing due to boundary leakage | 12-19-2022 | Between October 20 and October 27, 2022, Grand Gulf Nuclear Station, Unit 1 (GGNS) experienced two similar events. ODun rJinunge t h3e0, 2p0e2r2fo armt 1a1n4c5e h oouf rtsh,e w Sittha tnhdeb Gyr Ganads G Turlef aNtmucelenatr S Sytasttieomn iTn rMaiond Ae 1s uanrvde 1il0la0n pceer cteenstt pGowGeNr,S t hwea rse aucntoarb wlea st om manauianltlayi n tSriepcpoendd daurey tCo othnet aloinssm oefn bta plarnecses uofr ep,l aanst r(eBqOuPir)e tdra bnsyf oTremcehrn 2ic3a. l ASlpl ecocniftircoalt rioond sS fuulrlvye iinllsaenrcteed Rinetoq uthiree cmoeren ta n3d.6 a.l4l .s1y.s4t,e mgrse ater rthesapno nodr eedq aupaplr toop r0ia.2te6l6y. inches of water vacuum for 1 hour at a flow rate of less than or equal to 4000 cubic feet per minute (cfm). During both events the test was secured. Secondary Containment was declared inoperable and Technical Specification 3.6.4.1 A.1 was entered. Secondary Containment was restored to operable status by restoring Stathnedb cyo Snefirgvuicrea tWioant etor Aa apnrde vBio wuesrley mknaonwuanll yo pineirtaiabteled ctoo nsudpitpiolyn .c oTohlien gd itroe ctht ec Cauosnetr oolf R thoeomse A eivr ecnotnsd iwtiaosn itnhge, Ecnugminueleartiinvge Safety Feiantluerae k(aEgSeF )o sfw thitec hSgeeacro rnodoamry c oCoolenrtsa ainnmd epnlatn Bt aouuxnidliaarryy .l oads. Following corrective actions including repairing the source of inleakage the surveillance testing was successfully completed on December 9, 2022. There were no consequences to the safety of the public, nuclear safety, industrial safety, or radiological safety. No radiological releases occurred due to this event. This report is made in accordance with 10 CFR 50.73(a)(2)(v)(C) for an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the Release of Radioactive Material. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV NUMBER NO. Grand Gulf Nuclear Station, Unit 1 50-416 2022 002 - 00 | PLANT CONDITIONS: Event # 1 - Mode 1, 100 percent power Event # 2 - Mode 1, 88 percent power DESCRIPTION OF EVENTS Event # 1: At 0427 on October 20, 2022, Grand Gulf Nuclear Station, Unit 1 (GGNS) was in Mode 1 at 100 percent power when a failure of the Standby Gas Treatment System Train [BH] A draw down surveillance resulted in the inoperability of Secondary Containment [NG]. During the performance of the surveillance GGNS was unable to maintain Secondary Containment pressure, as required by Technical Specification Surveillance Requirement 3.6.4.1.4, greater than or equal to 0.266 inches of water vacuum for 1 hour at a flow rate of less than or equal to 4000cfm. The test was secured. Secondary Containment was declared inoperable and Technical Specification 3.6.4.1 A.1 was entered at 0427. Secondary Containment was restored to operable status at 0520 by restoring the configuration to a previously known operable condition. Event # 2: At 1228 on October 27, 2022, GGNS was in Mode 1 at 88 percent power when a failure of the Standby Gas Treatment System Train A draw down surveillance resulted in the inoperability of Secondary Containment. During the performance of the surveillance GGNS was unable to maintain Secondary Containment pressure, as required by Technical Specification Surveillance Requirement 3.6.4.1.4, greater than or equal to 0.266 inches of water vacuum for 1 hour at a flow rate of less than or equal to 4000cfm. The test was secured. Secondary Containment was declared inoperable and Technical Specification 3.6.4.1 A.1 was entered at 1228. Secondary Containment was restored to operable status at 1240 by restoring the configuration to a previously known operable condition. REPORTABILITY This report is made in accordance with 10 CFR 50.73(a)(2)(v)(C) for an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the Release of Radioactive Material. CAUSE Direct Cause: The direct cause of these events was the cumulative inleakage of the Secondary Containment Boundary in the tested configuration. The two identified sources of inleakage to Secondary Containment are the Railroad Area Door and the Rail Bay Floor Plugs. CORRECTIVE ACTIONS 1. Replace door seals to improve the seal around the Secondary Containment doors to prevent inleakage to boundary. 2. Replace the Rail Bay Floor Plug gasket with a softer material approved by an Engineering Change. 3. Update the model work order for replacing the floor plug seals or reinstallation of floor plugs with a PMT. 4. Revise model work order to include steps to ensure the mating surface is cleaned and any sealant from past replacements. | ML22353A290
i | Unknown Unit | Main Control Room and Auxiliary Electric Room HVAC Declared Inoperable Due to Multiple Component Failures. | 12-28-2022 | 12. Licensee Contact for this LER Licensee Contact 'Phone Number (Include area code) CJ Smith, Operations Director (815) 415-2200 13. Complete One Line for each Component Failure Described In this Report Cause System Component Manufacturer Reportable to IRIS . Cause System Component Manufacturer Reportable to IRIS D VI BKR E062 y 14. Supplemental Report Expected Month Day Year I I 15. Expected Submission Date 12:1 No D Yes (If yes, complete 15. Expected S4bmission Date) I 6. Abstract (Limit to 1560 spaces, i.e., approximately 15 single-spaced typewritten lines) On May 20, 2022, both Units 1 and 2 were in Mode 1 and at 100% power. The B train of the Main Control Room Ventilation (VC) and Auxiliary Electric Room Ventilation (VE) was inoperable due to a planned maintenance window. The Main Control Room ventilation envelope consists of both the Main Control Room and the Auxiliary Electric Equipment Room. Both trains of VC and VE were required to be operable at the time of these events. On 5/20/22 at 0905 and again on 5/23/22 at 1256, various equipment on the A VCNE train tripped following train swaps to support ongoing maintenance activities. This resulted in the A VCNE train being declared inoperable. With both the A and B trains being simultaneously inoperable, the VCNE system was in a condition that could have prevented fulfillment of a safety function. The cause of the event is an inadequate breaker setting resulting in the breaker tripping prematurely on fan start. NRC FORM 366A (08-2020) Page _2_ of _5_ NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply wilh lhis mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. LICENSEE EVENT REPORT (LER) Nudear Regulatory Commission, Wastington, DC 20555-0001, or by e-maU to CONTINUATION SHEET lnlocollects.Resource@nrc.gov, and lhe 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 171h Street NW, Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1O22, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of inlonnation unless lhe document http://www. n re.gov/reading-rm/ doc-col lections/nuregs/staff/sr1 022/r3/) requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR LaSalle County Station, Unit 1 05000- 373 NUMBER NO. 2022 • 003 02 | Plant and System Identification LaSalle County Station Unit 1 and 2 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the Main Control Room Area Ventilation system (VC) and the Auxiliary Equipment Room Ventilation System (VE). Condition Prior to Event Unit(s): 1/2 Date: May 20, 2022 Time: 0905 CDT Reactor Mode(s): 1/1 Mode(s) Name: Power Operation Power Level: 100%/100% Description On May 20, 2022 the station was executing a 8 VCNE work window and in the following TS actions: 3. 7.4 A.1, restore 8 train to operable status (expires 5/23/22 at 0500) and 3.7.5 A.1, restore B train to operable (expires 6/15/2022 at 0300). The station began procedures to swap to the A train to allow repairs identified during post maintenance testing on the 8 train. After swapping to A VCNE, the A VE return fan tripped and immediately tripped after a second attempt to start. At 0905, the A train was declared inoperable for both TS 3.7.4, (CRAF) and 3.7.5 (MCR ventilation). With both trains ofVCNE inoperable, the Station entered TS 3.7.4 RA E.1 be in mode 3 within 12 hours, TS 3.7.5 RA 8.1 to verify control room area temperature less than 90 degrees once per four hours, and RA 8.2 to restore one control room area ventilation air conditioning subsystem to operable status within 72 hours. The Electrical Maintenance department performed basic troubleshooting. The fan was restarted and following sufficient run time of the A VE return fan, the A VCNE train was declared operable at 1200. TS actions 3.7.5 E.1 and 3.7.4 B.1 and 8.2 were exited. On 5/23/2022 the station began activities to swap to A VCNE to allow for system restoration on 8 VCNE. After swapping to A VCNE, the A VE return fan tripped at 1256. Operations reset the breaker and restarted the fan. The A VCNE train was declared inoperable for CRAF (3.7.4) and MCR ventilation (3.7.5). The station entered the following time clocks: 3.7.4 A.1, restore A train to operable status within 7 days, 3.7.5 RA 8.1 to verify control room area temperature less than 90 degrees once per four hours, and RA 12 to restore one control room area ventilation ~ir conditioning subsystem to operable status within 72 hours (Note: The 8 train was declared operable for CRAF on 5/20/22 at 1841 following repairs, but the 8 train re ained in the 3.7.5 MCR ventilation LCO for continued maintenance activities from the previous week that resulted in the condition discussed above on 5/23.) The B train was fully restored to operable status at 1755 on 5/23/22. TS action 3.7.5 B.1/8.2 were exited. The station declared the A train operable on 5/24/22 at 2230 after completion of an Operability evaluation and subsequent run time. Cause The cause of the event is an inadequate breaker setting resulting in the A VE Return Fan breaker tripping prematurely on fan start. I | ML22362A013
Nine Mile Point | Unit 2 | Reactor Protection System Actuation While Shutdown | 12-20-2022 | On Sunday, September 4, 2022, at approximately 1638 hours with reactor power at 0%, Nine Mile Point Unit 2 (NMP2) experienced a Reactor Protection System (RPS) actuation on Reactor Pressure Vessel (RPV) Low Water Level (Level 3) of 159.3 inches. At the time of the RPS actuation, the reactor was already in a shutdown condition with all rods fully inserted. The Level 3 condition also initiated an isolation signal to Groups 4 and 5 Primary Containment Isolation Valves (PCIVs), which were already closed. Operators took action to restore RPV water level to the normal operating band. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A). The cause of the event was due to a lack of procedural guidance in N2-SOP-101 C, Reactor SCRAM, the Control Room staff did not utilize the proper pressure reduction detail section for a planned cooldown. The Turbine Bypass Valve response to a pressure reduction strategy of 1.5 psig/second caused a rapid opening and closure of bypass valves that complicated level control resulting in Level 3 and RPS actuation. The event described in this LER is documented in the plant's Corrective Action Program (CAP) as IR 04520704. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08--2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and lnfonnation Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory I Affairs, (3150-0104), Atjn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRG may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document http·t/www nrc.govtreading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER I I • DYEA R SEQUENTIAL REV ~- I NUMBER 1- 0N O. 05000- 10 I 002 | THE ENERGY INDUSTRY IDENTIFICATION SYSTEM (EIIS) COMPONENT FUNCTION IDENTIFIER AND SYSTEM NAME OF EACH COMPONENT OR SYSTEM REFERRED TO IN THIS LER ARE ENCLOSED WITHIN [BRACKETS] L DESCRIPTION OF EVENT A PRE-EVENT PLANT CONDITIONS: Prior to the event, NMP2 was in Mode 3 (Hot Shutdown}, performing a cooldown to support a planned maintenance outage. 8_E VENT: On Sunday, September 4, 2022, at approximately 1638 hours, NMP2 experienced an actuation of the Reactor Protection System (RPS) [JC] due to Reactor Low Water Level (Level 3) while in Mode 3, Hot Shutdown. At the time of the RPS actuation, all control rods were already fully inserted and Groups 4 and 5 PCIVs were already closed. The Containment Isolation [JM] signal impacted Residual Heat Removal (RHR) [BO], Shutdown Cooling, RHR letdown to radwaste, and RHR sampling valves. Following the RPS actuation, Operators restored reactor water level utilizing level control valve CNM-LV137_ Nine Mile Point Unit 1 (NMP1) was unaffected by the NMP2 RPS actuation. On September 4, 2022 at approximately 2131 hours, this event was reported to the NRG via Event Notification #56089 pursuant to the requirements of of 10CFR50.72(b)(3)(iv)(A) Specified System Actuation of any of the systems listed in 10 CFR50.7 2(b )(3)(iv)(B). C. INOPERABLE STRUCTURES, COMPONENTS, OR SYSTEMS THAT CONTRIBUTED TO THE EVENT: None. D. DATES AND APPROXIMATE TIMES OF MAJOR OCCURENCES AND OPERATOR ACTIONS: September 4, 2022: 1506 - NMP2 entered Mode 3 on a planned reactor SCRAM to enter a maintenance outage. 1512 -Operators manually close the Main Steam Line (MSL) drain system due to reactor pressure lowering. 1534 -Operators suspected leak by past Feedwater Level Control Valve, Feedwater Pump 'B' Level Control Valve (2FWS-LV1 OB) and subsequently manually closed the blocking valve which stabilized reactor water level. 1556 - Reactor water level continued to rise. Operators suspected leak by past High Pressure - Low Feedwater Level Control Valve (2FWS-LV55B}, and subsequently manually isolated the valve which stabilized reactor water level. NRG FORM 366A (08-2020) Page 2 of 4 | ML22362A073
Quad Cities Nuclear Power Station | Unit 2 | Manual Scram Due to Feedwater Regulator Valve Failure Increasing Reactor Water Level | 12-30-2022 | On November 4, 2022, Unit 2 was at 100% power with no surveillance activities in progress that contributed to the event. At 1359 hours the 2B Feedwater Regulating Valve (FRV) failed in the open position and locked up, causing an increase in reactor vessel water level. Attempts at manual control of the feedwater system to decrease level were not successful. At 1400, a manual scram was inserted in accordance with operating procedures. All control rods inserted, and the scram was uncomplicated. The cause of this event is foreign material partially or completely blocking hydraulic oil flow internal to a servo valve in the 2B FRV that caused it to move rapidly to the fully open position. This caused Unit 2 reactor vessel water level to rapidly rise until it reached the established scram criteria of +44 inches, at which time a manual scram was inserted. This report is being submitted in accordance with 10 CFR 50.73(a)(2)(iv)(A) for an event or condition that resulted in manual or automatic actuation of the reactor protection system including a reactor scram. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira submission@omb.eoo.gov. The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1 022/r3/) requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Quad Cities Nuclear Power Station Unit 2 05000- 265 YEAR SE N Q U U M E B N E T R IA L R N E O V . 2022 - 003 00 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Manual Scram Due to Feedwater Regulator Valve Failure Increasing Reactor Water Level CONDITION PRIOR TO EVENT Unit: 2 Event Date: November 4, 2022 Event Time: 1400 CDT Reactor Mode: 1 Mode Name: Power Operation Power Level: 100% No structures, systems or components were inoperable at the start of this event that contributed to the event. A. DESCRIPTION OF EVENT On November 4, 2022, Unit 2 was operating at 100% power. There were no surveillances in progress that contributed to the event. At 1359 hours, main control room (MCR) alarms indicated the 28 Feedwater (FW) [JB] Regulating Valve (FRV) [FCV] failed in a manner that drove it to an open position and caused the valve to lock up. As a result, reactor vessel water level began to rise. The other FRV, 2A was in service and responded as designed anq automatically closed to control reactor water level. With the 2A FRV fully closed, reactor water level continued to rise and when the level reached the established scram criteria of +44 inches, the Unit Supervisor directed a manual scram in accordance with station operating procedures. The scram was inserted at 1400 hours. All control rods were inserted, and the scram was uncomplicated. The NRC was notified via ENS Report 56210 at 1710 EDT on November 4, 2022. Following replacement of the 28 FRV servo valve [FSV], Unit 2 returned to power operations on November 6, 2022. NRG FORM 366A (08-2020) Page_2_ of _4_ | ML22364A273
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Inadequate Protection Devices for DC Motor Field Shunt Cables Through Separate Fire Areas | 01-10-2023 | During an extent of condition review for unprotected circuits, the James A. FitzPatrick Nuclear Power Plant (JAF) staff identified three cables for which a postulated fire event could potentially short circuit and cause secondary cable damage. The main circuit breakers in the motor control center compartment do not provide adequate protection of the shunt field circuit cable. This condition affects the DC motors to 27MOV-123, torus exhaust isolation bypass valve, 23MOV-14, HPCI turbine steam inlet isolation valve, and 23MOV-24, HPCI full flow test return to condensate storage isolation valve. The cables for these circuits are routed thru fire areas in South Cable Tunnel, Reactor Building Eastside, and Reactor Building West Crescent; where safe shutdown equipment could be affected by this condition. The cause of the condition is that the original plant design, prior to 10 CFR 50 Appendix R, did not include overcurrent protection for DC motor shunt field cables in all applicable Safe Shutdown Analysis circumstances. Compensatory actions were established for the affected Fire Zones and modifications were completed for the affected circuits. NRC FORM 366 (08-2020) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments CONTINUATION SHEET regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 – 333 NUMBER N0. 2021 – 001 – 01 | Background The James A. FitzPatrick Nuclear Power Plant (JAF) 10 CFR 50 Appendix R Safe Shutdown Analysis is based on the occurrence of a single fire. The only failures that are considered are those directly attributable to the fire, and spurious operations that can be postulated to occur as a result of the fire. No other concurrent failures are assumed to occur (i.e., single failure). Fire areas are established to meet the separation requirements of Section III.G of Appendix R for safe shutdown systems. The fire areas at JAF are further sub-divided into fire zones. It is postulated that a fire in one fire area could cause a short-circuit, cause overcurrent and overheat cables, then produce secondary damage to adjacent cables in other fire areas where the cables are routed. Fuses in electrical circuits prevent this type of propagation. Secondary cable failures are outside the assumptions of the 10 CFR 50 Appendix R Safe Shutdown Analysis. In a direct current (DC) shunt motor, the armature and field (shunt) windings are connected in parallel. The shunt (field) windings of a DC shunt motor are made of smaller gauge wire, but they have many more turns than a series-wound DC motor. The high number of turns allows a strong magnetic field to be generated, but the smaller gauge wires provide a high resistance and limit the current flowing through the shunt coil. Event Description On August 24, 2021, an extent of condition evaluation from the condition reported by LER: 2020-002, identified three additional circuits, vulnerable to a potential hot short condition impacting secondary fire areas. The three circuits identified are associated with DC Motors with field shunt cables that transverse multiple fire areas. The feeder breaker protects the armature cables but the smaller 12 AWG (American Wire Gauge) field shunt cables are inadequately protected by the feeder breaker. In the event of a fire-induced hot short, the potential exists, based on the available fault current, cable size, and characteristics of the protective device, for the shunt cable to be overheated. This situation has the potential to cause secondary cable failures that are outside the assumptions of the 10 CFR 50 Appendix R Safe Shutdown Analysis. This condition was reported to the NRC on August 24, 2021 (ENS 55427) per 10 CFR 50.72(b)(3)(ii)(B). The required actions of the Technical Requirement Manual (TRM) 3.7.M, Fire Barrier Penetrations, were established for the affected fire areas. Page 2 of 4 | ML23010A180
Cooper Nuclear Station 05000 298 1 OF 4 | Unknown Unit | Actuation of Reactor Protection System Initiates a Full Reactor Scram | 01-11-2023 | On November 12, 2022, during plant start up from Refueling Outage 32, operations personnel commenced a surveillance for High Pressure Coolant Injection (HPCI) Beginning of Cycle Testing. While performing the test, a HPCI injection valve unexpectedly opened, injecting water into the reactor vessel. The injected water increased reactivity and the Intermediate Range Monitors initiated a reactor scram. As such, the test was stopped. In April 2021, an undervoltage relay for the valve had been removed due to reliability concerns with that specific type of relay - if the relay would fail, it would cause the valve to fail. Investigation revealed that the modification process to remove the undervoltage relay did not identify a change was required to the HPCI surveillance procedure. There was no impact on nuclear safety, plant reliability, radiological safety, or industrial safety. This event was reported under Event Notification 56220 on November 12, 2022. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: (08-2020) 08/31/2023 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory (See NUREG-1022, R.3 for instruction and guidance for completing this form Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, https://www.nrc.gov/readinq-rm/doc-collections/nureqs/staff/sr1022/r3/) Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LERNUMBER YEAR SEQUENTIAL REV Cooper Nuclear Station 05000- 298 NUMBER NO. 2022 - 003 00 | PLANT STATUS Cooper Nuclear Station was in Mode 2, Startup, at 2 percent power at the time of the event on November 12, 2022. BACKGROUND The Reactor Protection System (RPS) provides timely protection against the onset and consequences of conditions that threaten the integrity of the fuel barrier and the reactor coolant pressure boundary. The RPS includes sensors, relays [EIIS: RL Y], bypass circuits, and switches that are necessary to cause initiation of a reactor [EIIS: RPV] scram. The Intermediate Range Monitors (IRM) generate a trip signal that can be used to prevent fuel damage resulting from abnormal operational transients that occur while operating in the intermediate power range. The Emergency Core Cooling System (ECCS) [EIIS: BJ, BM, BO] control and instrumentation initiates appropriate response from the various cooling systems so fuel is adequately cooled under abnormal and accident conditions. The controls and instrumentation for the ECCS are identified as that equipment required for the initiation and control of the High Pressure Coolant Injection System (HPCI), the Automatic Depressurization System, the Core Spray System, and the Low Pressure Coolant Injection System. When actuated, the HPCI system pumps water from either the emergency condensate [EIIS: SD] storage tanks (ECST) or the suppression chamber to the reactor vessel via the feedwater pipeline. 250 volt direct current (VDC) provides motive power and 125 VDC provides control power for pumps [El IS: P] and valves [EIIS: V]. At the beginning of the operating cycle, HPCI is tested to assess operational readiness prior to exceeding 165 pounds per square inch gauge. The surveillance aligns the system in the test return flow lineup, by placing HPCI-MO-21 (test bypass valve to ECST) and HPCI-MO-24 (ECST test line shutoff valve) in the OPEN position, and HPCI-MO-19 (injection valve) in the CLOSED position. 250 VDC power to the three valves is removed to prevent operation of the valves during the surveillance. A test switch is used to initiate the HPCI response. The HPCI system logic provides a CLOSE signal to HPCI-MO-21 and HPCI-MO-24, and an OPEN signal to HPCI-MO-19 via relay contacts. After HPCI system flow is verified and HPCI component functions are verified to have operated correctly, the test switch is placed to OFF, de-energizing the relays and the HPCI initiation signal is reset de-energizing other relays. 250 VDC power to the HPCI- MO-21, HPCI-MO-24, and HPCI-MO-19 valves is then restored. EVENT DESCRIPTION On November 12, 2022, during plant start up from Refueling Outage 32 (RE32), operations personnel commenced surveillance procedure HPCI Beginning of Cycle Test. The purpose of this surveillance is to | ML23011A111
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Mode Switch Failed to Bypass Low Main Steam Line in Mode 2 Resulting in MSIV and RPS System Actuation | 01-31-2023 | On September 26, 2022, at 0306 EDT, while the reactor was sub-critical and inserting control rods for a planned refueling outage, James A. FitzPatrick Nuclear Power Plant (JAF) experienced a reactor scram and Group 1 isolation on low steam line pressure logic. As a result of Group 1 isolation signal seven out of eight Main Steam Isolation Valves (MSIV) isolated. ‘A’ outboard MSIV (29AOV-86A) failed to isolate on the initial signal. The Reactor Protection System (RPS) actuated, resulting in all control rods being fully inserted, and manual actuation of RCIC. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). The RPS actuation was determined to be a failure of the reactor mode switch (05A-S1) to enact the logic required to bypass MSIV isolation on low main steam line pressure and RPS actuation on MSIV closed position. Operating Procedure OP-65 was revised to ensure proper switch contact logic is validated by redundant indications. NRC FORM 366 (08-2020) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments CONTINUATION SHEET regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV James A. FitzPatrick Nuclear Power Plant 05000 – 333 NUMBER N0. 2022 – 002 – 01 | Background The Reactor Mode Switch (05A-S1) controls the operating Plant Mode of the Reactor. It has four positions, Shutdown, Refuel, Start & Hot Stby, and Run. The pistol grip locking handle assembly drives 4 banks of contacts with a total of 64 contacts. The Mode Switch contacts enact the plant parameter logic required by the Plant Mode for Reactor Protection System (RPS) [EIIS identifier: JE], Reactor Manual Control System [JD], Primary Containment Isolation System (PCIS) [JM], Refuel Interlocks [DF], Neutron Monitoring Systems [IG], and Plant Process Computer [ID] to ensure the correct setpoints and circuits are active. Event Description On September 26, 2022, James A. FitzPatrick Nuclear Power Plant (JAF) was reducing power for a planned plant shutdown for a refuel outage. At the time of the Scram, no structures, components, or systems were inoperable at the start of the event and contributed to the event. Control rods [AA] were being inserted and reactor power and pressure was decreasing. At 0230, operators placed the mode switch (05A-S1) in Startup/Hot Standby (Mode 2). At 0306, an unplanned Scram signal was received due to a Group 1 isolation on low main steam line [SB] pressure. All control rods were fully inserted. Main Steam Isolation Valves (MSIV) isolated except ‘A’ outboard MSIV (29AOV-86A) failed to close. PCIS isolated valves in multiple systems according to group 1 isolation. When the PCIS was reset, 29AOV-86A was then manually isolated. At 0530, Operators made the decision to place Reactor Core Isolation Cooling (RCIC) system [BN] in service to augment pressure and level to assist in transition to feedwater [SJ] and condensate [SD] systems. At 0751, RCIC was shut down and in a standby lineup. The NRC was notified of this event at 0541 by ENS 56119 in accordance with 10 CFR 50.72(b)(2)(iv)(B) RPS actuation while critical and 10 CFR 50.72(b)(3)(iv)(A) for systems actuation. A reactor engineering analysis of reactor criticality was performed for the period of time prior to the event, and it was determined that the reactor was sub-critical. On October 4, 2022, ENS 56119 was updated to retract 10 CFR 50.72(b)(2)(iv)(B). The ‘A’ outboard MSIV (29AOV-86A) failed to close, but the safety function for ‘A’ main steam line isolation was successful because the inboard MSIV isolated successfully. Failure of the MSIV to close was documented and evaluated under IR 04524581. Page 2 of 4 | ML23031A225
Grand Gulf Nuclear Station | Unit 1 | Manual Reactor SCRAM due to a loss of the Condensate and Feed Water System | 02-16-2023 | At 2058 on December 19, 2022, Grand Gulf Nuclear Station, Unit 1 experienced a trip of Condensate Booster Pump A. At 2101, Reactor Feedwater Pump A tripped, and the reactor was manually scrammed. All control rods were fully inserted into the core. At 2104, Reactor Feedwater Pump B tripped. At 2121 High Pressure Core Spray (HPCS) was manually injected to maintain reactor water level. At 2126 Reactor Feedwater Pump A was successfully restarted. Following the reactor SCRAM, the HPCS system was used to maintain reactor water level. The direct cause of the SCRAM was the Heater Drain Tank (HOT) Level Control Valves were not capable of responding quickly enough to mitigate the HOT level oscillations during the transient caused by Condensate Booster Pump Trip and subsequent Fast Detent. There were no consequences to the safety of the public, nuclear safety, industrial safety, or radiological safety. No radiological releases occurred due to this event. This report is made in accordance with 10 CFR 50.73(a)(2)(iv)(A) for any event or condition that resulted in manual of automatic actuation of any system listed in paragraph 10 CFR 50.73 (a)(2)(iv)(B). The Reactor Protection System including reactor SCRAM or trip is included in 10 CFR 50.73 (a)(2)(iv)(B). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 12/31/2023 (01-10-2023) Estimated burden per response to comply wnh this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and lnfonmation Collection Branch (T-6 A10M), U.S Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of lnfonmation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 72517th Street NW, Washington, DC 20503; e-mail. crra sutmissl()n@omb.eop.gov. The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document https :// VNIW .n re. gov /reading-rm/doc-collectionsln ur egs/staff /sr1 022/r3/) requesting or requiring the colloction displays a currently valid 0MB conlrol number 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ~ 050 YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 >-------< 416 NUMBER NO. 2022 - 003 -00 □ 052 | PLANT CONDITIONS: Mode 1 , 78 percent power DESCRIPTION OF EVENTS At 2058 on December 19, 2022, while the plant was operating at 100 percent reactor power, Condensate Booster Pump (CBP)[SD] A tripped. Control Room Operators entered the Feedwater System Malfunction Off-Normal Event Procedure (ONEP) and reduced core flow to 70 million pound-mass per hour. While performing steps of the ONEP operators identified Reactor Feedwater Pump "A" and "B" suction pressures were rapidly lowering. At 2101, Reactor Feedwater Pump "A" tripped on low suction pressure. A recirc flow control valve runback occurred as designed. Reactor water level continued to lower because of a reduction in feed flow. At approximately 17 inches of water and trending down, the At-The-Controls Operator placed the Reactor Mode Switch in Shutdown at 2101. At 2121 High Pressure Core Spray (HPCS) [BG] was manually injected to maintain reactor water level. The manual SCRAM on low reactor water level resulted from constricting Feed Flow when the Heater Drain Tank Level Control Valves closed, which is a plant response that should have been found in the results of calculation for the "Condensate and Feedwater Transient Analysis" (CFTA ). This oversight, along with other issues found in the CFT A calculation led to the Root Cause of "Transients caused by CBP Trip have not been adequately analyzed", and this condition will be corrected by performing an analysis to determine the best corrective modification and implementing that modification during the next refueling outage. REPORT ABILITY This report is made in accordance with 10 CFR 50.73(a)(2)(iv)(A) for any event or condition that resulted in manual of automatic actuation of any system listed in paragraph 10 CFR 50. 73 (a)(2)(iv)(B). The Reactor Protection System including reactor SCRAM or trip is included in 10 CFR 50.73 (a)(2)(iv)(B). CAUSE Direct Cause: Heater Drain Tank (HOT) Level Control Valves were not capable of responding quickly enough to mitigate the HOT level oscillations during the transient caused by Condensate Booster Pump Trip and subsequent Fast Detent. Root Cause: Transients Caused by Condensate Booster Pump Trip have not been adequately analyzed. CORRECTIVE ACTIONS 1. Replace CBP A Motor - The CBP A Motor has been replaced. 2. Corrective Action to Prevent Recurrence (CAPR) - Modification will be performed to implement long term solutions as determined to analyze the transient effects of the following on Feed Flow and Post Extended Power Uprate (EPU) and Maximum Extended Load Line Limit Analysis Plus (MELLA+) conditions: Condensate Pump trip, CBP trip, HOP trip. Develop potential solutions to solve latent design issues in Feed Flow transient response. NRG FORM 366A (01-10-2023) Page 2 of 3 | ML23047A547
i | Unknown Unit | : | 02-22-2023 | On January 5, 2023, at 1242, with the reactor in Mode 1 and at 98% rated thermal power, an automatic reactor trip occurred due to lowering water level in the reactor vessel. The High Pressure Core Spray (HPCS) and Reactor Core Isolation Cooling (RCIC) systems were manually initiated to restore and control water level in the reactor vessel. The direct cause of the reactor trip was attributed to the failure of the Digital Feedwater Control System (DFWCS) to control reactor water level, following corrective maintenance on one of the power sources to the system. A latent configuration control issue in the system caused unexpected indication losses during the maintenance. Upon re- energizing the power source, two component failures in DFWCS, and an overloaded communications network, caused the system to lower reactor water level, which resulted in a reactor trip. The failed components were replaced, and the reactor was re-started on January 8, 2023. This event is being reported in accordance with 10 CFR 50. 73(a)(2)(iv)(A) due to an automatic Reactor Protection System (RPS) actuation and the manual initiation of two Emergency Core Cooling System (ECCS) systems. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 12/31/2023 (01-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the Information Services Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB CONTINUATION SHEET reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: (See NUREG-1022, R.3 for instruction and guidance for completing this form oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of infonmation unless the document requesting or requiring the collection displays http://www.n r e.gov /reading-rm/doc-collections/nu regs/staffl s r1 022/r3/ a currently valid 0MB control number. 2. DOCKET NUMBER ______3 _. _LE_R_N_U_M. .B_ E_R_ ____ 1- FACILITY NAME 050 SEQUENTIAL REV YEAR NUMBER NO. Perry Nuclear Power Plant 00440 2023 001 00 □ 052 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. EVENT DESCRIPTION On January 5, 2023, planned corrective maintenance was being performed on a voltage-regulating transformer [XFMR] which is one of the redundant power sources to the Digital Feedwater Control System (DFWCS) [SJ]. When the transformer was de-energized for the work to be performed, Operators received some unexpected losses of DFWCS indication, resulting in the loss of all of the DFWCS Operator interface screens. Reactor power, pressure and level remained stable at this time, indicating that DFWCS maintained control. Based on the plant remaining stable, a decision was made to continue with the work on the transformer. Upon the post-maintenance energization of the voltage regulating transformer, a reactor water level transient of three inches occurred, and then stabilized. A walkdown of DFWCS identified a failed level control processor module [CPU] and a degraded power supply [JX]. The decision was made to perform a Nodebus Check (online diagnostic test) to restore the lost indication in the system. Due to the loss of all the DFWCS interface screens, the Operators did not recognize that the system demanded zero level to the DFWCS controllers during a re-sync of the level control processor modules. This zero demand signal was sent to the Reactor Feed Pump Turbines (RFPTs) [Pl governor [65] thereby causing the RFPTs to reduce output to idle and minimum flow. The reduced feedwater flow resulted in the reactor water level lowering to Level 3, which caused an automatic reactor trip at 1242. Operators then manually initiated two Emergency Core Cooling Systems (ECCS), High Pressure Core Spray (HPCS) [BG] and Reactor Core Isolation Cooling (RCIC) [BN] to restore and control reactor water level. The Motor Feed Pump became available at 1251 and was started at 1253 to control reactor water level. At 1254, the Motor Feed Pump was controlling reactor water level through DFWCS. The Condition Report investigation revealed that the cause of the reactor trip was attributed to the failure of a DFWCS level control processor module along with a degraded power supply, concurrent with a DFWCS network communications overload. Additionally, a configuration control issue was found with some of the DFWCS media translators [CNV] being connected to the incorrect power source. This resulted in the unexpected loss of additional DFWCS workstations and indications to the Operators when power was removed for the maintenance. It also caused increased DFWCS network communication traffic, due to the loss of interface screens hindering the Operator's ability to acknowledge alarms. NRC notification (EN 56298) was made on January 5, 2023, at 1539, under 10 CFR 50.72(b)(2)(iv)(A) - ECCS Injection and 10 CFR 50.72(b)(2)(iv)(B) - RPS Actuation. The faulty DFWCS power supply and the failed secondary control processor module were replaced. The configuration control issue was also corrected with the media translators. Post maintenance testing for DFWCS was performed satisfactorily, and a successful reactor startup was completed on January 8, 2023. CAUSES OF EVENT The direct cause of the automatic reactor trip was attributed to the failure of one of the DFWCS level control processor modules, along with an intermittent power supply failure, and combined with a network traffic overload which overall resulted in a zero percent output demand signal to the Reactor Feed Pump Turbine (RFPTs) governor, causing the RFPTs to reduce speed to idle and minimum flow output. Page 2 of3 | ML23053A083
Vogtle Electric Generating Plant | Unit 1 | Partial Loss of Offsite Power results in Emergency Diesel Generator and Auxiliary Feedwater Actuation | 02-27-2023 | On January 03, 2023 at 2259 EST, with both Unit 1 and Unit 2 in Mode 1 and 100 percent power, an automatic actuation of the Unit 1 Bravo and the Unit 2 Alpha Emergency Diesel Generator Systems and associated Auxiliary Feedwater Systems occurred. These systems actuated due to the failure of a lightning arrestor associated with the Unit 1 Bravo Reserve Auxiliary Transformer. This resulted in the upstream breaker to the Unit 1 Bravo and Unit 2 Alpha Reserve Auxiliary Transformers opening, causing the Unit 1 Bravo and Unit 2 Alpha emergency electrical buses to de-energize and the automatic start of the associated Emergency Diesel Generator and Auxiliary Feedwater Systems. The units remained in Mode 1 and 100 percent power, and the operating crew performed as expected. The lightning arrestor was replaced and the Reserve Auxiliary Transformers were returned to service. Due to the automatic actuation of the Emergency Diesel Generator and Auxiliary Feedwater Systems on each unit, this event is being reported under 10 CFR 50.73(a)(2)(iv)(A). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 12/31/2023 (01-10-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 YEAR SEQUENTIAL REV NUMBER NO. Vogtle Electric Generating Plant, Unit 1 00424 2023 052 - 001 - 00 | NARRATIVE A. Event Description On January 3, 2023 at 2259 EST, with both Unit 1 and Unit 2 in Mode 1 and 100 percent power, a partial loss of offsite power occurred due to a failed Hubbell MVN lightning arrestor [LAR] on the Unit 1 Bravo Reserve Auxiliary Transformer (RAT)[XFMR]. This resulted in the upstream breaker [BKR] to the Unit 1 Bravo and Unit 2 Alpha Reserve Auxiliary Transformers opening, causing the Unit 1 Bravo and Unit 2 Alpha emergency electrical buses to de-energize and the automatic start of the associated Emergency Diesel Generator (EDG)[EK] and Auxiliary Feedwater Systems (AFW)[BA]. There were no Structures, Systems, or Components (SSCs) that were out of service at the beginning of the event that contributed to the event. Due to the actuation of the EDG and the AFW systems this event is being reported in accordance with 10 CFR 50.73(a)(2) (iv)(A). B. Cause of Event The cause of the event was a failure of the lightning arrestor on the Unit 1 Bravo Reserve Auxiliary Transformer. C. Safety Assessment When the lightning arrestor failed, the upstream breaker for offsite power opened. This resulted in one safety-related electrical bus on each unit becoming de-energized. The EDGs associated with the affected electrical buses started automatically and re-energized the electrical buses. The AFW systems started as a result of the electrical bus being de- energized. All the systems operated as designed. The operating crew responded as expected. The event was within the analysis of the Updated Final Safety Analysis Report, Chapter 15. There were no safety consequences as a result of this event. D. Corrective Actions The lightning arrestor for the affected transformer was replaced. E. Previous Similar Events None. | ML23058A432
Clinton Power Station | Unit 1 | Grid Fault Results in Switchyard Breaker Trips and Reactor Scram | 03-31-2023 | On 1/31/23, at 2343 CST, while operating at approximately 100% power, a phase-to-phase fault occurred on a 345 KV transmission line approximately 16 miles from Clinton Power Station (CPS). Gas Circuit Breaker Generator Output Breakers (GCBs) 4510 and 4514 tripped open to clear the fault. GCB 4510 failed to trip open properly, resulting in actuation of the GCB 451 O breaker failure protective relay, tripping open GCB 4506 and disconnecting the main generator from the grid. This resulted in a turbine trip and automatic reactor scram. The root cause of the failure of GCB 4510 to properly open, and subsequent trip open of GCB 4506, was due to corrosion of the GCB 4510 air system charging valve. Corrective actions taken and planned include: repairs to the 345 KV transmission line involved in the event, developing and implementing an improved Preventive Maintenance (PM) strategy for switchyard breakers, working with the switchyard operator to perform twelve-year breaker overhaul/replacement on affected GCBs/345 KV switchyard breakers, and providing training on effective design attribute review performance. There was no impact to the health and safety of the public or plant personnel from this event. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED.BY 0MB: NO. 3150-0104 EXPIRES: 12/31/2023 (01-10-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET ( lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-mi/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currenlly valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 SEQUENTIAL REV YEAR Clinton Power Station, Unit 1 00461 NUMBER NO. □ 052 ' 2023 - 001 - 00 | PLANT AND SYSTEM IDENTIFICATION General Electric -- Boiling Water Reactor, 3473 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in text as [XX]. EVENT IDENTIFICATION Grid Fault Results in Switchyard Breaker Trips and Reactor Scram A. Plant Operating Conditions Before the Event Unit: 1 Event Date: January 31, 2023 Event Time: 2343 CST Mode: 1 Mode Name: Power Operation Reactor Power: 100 B. Description of Event On January 31, 2023, at 2343 CST, while operating at approximately 100% power, a phase-to phase fault occurred on a 345 KV transmission line approximately 16 miles from Clinton Power Station (CPS). In response to the fault, Gas Circuit Breaker Generator Output Breakers (GCBs) 4510 and 4514 [FK:BRK] tripped open to clear the fault. GCB 4510 failed to trip open properly, resulting in actuation of the GCB 451 O breaker failure protective relay, tripping open GCB 4506 [FK:BRK] and disconnecting the main generator [EL:GEN] from the grid. This resulted in a turbine [TA:TRB] trip and automatic reactor [RCT] scram. Operators placed the reactor mode switch in shutdown and completed the scram response actions. All control rods fully inserted. As noted above, GCB 4514 tripped open successfully. However, breaker failure protective relaying was actuated due to detection of current flow through GCB 4510 after it received a trip open signal. This resulted in tripping open GCB 4506 to clear the fault. C. Cause of the Event When a GCB breaker opens, the breaker control circuits energize trip coils. Energizing the trip coils creates a magnetic force that releases a trip latch, allowing spring energy to open an air pilot valve. The pilot valve allows air from the associated air receiver to flow into the breaker's operating piston/operating cylinder. The compressed air forces the operating piston to stroke the operating rod, which is connected to the interrupter. In addition to opening the interrupter, the operating piston compresses the breaker's closing springs as it travels. The operating piston overtravels slightly allowing the breaker closing latch to cycle and capture the operating rod in the open position against closing spring pressure. The breaker will remain open until the closing latch is released by the associated closing coils. In this event, GCB 4510 failed to latch open. | ML23094A112
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Primary Containment Isolation System Isolation due to Initiation of Main Condenser Fire Protection Foam System | 04-19-2023 | At 0105 EST on February 19, 2023, with the James A. FitzPatrick Nuclear Power Plant (JAF) at 100 percent power, a High Main Steam Line Radiation signal initiated a primary containment isolation valve closure signal in multiple systems. During the performance of FPP-3.25 “Fire Protection Manifold #5 Sprinkler System Main Drain and Water Flow Alarm Test”, the main condenser foam system was inadvertently initiated, resulting in firefighting foam intrusion into a sump which migrated to the main condenser and eventually to the reactor coolant system. The cause was determined to be a human performance related error during testing. Corrective actions include conducting human performance training and evaluations and hardening of the impacted plant sump system. NRC FORM 366 (08-2020) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (03-14-2023) Estimated burden per response to comply with this mandatory collection request: 80 LICENSEE EVENT REPORT (LER) hours. Reported lessons learned are incorporated into the licensing process and fed CONTINUATION SHEET back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 YEAR SEQUENTIAL REV NUMBER NO. James A. FitzPatrick Nuclear Power Plant 05000333  052 2023 – 001 – 00 | Background James A. FitzPatrick Nuclear Power Plant (JAF) has two firefighting foam systems: the main condenser foam system [EIIS identifier: KQ], which is the subject of this event, and the High Pressure Coolant Injection (HPCI) foam System. The purpose of main condenser foam system is to provide fire extinguishment for the Main Condenser Liquid Holding Pit. The foam system was provided on the basis that the oil from any major turbine oil leak would drain to the pit and a foam system would be effective in fire extinguishment in a confined pit area. Inside the same building, the turbine building equipment drain sump [WK], also known as the low conductivity sump, is designed to collect, and hold leakage from turbine building equipment drains. During power operation, the low conductivity water in the sump is drawn into the main condenser [SD] with vacuum drag. This water is combined with main condenser condensate water and returned to the Reactor Coolant System (RCS) [AB]. Two pumps are also available to move water out of the sump to the condenser or radwaste treatment. Event Description On February 18, 2023, at 23:00, with the JAF at 100 percent power, a scheduled test began for FPP-3.25, Fire Protection Manifold #5 Sprinkler System Main Drain and Water Flow Alarm Test. The purpose of the test is to demonstrate water supply is available to the sprinkler system supplied from Manifold #5 and to demonstrate operability of the waterflow alarm. The step in the procedure being performed by the control room stated to “Press Acknowledge button at Panel FPP and verify Red CONDENSER PIT FOAM SYS light is on, and alarm bell is off”; however, the operator depressed the main condenser foam system initiation pushbutton instead of the acknowledge pushbutton, at 00:42 on February 19. The foam system injected, per design, into the Main Condenser Liquid Holding Pit and a foam/water mixture migrated to the nearby turbine building equipment drain sump. The main condenser vacuum drag drew the foam/water mixture out of the sump into the main condenser hotwell which was then introduced into the RCS via the condensate and feedwater system [JB]. At 01:06, Main Steam Line Hi-Hi radiation actuated Primary Containment Isolation System (PCIS) [JM] Group 1 isolation signal. Reactor Water Recirculation (RWR) [AD] sample valve 02-2AOV-39 and 02-2AOV-40 closed. The isolation signal also isolated the normally closed Main Steam Line Drain System [SB] and Condenser Air Removal System [SH]. At 01:14, Operators isolated the high conductivity sump vacuum drag flow path and aligned it to radwaste. This stopped the intrusion of high conductivity foam into the condenser. Conductivity, off-gas radiation, and main steam line radiation then returned to pre-transient values. This event was reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) via ENS 56373. This report is submitted in accordance 10 CFR 50.73(a)(2)(iv)(A). Page 2 of 3 | ML23109A246
LaSalle County Station | Unit 2 | Automatic Actuation of Reactor Protection System (RPS) | 05-02-2023 | At 0910 CST on March 4, 2023, with Unit 2 in Mode 4 at O percent power, an actuation of a reactor scram on low charging water header pressure occurred during restoration from ASME Class 1 System Leakage Test conditions. All control rods were already fully inserted prior to the receipt of the scram signal. The scram occurred due to a valid signal and all systems responded as expected. Low charging water header pressure is not required to be operable in Mode 4 but is active if not bypassed. The scram signal should have remained bypassed per station procedures. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 12/31/2023 (01-10-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira submission@omb.eop.gov. The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is nol required lo respond lo, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1 022/r3/l requesting or requiring lhe collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER (cid:127) 050 SEQUENTIAL REV YEAR NUMBER NO. LaSalle County Station, Unit 2 (cid:143) 374 052 - - 2023 003 00 | LaSalle County Station Unit 2 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the Reactor Protection System (RPS). RPS initiates a rapid insertion of all the control rods (scram) when monitored variables exceed their pre-established limits, neutron flux instrumentation becomes inoperable, or a manual scram signal is inserted by the operator. In addition, the setpoints, power sources, and controls and instrumentation are arranged in such a manner as to preclude spurious scrams. Condition Prior to Event Unit(s): 2 Date: March 4, 2023 Time: 0910 CST Reactor Mode(s): 4 Mode(s) Name: Cold Shutdown Power Level: 0% Description Following completion of required ASME Class 1 System Leakage Testing, actions were taken to commence reactor depressurization. As governed by the testing procedure, the Control Rod Drive (CRD) Charging Water Stop Valve was closed. The Low Charging Water Header Pressure scram signal was verified to be bypassed at the start of the Hydrostatic Test. The scram signal was then restored during the transition into scram time testing. With the CRD Charging water Stop valve closed and the Low Charging Water Header Pressure scram signal not bypassed, reactor depressurization resulted in an RPS Scram on Low Charging Water Header Pressure. At the time of the Scram, the unit was in Mode 4 with all rods inserted. The Low Charging Water Scram Signal is not required in Mode 4 for Rod Cycling and the Scram signal should have remained bypassed, in accordance with station procedures. Reportability and Safety Analysis The Low Charging Water Pressure Scram is only required to be enabled in Mode 2 and Mode 5 to ensure that a reactor scram is initiated before Scram capability is compromised during low reactor pressure operations. At the time of the event the reactor was in Mode 4 with all rods inserted. Therefore, there was no increased risk to the public as a result of this event. The event is reportable under 10 CFR 50. 72(b )(3)(iv)(A) as an event or condition that results in the valid actuation of the Unit 2 RPS system. An ENS report was made to the NRC at 1642 on March 4, 2023 (EN# 56389). Safety System Functional Failure Review The system equipment responses did not result in a safety system functional failure (SSFF) as defined in accordance with NEI 99-02, "Regulatory Assessment Performance Indicator Guideline." The RPS logic safety function was satisfied by its actuation for designed inputs. | ML23122A016
cooper nuclear station | Unknown Unit | Valve Test Failures Result in Condition Prohibited by Technical Specifications | 05-08-2023 | On March 7 and March 8, 2023, two Target Rock safety relief valve (SRV) pilot assemblies, removed during Refueling Outage 32, failed to lift within Technical Specifications (TS) lift setpoint requirements. The pressure setpoint of the first failed pilot assembly was 1080 psig; the SRV pilot assembly lifted at 1166.4 psig. The pressure setpoint of the second failed pilot assembly was 1100 psig; the SRV pilot assembly lifted at 1186.1 psig. Three subsequent lifts were performed for the failed SRV pilot assemblies and the results were within the TS pressure setpoint tolerance. The cause of the failure was determined to be corrosion bonding. Although the setpoint lift pressures of the SRV pilot valve assemblies exceeded TS requirements, an analysis of the event concluded the thermal limits, and American Society of Mechanical Engineers overpressure transients, did not exceed allowable limits. Public safety was not at risk. Safety of plant personnel, and plant equipment, was not at risk. A TS Amendment to TS 3.4.3 will be submitted that will address the failure to meet the TS criteria for the Target Rock two-stage SRVs. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (03-14-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by CONTINUATION SHEET email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 (See NUREG-1022, R.3 for instruction and guidance for completing this form 17th Street NW, Washington, DC 20503; email: oira submission@omb.eop.gov. The NRC may not http://www.nrc.gov/readinq-rm/doc-collections/nureqs/staff/sr1022/r3/} conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. FACILITY NAME 2. DOCKET NUMBER J. LEK"'' X 050 YEAR SEQUENTIAL REV Cooper Nuclear Station 00298 NUMBER NO. 052 2023 - 001 - 00 | PLANT STATUS Cooper Nuclear Station was in Mode 1, Power Operation, at 100 percent power, when the event was discovered, i.e., March 8, 2023. BACKGROUND The pressure relief system includes three American Society of Mechanical Engineers (ASME) code safety valves (SV) [EIIS: SB] and eight safety relief valves (SRV) [EIIS: RV], all of which are located on the main steam lines [EIIS: SB] within the drywell [El IS: NH], between the reactor vessel [EIIS: RPV] and the first main steam isolation valve [EIIS: ISV]. The SVs provide protection against over pressurization of the nuclear system and discharge directly into the interior space of the drywell. The SRVs discharge to the suppression pool and provide three main functions: overpressure relief operation to limit the pressure rise and prevent safety valve opening, overpressure safety operation to prevent nuclear system over pressurization, and depressurization operation (opened automatically or manually) as part of the emergency core cooling system [EIIS: BJ, BM, BO]. Technical Specification (TS) Limiting Condition for Operation (LCO) 3.4.3 requires the safety function of seven SRVs and three SVs to be operable. The nominal set pressure tolerances for these valves are established in CNS TS Surveillance Requirement (SR) 3.4.3.1. The SRVs installed at CNS are Target Rock Model 7567F, two-stage, pilot-actuated valves with pilot assemblies comprised of Stellite 21 pilot discs and Stellite 68 pilot body seats. The pilot assemblies had been in continuous service since installation in Refueling Outage (RE) 31, (Fall of 2020). Corrosion bonding is an industry known problem with Target Rock Model 7567F two-stage relief valves in which the pilot valve bonds/sticks to the in-body seat, resulting in an increased pressure needed to lift the valve. After the corrosion bonding is "broken" following the initial lift, the subsequent lifts are within tolerance. EVENT DESCRIPTION In the Fall of 2022, three main SRV body/pilot assemblies and five SRV pilot assemblies were removed during RE32. In March 2023, the eight SRV pilot assemblies were as-found tested at National Technical Systems Laboratories. The pressure setpoint for SRV pilot assembly serial number 387 is 1080 psig. The TS SR 3.4.3.1 as-found limit acceptance is 1080 +/- 3%. The first actual lift pressure of this SRV pilot assembly was recorded at 1166.4 psig, 8.0% above the pressure setpoint. A second, third, and fourth lift was performed, and the results were 1088 psig, 1084 psig, and 1084 psig, all three within 3% of the pressure setpoint. The pressure setpoint for SRV pilot assembly serial number 386 is 1100 psig. The TS SR 3.4.3.1 as-found limit acceptance is 1100 +/- 3%. The first actual lift pressure of this SRV pilot assembly was recorded at 1186.1 psig, 7.8% above the pressure setpoint. A second, third, and fourth lift was performed, and the results were 1111 psig, 111 O psig, and 1109 psig, all three within 3% of the pressure setpoint. BASIS FOR REPORT CNS is reporting this event as an operation or condition prohibited by plant TS per 10 CFR 50.73(a)(2)(i)(B), and also as a condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident as defined under 10 CFR 50.73(a)(2)(v)(D). | ML23128A133
cooper nuclear station | Unknown Unit | Manual Reactor Scram and Group I Isolation due to Main Turbine Bypass Valve Failing Open | 05-11-2023 | A reduction in power was performed on December 15, 2022, to repair a hydrogen leak on the main generator. On December 16, Operations personnel noted that both electro-hydraulic (EH) oil pressure and reactor vessel pressure were lowering and that two of three turbine bypass valves were closed with one full open. Operations personnel responded by starting a second EH fluid pump to restore EH system pressure, however, reactor vessel pressure continued to lower. As a result of reactor vessel pressure lowering, a manual reactor scram was inserted. Immediately following the manual reactor scram, a Primary Containment Group 1 Isolation was received. The cause of one of the turbine bypass valves being open was the failure of the fast-open solenoid operated valve (SOV) coil. All three of the SOV coils were sent to a lab for analysis to determine if there were any additional failure modes of the coil. The analysis determined the most likely cause of the premature failure of the SOV was a shorting of the coil due to a weak point along the coil wiring breaking down over time. The other two SOV coils, which did not fail, were also examined and found to be in good condition with no gross flaws. There was no impact to nuclear safety, radiological safety, or industrial safety. This event was reported under Event Notification 56278 on December 17, 2022. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (03-14-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. LICENSEE EVENT REPORT (LER) Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by CONTINUATION SHEET email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 (See NUREG-1022, R.3 for instruction and guidance for completing this form 17th Street NW, Washington, DC 20503; email: oira submission@omb.eop.gov. The NRC may not http://www. nrc. gov/ reading-rm/doc-collections/nu regs/staffl s r1 022/r3/) conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. FACILITY NAME 2. DOCKET NUMBER 3. Lt:.K NUMccn: X 050 YEAR SEQUENTIAL REV Cooper Nuclear Station 00298 NUMBER NO. 052 2022 - 004 01 | PLANT STATUS Cooper Nuclear Station was in Mode 1, Power Operation, at approximately 13 percent power, with the main turbine generator [EIIS:TA] out of service, at the time of the event on December 16, 2022. BACKGROUND The Main Turbine Bypass System [EIIS:SO] is designed to control steam pressure when reactor steam generation exceeds turbine [EIIS:TB] requirements during unit startup, sudden load reduction, and cooldown. It allows excess steam flow from the reactor [EIIS:RPV] to the condenser without going through the turbine. The bypass capacity of the system is 25 percent of the Nuclear Steam Supply System (EIIS:SB] rated steam flow. Sudden load reductions within the capacity of the steam bypass can be accommodated without safety relief valves [EIIS:RV] opening or a reactor scram. The Main Turbine Bypass System consists of three bypass valves (BPV) [EIIS:V] connected to the main steam lines between the main steam isolation valves (EIIS:ISV] and the turbine stop valves. The turbine utilizes a Digital Electro-Hydraulic (DEH) [EIIS:TG] system to control reactor pressure by positioning governor valves and condenser bypass valves. It consists of solid state governor devices, governor, startup control devices, emergency devices for turbine and plant protection (overspeed governor, master trip, vacuum trip, motoring protection, thrust bearing wear trip, low bearing oil pressure trip) and special control and test devices. The control system operates the main stop valves, governor valves, bypass valves, reheat stop and intercept valves and other protective devices. DEH system oil pressure is maintained by two hydraulic pumps [EIIS:P] located at the DEH reservoir tank [EIIS:T]. The function of the fast open permissive solenoid operated valve (SOV) is controlled by the DEH control system to be energized and closed when reactor power is below 115 MWe with the output breaker closed, or anytime the output breaker is open. During normal operation, above 115 MWe, the SOV is de-energized and open. There is a single SOV on each of the bypass valve actuators and controlled by redundant interposing relays at the DEH control cabinet rack. The fast open permissive SOV is only installed on the bypass valves. EVENT DESCRIPTION On December 9, 2022, a hydrogen leak was detected on the main generator. To repair this leak, a reduction in power was performed on December 15. On December 16, the three turbine BPVs were 40 percent open for reactor pressure control. At 23:49 hours, Operations personnel noted that both the electro-hydraulic (EH) oil pressure and reactor vessel pressure were lowering and that two of the three BPVs were closed with one full open. Operations personnel initially diagnosed the cause as an EH leak and responded by starting a second EH fluid pump to restore EH system pressure, however, reactor vessel pressure continued to lower. As a result of reactor vessel pressure continuing to lower, Operations personnel inserted a manual reactor scram at 23:51 hours. Immediately following the manual reactor scram, a Primary Containment Group 1 Isolation on Main Steam Line Low Pressure was received, and all Main Steam Isolation Valves and Steam Line Drain Valves closed. As a result, the station entered Mode 3, Hot Shutdown. The nominal setpoint for a Group 1 Isolation is 835 pounds per square inch gage (psig) main steam line pressure. The manual scram was inserted at 841 psig reactor pressure. The automatic Group 1 Isolation signal was received before scram action response to remove the mode switch from the RUN position, which would have bypassed the Group 1 isolation per Procedure 2.1.5, Reactor Scram. While the unit was in Mode 3, repairs were completed to resolve the hydrogen leak and troubleshooting was performed to determine why one BPV failed open. Initial finding determined the cause to be the failure of the fast-open SOV (TGF- SOV-BV-1) coil. | ML23132A132
MonticelloNuclearGeneratingPlant 052 | Unknown Unit | Main Steam Isolation Valve Leakage Exceeds Technical Specification Requirements Due to Stem Scoring | 05-17-2023 | A packing leak on valve AO-2-86C, “13 Outboard Main Steam Isolation Valve” (MSIV), exceeded the Technical Specification (TS) individual MSIV leakage limit of Surveillance Requirement (SR) 3.6.1.3.12 on March 4, 2023, based on subsequent evaluation. The condition was discovered on March 21, 2023, when it was concluded that a reasonable expectation of operability was not met, and the MSIV was declared inoperable in accordance with TS 3.6.1.3 Condition E. During a maintenance outage on March 26, 2023, the Local Leak Rate Test as-found leakage was 987.1 standard cubic feet per hour (scfh) which exceeded the TS SR limit for individual MSIV leakage. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the TSs. The cause of the packing leakage is attributed to scoring on the valve stem. During the planned maintenance outage, the MSIV was repacked to restore compliance with TS, and the valve packing gland was bored out and the stem was replaced during the 2023 Refuel Outage. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (03-14-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV NUMBER NO. Monticello Nuclear Generating Plant 263 2023 052 - 001 - 00 | EVENT DESCRIPTION While in Mode 1 at approximately 99 percent power, a packing leak being monitored on valve AO-2-86C, “13 Outboard Main Steam Isolation Valve” (MSIV), (i.e., the outboard MSIV on the “C” main steam line, hereafter referred to as the C outboard MSIV) exceeded the Technical Specification (TS) individual MSIV leakage limit of Surveillance Requirement (SR) 3.6.1.3.12 on March 4, 2023, based on subsequent evaluation. On March 21, 2023, engineering concluded that a reasonable expectation of operability for the C outboard MSIV [SB][ISV] was not met and operators declared the valve inoperable in accordance with TS 3.6.1.3 Condition E. During a planned maintenance outage on March 26, 2023, the 10 CFR 50, Appendix J Local Leak Rate Test (LLRT) as-found leakage for the C outboard MSIV was 987.1 standard cubic feet per hour (scfh) which exceeded the 100 scfh limit of SR 3.6.1.3.12 for individual MSIV leakage (when tested at greater than or equal to 44.1 psig). This condition is being reported within 60 days from the date of discovery, March 21, 2023, in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the TSs as discussed in the event analysis. Chronology In May 2021, the as-left LLRT leakage from the 2021 Refuel Outage (RFO) for the C outboard MSIV was 33.9 scfh. In June 2021 a packing leak on this valve was identified and an Adverse Condition Monitoring Plan established to monitor the leak. On March 4, 2023, packing material was observed on camera being ejected from the packing gland on this valve. On March 10, 2023, a four-degree Fahrenheit step change increase in main steam chase temperature occurred. On March 14, 2023, at 1645 hours, due to an increase in leakage, operators entered the procedure for steam leaks outside primary containment, and on March 16, 2023, a prompt operability determination was requested. On March 18, 2023, the C inboard MSIV was closed to isolate the leak. On March 21, 2023, engineering concluded that a reasonable expectation of operability for the C outboard MSIV was not met due to the estimated leakage, and operations declared the valve inoperable in accordance with the TS 3.6.1.3 Condition E. It was concluded that March 4, 2023, was likely the date the TS individual MSIV leakage limit had been exceeded. On March 26, 2023, during the maintenance outage the as-found LLRT for the C outboard MSIV was 987.1 scfh which exceeded the 100 scfh limit of SR 3.6.1.3.12 for individual MSIV leakage (when tested at greater than or equal to 44.1 psig). Following repacking of the C outboard MSIV during this outage an as- left LLRT leakage rate of 67.7 scfh was measured. The C main steam line was returned to service with startup from the maintenance outage until the 2023 RFO began. During the 2023 RFO the C outboard MSIV packing gland was bored out to provide additional clearance and the valve stem was replaced, and the valve tested satisfactorily. EVENT ANALYSIS The event was determined to be reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), “Any operation or condition which was prohibited by the plant's Technical Specifications.” Specifically, this occurrence is reportable as a condition prohibited by Specification 3.6.1.3, "Primary Containment Isolation Valves," because the MSIV had exceeded the individual leakage limit and had been inoperable for greater than the 8 hour Completion Time of Condition E and for greater than the Completion Times specified in Limiting Condition for Operation (LCO) 3.0.3, i.e., to be in Mode 2 within 7 hours, Mode 3 within 13 hours, and Mode 4 in 37 hours, respectively, when Condition E was not met. This event is not classified as a safety system functional failure since the C inboard MSIV was fully operational. | ML23137A275
Susquehanna Steam Electric Station (SSES) | Unit 2 | Inadvertent Contact Between Relay Cover and Relay Trip Contacts Resulted in Automatic Actuation of the ‘B’ Emergency Diesel Generator | 05-22-2023 | On March 23, 2023, while reinstalling a relay cover on Engineered Safeguard System (ESS) Bus 2A202, inadvertent contact was made between the target reset lever on the relay cover and the relay trip contacts. This resulted in a trip of all 4.16 kV breakers on the 2B ESS Bus 2A202, an ESS bus lockout, and automatic start of the ‘B’ Emergency Diesel Generator (EDG). This condition is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in manual or automatic actuation of any system listed in 10 CFR 50.73(a)(2)(iv)(B). This event was also reported via Event Notification 56430 in accordance with 10 CFR 50.72(b)(3)(iv)(A). The cause of the event was a momentary loss of focus on the relay target reset lever during reinstallation of the relay cover. This cause was attributed to a human performance error. Additional investigation concluded the potential impacts of an inadvertent error associated with the relay reinstallation activities were not adequately mitigated. Corrective actions included performing accountability per station procedures and planned procedure revisions to include continuous use checklists identifying removal and restoration work steps associated with relays that have the potential to trip protective devices. There were no actual consequences to the health and safety of the public. NRC FORM 366A U. S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (03-14-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported r¥·1 lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. i,.,, ·~- ../ CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to ,.. Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW (See NUREG-1022, R.3 for instruction and guidance for completing this form https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME ~ 050 2. DOCKET NUMBER YEAR 3. LER N SE U Q M U B E E N R TI AL REV NUMBER NO. Susquehanna Steam Electric Station (SSES) □ 052 05000388 2023 - 001 - 00 Unit 2 | CONDITIONS PRIOR TO EVENT Unit 1 – Mode 1, approximately 100 percent Rated Thermal Power (RTP) Unit 2 – Mode 5, zero percent RTP The described activity was performed during the Division 2 electrical maintenance outage with Division 1 systems protected. There were no structures, systems, or components that were inoperable at the start of the event and contributed to the event. EVENT DESCRIPTION On March 23, 2023, while reinstalling a relay cover on Engineered Safeguard System (ESS) [EIIS System Code: B] Bus 2A202 [EIIS System/Component Code: E/BU], inadvertent contact was made between the target reset lever on the relay [EIIS Component Code: RLY] cover and the relay trip contacts. This resulted in a trip of all 4.16 kV breakers [EIIS Component Code: BKR] on the 2B ESS Bus 2A202, an ESS bus lockout, and automatic start of the ‘B’ Emergency Diesel Generator (EDG) [EIIS System/Component Code: EK/DG]. The ‘B’ EDG operated as expected. The following timeline demonstrates the sequence of events: 03/23/2023 ~ 15:45: Relay and Test lead technician conducted a pre-job brief for critical relay calibrations on ESS Bus 2A202. 03/23/2023 ~ 16:15 – 17:00: Technicians arrived at the work area and performed a two minute drill. Removal, calibration, and reinstallation of the A-phase bus differential relay was completed. 03/23/2023 ~ 17:00 – 17:30: Removal and calibration activities for the B-phase bus differential relay was completed. 03/23/2023 ~ 17:33: During installation of the relay cover, inadvertent contact was made between the target reset lever on the relay cover and the relay contacts. This resulted in a trip of the 2B Bus lockout relays which opened all the bus supply breakers and started the ‘B’ EDG. 3/23/23 ~ 17:37: All work was stopped and the Unit 2 control room was contacted. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in manual or automatic actuation of any system listed in 10 CFR 50.73(a)(2)(iv)(B). This event was also reported via Event Notification 56430 in accordance with 10 CFR 50.72(b)(3)(iv)(A). CAUSE OF EVENT The cause of the event was a momentary loss of focus on the relay target reset lever during reinstallation of the relay cover. This cause was attributed to a human performance error. Additional investigation concluded the potential impacts of an inadvertent error associated with the relay reinstallation activities were not adequately mitigated. Page 2 of 3 | ML23142A269
i | Unknown Unit | Reactor Protection System Half Scram due to Motor Generator Set Output Breaker Trip | 05-25-2023 | On May 31, 2021, LaSalle Unit 2 was operating at 100 percent power, when the 2A reactor protection system (RPS) motor generator (MG) set output breaker tripped due to an overload condition, which resulted in a loss of 2A RPS bus. Loss of power to this bus created a half-scram and initiated closure of outboard isolation valves in multiple systems. The condition was an invalid actuation because it was not the result of actual plant conditions and not an intentional manual action. Actuations and isolations that occurred performed as designed, except for the outboard 2D main steam line isolation valve (MSIV) drain valve that was discovered later as having a slow closure time, rendering the component inoperable. The cause of the MG set breaker trip was a degraded voltage adjustment potentiometer on the associated MG set, which caused the output voltage to fluctuate. The RPS bus loss resulted in general containment isolation signals that affected containment isolation valves in more than one system while the unit was critical. Therefore, the condition is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). The cause of the MSIV drain valve slow closure was motor and bearing degradation from a nearby steam leak. There was no loss of safety function since an inboard isolation valve in the flow-path remained operable. However, the condition is reportable in accordance with 1O CFR 50. 73(a)(2)(i)(B) as an operation or condition prohibited by technical specifications (TS) due to having an inoperable component longer than permitted by TS. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory coUection request 80 hours. Reported .,,.. .. 1110"<-. lessons learned are incorporated into the licensing process and fed back to industry. Send comments (w,,.r..:.:1) regarding burden estimate to the FOIA, Libfary, and lnfonnation Collections Branch (T-6 A1 0M), U.S. LICENSEE EVENT REPORT (LER) Nudea.< Regulatory Commission, Washington, DC 20555-0001, or by e-mail to \~'~!~~/ CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at 0MB Office of lnfonnation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nudear Regulatory Commission, 725 17th Street NW. '1 ••••• Washington, DC 20503; e-mail: oira submission@lomb eoo gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of infonnation unless the document http://WfiW nrc.govtreadjng-rm/doc-coIIectjonstnuregs/s1afftsr1022/QD requesting or requiring the collection displays a currenUy valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR LaSalle County Station, Unit 2 05000- 374 NUMBER NO. 2021 002 02 | Plant and System Identification LaSalle Country Station Unit 2 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the "A" reactor protection system (RPS) logic and associated isolation functions. RPS initiates a rapid insertion of all the control rods (scram) when monitored variables exceed their pre-established limits, neutron flux instrumentation becomes inoperable, or a manual scram signal is inserted by the operator. In addition, the setpoints, power sources, and controls and instrumentation are arranged in such a manner as to preclude spurious scrams. Condition Prior to Event Unit(s): 2 Date: May 31, 2021 Time: 19:26 CDT Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 100 percent Description On May 31, 2021, the main control room (MCR) operating crew received an "A" RPS half scram due to loss of power to Unit 2 "A" (2A) RPS bus. The operating crew entered applicable abnormal operating procedure for the RPS power condition. Field operators determined that the 2A RPS MG set output breaker had overloaded and tripped. The loss of the power to the 2A RPS bus resulted in a half scram and closure of outboard isolation valves in multiple systems. The condition was considered an invalid actuation because it was not the result of a valid signal and not an intentional manual action. The actuations and isolations that occurred performed as designed except for the closure time of outboard main steam line isolation valve (MSIV) drain valve 2821-F067D. RPS MG Set The 2A RPS bus loss resulted in isolations of the reactor water cleanup system, main steam line (MSL) drains, RCS sampling, instrument nitrogen system, reactor recirculation hydraulic power unit outboard isolation valves, and containment monitoring valves. The condition also resulted in loss of power to portions of the average power range monitor, local power range monitor, oscillating power range monitor, control rod block systems; as well as portions of the radiation monitoring for main steam lines, reactor building ventilation, and fuel pool ventilation. Appropriate actuations and primary containment isolations occurred as designed. Due to the 2A RPS bus loss of power, applicable technical specification (TS) timeclocks were entered. Power was restored to 2A RPS bus in accordance with station procedures by transferring 2A RPS bus to the alternate power supply and resetting the half scram. When power was restored and the isolations were reset, the affected equipment was returned to operable status and timeclocks were exited. MSIV Drain Valve Position indication was lost on the Unit 2 "D" outboard MSIV drain valve (2821-F067D) while power was being restored. This condition caused the station to enter TS Required Action (RA) to restore required post-accident monitor (PAM) instrumentation channel within 30 days. Position indication was restored after a reset of thermal breaker overloads. The 2D MSIV drain valve indicated in the closed position, verifying it performed its design function when 2A RPS power had been lost. Subsequently, during reviews of computer traces from the loss of 2A RPS bus event, this valve was found to have exhibited closure time in excess of maximum isolation time limits specified in the technical requirements manual (TRM) and was declared inoperable as a primary containment isolation valve (PCIV). The station entered TS required actions to isolate the affected penetration flow path by use of at least one closed and de-activated automatic valve in four hours and to verify the affected penetration flow path is isolated once per 31 days. There was no loss of safety function as the penetration has two PCIVs in the flow-path, and the inboard PCIV remained operable. | ML23145A012
edwin i. hatch | Unknown Unit | - .. Unit 2 Manual SCRAM due to trip of both Reactor Recirculation Pumps -- | 05-26-2023 | On March 31, 2023 at 1430, with Unit 2 in mode 1 at 97 percent power, the reactor was manually tripped due to a loss of both recirculaion pumps. The recirculation pumps tripped due to a loss of the 2A and 2B Adjustable Speed Drives (ASOs). All safety equipment responded as expected. · The cause of the ASD trip was due to the high speed stops for the ASDs being set at a value greater than the over frequency relay trip setpoints. This resulted in the relay over frequency trip setpoint being reached prior to the ASD High Speed Stops when increasing ASD speed. To correct the issue, the ASD High Speed Stop setpoints values were returned to values less than the relay setpoint, to ensure the drive will not be able to be raised to a speed that would result in a trip due to over frequency. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual actuation of the reactor protection system. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/io23 (03-14-2023) Estimated burden per re.sponse to comply with this mandatory coHection request 80 hours. Reportea LICENSEE EVENT REPORT (LER) l r e e s g s a o rd ns in g le a b r u n r e d d en a r e e s t i i n m c a o t r e p o to ra t t h e e d F in O to IA !h , e L ib lic ra e , n y s , in a g n d p r In o f c o e r s m s a a ti n o d n f C ed ol l b e a ct c io k n to s B in r d a u n s c t h ry . ( T S -6 e n A d 1 0 o M om ), m U e . n S ts . CONTINUATION SHEET Nudoar Regulatory Commission, Washington, DC 20555--0001, or by email lo lnfocoUects.Resource@nrc.gov, and lhe 0MB reviewer at 0MB Office of lnfonnation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for lhe Nudear Regulatory Commission, 725 17111 Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; email: oinuubmissloo@omb oop,gov. The NRC may not conduct or bltp://www.nrc.gov/reading-rmld~l~ctions/nuregs/staff/sr10221c3/} r s e p q o u n e s s o t r i , n g a n o d r r a e q p u e i r r s in o g n lh is e n c o o t l l r e e c q ti u o i n re d d i s to p la re ys s p a o c n u d r r t e o n , U a y c v o a ll li e d c t 0 io M n B o f c o in n fo tr n o n l n a u ti m on b e u r n . l ess lhe doC1JmcnI , E 1. d - w FA in C - I I L . - IT H Y a - N tc A h - M N E u - clear - Plan - t Un - it 2 ------, 0 ■ 0 050 2. DOCKET NUMBER ~ YEA M R , 3 S . E L Q E U R E N N U TI M A B i.. E R REV I □ NUMBER INGNO. □ 052 00366 I 002 | EVENT DESCRIPTION On March 31, 2023 at 1430, with Unit 2 in MODE 1 at 97 percent power, the reactor was manually tripped due to a loss of both recirculation pumps [EIIS Code: AD]. The recirculation pumps tripped due to a loss of the 2A and 2B Adjustable Speed Drives (ASDs) [EIIS Code: AD, SC]. Over frequency relays [EIIS Code: AD,81] associated with the ASD's actuated at their trip setpoints based on recirculation pump motor speed. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual actuation of the reactor protection system. EVENT CAUSE ANALYSIS Causal analysis revealed that the 2A and 2B ASDs tripped due to actuation of over frequency relays when recirculation pump motor speed reached the actuation setpoints. System parameters for the 2A and 28 ASD were reviewed and found that during implementation of a design modification the high speed stop setpoints for the ASD's were set higher than the over frequency relay trip setpoints. The conflicting setpoints is the reason the over frequency trip setpoint was reached prior to the ASD high speed stops and resulted in the ASD trips. SAFETY ASSESSMENT There were no actual safety consequences as a result of this event. The Recirculation Pumps tripped as designed to prevent damage due to overspeed. A manual scram was inserted as required by procedures and the reactor protection system worked as expected. Pressure was controlled by EHC and Bypass valves. CORRECTIVE ACTIONS To correct the issue the ASD High Speed Stop setpoint values were adjusted lower than the over frequency relay trip setpoint. This change ensures the drive is not able to be raised to a speed that will result in a premature over frequency trip. PREVIOUS SIMILAR EVENTS None | ML23146A191
Susquehanna Steam Electric Station (SSES) | Unit 1 | Unplanned lnoperability of the High Pressure Coolant Injection (HPCI) System due Failure of the HPCI Turbine Stop | 08-31-2023 | On April 07, 2023, at approximately 20:52, during performance of the weekly Unit 1 High Pressure Coolant Injection (HPCI) Lube Oil System Functional Test, the HPCI Turbine Stop Valve failed to stroke fully closed as designed. Upon discovery of the condition, Operations entered Unit 1 Technical Specification (TS) 3.5.1, "ECCS [Emergency Core Cooling Systems]-Operating," Condition D for HPCI System inoperable. Operations exited TS 3.5.1, Condition D on April 08, 2023, at approximately 15:54 following valve cleaning and lubrication and satisfactory post maintenance testing. The cause of the HPCI Turbine Stop Valve failing to fully close was most likely internal corrosion and mechanical binding of the valve hydraulic drive mechanism caused by condensation from a steam leak past the HPCI Turbine Steam Supply Valve seat accumulating on the HPCI Turbine Stop Valve and dripping onto the hydraulic operating cylinder. The failure of HPCI Turbine Stop Valve as a result of the steam leak past the HPCI Turbine Steam Supply Valve seat was a previously unrecognized failure mode in the station's assessment of he steam leak, and therefore was not properly mitigated. Key corrective actions include repair of the HPCI Turbine Stop Valve and hydraulic operating cylinder and replacement of the HPCI Turbine Steam Supply Valve. In the interim, condition monitoring will be informed by weekly inspection of the HPCI Turbine Stop Valve. This event was reported by Event Notification 56458 in accordance with 10 CFR 50.72(b)(3)(v)(D). The condition is also being reported in accordance with 1O CFR 50. 73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of a safety function. There were no actual consequences to the health and safety of the public as a result of this event. U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory (See NUREG-1022, R.3 for instruction and guidance for completing this form Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 72517th Street NW https:/lwwN.nrc.gov/readinq-rm/doc-collections/nuregs/staff/sr1022/r3D Washington, DC 20503; email: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME ~ 050 2. DOCKET NUMBER 3. LERNUMBER YEAR SEQUENTIAL REV NUMBER NO. Susquehanna Steam Electric Station (SSES) D 052 05000387 2023 - 002 - 00 Unit 1 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, approximately 100 percent Rated Thermal Power (RTP) Unit 2 - Mode 5, zero percent RTP There were no structures, systems, or components that were inoperable at the start of the event and contributed to the event. EVENT DESCRIPTION On April 07, 2023, at approximately 20:52, during performance of the weekly Unit 1 High Pressure Coolant Injection (HPCI) [EIIS System Code: BJ] Lube Oil System Functional Test, the HPCI Turbine Stop Valve [EIIS Component Code: SHV] failed to stroke fully closed as designed. Upon discovery of the condition, Operations entered Unit 1 Technical Specification (TS) 3.5.1, "ECCS [Emergency Core Cooling Systems]- Operating," Condition D for HPCI System inoperable. Operations exited TS 3.5.1, Condition D on April 08, 2023, at approximately 15:54 following valve cleaning and lubrication and satisfactory post maintenance testing. This event was reported by Event Notification 56458 in accordance with 1O CFR 50. 72(b)(3)(v)(D). The condition is also being reported in accordance with 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of a safety function. CAUSE OF EVENT The cause of the HPCI Turbine Stop Valve failing to fully close was most likely internal corrosion and mechanical binding of the valve hydraulic drive mechanism caused by condensation from a steam leak past the HPCI Turbine Steam Supply Valve [EIIS Component Code: V] seat accumulating on the HPCI Turbine Stop Valve and dripping onto the hydraulic operating cylinder. The failure of HPCI Turbine Stop Valve as a result of the steam leak past the HPCI Turbine Steam Supply Valve seat was a previously unrecognized failure mode in the station's assessment of the steam leak, and therefore was not properly mitigated. ANALYSIS/SAFETY SIGNIFICANCE The condition described herein rendered the Unit 1 HPCI System inoperable. HPCI and Automatic Depressurization System (ADS) are independent high pressure ECCS. With HPCI rendered inoperable, the high pressure ECCS function would be fulfilled by ADS. During the period that HPCI was inoperable, both divisions of ADS were operable and available to fulfill the high pressure ECCS function. Since the high pressure ECCS function was maintained, the condition did not represent a safety system functional failure. Accordingly, this event will not be counted as a safety system functional failure in the Reactor Oversight Process Performance Indicators. There were no actual consequences to the health and safety of the public as a result of this event. | ML23157A176
Brunswick Steam Electric Plant (BSEP) | Unit 1 | Loss of Redundant Power Supply Operation Causes Turbine Trip and Subsequent Reactor Scram | 06-15-2023 | At 01:48 Eastern Daylight Time (EDT) on April 20, 2023, with Unit 1 in Mode 1 at approximately 100% power, an automatic reactor scram occurred due to a turbine trip. All control rods inserted as expected. Turbine bypass valves did not open on the scram; Safety Relief Valves (SRVs) opened automatically to control reactor pressure. Reactor Pressure reached approximately 1100 psig on the scram, exceeding the Reactor Protection System (RPS) setpoint. Reactor water level reached low level 1 following the scram resulting in automatic actuation of Primary Containment Isolation System (PCIS) Group 2, 6, and 8 isolation valves, by design. Operations responded and stabilized the plant. Operations transitioned pressure control from SRVs to main steam line drains to the condenser. Following the scram, reactor water level was maintained via the condensate and feedwater systems. The turbine trip and subsequent inoperative turbine bypass valves resulted from a complete loss of 24 Vdc power to the Turbine Protection system. The power supplies were replaced prior to restart. There was no impact on the health and safety of the public or plant personnel. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) due to valid actuation of the RPS and PCIS. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (03-14-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 SEQUENTIAL REV YEAR NUMBER NO. Brunswick Steam Electric Plant (BSEP), Unit 1 00325  052 2023 - 001 - 00 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. Background Initial Conditions At the time of the event, Unit 1 was in Mode 1 (i.e., Power Operation), at approximately 100 percent rated thermal power. Reportability Criteria This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) because it involved actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B). Specifically, the Reactor Protection System [JC] and Primary Containment Isolation System [JM] actuated during this event. The NRC was notified of this event per 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) via Event Notification 56478 at 05:24 Eastern Daylight Time (EDT) on April 20, 2023. Event Description At 01:48 Eastern Daylight Time (EDT) on April 20, 2023, with Unit 1 in Mode 1 at approximately 100% power, an automatic reactor scram occurred due to a turbine trip. All control rods inserted as expected. The turbine bypass valves [JI] did not open on the scram; main steam [SB] Safety Relief Valves (SRVs) 1C, 1F, 1G, 1K, and 1L cycled open automatically to control reactor pressure. Reactor pressure reached approximately 1100 psig on the scram; exceeding the 1060 psig Reactor Protection System (RPS) setpoint. Reactor water level reached the low level 1 (LL1) setpoint following the scram. Per design, the LL1 signal resulted in Primary Containment Isolation System Group 2 (i.e., floor and equipment drain isolation valves), Group 6 (i.e., monitoring and sampling isolation valves) and Group 8 (i.e., shutdown cooling isolation valves) isolations. Operations responded and stabilized the plant. Operations manually cycled open SRV 1B then transitioned pressure control from SRVs to the main steam line drains [SB] to the condenser [SG]. Following the scram, reactor water level was maintained via the condensate [SD] and feedwater [SJ] systems. Event Cause The direct cause of the turbine trip and subsequent inoperative turbine bypass valves was a complete loss of 24 Vdc power to the Turbine Protection system [JJ]. When 24 Vdc power was lost, Turbine Protection system data inputs for required pressure and flow transmitters were lost. With the loss of monitoring capability, the Turbine Protection system responded as designed by initiating a turbine trip to protect the turbine and inhibiting the opening of the turbine bypass valves to protect the condenser. 24 Vdc power is supplied to the Turbine Protection system via redundant power supplies [RJX]. Due to inadequacies in the vendor design, a unique combination of internal component failures on one power supply impacted the operation of the redundant power supply. As a result, both power supplies failed/shutdown within a short timeframe of one another resulting in a total loss of 24 Vdc power. | ML23166A081
LaSalle County Station | Unit 2 | Manual Scram due to lsophase Bus Duct Fire followed by 2A RPS Normal Power Supply Trip | 06-16-2023 | 12. Licensee Contact for this LER Licensee Contact rhone Number (Include area code) CJ Smith, Operations Director (815) 415-2200 13. Complete One Line for each Component Failure Described in this Report Cause System Component Manufacturer Reportable to IRIS Cause System Component Manufacturer Reportable to IRIS X EF RHE 0026 y B EL IPBU D312 y 14. Supplemental Report Expected Month Day Year I 15. Expected Submission Date [8J No D Yes (If yes, complete 15. Expected Submission Date) 6. Abstract (Limit to 1560 spaces, i.e., approximately 15 single-spaced typewritten lines) At 0238 CDT on September 26, 2022 with Unit 2 in Mode 1 at 100 percent power, a manual scram was initiated due to a reported fire on the isophase bus duct. The scram was uncomplicated with all systems responding normally with the exception of a loss of 2A reactor protection system (RPS) normal power supply. The 2A RPS normal power supply output breaker tripped on over voltage. Operations successfully transferred 2A RPS power to the alternate power supply. The fire was reported extinguished at 0240 CDT on September 26, 2022. The cause of the 2A RPS loss of normal power was a degraded voltage adjust potentiometer (POT) on the output breaker. The cause of the isophase bus duct (IPBD) fire was incorrect joint compound having been supplied and subsequently used during planned maintenance, resulting in high resistances at the shunt bolted connections. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimaled burden per response lo comply with this mandalory collection request· 80 hours. Reported lessons learned are incorporated inlo the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S LICENSEE EVENT REPORT (LER) Nuclear Regulalory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollecls.Resource@nrc.gov, and the 0MB reviewer al: 0MB Office of Information and Regulalory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulalory Commission, 72517th Street NW, Washington, DC 20503; e-mail: oira submission@ombeop.gov. The NRG may nol conducl or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/readinq-rm/doc-col lections/nu regs/staff/sr1 022/r3/l requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV LaSalle County Station, Unit 2 05000- 374 NUMBER NO. 2022 - 003 02 | Plant and System Identification LaSalle County Station Unit 2 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected systems were the Main Power system (MP) and the Reactor Protection System (RPS). The MP system provides safe and reliable distribution of electrical power from the Main Generator to the off-site transmission network. RPS initiates a rapid insertion of all the control rods (scram) when monitored variables exceed their pre-established limits, neutron flux instrumentation becomes inoperable, or a manual scram signal is inserted by the operator. In addition, the setpoints, power sources, and controls and instrumentation are arranged in such a manner as to preclude spurious scrams. Condition Prior to Event Unit(s): 2 Date: September 26, 2022 Time: 0238 CDT Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 100% Description Fire and manual scram Electrical Maintenance personnel identified smoke coming from the general area in the Unit 2 Turbine Building that contains the Unit 2 isolated phase bus duct and notified the Main Control Room (MCR). The Field Supervisor was dispatched and at 0230 CDT they notified the MCR that there was visible sparks, smoke and indications of a fire from the bus duct enclosure. Operations dispatched the fire brigade and entered abnormal operations procedures for a fire. The unit was manually scrammed at 0238 CDT. The brigade was able to successfully gain control of the fire using dry chem and the fire was reported extinguished at 0240 CDT. 2A RPS Breaker trip Following the Manual Scram, the 2A RPS Breaker normal feed tripped on overvoltage. All Primary Containment isolations occurred as expected following the loss of A RPS power. Operations entered abnormal operating procedures, swapped 2A RPS power to the alternate feed and restored containment isolations. Cause The cause of the isophase bus duct (IPBD) fire was incorrect joint compound having been supplied and subsequently used during the planned maintenance performed during the previous Unit 2 refueling outage in 2021. This resulted in high shunt bolted connection resistance causing overheating in the bolted connections. The overheating resulted in a failure of the IPBD support structure hardware and ignition of the retractable cover neoprene gasket. The cause of the 2A RPS Breaker trip was a degraded voltage adjust potentiometer. Reportability and Safety Analysis Fire and manual scram The fire was extinguished in less than 15 minutes of identification and the reactor was safely shutdown. Offsite power sources and station emergency power sources were available at all times throughout the event. Emergency response personnel acted promptly to extinguish the fire and there was no personnel injury during this event or damage to plant property from the fire other than the bus duct itself. | ML23167A076
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Emergency Diesel Generator Fuel Oil Supply Procedure Error “B” Subsystem | 06-23-2023 | On April 24, 2023, with the James A. FitzPatrick Nuclear Power Plant (JAF) at 100 percent power, Operators identified that the “B” Emergency Diesel Generator (EDG) subsystem fuel oil supply table in surveillance test (ST) ST-9AB contained incorrect information. This ST is performed to satisfy Surveillance Requirement (SR) 3.8.3.1. Due to the incorporate information contained in the ST, some previous SR performances for EDG fuel oil tanks 93TK-6B and 93TK- 6D resulted in fuel quantities that should have led to surveillance testing not meeting acceptance criteria. Therefore, circumstances for an operation prohibited by Technical Specifications occurred, reportable in accordance with 10 CFR 50.73(a)(2)(i)(B); and when reviewed with overlapping maintenance periods on the “A” EDG subsystem a condition that could have potentially prevented the fulfillment of a safety function, reportable per 10 CFR 50.73(a)(2)(v)(A), occurred. The cause of the event was an administrative error during the procedure revision to a new format. Once recognized, prompt action was taken to restore fuel oil quantities to meet surveillance test acceptance criteria. Corrective actions have been completed to perform a revision to the ST, completed an extent of condition on operations STs, and performance an engineering evaluation to determine the impact to safety function. NRC FORM 366 (08-2020) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (03-14-2023) Estimated burden per response to comply with this mandatory collection request: 80 LICENSEE EVENT REPORT (LER) hours. Reported lessons learned are incorporated into the licensing process and fed CONTINUATION SHEET back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB controlnumber. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 YEAR SEQUENTIAL REV NUMBER NO. James A. FitzPatrick Nuclear Power Plant 05000333  052 2023 – 003 – 00 | Background The Emergency Onsite Power Supply System [EIIS identifier: EK] consists of two redundant Emergency Diesel Generator (EDG) [DG] subsystems. Each EDG subsystem consists of two EDG units. Each EDG is provided with an independent Fuel Oil Storage and Transfer System [DE] consisting of a Diesel Fuel Oil Storage Tank (FOST), a Diesel Fuel Oil Day Tank (FODT) and two full-capacity motor-driven Fuel Oil Transfer Pumps. The Fuel Oil Transfer Pumps provide the capability to transfer fuel from the FOST to the FODT. Stored diesel fuel oil is required to have sufficient supply for 7 days of full load operation. This requirement, in conjunction with an ability to obtain replacement supplies within 7 days, supports the availability of EDGs required to shut down the reactor and to maintain it in a safe condition for an abnormal operational transient or a postulated Design Bases Accident with loss of power. Technical Specification (TS) Surveillance Requirement (SR) 3.8.3.1 verifies the capacity of the FOST. The acceptable quantity is calculated for each FOST and accommodates different fuel properties for American Petroleum Institute (API) gravity and tank geometry. SR 3.8.3.1 is performed monthly by procedure ST-9AB, EDG System B Fuel/Lube Oil Monthly Test, for the “B” EDG subsystem for FOST tanks 93TK-6B and 93TK-6D. Event Description On April 24, 2023, James A. FitzPatrick Nuclear Power Plant (JAF) was at 100% power, when a satisfactory performance of ST-9AB was reviewed by a Senior Reactor Operator (SRO) and the measured level was verified against the field support supervisor’s fuel ordering calculation spreadsheet, which recommended ordering fuel. The prompt investigation revealed the incorrect 6-day fuel oil supply table in place of the 7-day fuel oil supply table in ST-9AB. This procedure error affected the acceptable quantity of fuel oil in the “B” EDG subsystem, specifically, 93TK-6B and 93TK-6D FOST only. It was confirmed that procedure ST-9AA for the “A” EDG subsystem, 93TK-6A and 93TK-6C FOST, was not affected by this error and those fuel oil quantities met the required 7-day supply. Upon discovery, SR 3.8.3.1 was declared not met based on the required quantify of fuel oil being less than 7 days but greater than 6 days; the Limited Condition for Operation (LCO) 3.8.3 was declared not met on April 24 at 1406, a fuel delivery restored the required quantity, and the LCO was restored on April 25 at 0913. Event Analysis ST-9AB was converted to a electronic procedure with revision 9 on November 18, 2021. TS Bases 3.8.3 specifies a 6-day and a 7-day EDG Fuel Oil Supply table; however, these two tables were swapped. Between November 2021 and April 2023, this procedure error was effective. A review of records identified that the 7-day fuel oil supply requirement of SR 3.8.3.1 was not me for the “B” EDG subsystem between June 20, 2022 to September 12, 2022; November 7, 2022 to December 1, 2022; and March 27, 2023 to April 25, 2023. However, there was always a greater than 6-day supply. When SR 3.8.3.1 was not met, LCO 3.8.3 was not met. Action “A” states, when one or more EDGs with fuel oil level < a 7-day supply and > a 6-day supply in storage tank, then restore it within 48 hours. If this was not Page 2 of 4 | ML23174A067
Fermi 2 | Unknown Unit | Loss of Mechanical Draft Cooling Tower Fan Brakes dming High Speeds Leads to Loss of Safety Function and Inoperability | 06-23-2023 | At 1145 Eastem Daylight Time (ED1) on March 23, 2023, it was detennined that all Mechanical Draft Cooling Tower (MDC1) fan brakes would not pe1fon11 theii· design function during a tomado due to the speed switch not functioning over its published voltage range. The MDCT fan brakes are required to prevent fan over speed from a design basis tomado. The MDCT fans are requii·ed to suppo1t operability of the Ultimate Heat Sink (UHS), and the service water subsystems. At the time of discovery, the provisions ofLiiniting Condition for Operation 3.0.9 were being utilized for loss of the "D" MDCT fan brakes (ban-ier loss) thus the 24-hotu· allowance for restoration of at least one division was entered. This supplement expands the repo1t to include applicability of 10 CFR 21.2(c). Coll'ective actions were taken to develop a design change and install a potentiometer on each MDCT fan speed control system retuming the MDCT fans, UHS and the service water subsystems to service on March 24, 2023. The fan brake system is only required for a tomado. No tomado watches or wamings occtu1·ed dtuing the timeframe when all MDCT fan brakes were nonfunctional. Since there was no credible threat of a tomado, the MDCT fans and associated UHS would have been capable of pe1fon11.ing cooling for the service water subsystems. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (03-14-2023) Estimated burden per response lo C0"1>IYw ith this mandatory collection request 80 hours. Reported lessons learned are inro,poraled into the licensing process and fed back lo industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate lo the FOIA, Library, and Information Collections Branch (Hi A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email lo CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; email: oira submission@omb.eop.gov. The NRC may not conduct ot sponsor, and a person is not required lo respond lo, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-eollections/nuregs/staff/sr1022/r3/} requesting or requiring the colection displays a cunenfly valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 I I YEAR SEQUENTIAL REV □ NUMBER NO. ~ -I 1-0 Fermi 2 00341 052 001 I | INITIAL PLANT CONDITIONS Mode-1 Reactor Power - 100 There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT At 0923 Eastern Daylight Time (EDT) on March 13, 2023, the Division 11 Residual Heat Removal Service Water (RHRSW) System [Bl] Mechanical Draft Cooling Tower (MDCT)[CTW] Fan "D" Brake [BRK], was declared inoperable due to loss of speed indication at high speeds, which was discovered during an over-speed protection system calibration. The loss of speed indication also affects the fan brake operability during a design basis accident (DBA) tornado event. Limiting Condition for Operation (LCO) 3.0.9 was invoked for loss of the MDCT fan brake (barrier loss) for fan "D". LCO 3.0.9 allows 30 days before declaring the supported system(s) inoperable and the LCO(s) associated with the supported system(s) not met. The MDCT fans are required to support operability of the Ultimate Heat Sink (UHS) [BS], and the brakes prevent the fans from experiencing over-speed from a design basis tornado as described in Updated Final Safety Analysis Report (UFSAR) Section 9.2.5.2.2. Technical Specification (TS) 3.7.2 requires the UHS reservoir to be operable in MODES 1, 2, and 3. The UHS operability requirements in MODES 4 and 5 are determined by the systems the UHS supports. The UHS reservoir is divided into two, one-half capacity reservoirs, corresponding to Division I and Division II. Each reservoir is the cooling source for that division's service water subsystem (e.g., the Emergency Diesel Generators (EDGs) [DG] cooling water [LG], Emergency Equipment Cooling Water (EECW) system [CC], Emergency Equipment Service Water (EESW), RHR [BO] system, Core Spray [BG] system). UHS Safety Functions are as follows: (1) Remove the heat rejected by the RHR heat exchangers after reactor shutdown, (2) Remove the heat rejected by the RHR heat exchangers after an accident, (3) Remove the heat rejected by the EECW heat exchangers and the diesel generator heat exchangers, and (4) Provide sufficient cooling water for at least 7 days to permit safe shutdown and cooldown of the reactor without makeup water and to maintain the reactor in a safe shutdown condition. A two-cell MDCT is located above each of the one-half capacity reservoirs. Each cell is equipped with a MDCT fan. Two MDCT fans above each one-half capacity reservoir are required for it to be considered operable. The "A" and "C" MDCT fans are in Division I and the "B" and "D" fans are in Division II. Troubleshooting determined the Dynalco speed switch [SIS] (model SST-2400A-1) did not function over its full voltage range. Vendor-published data shows the speed switch voltage range is Oto 50 root-mean-square Voltage (Vrms) (0 to 141.42 Volts Direct Current (VDC)). The actual field voltage measured during troubleshooting was approximately 8.5 VDC; therefore, the range of the speed switch fully encompassed the field condition and should have performed and activated the brakes during an overspeed event. Based on vendor discussion and troubleshooting during the event, a load resistance had to be installed for the switch to function over the operating voltage range of the circuit. The Dynalco speed switch is found on all four MDCT fans. During the cause analysis performed on May 25, 2023, it was determined that Engine Systems, Inc. (ESI), who purchased and assembled the Dynalco speed switch (model SST-2400A-1 ), had added a load resistor to the four speed switches during vendor testing to allow it to function over the full range. This modification was not tracked as a nonconformance to the purchase order.This modification was applied to all four of the controllers; thus, caused a common failure mode for all four of the MDCT Fans. ESI originally qualified and documented the switch with the additional load resistor, but mock-up testing by Fermi, ESI and Dynalco in March 2023 could not duplicate the qualification results. The switch with the added load resistor did not function over its full voltage range. As a result, this event is reportable under 10 CFR 21.2(c). | ML23177A043
Limerick Generating Station | Unit 1 | Emergency Diesel Generator Lube Oil Pressure Sensing Line Leak Resulting in a Condition Prohibited by Technical Specifications | 06-26-2023 | On February 27, 2023, approximately 10 hours into a planned 24-hour endurance run for the 011 Emergency Diesel Generator (EOG), an oil leak was identified at a threaded fitting for an oil pressure indicator instrument line. The 011 EOG was emergently secured and declared inoperable. Subsequent investigation identified a crack in a threaded pipe nipple for the affected oil pressure indicator instrument line. Forensic analysis of the removed pipe nipple identified a crack initiated in the threaded fitting. The corrective action was to move the connection to a different location that does not experience high vibration. Although D11 EOG was not inoperable for greater than the allowed out of service time a second EOG was inoperable for greater than the allowed out of service time for two EDGs. This event is being reported as a condition prohibited by Technical Specifications (TS) in accordance with 10 CFR 50.73(a)(2)(i)(B). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (08-2020) Estimated burden per response to comply with this mandatory collection recuest: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and lnfonnation Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of lnfonnation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of infonnation unless the document http://www.nrc.gov/reading-rm/doc-col1ections/nuregs/staff/sr1022/r3/) requesting or recuiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER DYEA R SEQUENTIAL REV 05000-1 352 ~-I NUMBER NO. Limerick Generating Station Unit 1 I-~ I 001 | Unit Condition Prior to the event, Unit 1 was in Operational Condition (OPCON) 1 (Power Operation) at approximately 100% power. There were no structures, systems, or components out of service that contributed to this event. Description of the Event On February 27, 2023, during planned 24-hour endurance run of the D11 Emergency Diesel Generator (EOG) [EIIS-EK], an oil leak was identified at a threaded fitting for an oil pressure indicator instrument line. The one-quarter inch instrument line threaded connection tees off the 4-inch main lube oil piping near the discharge of the engine driven lube oil pump. The D11 EOG was started at 09:35 and fully loaded at 10:05. A dirty drip pan alarm came in at 19:42 and subsequently the lube oil leak was identified at 19:47. The EOG was secured and declared inoperable. Prior to the failure there was no leaks or degradation observed from the connection. The component was sent for failure analysis. The failure analysis identified a crack in a threaded pipe nipple for the affected oil pressure indicator instrument line. Forensic analysis of the removed pipe nipple concluded that the pipe nipple showed fatigue fracture that started from one side at the root of the last engaged thread, consistent with unidirectional cyclic bending loads due to vibration. The D11 EOG was determined to be inoperable from the last completed surveillance test on January 31, 2023, until restored to operable status following repair of the identified oil leak on February 28, 2023. Following the D11 EOG failure on February 27, 2023, vibration data was again collected on the 4-inch engine driven lube oil pump discharge piping. Comparison of this vibration data to vibration data previously collected for the D11 EOG in February 2020 concluded that the vibration signature of the piping had changed and that the D11 EOG was now susceptible to the same failure mechanism previously identified for the D24 EOG. Inspection of the pipe clamp on the 4- inch engine driven lube oil pump discharge piping adjacent to the instrument line connection identified that the nuts of the U-bolt clamp were not tight. A work order history review was completed, and no maintenance activity was identified that altered or adjusted the 4-inch engine driven lube oil pump discharge piping since vibration data was previously collected in February 2020. No engine operating data or maintenance activity could be cited as the cause for the change in the vibration signature of the 4-inch engine driven lube oil pump discharge piping other than vibration causing loosening of the U-bolt nuts. Analysis of the Event The failure analysis of the instrument line on the D11 EOG concluded the EOG was inoperable from the last completed surveillance test on January 31, 2023, until restored to operable status following repair of the identified oil leak on February 28, 2023. During the period that the D11 EOG was inoperable, the D13 EOG was also inoperable for approximately 7 days between, February 12, 2023, and February 19, 2023, for a planned system outage window. Based on the completion of the failure analysis and the component history review the condition was determined to reportable on April 27, 2023. | ML23177A232
Browns Ferry Nuclear Plant | Unit 1 | Full Reactor Scram due to an Oscillation Power Range Monitor Confirmation Density Algorithm Trip | 07-19-2023 | On May 20, 2023, at 0315 Central Daylight Time (CDT), while performing quarterly turbine control valve (TCV) testing at 80 percent reactor thermal power (RTP) and 70 percent core flow, Unit 1 automatically scrammed due to an Oscillation Power Range Monitor (OPRM) Confirmation Density Algorithm (CDA) trip. The plant responded to the reactor scram as expected and there were no human performance challenges during the turbine control valve testing or subsequent plant shutdown. The root cause of the event was determined to be that the sensitivity of the CDA trip during off-normal plant conditions was not embedded into processes or procedures, thus preventing development of appropriate risk elimination or mitigation actions. The Corrective Actions to Prevent Recurrence are to revise Surveillance Requirements for the Turbine Control Valve Fast Closure on Turbine Trip and RPT Initiate Logic to specify the appropriate power level and associated valve position for performing the test to ensure no control valve oscillations and that conditions remain outside of the OPRM trip enabled region when possible; revise Technical Instructions for the Reactivity Control Plan Development and Implementation to increase awareness of entry into the OPRM trip enabled region due to the risk of spurious scrams from the CDA instability detection method; revise Design Criteria for the Turbine Electro Hydraulic Control System (EHC) systems to add details with regards to the interrelationship between EHC and OPRM; and revise Design Criteria for Neutron Monitoring Systems to add details on OPRM Algorithms. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (03-14-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME ☒ 2. DOCKET NUMBER 3. LER NUMBER 050 SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 1 ☐ 00259 NUMBER NO. 052 2023 - 002 - 00 | I. Plant Operating Conditions before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN) Unit 1 was in Mode 1 at approximately 80 percent power. II. Description of Event A. Event Summary On May 20, 2023, at 0315 Central Daylight Time (CDT), while performing quarterly turbine control valve (TCV) testing at 80 percent Reactor Thermal Power (RTP) and 70 percent core flow, Unit 1 automatically scrammed due to an Oscillating Power Range Monitor (OPRM) Confirmation Density Algorithm (CDA) trip. The plant responded to the reactor scram as expected and there were no human performance challenges during the TCV testing or subsequent plant shutdown. The Tennessee Valley Authority (TVA) is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(iv)(A), as any event or condition that resulted in a manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B), including: the reactor protection system (RPS) [EIIS: JC] which includes a reactor scram or a reactor trip, and general containment isolation signals affecting containment isolation valves in more than one system. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML23200A238
Browns Ferry Nuclear Plant | Unit 3 | Pressure Boundary Leak on Residual Heat Removal System Low Pressure Coolant Injection Test Line due to Fatigue Failure | 07-31-2023 | On December 2, 2022, at 2330 Central Standard Time (CST), during a drywell entry for leak identification, BFN Engineering personnel discovered a through-wall piping leak on a test line between the two Residual Heat Removal Shutdown Cooling test line isolation valves. On December 3, 2022, at 1000, it was determined that this test line was classified as American Society of Mechanical Engineers Code Class 1 piping and constitutes part of the BFN, Unit 3 Reactor Coolant System pressure boundary. Operations personnel maintained BFN, Unit 3 in Mode 4 or 5 until the leak was repaired. On December 3, 2022, at 1205 CST, eight-hour Event Notification 56257 was made to the NRC. The test line was cut and capped. The POE for this event determined that the LPCI mode of the BFN, Unit 3 RHR system can still meet the required LPCI flow to the reactor pressure vessel in the worse-case scenario of a small break LOCA for the duration of the mission time. During this time the HPCI system, both loops of the Core Spray system, and all ADS valves remained operable when required, aside from periods of planned maintenance and testing, and were available to provide coolant flow to the core during an emergency. The root cause of this event was that the small bore piping was not analyzed for vulnerability of fatigue failure due to operational or resonance vibration. Corrective actions are to implement Engineering Changes that will result in bounded life cycles for all levels of vibrational stress that the piping will experience; and to implement additional actions, for U3 systems where failure of small bore branch piping would cause a unit shutdown or loss of RCS boundary, to either modify operating ranges of the system and/or to modify the piping assembly. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 12/31/2023 (01-10-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ☒ 050 SEQUENTIAL REV YEAR NUMBER NO. Browns Ferry Nuclear Plant, Unit 3 00296 ☐ 052 2022 - 003 - 01 | I. Plant Operating Conditions before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN) Unit 3 was in Mode 4 at approximately zero percent power. II. Description of Event A. Event Summary On December 2, 2022, at 2330 Central Standard Time (CST), during a drywell entry for leak identification, BFN Engineering personnel discovered a through-wall piping leak on a test line [PSF] between the two Residual Heat Removal (RHR)[BO] Shutdown Cooling (SDC) test line isolation valves [SHV]. On December 3, 2022, at 1000, it was determined that this test line was classified as American Society of Mechanical Engineers (ASME) Code Class 1 piping and the identified leak location was identified as part of the BFN, Unit 3 Reactor Coolant System (RCS) [AC] pressure boundary. Operations personnel maintained BFN, Unit 3 in Mode 4 or 5 until the leak was repaired. On December 3, 2022, at 1205 CST, eight-hour Event Notification (EN) 56257 was made to the NRC. The test line was cut and capped. The TVA is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant’s Technical Specifications (TS); and 10 CFR 50.73(a)(2)(ii)(A), as any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML23212B015
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Reactor Protection System Electric Power Monitoring System Trip Caused Primary Containment Isolation | 08-14-2023 | On April 14, 2023, at 05:11, James A. FitzPatrick Nuclear Power Plant (JAF) received indication of a half-scram on the “B” side Reactor Protection System (RPS). The cause was determined to be an overvoltage condition that tripped the Electrical Protection Assembly (EPA) for the “B” RPS Motor Generator (MG) Set. The same condition occurred on May 25, 2023, at 23.59. These events caused invalid primary containment isolation signals in multiple systems, reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). The cause was corrosion buildup in the voltage adjust potentiometer which led to the overvoltage trip of the EPA. Corrective actions included replacing the voltage adjust potentiometer. NRC FORM 366 (08-2020) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 08/31/2023 (03-14-2023) Estimated burden per response to comply with this mandatory collection request: 80 LICENSEE EVENT REPORT (LER) hours. Reported lessons learned are incorporated into the licensing process and fed CONTINUATION SHEET back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 YEAR SEQUENTIAL REV NUMBER NO. James A. FitzPatrick Nuclear Power Plant 05000333  052 2023 – 002 – 01 | Background Reactor Protection System (RPS) [EIIS: JE] Electric Power Monitoring System is provided to isolate the RPS bus from the motor generator (MG) set or an alternate power supply in the event of overvoltage, undervoltage, or underfrequency. This system protects the loads connected to the RPS bus against unacceptable voltage and frequency conditions and forms an important part of the primary success path of the essential safety circuits. Some of the essential equipment powered from the RPS buses includes the RPS logic, scram pilot valve solenoids, and various valve isolation logic. RPS electric power monitoring assembly will detect any abnormal high or low voltage or low frequency condition in the outputs of the two MG sets or the alternate power supply and will de-energize its respective RPS bus, thereby causing all safety functions normally powered by this bus to de-energize. (Safety functions powered by the RPS buses deenergize to actuate.) Two redundant Class IE circuit breakers are connected in series between each RPS bus and its MG set, and between each RPS bus and its alternate power supply. Each of these circuit breakers has an associated independent set of Class IE overvoltage, undervoltage, and under frequency sensing logic. Together, a circuit breaker and its sensing logic constitute an electric power monitoring assembly. If the output of the inservice MG set or alternate power supply exceeds predetermined limits of overvoltage, undervoltage, or underfrequency, a trip coil driven by this logic circuitry opens the circuit breaker, which removes the associated power supply from service. Event Description On April 14, 2023, at 05:11 when James A. FitzPatrick Nuclear Power Plant (JAF) was at 100% power, the station received indication of a half-scram on “B” side RPS. AOP-60, Loss of RPS Bus B Power, was entered and the cause was determined to be a trip of the “B” RPS MG set due to an overvoltage condition. The direct cause of the output breaker tripping was due to an Electric Power Monitoring System overvoltage trip on 71EPA-RPS1B1G, Electrical Protection Assembly (EPA). On May 25, 2023, at 23:59, when JAF was at 100% power, the station received indication of a half-scram on the “B” side RPS. AOP-60 was entered and the cause was determined to be a trip of the “B” RPS MG set due to an overvoltage condition. The direct cause of the output breaker tripping was due to an Electric Power Monitoring System overvoltage trip on 71EPA-RPS1B1G, EPA. In both events, the RPS bus power was restored when it was placed on the alternate power supply. Both events resulted in invalid system actuations of "B" side half scram and Primary Containment Isolation System (PCIS) [JM] isolations. The following systems isolated as a result of the loss of “B” RPS bus: Reactor Water Cleanup [CE], Reactor Building ventilation [NG], “B” Containment Atmosphere Dilution [BB], Torus Vent and Purge, Drywell Equipment and Floor Drain Sumps [WK], “B” Drywell Containment Atmospheric Monitors [IP], Recirculation System Sample Line, and Main Steam Line Drains [SB]. “B” Standby Gas Treatment System [BH] started as designed. These system actuations were not initiated by signals in response to actual plant conditions or parameters satisfying the requirements for initiation of the system. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). Page 2 of 4 | ML23226A139
River Bend Station | Unit 1 | Division I and II Diesel Generators Inoperable due to Exceeding Load Sequence Times | 09-13-2023 | On February 12, 2023, with River Bend Station (RBS) in Mode 4 during Refueling Outage 22, testing of the Division II Emergency Core Cooling System (ECCS) revealed that both Division II Control Building Chillers (HVK-CHL1B and HVK- CHL1D) failed to sequence onto the emergency bus within the Technical Specification (TS) required time. Investigation of the issue revealed that the same condition was present for the Division I Control Building Chillers (HVK-CHL1A and HVK- CHL1C). The condition described above was caused by a modification that replaced the Control Building Chiller controllers. The preliminary root cause identified that when the controllers were replaced, a delay was introduced in the start logic. Corrective actions to restore TS compliance were completed prior to the next mode of applicability. This condition resulted in the inability to comply with a Surveillance Requirement of TS 3.8.1. At the time of discovery, TS 3.8.1 was not applicable. An evaluation determined that the TS 3.8.1 Surveillance Requirement was not met prior to time of discovery and Required Actions were not taken within the associated allowed Completion Times in accordance with TS 3.8.1 - AC Sources – Operating. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 09/30/2023 (09-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  River Bend Station, Unit 1 050 YEAR SEQUENTIAL REV NUMBER NO. 458 ☐ 2023 - 002 - 01 052 | EVENT DESCRIPTION On February 12, 2023, RBS performed STP-309-0602, DIVISION II ECCS TEST. During the performance of Section 7.4, ECCS/LOP/LOCA Test Initiation, HVK-CHL1B [KM] did not load sequence within the required time. Load sequence time was 237.1 seconds with acceptance criteria of 180.9 to 221.1 seconds. During performance of Section 7.25, ECCS/LOP Test Initiation, HVK-CHL1D [KM] did not load sequence within the required time. Load sequence time was 241 seconds with acceptance criteria of 180.9 to 221.1 seconds. Condition Reports were generated for both issues. On May 2, 2023, the station determined that the Division I and Division II Diesel Generators [EK] had been inoperable as a result of the chiller controller modification. HVK-CHL1C [KM] and HVK-CHL1D modifications were completed in 2014. HVK-CHL1A [KM] and HVK-CHL1B modifications were completed in 2020. The discovery date was determined to be February 12, 2023. The event is reportable as an Operation or Condition Prohibited by Technical Specifications per 10 CFR 50.73(a)(2)(i)(B) and an Event or Condition that Could Have Prevented Fulfillment of a Safety Function per 10 CFR 50.73(a)(2)(v)(A) and (D). EVENT CAUSE This event was caused by an error that was introduced during a modification to the HVK-CHL1(A)(B)(C)(D) control logic. Beginning in 2014, the analog control logic was modified to digital control logic. A bypass timer in the analog logic was not replicated in the new digital logic. The bypass timer blocked a low chiller condenser water flow signal for a short duration during the chiller start sequence. If received, the low water flow signal causes the chiller start sequence to reset. Because the signal was no longer blocked in the digital control logic, the low chiller condenser flow signal was capable of causing the chiller start sequence to reset resulting in an extended chiller start sequence. SAFETY ASSESSMENT The Division I and II Diesel Generators were declared inoperable based on load sequence time of the HVK Chillers exceeding TS SR 3.8.1.18 requirements. The following engineering analysis provided evidence that the delay had no effect on the generator loading sequence. Calculation E-192, STANDBY DIESEL GENERATOR LOADING CALCULATION, evaluates the loading of the standby diesel generators during the worst-case loading conditions (LOP concurrent with LOCA). The calculation verifies that the maximum magnitude for the load blocks is within the tested values of loading established by the vendor. HVK-CHL1B/D are in the 1.5-10-minute load block for the Division II Diesel Generator. The chiller is the last component in the load block to start with a listed start time of 211 seconds from the LOP. The next component to start is at the 10-minute mark. HVK- CHL1A/C are in the 1.5-10-minute load block for the Division I Diesel Generator. The chiller is the last component to start in the 1.5-10-minute load block with a start time of 241 seconds. Even with the additional 40 second delay, the chiller will remain in the 1.5-10-minute load block and there will be at least 5 minutes between a chiller start and the start of the next component. Therefore, the delay has no effect on the generator loading sequence. NRC Form 366A (09-01-2023) Page 2 of 3 . | ML23256A200
Fermi 2 | Unknown Unit | Technical Specification Completion Time Exceeded Due to Repairs on the MDCT Fan D. | 09-15-2023 | 12. Licensee Contact for this LER Licensee Contact Phone Number (Include area code) Eric Frank-Manager, Nuclear Licensing 734-586-4 772 13. Complete One Line for each Component Failure Described in this Report Cause System Component Manufacturer Reportable to IRIS Cause System Component Manufacturer Reportable to IRIS B cc SPT X999 y B cc VB M085 y 14, Supplemental Report Expected Month Day Year 1S. Expected Submission Date IZ] No □ Yes (If yes, complete 15. Expected Submission Date) 16, Abst.ract (Limit to 1326 spaces, i,e,, approximately 13 singl~spaced typewritten lines) At 0424 Eastern Daylight Time (EDD on July 18, 2023, the Division II Mechanical Draft Cooling Tower (MDCT) fan "D" was declared inoperable due to a trip of the fan motor while running at high speed. The MDCT fans are required to support operability of the Ultimate Heat Sink (UHS). The UHS is required to support operability of the Division II Emergency Equipment Cooling Water (EECW) system and the Emergency Equipment Service Water (EESW) system. The cause of the event was either the degraded mounting hardware between the gear reducer and the pedestal, and/or the degraded bushings on the driveshaft coupling to the gear reducer. The necessary repairs extended beyond the end of the 72-hour completion time prescribed by Technical Specification (TS) 3.7.2. A Notice of Enforcement Discretion (NOED) was approved by the NRC on July 20th, 2023, expiring at 2324 on July 25, 2023. This event is being reported under 10 CFR 50 .73(a)(2)(i)(B) for operation or condition prohibited by TS. Repairs were completed on the degraded mounting hardware and the degraded bushings, and the Division II MDCT fan "D" was declared operable at 1557 on July 22, 2023. There were no radiological releases associated with this event. At no time during this event was there a potential for endangering the public health and safety. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 09/30/2023 (00-01-2023) Estimated bLXden per response to comply with this mandalQl'Y collection request 80 hours. Reported lessons learned are incorporated into the licensing process and fed back lo industry. Send corrments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and lnfonnation Collections Branch (T-6 A10M), U. S. Nuclear Reguafory Commission, Washington, DC 20555-0001, or by email lo CONTINUATION SHEET lnfocollecls.Resource@nrc.gov, and the 0MB reviewer at 0MB Office of Information and RegulatOl'Y Affairs, (3150--0104), Attn: Desk Officer for the Nuclear Regula!Ol'Y Commission, 7'lf, 17th Street NW, Washington, DC 20503; email: oira submission@omb.eop.gov. The NRG may not condlrl or {See NUREG-1022, R3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http:/fwww.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/l requesting er requiring the cdleclion displays a rurrenHy valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV IFermi I I ~ □ -I NUMBER 1-0 N O. 2 052 0~1 002 | INITIAL PLANT CONDITIONS Mode-1 Reactor Power - 100 There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT At 0424 Eastern Daylight Time (EDT) on July 18, 2023, the Division II Residual Heat Removal Service Water (RHRSW) [Bl] Mechanical Draft Cooling Tower (MDCT)[CTW] Fan "D" [FAN], was declared inoperable due to a trip of the fan motor while running at high speed. The MDCT fans are required to support operability of the Ultimate Heat Sink (UHS) [BS]. The UHS reservoir is divided into two, one-half capacity reservoirs, corresponding to Division I and Division II. A two-cell MDCT is located above each of the one-half capacity reservoirs. Each cell is equipped with a MDCT fan. Two MDCT fans above each one-half capacity reservoir are required for it to be considered operable. Each reservoir is the cooling source for that division's service water subsystem (e.g., the Emergency Diesel Generators (EDGs) [DG] cooling water [LG], Emergency Equipment Cooling Water (EECW) system [CC], Emergency Equipment Service Water (EESW}, RHR [BO] system, Core Spray [BG] system). The Division II EECW system cools the High-Pressure Coolant Injection (HPCI) [BJ] system room cooler [CLR]. Typically, when Division II UHS is declared inoperable, then the high-pressure coolant injection (HPCI) system is declared inoperable; however, an Engineering analysis has been performed for HPCI operability which determined that there is reasonable assurance that HPCI would have performed its design function for its given mission time and remained operable. Investigation found that the cause of the trip was due to high vibrations caused by either the degraded mounting bolt (one of three) of the gear reducer to the pedestal [SPT] and/or the degraded bushings [VB] (Manufacturer Marley Company, Part# 69-29-02.) on the driveshaft coupling to the gear reducer. Further analysis is being done to determine the cause of the degradation on those parts. Based on the equipment history of the MDCT fans and the cause of the failure, there is no firm evidence to identify that the failure would have existed previously. Based on NUREG-1022 Section 3.2.2 guidance, the failure is assumed to have occurred at the time of discovery. The necessary repairs extended beyond the end of the 72-hour completion time prescribed by REQUIRED ACTION A.1 of Technical Specification (TS) 3.7.2.(Emergency Equipment Cooling Water (EECW}, Emergency Equipment Service Water (EESW) and Ultimate Heat Sink (UHS)- one reservoir inoperable). A Notice of Enforcement Discretion (NOED) was approved by the NRC on July 20, 2023, effective from 0424 EDT on July 21, 2023, to 2324 EDT on July 25, 2023. The enforcement discretion provided authorization for temporary non-compliance with TS 3.7.2 CONDITION A as described above. In addition, the following TS were also exceeded, TS 3.8.7 CONDITION A (Distribution Systems Operating, one or more required AC Electrical Distribution subsystems inoperable), and CONDITION B (one or more required DC Electrical Distribution subsystems inoperable}, TS 3.8.4 CONDITION B (DC sources operating, one DC Electrical Power Subsystem inoperable) and TS 3.8.1 CONDITION B (AC Sources Operating, both EDGs in one division inoperable). Following the degraded bushing replacement and removal and regrouting of the gearbox foundation bolts, the MDCT Fan "D" was declared operable at 1557 EDT on July 22, 2023. | ML23258A067
Browns Ferry Nuclear Plant | Unit 2 | Pressure Boundary Leak on Recirculation Pump Discharge Isolation Valve Drain Line Due to Fatigue Failure | 09-18-2023 | On February 17, 2023, during a drywell entry for leak identification, Browns Ferry Nuclear Plant (BFN) personnel discovered a cracked weld on the 2A Recirculation Pump discharge isolation valve drain line. On February 18, 2023, at 0439 Central Standard Time (CST), it was determined that this drain line was classified as American Society of Mechanical Engineers Code Class I piping and constitutes part of the BFN, Unit 2 Reactor Coolant System (RCS) pressure boundary. On February 18, 2023, at 1025 CST, eight-hour Event Notification 56371 was made to the NRC. On March 19, 2023, work was completed to remove and replace the drain line. The root cause of this event was that small bore piping was not analyzed for vulnerability of fatigue failure due to operational or resonance vibration. Corrective actions are to implement changes that will result in bounded life cycles for all levels of vibrational stress that the piping will experience; and to implement additional actions, for Unit 2 systems where failure of small bore branch piping would cause a unit shutdown or loss of RCS boundary, to modify the operating ranges of the system and/or the piping assembly. TVA has concluded that sufficient systems were available to provide the required safety functions needed to protect the health and safety of the public. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 12/31/2023 (01-10-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1.FACILITY NAME 2.DOCKET NUMBER 3. LER NUMBER (cid:1800) 050 SEQUENTIAL REV YEAR NUMBER NO. Browns Ferry Nuclear Plant, Unit 2 00260 (cid:1798) 052 2023 - 001 - 01 | I. Plant Operating Conditions before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN) Unit 2 was in Mode 4 at approximately zero percent power. II. Description of Event A. Event Summary On February 17, 2023, during a drywell entry for leak identification, BFN personnel discovered a cracked weld on the 2A Recirculation Pump [AD] discharge isolation valve [ISV] drain line [PSF]. On February 18, 2023, at 0439 Central Standard Time (CST), it was determined that this drain line was classified as American Society of Mechanical Engineers (ASME) Code Class I piping and constitutes part of the BFN, Unit 2 Reactor Coolant System (RCS) pressure boundary. Operations personnel maintained BFN, Unit 2 in Mode 4 or 5 until the leak was repaired. On February 18, 2023, at 1025 CST, eight-hour Event Notification 56371 was made to the NRC. On March 19, 2023, work was completed to remove and replace the drain line. The TVA is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant’s Technical Specifications (TS); and 10 CFR 50.73(a)(2)(ii)(A), as any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML23261C399
Hope Creek Generating Station | Unknown Unit | Technical Specification Required Shutdown due to Declaring the Suppression Chamber and Primary Containment Inoperable | 09-25-2023 | On April 30, 2023, Hope Creek Generating Station (HCGS) completed a technical specification (TS) required shutdown because limiting condition for operation (LCO) 3.6.1.1, Primary Containment Integrity, was not met. LCO 3.6.1.1 was not met because drywell-to-torus differential pressure could not be established to perform surveillance requirement (SR) 4.6.2.1.f, and LCO 3.6.2.1, SUPPRESSION CHAMBER, could not be met. HCGS demonstrated containment Operability and returned to power operation. This licensee event report (LER) supplement provides the results of a root cause evaluation (RCE). The direct cause was mechanical interference that prevented seating of one torus-to-drywell vacuum breaker and the root cause was failure to adequately assess and manage risk associated with torus-to- drywell vacuum breaker maintenance. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 09/30/2023 (09-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments f ~ ~ c,J>P. t REG ? t,(,.>O . LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to ~ CONTINUATION SHEET ~ ,i Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory ..;.+-, ••11t•• +O' Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ~ 050 YEAR SEQUENTIAL REV I □ NUMBER NO. Hope Creek Generating Station 354 D □ 052 I 2023 - I 001 I - 02 | IDENTIFICATION OF OCCURRENCE Event Date: April 30, 2023 Discovery Date: April 30, 2023 The root cause evaluation (RCE) determined the condition was first identified and misdiagnosed on October 18, 2022. Hope Creek entered an OPERATIONAL CONDITION (OPCON) that was applicable for the limiting conditions for operation (LCO) on October 28, 2022. CONDITIONS PRIOR TO OCCURRENCE OPCON 1, POWER OPERATION. No other structures, systems or components that could have contributed to the event were inoperable during the event. HCGS was in OPCON 1, POWER OPERATION, when drywell-to-torus bypass leakage was acceptable on September 28, 2022, as shown by successfully completing surveillance requirement (SR) 4.6.2.1.f. HCGS subsequently shutdown to complete a refueling outage. Preventative maintenance was performed on three of the eight torus-to-drywell vacuum breakers during the refueling outage. HCGS entered OPCON 2 and raised reactor coolant temperature above 200 degrees Fahrenheit on October 28, 2022. HCGS declared primary containment inoperable while in OPCON 1, POWER OPERATION at 100 percent rated thermal power on April 30, 2023 because Operators could not establish test conditions required to complete SR 4.6.2.1.f. DESCRIPTION OF OCCURRENCE On April 30, 2023, HCGS attempted to perform surveillance requirement (SR) 4.6.2.1.f but could not establish the initial test conditions (drywell-to-torus differential pressure). HCGS declared SUPPRESSION CHAMBER and PRIMARY CONTAINMENT INTEGRITY inoperable and completed a plant shutdown in accordance with TS. Event notification (EN) 56495 reported the technical specification required shutdown per 10 CFR 50.72(b)(2)(i) and this LER is required by 10 CFR 50.73(a)(2)(i)(A). EN 56494 reported a seriously degraded principal safety barrier per 10 CFR 50.72(b)(3)(ii)(A) and a condition that could prevent fulfillment of a safety function per 10 CFR 50.72(b)(3)(v)(D). Subsequent engineering analysis demonstrates that principal safety barriers were not seriously degraded. Therefore, a LER is not required by 10 CFR 50.73(a)(2)(ii). The engineering analysis also demonstrates that the primary containment safety function would be fulfilled if called upon. However, this LER is required by 10 CFR 50.73(a)(2)(v)(D) because primary containment is a single train system that was declared inoperable based on the inability to establish test conditions. | ML23269A205
i | Unknown Unit | : | 09-28-2023 | On August 10, 2023, at 0039, with the reactor in Mode 1 and 100% rated thermal power, an automatic Scram occurred caused by the loss of both Reactor Protection System (RPS) busses while transferring the power supply on RPS B bus from Alternate B to Normal. This also caused an isolation signal to all the Main Steam Isolation Valves (MSIVs). High Pressure Core Spray (HPCS) and Reactor Core Isolation Cooling (RCIC) systems automatically initiated, due to lowering water level in the reactor vessel, to restore and control water level in the reactor vessel. Reactor vessel pressure control was accomplished by cycling the Safety Relief Valves (SRVs). The RPS Power Transfer Switch was replaced, and the reactor was restarted on August 15, 2023. The direct cause of the reactor trip was inadvertent overtravel of the RPS power transfer switch, which interrupted power to both RPS busses. The root cause of the reactor trip is attributed to a failure to implement a design change for the RPS power transfer switch to prevent recurrence of a plant scram due to a known design vulnerability. The RPS Power Transfer Switch was replaced with a like-for-like switch as an immediate corrective action, and a planned corrective action is to upgrade the switch to remove the known design vulnerability. This event is reportable due to the actuation of RPS, including a reactor scram, isolation of the MS IVs, and the actuation of Emergency Core Cooling Systems (ECCS) under 10 CFR 50.73(a)(2)(iv)(A). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 08/31/2023 (03-14-2023) Eslimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) r C e o g m ar m di i n s g s io b n u , r d W en a s e h s in ti g m to a n te , D to C t h 2 e 0 5 In 5 f 5 o - r 0 m 0 a 0 t 1 io , n o r S e b r y v i e c - e m s a B il ra to n c ln h fo (T co -6 lle A c 1 t s O .R M e ). s o U u .S rc . e N @ u n cl r e c a .g r o R v, e g .m ula to th r e y CONTINUATION SHEET 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required (See NUREG-1022, R.3 for instruction and guidance for completing this form to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/ displays a currently valid 0MB control number. 2.DOCKETNUMBER !----,r-3_-~LE~R~NU~M~B~E~R;._ __- --t 1. FACILITY NAME 181 050 YEAR SE N Q U U M E B N E T R IA L R N E O V . Perry Nuclear Power Plant 00440 2023 003 00 □ 052 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. EVENT DESCRIPTION: On August 10, 2023, at 0039, with the plant operating in Mode 1 and approximately 100 percent power, a reactor scram occurred during the transfer of the Reactor Protection System (RPS) [JC] B power supply [JX] from the alternate power supply to the normal power supply. During the transfer, a loss of both RPS A and B busses [BU] occurred, causing the Main Steam Isolation Valves (MSIVs) [ISV] to isolate, and a reactor scram. Safety Relief Valves (SRVs) [RV] automatically opened to lower and maintain pressure in the reactor vessel [RCT], due to the loss of the Condenser [COND] resulting from the MSIV closures. Water level in the reactor vessel dropped to Level 2 (130 inches above the reactor core), and High Pressure Core Spray (HPCS) [BG] and Reactor Core Isolation Cooling (RCIC) [BN] automatically initiated to restore and maintain water level in the reactor vessel. The plant responded to the unexpected RPS actuation and reactor scram as designed. The Control Room Operator was transferring the RPS B power supply from the B alternate feed transformer [XFMR] to the normal B motor-generator [MG] set, in accordance with the operating procedure, following restoration from RPS breaker maintenance. The transfer of RPS power is a non-paralleling "break before make" transfer, causing the RPS bus loads to be momentarily de-energized. A Division 2 half-scram is expected during the transfer. However, an unexpected break in power to the RPS A bus also occurred, providing the second half scram signal and a full RPS actuation. The RPS power switch operation was suspect and was subsequently replaced. The reactor was restarted on August 15, 2023. To perform a transfer from the B alternate transformer to the normal B MG set, the RPS power transfer switch [JS] is rotated from the 45-degree position (ALT 8) to the 0-degree position (NORM). Similarly, to transfer the RPS bus A power supply from the normal A MG set to the A alternate transformer, the power transfer switch is rotated from the 0-degree position (NORM) to the 315-degree position (ALT A). The operating procedure contains a caution statement that reads, "Movement of the MG SET TRANSFER switch 1C71-S1 shall be performed in a slow and steady motion. When placing it in NORM, 3 to 5 degrees of over-travel may cause loss of RPS bus A." This caution statement was added due to a similar incident that occurred in 1988. INVESTIGATION: As part of the root cause investigation, vendor testing was performed on the removed switch and did not identify any functionality issues. It was determined that the RPS A or B bus power break occurs when the power transfer switch over travels by approximately 10 degrees from the NORM position, in either direction. A review of internal operating experience identified that the RPS power transfer switch has a latent design error that allows for overtravel of the switch and subsequent de-energization of both RPS busses. The switch design places operators in an error likely situation by not eliminating the human factor from the switch manipulation. Overtravel of the RPS power transfer switch is possible and has resulted in a previous plant scram (1988). Page 2 of 4 | ML23271A026
Donald C. Cook Nuclear Plant | Unit 1 | Two Trains of Fuel Handling Area Exhaust Ventilation Inoperable | 09-28-2023 | On July 25, 2023, with Donald C. Cook Nuclear Plant Units 1 and 2 operating at 100 percent power, Operators identified the Fuel Handling Area Exhaust Ventilation (FHAEV) System filter unit difference in pressure (DP) readings were below administrative limits. Subsequently, irradiated fuel movement occurred in the spent fuel pool on July 31, 2023 and August 1 , 2003. Later inspection of each train FHAEV System backdraft damper on August 2, 2023 identified degraded conditions that rendered each FHAEV train inoperable back to July 23, 2023. Technical Specifications require one train of the FHAEV System to be operable during movement of irradiated fuel assemblies in the auxiliary building. There were two occurrences of irradiated fuel movement in the auxiliary building during the time period when both FHAEV trains were inoperable. The event is reportable per 10 CFR 50.73(a)(2)(i)(B) "Operation or Condition Prohibited by Technical Specifications", 10 CFR 50.73(a)(2)(v)(D) "Event or Condition that Could Have Prevented Fulfillment of a Safety Function", and 10 CFR 50.73(a)(2)(vii) "Common Cause Inoperability of Independent Trains or Channels" ,_ - -- ,,. NRC FORM 366A (09-01-2023) LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) EXPIRES: 09/30/2023 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to lnfocollects.Resource@nrc.gov, and the OMB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Ann: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oita submission@omb.eop.g0¥. The NRC may not conduct or sponsor, and a person is not required lo respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 1. FACILITY NAME al ------------. □ | 050 052 2. DOCKET NUMBER I 00315 3. LER NUMBER I YEAR SEQUENTIAL REV [~]] use l=el « Hal Donald C. Cook Nuclear Plant Unit 1 Event Description On July 25, 2023, the Donald C. Cook Nuclear Plant Units 1 and 2 were operating at 100 percent power. Operators identified the Fuel Handling Area Exhaust Ventilation (FHAEV) System [VL] high efficiency particulate air filter (HEPA) and activated charcoal adsorber section difference in pressure (DP) readings were below administrative limits and commenced troubleshooting activities. Operators observed later during a system walkdown that with 12-HV-AFX-2, "Auxiliary Building Ventilation Fuel Handling Area Exhaust Fan #2" [VLJ[FAN] operating, there was reverse flow sufficient to cause "windmilling" of the opposite train fan 12-HV-AFX-1 "Auxiliary Building Ventilation Fuel Handling Area Exhaust Fan #1" [VLJ[FAN] while in standby. Similar symptoms of reverse flow were observed on 12-HV-AFX-2 when idle, while 12-HV-AFX-1 was operating. Internal inspections of each train FHAEV System backdraft damper assemblies 12-HV-BD-AFX-1, "Auxiliary Building Ventilation Fuel Handling Area Exhaust Fan HV-AFX-1 Discharge Backdraft Damper'' [VL][UDMP] and 12-HV-BD-AFX-2, "Auxiliary Building Ventilation Fuel Handling Area Exhaust Fan HV-AFX-2 Discharge Backdraft Damper'' [VL][UDMP] identified both damper mechanisms were partially stuck open and degraded which caused reduced system airflow. The identified conditions rendered each FHAEV System train inoperable. An engineering review of air flow data from 1-VFR-315 "Unit Vent Stack Flow Recorder Transmitter" [VL][FT] indicated system air flow was less than the operability range following a swap from 12-HV-AFX-1 to 12-HV-AFX-2, on July 23, 2023. No symptoms of degraded conditions were detected prior to that time. Repairs to the backdraft dampers were completed and required surveillance testing restored the FHAEV System to an operable status on August 5, 2023. Subsequently, during the time period between July 23, 2023 and August 5, 2023, when the FHAEV System was inoperable, irradiated fuel was moved in the auxiliary building on July 31, 2023 and August 1, 2023. Technical Specification Limiting Condition for Operation (LCO) 3.7.13 "Fuel Handling Area Exhaust Ventilation (FHAEV) System" requires "One FHAEV train shall be OPERABLE and in operation" and is applicable "During movement of irradiated fuel assemblies in the auxiliary building." LCO 3.7.13 requires the FHAEV system to be capable of removing airborne activity originating from a failed fuel assembly any time irradiated fuel is being moved. The mission time of the system is 30 days, which includes the radiological consequences analysis of record for a fuel handling accident in the auxiliary building, which credits the FHAEV System to filter the release through the unit vent. This filtered pathway is credited for the entire analyzed release duration. In order to accomplish the filtration safety function, the Bases for LCO 3. 7 .13 specifies for each FHAEV train, that ductwork, valves, and dampers are operable, and air flow can be maintained. Therefore, the event is reportable under 10 CFR 50.73(a)(2)(i)(B) "Operation or Condition Prohibited by Technical Specifications" due to irradiated fuel being moved when the FHAEV System was incapable of performing its safety function, contrary to LCO 3. 7.13 licensing basis requirements; 10 CFR 50.73(a)(2)(v)(D) "Event or Condition that Could Have Prevented Fulfillment of a Safety Function" due to neither train of the FHAEV being capable of performing the filtration safety function during movement of irradiated fuel; and, 10 CFR 50.73(a)(2)(vii) "Common Cause lnoperability of Independent Trains or Channels", when two independent trains (backdraft dampers) of the single system (FHAEV) were inoperable and would have impacted the ability to mitigate the consequences of an accident. " " _ " = | ML23271A098
Browns Ferry Nuclear Plant | Unit 1 | High Pressure Coolant Injection System Declared Inoperable Due to a Corroded Actuator | 10-12-2023 | On July 12, 2022, during a routine surveillance test, the Browns Ferry Nuclear Plant (BFN), Unit 1, high pressure coolant injection (HPCI) turbine control (governor) valve did not open as expected. Upon investigation, it was discovered that the electro-governor remote hydraulic actuator (EGR) had internal corrosion, which resulted in binding of the pilot plunger and associated pilot bushing and a subsequent failure to supply the hydraulic oil needed to open the governor valve. The resulting inoperability of the single-train HPCI system would have prevented HPCI from fulfilling its safety function to mitigate the consequences of an accident if demanded. The event was caused by inadequate procedural guidance which led to failing to identify corrosion which led to the valve failure. Additionally, BFN’s maintenance strategy was not aligned with industry best practices and was insufficient for making risk-based decisions related to the reliability of the U1 HPCI EGR. The EGR and remote servo were promptly replaced. As corrective actions to prevent recurrence, BFN revised maintenance procedures to include enhanced acceptance criteria (both wording and images) and now requires photographing inspection results. HPCI / Reactor Core Isolation Cooling (RCIC) moisture content limits, action levels and recovery actions were revised to reflect the new recommended levels. The HPCI Auxiliary Lube Oil Pump is now placed in service on a biweekly basis to recoat the EGR internals and provide real-time validation of anticipated governor valve response. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 12/31/2023 (01-10-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME (cid:1409) 050 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 1 05000-259 NUMBER NO. (cid:1407) 052 2022 - 002 - 01 | I. Plant Operating Conditions before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN) Unit 1 was in Mode 1 at approximately 97 percent power. II. Description of Event A. Event Summary On July 12, 2022, when assistant unit operators (AUOs) locally started the high pressure coolant injection (HPCI) [BJ] auxiliary oil pump [P], HPCI control valve 1-FCV-073-0019 (governor valve) [FCV] did not open as expected during the prerequisite startup checks for BFN, Unit 1 HPCI Flowrate surveillance test 1-SR-3.5.1.7. Subsequent troubleshooting identified that with the turbine at rest, and the auxiliary oil pump running, the electro-governor remote hydraulic actuator (EGR) [SM] did not immediately supply the hydraulic oil needed to open the governor valve. Operations personnel declared HPCI inoperable and entered Technical Specification (TS) 3.5.1, "Emergency Core Cooling System (ECCS) - Operating," Condition C and verified that reactor core isolation cooling (RCIC) [BN] was operable as required. Troubleshooting confirmed that the EGR had failed due to mechanical binding as a result of accumulated corrosion product around the pilot plunger which reduced critical clearances needed for component operation. The resulting inoperability of the single-train HPCI system would have prevented HPCI from fulfilling its safety function that would be needed to mitigate the consequences of an accident. HPCI was returned to standby readiness and was declared operable on July 15, 2022, at 0915 CDT, thus exiting TS 3.5.1 Condition C. The Tennessee Valley Authority (TVA) is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(v)(D), as any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML23285A192
Hope Creek Generating Station | Unknown Unit | Shutdown Margin Less than Expected Resulting in a Condition Prohibited by Technical Specifications | 10-20-2023 | On May 4, 2023, during reactor start-up following a maintenance outage, nuclear instrumentation readings (Source Range Monitor (SRM)) were observed to be rapidly rising during withdrawal of a control rod blade (CRB). The Reactor Operator was directed to re-insert the CRB. Nuclear instrumentation readings stabilized and began to lower when the CRB was re-inserted. The Operating Crew subsequently performed a reactor shutdown by fully inserting all CRBs. The start-up was re-commenced on May 5, 2023 with an adjusted start-up sequence. The start-up was successfully completed with normal responses from nuclear instrumentation. Subsequent collection of data determined that there had been a loss of reactivity worth in two CRBs. On August 21, 2023, Hope Creek Generating Station received the results of a Shutdown Margin (SDM) Analysis performed by Global Nuclear Fuel (GNF). The analysis determined that with the reduced reactivity worth of the two CRBs, the calculated SDM for the current fuel cycle was lower than expected, and less than required by Technical Specification 3.1.1, Shutdown Margin, during the early portion of the fuel cycle. This condition is reportable under 10 CFR 50.73(a)(2)(i)(B). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and (See NUREG-1022, R.3 for instruction and guidance for completing this form a person is not required to respond to, a collection of information unless the document requesting or requiring http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3.LER NUMBER Hope Creek Generating Station X 050 SEQUENTIAL REV YEAR NUMBER NO. 00354 2023 - 002 - 00 052 | IDENTIFICATION OF OCCURRENCE Event Date: May 4, 2023 Discovery Date: August 21, 2023 CONDITIONS PRIOR TO OCCURRENCE At the time of the unexpected increase in SRM readings, May 4, 2023, Hope Creek was in Operational Condition (OPCON) 2, Start-up, 0 percent power, with the reactor subcritical. No other structures, systems or components that could have contributed to the event were inoperable at the time of the event. When the analysis from Global Nuclear Fuel (GNF) was accepted, August 21, 2023, Hope Creek was in OPCON 1, Power Operation, at 100 percent rated thermal power. DESCRIPTION OF OCCURRENCE During reactor start-up following a maintenance outage, nuclear instrumentation readings (Source Range Monitor (SRM)) were observed by the Reactor Operator to be rapidly rising during continuous withdrawal of a CRB. The Reactor Operator was directed to re-insert the CRB. Nuclear instrumentation readings stabilized and began to lower when the CRB was re-inserted. The Operating Crew subsequently performed a reactor shutdown by fully inserting all CRBs. An initial investigation did not reveal any errors in sequence development, Estimated Critical Positions (ECP), or CRB reactivity worth calculations. These items were independently checked by the fuel vendor. However, the start-up sequence was revised and a second start-up proceeded without any issue. Evaluation of Local Power Range Monitor (LPRM) responses and Traversing Incore Probe (TIP) data later determined that there was a loss of reactivity worth in two CRBs. Initially four CRBs were inserted to ensure shutdown margin requirements were met. After a calculation performed by GNF, three of the CRBs were withdrawn, leaving one inserted. GNF was engaged to perform a Shutdown Margin (SDM) analysis of the Cycle 25 reactor core. The analysis concluded that the minimum SDM at Beginning of Cycle (BOC) 25 was below the Technical Specification limit of 0.38% delta k/k. Cycle 25 began on October 28, 2022 with reactor start-up from refuel outage R24. This condition existed until core average exposure reached approximately 500 Megawatt-Days per Short Ton (MWD/ST) on November 21, 2022. At that time, the SDM was determined to have been greater than 0.38% delta k/k and therefore compliance with Technical Specifications was restored. CAUSE OF EVENT A Root Cause Evaluation (RCE) was conducted. The Direct Cause of the event was determined to be a reduction of boron-10 in two (2) CRBs, reducing the reactivity worth of these two CRBs. The Root Cause was determined to be that established procedural and administrative criteria for CRB management was ineffective at identifying mechanical end of life. As part of the Extent of Condition review, PSEG identified indications of reduced reactivity worth for two CRBs discharged during the last refueling outage, R24. This was documented in the Corrective Action Program. Visual inspection of the two CRBs was completed and assessment is on-going as part of the Corrective Actions for this event. | ML23293A002
Nine Mile Point | Unit 2 | Automatic Reactor SCRAM on low Level Due to Partial Loss of Feedwater | 10-27-2023 | On 9/2/2023 at 0632 EDT, with Nine Mile Point Nuclear Station operating at 100% power, a Feedwater transient occurred resulting in a Reactor Protection System {RPS) Automatic Reactor Scram on Low Level (level 3, 159.3"). Follow_ing the scram, reactor water level dropped below Level 2 (108.8") resulting in a Group 2 Recirc Sample System Isolation, Group 3 Traversing lncore Probe (TIP) Isolation Valve Isolation, Group 6 and 7 Reactor Water Cleanup Isolation, and Group 9 Containment Purge Isolations. All control rods inserted as expected. High Pressure Core Spray and Reactor Core Isolation Cooling initiated (RCIC) and injected as expected. Emergency Core Cooling Systems (ECCS) and RCIC were secured and normal reactor pressure and level control was established for hot shutdown. This event is reportable in accordance with 10 CFR 50. 73(a){2)(iv)(A). N~C FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03131/2024 (10-01-2023) Estimated burden per respoose to oomply wilh lllis mandatory collection request 80 hours. Reported lessons learned are incorporated into !he licensing process and fed back lo indusuy Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate lo the FOIA. Library .. and l11fOll!laoon Collecllons Branch fT·6 Al OM). U. S. Nuclear Regulatory Commission. Washington. DC 20555-0001, or by email to CONTINUATION SHEET lnfocoitects.Resource@nrc.gov, and tha 0MB reviewer al: 0MB Office of lnfo!lllllfion and Regulaloiy Affairs. (3!50-0104), Attn: Desk Officer for the Nuclear Regulatory Commission. 725 17111 Street NW Washington. DC 20503; email: fl!rn. &Jbm~o11@qm!1,sl0ll-JO~. The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor. and a parson is not required to respond !o. a collection of information un!ess !he documenl http:/lwww.nrc.gov/reading-rm/doc-colk,ctlonsfnl.lreqs[staff/sJ'LQ22/rM requesting or requiring the colleclion <lispfays a currently valid 0MB control number 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 I YEAR SEQUENTIAL REV ~□- I NUMBER 1-NO0. !Nine Mlle Point Unit 2 50-410 I 052 001 | .THE ENERGY INDUSTRY IDENTIFICATION SYSTEM (EIIS) COMPONENT FUNCTION IDENTIFIED AND SYSTEM NAME OF EACH COMPONENT OR SYSTEM REFERRED TO IN THIS LER ARE ENCLOSED WITHIN [BRACKETS] I. DESCRIPTION OF EVENT A. PRE-EVENT PLANT CONDITIONS: Prior to the event, NMP2 was in Mode 1 (Power Operation) at 100% power. B. EVENT: On 9/2/2023 at 0632 EDT, with Nine Mile Point Nuclear Station operating at 100% power, a Feedwater [SJ] transient occurred resulting in an RPS Automatic Reactor Scram on Low Level (Level 3, 159.3"). Following the Scram, reactor water level dropped below Low Low Level (Level 2, 108.8") resulting in a Group 2 Recirc Sample System Isolation [AD], Group 3 TIP Isolation Valve Isolation. Group 6 and 7 Reactor Water Cleanup Isolation [CE}. and Group 9 Containment Purge Isolations [BBJ. All control rods inserted as expected. High Pressure Core Spray [BGJ and Reactor Core Isolation Cooling [BNJ initiated and injected as expected. ECCS Systems and RCIC were secured and normal reactor pressure and level control was established for hot shutdown. This event is reportable in accordance with 10 CFR 50.73(a){2)(iv){A). C. INOPERABLE SYSTEMS, STRUCTURES, OR COMPONENTS THAT CONTRIBUTED TO THE EVENT: None. Any non-safety related equipment that contributed to the event will be provided in the supplement. D. DATES AND APPROXIMATE TIMES OF MAJOR OCCURENCES AND OPERATOR ACTIONS: The dates, times, major occurrences, and operator actions for this event are as follows. September 2, 2023: 0632-A sudden reduction in Feedwater flow causes level lowering to Low Level (Level 3, 159"), resulting in an RPS Automatic Reactor Scram. 0632-Shortly following the scram, Low Low Level (Level 2, 108.8") is reached, resulting in Group 2, 3, 6, 7, 8, and 9 isolations. Recirculating Pumps trip, and High Pressure Core Spray (HPCS) and Reactor Core Isolation Cooling (RCIC) automatically initiate. 0635 - Turbine tripped on reverse power. None. Additional dates and times of major occurrences and operator actions may be provided in the supplement when the evaluation is complete. | ML23306A048
Peach Bottom Atomic Power Station | Unit 3 | Standby Liquid Control Pump Inoperable for Greater than LCO Window due to Gas Intrusion | 11-07-2023 | On September 9, 2023, during performance of a functional test, the Unit 3 ‘B’ Standby Liquid Control Pump did not produce discharge pressure. The pump was declared inoperable and Technical Specification Limiting Condition for Operation (LCO) 3.1.7 Condition B was entered. Troubleshooting identified that the pump and part of the discharge piping was not sufficiently filled with water. The most likely source of gas intrusion was the nitrogen filled accumulator located on the discharge piping between the pump and the discharge check valve. The piping was refilled and the accumulator was replaced, after which the pump was run successfully. The system was restored to operable and the LCO was exited on September 12, 2023. The gas leakage rate was slow and therefore, the system was likely inoperable longer than the LCO-allowed outage time (i.e., 7 days). Therefore, the condition is being reported under 10CFR 50.73(a)(2)(i)(B). There were no other systems which were inoperable during this identified condition that contributed to this event. There were no actual safety consequences as a result of this event. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 SEQUENTIAL REV YEAR NUMBER NO. Peach Bottom Atomic Power Station, Unit 3 00278  052 2023 - 001 - 00 | Event Description On September 9, 2023, during performance of a functional test, the Unit 3 ‘B’ Standby Liquid Control (SLC, EIIS: BR) Pump (EIIS: P) did not produce discharge pressure. The pump was declared inoperable and Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.1.7 Condition B was entered at 20:32 hours. Troubleshooting identified that the pump and part of the discharge piping was not sufficiently filled with water. The most likely source of gas intrusion was a leaking bladder inside the pneumatic-hydraulic accumulator (EIIS: ACC). The device is installed on the piping near the SLC pump discharge relief valve to dampen pulsations from the pumps to protect the system piping. Nominal accumulator pressure is between 325 psig and 450 psig. The accumulator bladder was replaced, after which the pump and discharge piping were filled and the pump was run successfully. The system was restored to operable and the LCO was exited on September 12, 2023 at 17:39 hours. At the time of discovery, Unit 3 was operating in MODE 1 at approximately 91% power, due to end-of-cycle coast down. Peach Bottom TS LCO 3.1.7 Required Action B.1 requires that a SLC subsystem be restored to operable status within 7 days or in accordance with the Risk Informed Completion Time Program. If this action is not met, the plant is required to be in MODE 3 within 12 hours and MODE 4 within 36 hours. The most likely cause of the condition is gas leakage through the accumulator bladder. The estimated leak rate was small, because no visible sources of leakage were found on the accumulator bladder and the rate of pressure decay within the accumulator was slow. Failure analysis is being performed on the bladder, but at this time, the exact cause of the leakage is unknown. The 3B SLC subsystem was last run successfully on May 29, 2023. Trending of available accumulator pressure data did not provide a conclusive time of failure. Due to the slow nature of the leakage and the volume of gas intrusion present, it is highly likely that the condition existed longer than the LCO-allowed outage time. Since the 3B train of SLC was likely inoperable for greater than the LCO-allowed outage time, this condition is being reported under 10CFR 50.73(a)(2)(i)(B). The Energy Industry Identification System component function identifier and name of each component or system: EIIS: Standby Liquid Control System, BR 3BT076, Standby Liquid Control N2 Accumulator Manufacturer: Greer Hydraulics, Inc Model: A68514-200 Safety Consequences The SLC System is designed to provide the capability of bringing the reactor, at any time in a fuel cycle, from full power and minimum control rod inventory (which is at the peak of the xenon transient) to a subcritical condition with the reactor in the most reactive, xenon free state without taking credit for control rod movement. The SLC System satisfies the requirements of 10 CFR 50.62 on anticipated transient without scram using highly enriched boron. The SLC System is also used to maintain suppression pool pH at or above 7 following | ML23311A061
Susquehanna Steam Electric Station (SSES) | Unit 1 | D Diesel Generator Inoperable due to Clogged Fuel Injectors | 11-09-2023 | On September 12, 2023, at approximately 05:01, during the performance of surveillance testing, the D Diesel Generator (DG) failed to reach the required frequency within the acceptance criteria specified in Surveillance Requirement (SR) 3.8.1.7. Operators declared SR 3.8.1.7 failed and entered Technical Specification (TS) Limiting Condition of Operation (LCO) 3.8.1, Condition B, on both Susquehanna Steam Electric Station Unit 1 and 2 for the inoperable D DG. The other three DGs (A, B, and C) were verified to be OPERABLE and operators substituted the E DG in for the D DG. After completion of the E DG substitution, LCO 3.8.1, Condition B, was exited on September 12, 2023, at approximately 22:52. The failure to reach the required frequency within the acceptance criteria was the result of clogged fuel injectors. The condition of the inoperable D DG was determined to likely have existed for longer than allowed by TS, and ~he event was determined to be reportable in accordance with 10 CFR 50. 73(a)(2)(i)(B) as a condition prohibited by TS. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-202,,3,,), ...... Estimaled burden per response lo comply with this mandatory collection request: 80 hours. Reported ,~;-, lessons learned are incorporated into the licensing process and fed back to induslry. Send comments • "' t LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Ubrary, and lnfonmation Collections Branch (T-6A10M), U.S. \ ':/.I .,.,. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory (See NUREG-1022, R.3 for instruction and guidance for completing this form Affairs, (3150-0104), Attn: Oesk Officer for the Nuclear Regulatory Commission, 72517th Street NW https://www.nrc.gov/readinq-nm/doc-collections/nuregs/stafflsr1022/r30 Washington, DC 20503; email: oira submlssion@omb.eop.gov. The NRC may nol conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 181 050 YEAR SEQUENTIAL REV NUMBER NO. Susquehanna Steam Electric Station (SSES) D 052 05000387 2023 - 003 - 00 Unit 1 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, approximately 100 percent Rated Thermal Power (RTP) Unit 2 - Mode 1, approximately 93 percent RTP There were no structures, systems, or components that were inoperable at the start of the event and contributed to the event. EVENT DESCRIPTION On September 12, 2023, at approximately 05:01, operators started the D Diesel Generator (DG) [EIIS Code/Component Code: EK/DG] in accordance with the applicable surveillance procedure. The D DG reached the required frequency at a time of 12.6 seconds, which exceeds the acceptance criteria of 10 seconds specified in Surveillance Requirement (SR) 3.8.1.7. Operators declared SR 3.8.1.7 failed and entered Technical Specification (TS) Limiting Condition of Operation (LCO) 3.8.1, Condition B, on both Susquehanna Steam Electric Station (SSES) Unit 1 and 2 for the inoperable D DG. The other three DGs (A, B, and C) were verified to be OPERABLE and operators substituted the E DG in for the D DG. After completion of the E DG substitution, LCO 3.8.1, Condition B, was exited on September 12, 2023, at approximately 22:52. The condition of the inoperable D DG was determined to likely have existed for longer than allowed by TS, and the event was determined to be reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. The following is a timeline of events: February 2023 to August 2023 - The D DG has higher than normal accumulated low load run time, which was considered as a possible contributor to the clogged injectors. However, start times were acceptable after the low load operation, and there was not an increasing trend in start time. 08/17/2023 - D DG monthly surveillance start time was 8.65 seconds. 09/12/2023 - D DG monthly surveillance start time was 12.6 seconds. LCO 3.8.1, Condition B, was entered at approximately 05:01 due to the D DG being inoperable. The E DG was substituted for the D DG and LCO 3.8.1, Condition B, was exited at approximately 22:52. 09/21/2023 - Troubleshooting identified fuel injectors had excessive carbon buildup. The fuel injectors were cleaned. 09/22/2023 - D DG monthly surveillance was performed successfully with a start time of 7.95 seconds. D DG was substituted back in for the E DG and the D DG was declared operable at approximately 02: 10 on 09/23/2023. SSES TS LCO 3.8.1 requires, in part, that four DGs are OPERABLE in MODES 1, 2, and 3. Condition B requires that an inoperable DG be restored to OPERABLE status within 72 hours or that each unit be shut down to MODE 3 in 12 hours and MODE 4 in 36 hours. Based on the identified cause of the D DG slow start, this condition likely existed for longer than allowed by TS. As a result, this condition was determined to be reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. Page .l_ of.]_ NRG FORM 366A (10-01-2023) NRG FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported <,)I-'' ... , lessons learned are incorporated into the licensing process and fed back to industry. Send comments (~) LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. •1,,• CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory (See NUREG-1022, R.3 for instruction and guidance for completing this form Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW https:/lwww.nrc.gov/readinq-rm/doc-collections/nureqs/staff/sr1022/r3D Washington, DC 20503; email: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER [gJ 050 YEAR SEQUENTIAL REV • NUMBER NO. Susquehanna Steam Electric Station (SSES) D 052 05000387 2023 - 003 - 00 Unit 1 NARRATIVE CAUSE OF EVENT The cause of the slow start was clogged fuel injectors. ANALYSIS/SAFETY SIGNIFICANCE As described in Section 8.3 of the Susquehanna Updated Final Safety Analysis Report (UFSAR), and required by 10 CFR 50, Appendix A, General Design Criterion 17, a single failure of a DG will not prevent safe shutdown of the units in the event of a design basis accident. While the D DG was inoperable, the three remaining DGs (A, B, and C) were aligned and operable. Therefore, the slow start of the D DG did not prevent the DGs from fulfilling their safety function. The safety function of the DGs is to provide power to equipment as assumed in the safety analyses described in Chapter 15 of the Susquehanna UFSAR. In this case, the safety analyses assume the DGs will start in 25.1 seconds of a valid start signal. Additionally, the loading analysis for the DGs assume the Residual Heat Removal motors are loaded at 13 seconds to ensure the DG can handle the load of the large motors. The start time of 12.6 seconds observed during the September 12, 2023, surveillance test was within that assumed in the accident analyses. Therefore, the D DG was able to perform its safety function. Based on engineering analysis, this event will not be counted as a safety system functional failure under the NRC Reactor Oversight Process Performance Indicator. CORRECTIVE ACTIONS Key corrective actions included all D DG fuel injectors being cleaned. Although the station had implemented vendor guidance for low load run time on the DG, Susquehanna is also taking additional actions to refine guidance on low load run times for the DGs. COMPONENT FAILURE INFORMATION Component Name - Diesel Generator 'D' Component Identification - 0G501 D Manufacturer - Cooper Energy Services PREVIOUS OCCURRENCES None. NRG FORM 366A (10-01-2023) Page .1. of .1. | ML23313A196
Monticello Nuclear Generating Plant | Unknown Unit | Reactor Scram and Containment Isolation due to Valve Responses during Main Turbine Control Valve Testing | 11-13-2023 | On September 27, 2023 at 1041 CDT, with Monticello Nuclear Generating Plant in Mode 1 at approximately 75 percent power for the semiannual Turbine Control Valve (CV) test, an unplanned Reactor Scram, Group I Primary Containment Isolation, and Group II Primary Containment Isolation occurred. The cause of the Reactor Scram was exceeding the Reactor Pressure Vessel (RPV) high pressure scram setpoint during CV testing. CV-1, CV-2 and CV-3 percentage open did not increase enough when CV-4 was closed for testing. The reduction in steam flow caused the RPV pressure to exceed the scram setpoint. Subsequently, an expected low RPV level caused the Group II Primary Containment Isolation. The cause of the Group I Primary Containment Isolation was a transient in the steam line high flow instrumentation sensing lines for the C Main Steam Line. Corrective actions included inspection and adjustment of the four CVs to within manufacturer's specifications. Channel calibration and functional tests were performed to verify that all C Main Steam Line flow instruments met requirements. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME ■ 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV NUMBER NO. Monticello Nuclear Generating Plant 263 052 2023 - 002 - 00 | EVENT DESCRIPTION On September 27, 2023 Monticello Nuclear Generating Plant (MNGP) was operating in Mode 1 and approximately 75 percent power for the semiannual Turbine-Generator Operational Tests. At 1041 Central Daylight Time (CDT), while cycling closed the Turbine Control Valve 4 (CV-4) per the Turbine CV Test, an unplanned Reactor Scram, Group I Primary Containment Isolation, and Group II Primary Containment Isolation occurred. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) for an event or condition that resulted in the automatic actuation of the Reactor Protection System (RPS) [EIIS CODE: JC] including reactor scram and containment isolation signals affecting containment isolation valves in more than one system and multiple Main Steam Isolation Valves (MSIVs) [EIIS CODE: ISV]. EVENT ANALYSIS The Turbine Control Valves (CVs) [EIIS CODE: FCV] are a part of the MNGP Main Turbine System [EIIS CODE: TA]. The CVs control reactor pressure, in conjunction with the turbine bypass valves, by adjusting position to control steam flow. During the semiannual Turbine-Generator Operational Tests, reactor power is reduced to approximately 75 percent to allow for testing of each of the four CVs. While one CV is stroked closed, the other three CVs are expected to increase percent open to compensate for the increased reactor pressure. While stroking CV-4 closed per the procedure, the percent open of CV-1 and CV-2 initially increased then stalled and CV-3 percent open did not change. In turn, total steam flow through the CVs lowered and the reactor pressure exceeded the (RPV) high pressure scram setpoint, resulting in an automatic Reactor Scram. The RPV water level lowered to below the Group II isolation setpoint as expected, resulting in a Group II Primary Containment Isolation. Additionally, a Main Steam Line high flow condition was sensed in C Main Steam Line, resulting in a Group I Primary Containment Isolation and closure of the Main Steam Isolation Valves. There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. ASSESSMENT OF SAFETY CONSEQUENCES All safety systems functioned properly during the transient. All control rods fully inserted during the scram. The High Pressure Coolant Injection (HPCI) system was placed in service to control RPV pressure, but HPCI did not inject into the RPV and was not needed to control RPV water level. There were no radiological, environmental, or industrial impacts associated with this event. The health and safety of the public and site personnel were not impacted during this event. | ML23317A359
River Bend Station | Unit 1 | Drywell Atmosphere Radiation Monitor Particulate and Gaseous Channels Inoperable due to Out of Tolerance Conversion Factors | 11-15-2023 | On August 29, 2023, with River Bend Station (RBS) operating at 100% power, personnel recognized that the Drywell Atmosphere Radiation Monitor (RMS-RE 112) particulate and gaseous channel conversion factors were out of tolerance. The monitor was declared inoperable and the appropriate Technical Specification (TS) Condition was entered. This event was caused by configuration controls that were inadequate to prevent human performance errors in development of radiation detector digital parameters and transfer of parameters into the detector's database at initial setup. The RMS-RE112 conversion factors have been corrected and the monitor was declared operable on September 7, 2023. This condition is being reported as an Operation or Condition Prohibited by Technical Specifications per 10 CFR 50. 73( a)(2)(i)(B). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensmg process and fed back to industry. Send comments regarding burden estimate to the FOIA Library. and Information Colleclion Branch (T-6 A10MJ US. CONTINUATION SHEET Nuclear Regulatory Commission. Washington. DC 20555-0001. or by e-mail to lnfocollects Resourceilnrc gov. and the OMS reviewer at OMS Office of Information and Regulatory Attairs. (3150-0104). Attn: Desk Officer for the Nuclear Regulatory Commission. 725 17th Street NW Washington. DC 20503. e-mail • _ : • . _ - _ . The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor. and a person is not required to respond to a collection of information unless the document stafts:10:22:3 requesting or requiring the collection displays a currently valid 0MB control number 1. FACILITY NAME ■ 2. DOCKET NUMBER 3. LER NUMBER River Bend Station, Unit 1 050 YEAR SEQUENTIAL REV NUMBER NO. 458 □ 2023 - 003 - 01 052 | EVENT DESCRIPTION On August 29, 2023, River Bend Station (RBS) personnel recognized that the Drywell Atmosphere Radiation Monitor (RMS-RE112) [IL] [MON] particulate and gaseous channel conversion factors were out of tolerance. The monitor was declared inoperable and Technical Specification (TS) Limiting Condition of Operation 3.4.7, Reactor Coolant System Leakage Detection Instrumentation, Condition B was entered. The RMS-RE112 conversion factors were corrected, and the monitor was declared operable on September 7, 2023. The discrepancy was identified as part of an extent of condition review performed due to the Notice of Violation (ML23201A 132) issued to RBS on August 15, 2023, for failing to maintain reliable and accurate indications on five effluent radiation monitors. On July 17, 2023, a condition report was initiated requesting a work order to review and validate the RMS-RE112 conversion factors. On August 29, 2023, RBS personnel recognized that information had been available to determine that the conversion factors were out of tolerance since the condition report was initiated on July 17. Therefore, the date of discovery is July 17, 2023. The conversion factors have been out of tolerance for the life of the plant. Therefore, this event is being reported as an Operation or Condition Prohibited by Technical Specifications per 10 CFR 50.73(a)(2)(i)(B). EVENT CAUSE This event was caused by configuration controls that were inadequate to prevent human performance errors in development of radiation detector digital parameters and transfer of parameters into the detector's database at initial setup. SAFETY ASSESSMENT Limits on leakage from the Reactor Coolant Pressure Boundary (RCPB) are required so that appropriate action can be taken before the integrity of the RCPB is impaired. Leakage detection systems for the Reactor Coolant System (RCS) are provided to alert operators when leakage rates above normal background levels are detected and to supply quantitative measurement of rates. RMS-RE112 comprises one of three RCS leakage detection instrumentation systems required by RBS TS 3.4.7. At least one of the two remaining RCS leakage detection instrumentation systems of TS 3.4.7 remained operable during the 3-year LER past operability period. RMS-RE112 is not used to recognize and properly classify emergency conditions and is not classified as Equipment Important to Emergency Response (EITER). This event was of minimal significance to the health and safety of the public. CORRECTIVE ACTIONS Completed: The RMS-RE112 conversion factors were corrected and the monitor was declared operable on September 7, 2023. NRC Form 366A (10-01-2023) Page _2_ of _3_ | ML23319A429
River Bend Station | Unit 1 | High Pressure Core Spray Inoperable due to Transformer Failure 8. Other Facilities Involved | 11-15-2023 | At 0132 CDT on September 19, 2022, River Bend Station (RBS) was operating at 100% power when the High Pressure Core Spray System (HPCS) was declared inoperable due to a transformer fault that occurred during Division Ill Standby Diesel Generator monthly surveillance testing. RBS entered Technical Specification 3.8.9, Condition E and declared HPCS and Standby Service Water System Pump 2C (SWP-P2C) inoperable. Reactor Core Isolation Cooling (RCIC) was verified operable. HPCS is a single train system at RBS, therefore an 8-hour report was submitted in accordance with 10 CFR 50.72(b)(3)(v)(D) as an event or condition that could have prevented the fulfilment of a safety function (EN 56116). This event is also being reported in accordance with 10 CFR 50. 73(a)(2)(v)(D) as an event or condition that could have prevented the fulfilment of a safety function. The condition was corrected by replacing the transformer on September 30, 2022. HPCS and SWP-P2C were restored to operable at 0921 CDT on September 30, 2022. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comp� wrth this mandatory collection request. 80 hours Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry Send comments regarding burden estimate to the FOIA Library. and lnfomnation Colleclion Branch (T-6 A10M). US CONTINUATION SHEET Nuclear Regulatory Commission. Washington. DC 20555-0001. or by e-mail to lnfocollects Resource il nrc.gov. and the 0MB reviewer at: 0MB Office of lnfomnation and Regulatory Affairs. (3150-0104). Attn. Desk Officer for the Nuclear Regulatory Comm,ssion. 725 17th Street NW. Washington. DC 20503: e-mail The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor. and a person is not required to respond to a collection of information unless the document htto \','.'✓W .. r1r:rfQ:i_§tc{f�srJ02_ 2 r3 requesting or requiring the collection displays a current� valid 0MB control number 1. FACILITY NAME ■ 2. DOCKET NUMBER 3. LER NUMBER River Bend Station, Unit 1 050 YEAR SEQUENTIAL REV NUMBER NO. 458 □ 2022 - 004 - 01 052 | EVENT DESCRIPTION At 0132 CDT on September 19, 2022, River Bend Station (RBS) was operating at 100% power. There were no other inoperable structures, systems, or components (SSCs) that contributed to this event. The Division Ill Diesel Generator [DG] was started per STP-309-0203, DIVISION Ill DIESEL GENERATOR OPERABILITY TEST. Approximately 5 seconds later the Main Control Room received multiple alarms on Division 3 components. The field operator performed a visual inspection of the Division Ill switchgear and discovered that the E22-S003, HPCS TRANSFORMER [XFMR] was damaged. The Division Ill Diesel Generator was secured and placed in maintenance mode. The transformer failure caused a loss of power to E22-S002, Division Ill 480 VAC switchgear [SWGR]. E22-S002, Division Ill 480 VAC switchgear supplies power to HPCS motor operated valves that are required to align flow to the reactor pressure vessel following system initiation. RBS entered Technical Specification (TS) 3.8.9, Condition E and immediately declared the High Pressure Core Spray System (HPCS) [BG] and Standby Service Water System Pump 2C (SWP-P2C) [Pl inoperable. This also placed RBS in a 14-day TS LCO shutdown action statement due to the inoperability of HPCS. Reactor Core Isolation Cooling (RCIC) [BN] was verified operable. On June 21, 2022, Preventive Work Order 53003640 was performed on the transformer. No signs of degradation were noted, and all acceptance criteria were met satisfactory. Following the completion of the preventive work and prior to the transformer fault, STP-309-0203, DIVISION Ill DIESEL GENERATOR OPERABILITY TEST was successfully completed on July 25, 2022, and again on August 22, 2022. Prior to this event HPCS and the Division 3 Transformer power source were operable. At time of discovery, the HPCS lost its initiation capability because the E22-S002, Division Ill 480 VAC switchgear would not have been powered from the Division Ill Standby Diesel Generator on any HPCS initiation signal. HPCS was inoperable and incapable of performing its design function during this event. RBS is reporting the event in accordance with 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfilment of a safety function. SAFETY ASSESMENT The RBS UFSAR states that in the event of a HPCS system failure such that HPCS cannot maintain reactor water level, the Automatic Depressurization System (ADS), which is independent of any other Emergency Core Cooling System (ECCS), reduces the reactor pressure so that flow from Low Pressure Coolant Injection (LPCI) [BO] and Low Pressure Core Spray (LPCS) [BM] systems enters the reactor vessel in time to cool the core and limit fuel cladding temperature. Additionally, high pressure makeup was available from RCIC. Two of three divisions of ECCS are required for the RBS loss of coolant accident analysis. While HPCS was out of service, Division 1 ECCS and Division 2 ECCS systems and ADS were operable and would have met the ECCS performance criteria of 1 0CFR50.46. The out of service time was maintained within the limits of RBS Technical Specifications. There were no actual Nuclear or Radiological safety consequences due to this event. This event was of minimal significance to the health and safety of the public. NRC Form 366A (10-01-2023) Page _2_ of _3_ | ML23319A436
Grand Gulf Nuclear Station | Unit 1 | Valve Closure Test Failure Resulting in Condition Prohibited by Technical Specification | 11-30-2023 | On June 13, 2023, while trending as found periodic data from motor operated valve diagnostic test on 1 E61 F003B Drywell Purge Inlet Isolation Valve, it was identified that the butterfly valve disc was traveling past the valve seat, resulting in 1 E61 F003B and Division 2 of the drywell purge and initial vacuum relief subsystem being declared inoperable. 1 E61 F003A Division 1 drywell purge and initial vacuum relief subsystem was operable during this time. Per Grand Gulf Technical Specifications, two drywell post-Loss-of-Coolant Accident and two drywell purge vacuum relief subsystems shall be operable in MODES 1, 2 and 3. Division 2 drywell purge and vacuum relief subsystem was determined to have been inoperable since October 26, 2017. There were no consequences to the general safety of the public, nuclear safety, industrial safety or radiological safety. No radiological releases occurred due to this event. This report is made pursuant to 10 CFR 50.73 (a)(2)(i)(B), any operation or condition which was prohibited by the plant's Technical Specifications. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request 80 hours Reported LICENSEE EVENT REPORT (LER) lessons leamed are il<:orporated ilto the licensilg process and fed back to industry Send comments regardi1g burden estvnate to the FOIA. Library, and Information Colection Branch (T-6 A10M). US. CONTINUATION SHEET Nuclear Regulatory Convnission, Washr,gton, OC 20555-0001, or by e-mai to fnfocoUects Resource@nrc gov, and the 0MB reviewer at: 0MB Office of lnfoITT1Btion and Regulatory Affairs, (3150-0104), Atln: Oesk Officer for the Nuclear Regulatory Coornission, 725 17th Street NW, Washington. DC 20503; e-mail: o,ra subm1ss10n@omb eop gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of infoITT1Btion unless the doeument http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requimg the collection displays a currently valid 0MB control number 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Grand Gulf Nuclear Station, Unit 1 ■ 050 YEAR SE N Q U U M E B N E T R IA L R N E O V . 416 2023 - 001 - 01 □ 052 | Plant Conditions: Mode 1, 98 percent power Description of Event: On October 26, 2017, while performing surveillance for Division 2 post- Loss-of-Coolant Accident (LOCA) Drywell Vacuum Breaker operability, the operator did not observe any movements from the stem of the valve 1 E61 F003B Drywell Purge Inlet Isolation Valve upon initiation. The control room indications were indicating that the valve was opened and closed. Movements of the stem are required for Technical Specification Acceptance Criteria. Thus, the surveillance was completed unsatisfactory. The valve 1 E61 F003B and Division 2 Drywell Purge/Initial Vacuum Relief was declared inoperable. Upon inspection, the spline adapter of valve 1 E61 F003B was found slipping down the valve stem, causing the disengagement between the valve stem and the drive sleeve. Thus, the actuator was moving and indicating opened/closed. However, the valve didn't move. On October 27, 2017, the spline adapter was reinstalled per a work order and surveillance was re-performed satisfactorily. This included a current and switches only diagnostic test which was the current test standard for limit controlled soft seated butterfly valves. On January 24, 2019, it was identified that the diagnostic testing on motor operated valve (MOV) butterfly valves did not currently meet the requirements of GL 96-05/JOG program. This was due to not using a strain gauge to measure valve stem torque. The preventative maintenance requirements (PMRQs) and model work orders (MWOs) were updated for all applicable butterfly valves to reflect that the diagnostic testing required measuring the valve stem torque. On June 6, 2023, the periodic 1 E61 F003B MOV diagnostic test was performed with strain gauge on the stem per work order. The test data was within the criteria in the motor operator valve data record. On June 13, 2023, while trending as found periodic data from the MOV diagnostic test on 1 E61 F003B, it was identified that the butterfly valve's disc is traveling past the valve seat, resulting in valve 1 E61 F003B and Division 2 Drywell Purge/Initial Vacuum Relief being declared inoperable. The test data indicates that the valve is contacting the seat at 40 secs of the full 60 sec stroke time. After contacting the seat, the seating torque decreases (relaxes) and the valve continues to travel for 20 secs past the seat. This MOV design has a full travel of 90 degrees. With the actuator in the full open position, the valve disk is 60 degrees open. Conversely with the actuator in the full closed position, the valve disk is 30 degrees open. This valve has no torque switch in the circuit and is seated using the limit switches. On June 16, 2023, the actuator/valve assembly was adjusted to the proper required position per work order. This was followed by a satisfactory as left diagnostic test using strain gauge to measure valve stem torque. The diagnostic test indicated that the valve disk is now going to full closed position when the actuator is stroked to the full close position. NRC Form 366A (10-01-2023) Page _2_ of __3 _ | ML23334A051
Quad Cities Nuclear Generating Station | Unit 2 | Turbine Trip and Automatic Reactor Scram due to High Moisture Separator Level | 11-30-2023 | On August 11, 2023, at 0329, Quad Cities Unit 2 had an automatic scram from full power due to a trip of the main turbine. A fault in the Essential Service System (ESS) caused a feedwater heater (FWH) system transient. The drain valve for the 2A Moisture Separator Drain Tank (MSDT) did not open rapidly enough to prevent water level in the moisture separators from reaching the established turbine trip setpoints. The Unit 2 Main Turbine tripped as designed and generated an automatic reactor scram. All control rods inserted and the scram was uncomplicated. Containment isolation valves actuated closed in multiple systems on a valid Group II signal. The cause of the event is an improperly tuned Level Controller for the 2A MSDT allowing the high level turbine trip to be reached following a FWH transient. Completed corrective action was a component recalibration. Planned actions are procedure changes and training. This report is being submitted per 10 CFR 50.73(a)(2)(iv)(A) for an event that resulted in manual or automatic actuation of the reactor protection system including a reactor scram. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Litrary, and Information CoDections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of lnfonnation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclea.< Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of infonnalion unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3Q requesting or requiring the collection displays a currently vaUd 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 00 050 SEQUENTIAL REV YEAR NUMBER NO. Quad Cities Nuclear Generating Station Unit 2 05000-265 0 052 2023 - 001 01 | PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in text as [XX]. EVENT IDENTIFICATION Turbine Trip and Automatic Reactor Scram due to High Moisture Separator Level CONDITION PRIOR TO EVENT Unit: 2 Event Date: August 11, 2023 Event Time: 0329 CDT Reactor Mode: 1 Mode Name: Power Operation Power Level: 100% No structures, components, or systems that were inoperable at the start of the event that contributed to the event. A. DESCRIPTION OF EVENT On August 11th, 2023, at 0329, Quad Cities Unit 2 had an automatic scram from full power due to a trip of the main turbine [TRB]. A fault in the Essential Service System (ESS)[UJX] caused a feedwater heater (FWH)[HX] system transient. The drain valve [LC] for the 2A Moisture Separator Drain Tank (MSDT)[SN][TK] did not open rapidly enough to prevent water level in the moisture separators [MSR] from reaching the established turbine trip setpoints. The Unit 2 Main Turbine tripped as designed and generated an automatic reactor scram. All control rods were inserted and the scram was uncomplicated. Containment isolation valves actuated closed in multiple systems on a valid Group II signal. B. CAUSES OF EVENT The cause of the scram was an improperly tuned emergency level control valve (LCV) for a MSDT. Tuning was performed by a utility technician based on knowledge of the component and their understanding of plant response without adequate work instructions. There was no evidence of time pressure during this evolution. The controller's [LCO] setpoints were configured to provide a slower response than was appropriate for responding to a FWH level transient. In this case, the valve did not respond rapidly enough to prevent overfilling the associated MSDT and eventually tripping the turbine on high level in the moisture separators. C. SAFETY ANALYSIS SYSTEM DESIGN Moisture Separator Drain Tank Level Controller High pressure turbine exhaust steam is routed to four moisture separators prior to entering the low-pressure turbines. Steam passes through chevron separator elements to remove water droplets which drain to two MSDTs. On a High Level in the MSDT, the MSDT emergency drain valve opens and the normal MSDT LCV | ML23334A076
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Misaligned Spacer Prevented Tie Breaker Closing Coil Armature Operation on a Magne-Blast for EDG A Subsystem | 12-01-2023 | On April 12, 2023, with James FitzPatrick Nuclear Power Plant (JAF) was at 100% power the Emergency Diesel Generator (EDG) “A” and “C” tie breaker (71-10504) did not close during a performance of monthly full load surveillance test (ST-9BA). This was caused by binding of the closing coil armature of the breaker due to a misaligned spacer installed in June 2021. The cause of this condition is inadequate procedural guidance to ensure proper orientation/alignment of the close coil sleeve and spacers. Tie breaker failure to close rendered the “A” Emergency Diesel Generator (EDG) subsystem inoperable. It was determined that this deficiency began after the last successful test/actuation on March 13, 2023. This condition was prohibited by Technical Specifications (TS), which is reportable per 10 CFR 50.73(a)(2)(i)(B) and 10 CFR 50.73(a)(2)(v)(A). The condition was corrected when the 71-10504 Tie Breaker was replaced on April 13, 2023. A corrective action was completed to revise MP-054.01 and MP-054.03 to improve spacer installation process and ensure proper breaker actuation. NRC FORM 366 (10-01-2023) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 LICENSEE EVENT REPORT (LER) hours. Reported lessons learned are incorporated into the licensing process and fed CONTINUATION SHEET back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory (See NUREG-1022, R.3 for instruction and guidance for completing this form Commission, 725 17th Street NW, Washington, DC 20503; email: http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 YEAR SEQUENTIAL REV NUMBER NO. James A. FitzPatrick Nuclear Power Plant 05000333  052 2023 – 004 – 00 | Background The Emergency Onsite Power Supply System [EIIS identifier: EK] consists of two redundant Emergency Diesel Generator (EDG) subsystems. Each EDG subsystem consists of two EDG units. The capability of the two units in the subsystem to start, force parallel, and attain rated voltage and frequency together within 10 seconds, and run the necessary engineered safeguard loads, meets the requirements for the Emergency AC Power System. The EDG logic system utilizes a force parallel design. This allows two EDG units to parallel onto the respective Emergency AC bus together to provide a combined load. The “A” subsystem tie breaker (71-10504) force parallels the “A” and “C” EDG units. Event Description On April 12, 2023, with James FitzPatrick Nuclear Power Plant (JAF) at 100% power the EDG “A” and “C” tie breaker (71-10504) did not close during a performance of monthly full load surveillance test (ST-9BA). The “B” EDG subsystem was verified to be operable. Troubleshooting identified that the issue was internal to the breaker. On April 13, the 71-10504 Magne-Blast circuit breaker was replaced and at 23:00 the “A” EDG subsystem was restored to service. Total out of service time was approximately 43 hours. Event Analysis The removed Magne-Blast circuit breaker was sent to General Electric (GE) for evaluation. The GE investigation identified that intermittent binding of the close coil armature occurred, which prevented the full stroke required to close the circuit breaker. The binding was repeated multiple times during the investigation. Visual inspection confirmed the closing coil appeared to be askew in the assembly and the spacers were not aligned correctly. The misaligned spacer did not allow the closing coil sleeve to seat properly in the cutout of the support. This decreased the clearance required for the closing coil armature to move freely inside the full length of the assembly. The decreased clearance caused the armature to bind against the spacer and the inside of the sleeve. The armature does not experience binding in all positions of the armature. The armature was rotated and then it was identified that it only became bound in certain positions. A properly installed coil assembly will not become loose, and closing coil will be able to operate without binding. It was determined that the misaligned spacer was installed in June 2021 when 71-10504 was replaced. All subsequent surveillance tests were successful from June 2021 until the failure on April 12, 2023. On October 19, 2023, JAF performed tests of the removed breaker closing coil armature to demonstrate how the armature rotates during each breaker actuation. It rotates at a regular fix quantity during each actuation; therefore, the specific position which caused binding was rotated to that position during the last test on March 13, 2023. Based on this evaluation, the “A” EDG subsystem tie breaker 71-10504 would not have closed between March 13 and April 12, a condition which would have caused the “A” EDG subsystem to be inoperable. Page 2 of 4 | ML23335A068
i | Unknown Unit | Turbine Stop Valve Limit Switch Failure due to Lubricant Degradation | 12-04-2023 | On 9/7/2023 during surveillances of the turbine stop valves (TSV), limit switch 1 C71-N006G failed. The component was sent offsite for failure analysis. Component failure analysis was complete on 10/18/2023 and determined that the cause was attributed to degradation of switch lubricant which established firm evidence that a past inoperability condition existed. The component 1C 71-N006G is the TSV-4 closure Reactor Protection System (RPS) channel A2 scram limit switch. This device is required by technical specifications to support LCO 3.3.1.1 function 8 (RPS) and LCO 3.3.4.1 (End of Cycle - Recirculation Pump Trip or EOC-RPT). Each TSV position is monitored by two limit switches (for TSV-4, A2 and 82 channels). This condition results in the TSV-4 input to RPS A2 as well as one channel of the EOC-RPT trip being INOPERABLE. The appropriate LCO Conditions and Required Actions were entered and tracked. The RPS and EOC RPT functions were maintained due to the redundant channels remaining OPERABLE. There were no reportability thresholds applicable to this issue at the time of the event, and there was no loss of safety function. The condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) for operation or condition prohibited by Technical Specifications. Immediate corrective actions were taken to replace the component and restore the associated channel to OPERABLE. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send conments regarding burden estimate to the FOIA, Library, and lnfonnation Collections Branch (T-6 A10M), U.S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mai to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Slreet NW, Washington, DC 20503; e-mal: oira submiss1on@omb.eop.gov. The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document h Hp://www.nrc.gov/reading-rm/d oc-co Il ections/nuregs/staff/ sr1 022/r3/) requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Ix] 050 YEAR SEQUENTIAL REV LaSalle County Station, Unit 1 (cid:143) 00373 2023 - 002 00 052 | Plant and System Identification LaSalle Country Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the main turbine system. The affected component was the turbine stop valve (TSV) limit switch 1C71-N006G. This is the limit switch for the TSV number 4 Closure Reactor Protection System (RPS) A2 channel. Condition Prior to Event Unit(s): 1 Date: October 18, 2023 Time: 00:00 CDT Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 100 percent Description On 09/07/2023 the limit switch on Unit 1 TSV-4 failed to actuate during surveillance testing. The limit switch is normally held in the actuated position during unit operation and only allowed to return to the relaxed, shelf state position, upon closure of the turbine stop valve. The failed limit switch, 1C71-N006G, was replaced and sent offsite for component testing and failure analysis. The component failure analysis (documented in report dated October 18, 2023) verified the limit switch malfunction and determined the cause was attributed to degradation of switch lubricant. Cause Analysis attributed the failure to the switch shaft and shaft bearing degraded lubrication causing the shaft to bind in the actuated (Turbine Stop Valve open) position. The cause of the limit switch lubricant degradation was elevated temperatures due to a steam leak in close proximity. This steam leak has circumvented previous corrective actions such as use of high temperature switches and limit switch housing modifications. Reportability and Safety Analysis The component 1C71-N006G is the TSV-4 Closure RPS channel A2 scram limit switch. This device is required to be OPERABLE per LCO 3.3.1.1 Function 8 (RPS) and LCO 3.3.4.1 (EOC-RPT). TSV-4 was fully closed during the surveillance, which should have resulted in the 1C 71-N006G switch being open. Each TSV position is monitored by two limit switches (for TSV-4, A2 and B2 channels). This condition results in the TSV-4 input to RPS A2 as well as one channel of the EOC-RPT trip being INOPERABLE. The appropriate LCO Conditions and Required Actions were entered and tracked. The RPS and EOC-RPT functions were maintained due to the redundant channels remaining OPERABLE. There were no reportability thresholds applicable to this issue at the time of the event, and there was no loss of safety function. Upon receipt of the failure analysis on October 18, 2023, the station was made aware that a past inoperability period existed from the test failure that occurred on September 7, 2023. The inoperability period was greater than allowed by TS LCO 3.3.1.1 and 3.3.4.1, as indicated below. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's TS. • LCO 3.3.1.1 requires that the RPS instrumentation for each function is OPERABLE, and Condition A applies to one or more required channels being inoperable requires that the channel or its associated trip system is placed in trip within 12 hours. In this case, the station had exceeded the completion time of 12 hours, when the | ML23338A183
Monticello Nuclear Generating Plant | Unknown Unit | Condition Prohibited by Technical Specifications due to Inoperable Main Steam Line Low Pressure Isolation Switch | 12-04-2023 | On October 10, 2023 at 0826, with Monticello Nuclear Generating Plant in Mode 1 at 100 percent power, calibration commenced for PS-2-134B, the B1 Channel Main Steam Line Low Pressure Isolation switch. The calibration is required for the Low Main Steam Line Pressure Isolation function for Technical Specification 3.3.6.1, Primary Containment Isolation Instrumentation. The B1 Channel switch was found out of tolerance low. On October 7, 2023 at 0228, while at 10 percent power, the plant entered Mode 1, which is the Mode of Applicability for this Technical Specification 3.3.6.1 function. The condition of inoperability of the B1 Channel was not known upon entering Mode 1 and the required technical specification actions to place this Channel in trip were not taken. This event is reportable under 10CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by TS 3.3.6.1. The cause of the inoperability was instrument drift. The B1 Channel switch was brought within tolerance prior to completion of the B1 channel calibration procedure on October 10, 2023 at 0901. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported r;»•"fOt,<., lessons learned are incorporated into the licensing process and fed back to industry. Send comments l~\ LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. = : Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET \ .r Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory ., •it••·♦ Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME ■ 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV I I~ I I □ NUMBER NO. Monticello Nuclear Generating Plant 263 D 052 2023 - I 003 - 00 I | EVENT DESCRIPTION On October 10, 2023 at 0826, with Monticello Nuclear Generating Plant in Mode 1 at 100 percent power, testing commenced for PS-2-134B [EIIS CODE: JM], the B1 Channel Main Steam Line Low Pressure Isolation switch, per the quarterly Technical Specification (TS) Surveillance Requirement (SR) 3.3.6.1.4 channel calibration procedure for function 1.b. Function 1.b is the Low Main Steam Line (MSL) Pressure Isolation function for TS 3.3.6.1, Primary Containment Isolation Instrumentation. The B1 Channel switch was found out of tolerance at 641.6 psig compared to the TS allowable value of greater than or equal to 815 psig. The B1 Channel switch was brought into tolerance prior to completion of the B1 Channel switch SR 3.3.6.1.4 channel calibration procedure on October 10, 2023 at 0901. On October 24, 2023, a review of past Operability was completed for the B1 Channel switch. The B1 Channel switch as- found and as-left values were acceptable during the previous SR 3.3.6.1.4 channel calibration procedure on July 3, 2023. Based on review of the plant process computer MSL pressure data, the B1 Channel switch acceptably tripped at greater than the TS allowable value during the September 27, 2023 Scram. However, when the plant was starting up, in Mode 2, at 4 percent power on October 7, 2023 at 0047, the data showed the B1 Channel switch reset prior to 686.7 psig. Since this switch is designed to reset at a higher pressure than the trip pressure, this was the first indication that the B1 Channel switch was below the allowable value. Since the plant mode switch was in Startup, the MSL low pressure Containment Isolation signal was bypassed. On October 7, 2023 at 0228 while at 10 percent power, the plant entered Mode 1, which is the Mode of Applicability for Technical Specification 3.3.6.1 function 1.b. The condition of inoperability of the B1 Channel was not known upon entering Mode 1 and the required technical specification actions to place this Channel in trip were not taken. The Primary Containment Isolation system receives inputs from four channels for the MSL Low Pressure trip function. The trip function, active only during Mode 1, uses a one-out-of-two taken twice logic to initiate isolation of all Main Steam Isolation valves (MSIVs), MSL drain valves, and recirculation sample isolation valves. One of the two A channels and one of the two B channels must trip to initiate the Primary Containment Isolation. In Mode 1, with one channel inoperable, TS 3.3.6.1 Condition A requires placing that channel in trip within 24 hours. When Condition A is not met, Condition E, as directed by Condition C and Table 3.3.6.1-1 requires entry to Mode 2 within 6 hours. This event is reportable under 10 CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by TS 3.3.6.1. DATES AND APPROXIMATE TIMES OF MAJOR OCCURANCES • July 3, 2023 at 0850: The B1 Channel switch as-found and as-left values were acceptable per the SR 3.3.6.1.4 channel calibration procedure. • September 27, 2023 at 1041: During Reactor Scram and Group 1 isolation on C channel MSL high flow, the B1 Channel switch tripped at 925.5 psig, which is acceptably greater than the TS minimum allowable value. • October 7, 2023 at 0047: During plant startup, the B1 Channel switch reset prior to 686.7 psig, which is less than the TS minimum allowable value. • October 7, 2023 at 0228: Event Date. Plant mode switch was placed in run and the plant entered Mode 1. • October 8, 2023 at 0228: The required completion time to place the B1 Channel in trip based on TS 3.3.6.1 Condition A for “One or more required channels inoperable.” • October 8, 2023 at 0828: The required completion time to be in Mode 2 due to TS 3.3.6.1 Condition E, as directed by Condition C and Table 3.3.6.1-1. | ML23338A184
Peach Bottom Atomic Power Station | Unit 3 | Main Steam Isolation Valves Stroke Times Exceed Technical Specification Limit | 12-14-2023 | On October 16, 2023, during performance of a surveillance test while beginning a refueling outage, the stroke times of Main Steam Isolation Valves (MSIVs) exceeded the Technical Specifications limit of five (5) seconds. The apparent causes attributed to two (2) of the MSIVs had the potential to exist during the previous operating cycle. Therefore, the two (2) MSIVs are being reported under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications because the apparent causes had the potential to have existed longer than allowed by Technical Specifications. The condition was corrected and the valves were returned to satisfactory performance by adjusting the dashpots and exhaust restrictors as needed. There were no safety consequences associated with this condition, as the valve stroke times did not exceed the times considered in the safety analysis. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 SEQUENTIAL REV YEAR NUMBER NO. Peach Bottom Atomic Power Station, Unit 3 00278  052 2023 - 002 - 00 | Event Description On October 16, 2023, during performance of a surveillance test, the stroke time of the ‘A’ Outboard Main Steam Isolation Valve (MSIV) exceeded the Technical Specifications limit of five (5) seconds. The valve stroke time was 6.2 seconds. This test was performed in Mode 3 (hot shutdown) while the unit was being shut down for a refueling outage. Transition to Mode 4 (cold shutdown) was made shortly after completion of the test, and the mode of applicability was exited. The cause of the slow stroke time was attributed to drift in the valve dashpot. Follow-up testing was performed during the outage and adjustments were made as needed. The stroke time was verified to be satisfactory before the unit was restarted from the refueling outage. Additionally, the ‘B’ Inboard MSIV also exhibited a slow stroke time of 5.1 seconds. The cause of this condition was attributed to delayed actuation, likely due to debris or contamination in the solenoid valve. The ‘B’ Outboard MSIV stroked in 5.5 seconds, however this could not be replicated in subsequent testing. The stroke times for these valves were adjusted accordingly and were verified to be satisfactory before the unit was restarted from the refueling outage. The remaining valves stroked within specified Technical Specifications limits. There are two (2) MSIVs welded in a horizontal run of each of the four (4) main steam lines, with one (1) valve as close as possible to the primary containment barrier inside, and the other just outside the barrier. The valves, when closed, form part of the nuclear system process barrier. The MSIVs are operated by pneumatic pressure and by the action of compressed springs. The upper end of the valve stem is attached to a combination air cylinder and hydraulic dashpot that are used for opening and closing the valve and for speed control, respectively. Speed is adjusted by a valve in the hydraulic return line alongside the dashpot. Verifying that the isolation times of each MSIV is within the specified Technical Specifications limits is required to demonstrate operability. The isolation time test ensures that the MSIVs will isolate in a time period that does not exceed the times assumed in the design basis accident analyses. In all cases, the times in the accident analysis were not exceeded because the analysis is performed assuming at least 10 seconds for the MSIV closure time. This report is being made under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. Although there was no evidence of degradation during the prior refueling outage or operating cycle, the condition associated with the ‘A’ Outboard MSIV likely existed for longer than allowed by Technical Specifications. Similarly, there was no evidence of degradation for the MSIVs on the ‘B’ main steam line. The time frame associated with the condition which caused the ‘B’ Inboard MSIV to exhibit a slow stroke time cannot be determined, but the valve is conservatively being included in this report. The ‘B’ Outboard MSIV stroke time that was not repeatable has no firm evidence of existing prior to the time of discovery and is not included within the reportable scope of this LER. The performance of the valves has been entered into the Corrective Action Process for further evaluation of the test performance and evaluation methodology. There were no other systems, structures or components that were inoperable that contributed to the event. | ML23348A260
edwin i. hatch | Unknown Unit | Manual Reactor Trip Due To Loss of Feedwater 5. Evant Data I. LER Number 7. Report Data 8. Other FacllltlH Involved Month Day Year y.., lle N q u u m e b n e ll r a l Rev N i o s . i on Month Day y.., Faclllly Name □ 050 Dockal Number - - 11 01 2023 2023 003 00 12 19 r 2023 Faclllly Nam• □ 052 Dockal Number 9. Operating Mode 0. Po-r Laval 1 056 11. This Report Is Submitted Pursuant to the Requirements of 10 CFR §: (Check all that apply) 10 CFR Part 20 □ 20.2203(a)(2)(vl) 10 CFR Part 50 □ 50.73(a)(2)(11)(A) □ 50.73(a)(2)(vlll)(A) □ 73.1200(8) □ 20.2201(b) □ 20.2203(8)(3)(1) □ 50.36(c)(1 )(l)(A) □ 50. 73(8)(2)(11)(8) □ 50.73(a)(2)(vlll)(B) □ 73.1200(b) □ 20.2201(d) □ 20.2203(8)(3)(11) □ 50.36(c)(1 )(ll)(A) □ 50. 73(8)(2)(111) □ 50. 73(a)(2)(Ix)(A) □ 73.1200(c) □ 20.2203(8)(1) □ 20.2203(8)(4) □ 50.36(c )(2) ~ 50. 73(a)(2)(Iv)(A) □ 50.73(a)(2)(x) □ 73.1200(d) □ 20.2203(a)(2)(I) 10 CFR Part 21 □ 50.46(8)(3)(11) □ 50.7 3(a)(2)(v)(A) 10 CFR Part 73 □ 73.1200(e) □ 20.2203(8)(2)(11) □ 21.2(c) □ 50.69(g) □ 50. 73(a)(2)(v)(B) □ 73.77(8)(1) □ 73.1200(f) □ 20.2203(8)(2)(111) □ 50.73(a)(2)(I)(A) □ 50. 73(8)(2)(v)(C) □ 73. 77(8)(2)(1) □ 73.1200(g) □ 20.2203(a)(2)(Iv) □ 50. 73(8)(2)(1)(8) □ 50. 73(8)(2)(v)(D) □ 73. n(a)(2)(11) □ 73.1200(h) □ 20.2203(a)(2)(v) □ 50.73(a)(2)(I)(C) □ 50.7 3(a)(2)(vll) □ OTHER (Specify here, in abstract, or NRC 366A). 12. Licensee Contact for this LER Llcanaaa Contact Phone Number (Include area coda) Jimmv Collins - Licensina Manaaer 9124532342 13. Complete One Line for each Component Failure Described In this Report Cau■a System Component Manufacturer Reportable to IRIS Cause System Component Manufacturer Reportable to IRIS X SJ p 8580 y 14. Supplemental Report Expected Month Day Year 15. Expected SubmlAlon Data ~ No □ Yes (If yes, complete 15. Expected Submission Date) 11. Abatract (Limit to 1326 spaces, i.e., approximalely 13 single-spaced typewritten lines) On November 1, 2023, reactor power was being lowered on Unit 2 to support removal of the 'A' Reactor Feed Pump (RFP} from service due to a suction pipe drain line leak. The 'A' RFP was removed from service and isolated at 0642 EDT. During this evolution, water from the leak on the drain line of the 'A' RFP entered various electrical cabinets and components related to the 'B' RFP, causing the 'B' RFP to trip at 0648 EDT. The trip of the 'B' RFP resulted in a loss of feedwater and lowering of reactor water level. Due to the lowering reactor water level, operators manually inserted a reactor trip in anticipation of water level dropping to the automatic reactor protection system (RPS} trip setpoint. The Reactor Core Isolation Cooling (RCIC) and High Pressure Coolant Injection (HPCI) pumps were used to restore reactor water level. All safety system responded as required. The cause of the leak from the 'A' RFP suction drain line was a pipe shear due to excessive stresses from thermal cycling and flow induced vibration. This was corrected by implementing a design change that cut and capped that portion of piping. The cause of the 'B' RFP trip was electrical grounding due to water intrusion from the 'A' RFP leak resulting in an invalid low suction pressure trip on the 'B' RFP. NRC FORM 388A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Ellllmatad burden per l8Sp0IIS8 to comply with this mandaby collection requell: 80 hours. Reported lessons learned ara lncorporatad Into the lk:enslng process and fed back to lnduatly. Send comments LICENSEE EVENT REPORT (LER) regardng burden estimate to the FOIA, Library, and lnfonnallon Collections Bnlnch (T-8 A10M), U. S. CONTINUATION SHEET Nuclear Regulatory Commlulon, Watlqton, DC 20566-0001, or by email to lnfoc:alledl.Resoun:e@nre.gov, and the 0MB r9¥1eMr at 0MB Offlce of Information and Regulaloly AffallB, (3150-0104), Altn: Delk Officer for the Nuclear Regufaby Commlalion, 725 17th Slreel NW, (See NUREG-1022, R.3 for Instruction and guidance for completing this fonn Washington, DC 20503; ernall: oira submlssicn@omb 80J) gov. The NRC may not conduct or htto·/fwww.nrc.gov/reading-rm/doe:collections/nuregs/staff/s.l1022lQLl sponsor, and a pe!S011 la not required to respond to, a c:olledion of lnfonnatlon unless the d0a1ment requesting or requiring the c:ollection displays a cum,ntly valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV IEdwin I. Halch, Unit 2 00366 _□t5- I NUMBER 1-NO0. I 052 003 NARRATIVE EVENT DESCRIPTION On November 1, 2023, reactor power was being lowered on Unit 2 to support removal of the 'A' Reactor Feed Pump (RFP) [EIIS Code: SJ] from service due to a leak on a drain line connected to the suction piping of the pump. At 0642 EDT with the reactor at approximately 56% rated thermal power, the 'A' RFP was removed from service and isolated. While removing the 'A' RFP from service, water from the leak on the drain line of the 'A' RFP entered various electrical cabinets and components related to the 'B' RFP, causing the 'B' RFP to trip at 0648 EDT. The trip of the 'B' RFP resulted in a loss of feedwater and reactor water level lowering. Due to the lowering reactor water level, operators manually inserted a reactor trip in anticipation of water level dropping to the automatic trip setpoint. The Reactor Core Isolation Cooling (RCIC) [EIIS Code: BN] and High Pressure Coolant Injection (HPCI) [EIIS Code: BJ] pumps automatically started and were used to restore reactor water level. Secondary containment isolated and Standby Gas Treatment (SBGT) [EIIS Code: BH] autostarted, and Group 2 and Group 5 primary containment isolation valves [EIIS Code: JM] isolated as expected when their setpoints were reached. There was no safety related equipment inoperable at this time and no other nonfunctional, non-safety equipment that contributed to this event. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual actuation of the reactor protection system and automatic actuation of general containment isolation signals affecting containment isolation valves in more than one system. Additionally, HPCI and RCIC automatically started when their reactor water level setpoints were reached. EVENT CAUSE ANALYSIS A root cause analysis was performed and determined that the direct cause of the leak from the 'A' RFP suction drain line was a pipe shear due to excessive stresses from thermal cycling and flow induced vibration. The cause of the 'B' RFP trip was electrical grounding due to water intrusion from the 'A' RFP leak resulting in an Invalid low suction pressure trip on the 'B'RFP. SAFETY ASSESSMENT There were no safety consequences as a result of this event. All safety related systems functioned as designed during this event. The operating crew responded correctly to the event. The applicable abnormal/emergency operating procedures were entered. The event was within the analysis of the Updated Final Safety Analysis Report (UFSAR) Chapter 15. No radiological release occurred due to this event. CORRECTIVE ACTION The leak from the 'A' RFP suction piping drain line was corrected by implementing a design change that cut and capped that portion of piping. The cause of the 'B' RFP trip was electrical grounding due to water intrusion from the 'A' RFP leak resulting in an invalid low suction pressure trip on the 'B' RFP. All electrical components related to the 'B' RFP were investigated. Impacted components were dried out or replaced as required. PREVIOUS SIMILAR EVENTS None. NRC FORM 386A (1~1-2023) Page 2 of 2 | 12-19-2023 | 12. Licensee Contact for this LER Llcanaaa Contact Phone Number (Include area coda) Jimmv Collins - Licensina Manaaer 9124532342 13. Complete One Line for each Component Failure Described In this Report Cau■a System Component Manufacturer Reportable to IRIS Cause System Component Manufacturer Reportable to IRIS X SJ p 8580 y 14. Supplemental Report Expected Month Day Year 15. Expected SubmlAlon Data ~ No □ Yes (If yes, complete 15. Expected Submission Date) 11. Abatract (Limit to 1326 spaces, i.e., approximalely 13 single-spaced typewritten lines) On November 1, 2023, reactor power was being lowered on Unit 2 to support removal of the 'A' Reactor Feed Pump (RFP} from service due to a suction pipe drain line leak. The 'A' RFP was removed from service and isolated at 0642 EDT. During this evolution, water from the leak on the drain line of the 'A' RFP entered various electrical cabinets and components related to the 'B' RFP, causing the 'B' RFP to trip at 0648 EDT. The trip of the 'B' RFP resulted in a loss of feedwater and lowering of reactor water level. Due to the lowering reactor water level, operators manually inserted a reactor trip in anticipation of water level dropping to the automatic reactor protection system (RPS} trip setpoint. The Reactor Core Isolation Cooling (RCIC) and High Pressure Coolant Injection (HPCI) pumps were used to restore reactor water level. All safety system responded as required. The cause of the leak from the 'A' RFP suction drain line was a pipe shear due to excessive stresses from thermal cycling and flow induced vibration. This was corrected by implementing a design change that cut and capped that portion of piping. The cause of the 'B' RFP trip was electrical grounding due to water intrusion from the 'A' RFP leak resulting in an invalid low suction pressure trip on the 'B' RFP. NRC FORM 388A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Ellllmatad burden per l8Sp0IIS8 to comply with this mandaby collection requell: 80 hours. Reported lessons learned ara lncorporatad Into the lk:enslng process and fed back to lnduatly. Send comments LICENSEE EVENT REPORT (LER) regardng burden estimate to the FOIA, Library, and lnfonnallon Collections Bnlnch (T-8 A10M), U. S. CONTINUATION SHEET Nuclear Regulatory Commlulon, Watlqton, DC 20566-0001, or by email to lnfoc:alledl.Resoun:e@nre.gov, and the 0MB r9¥1eMr at 0MB Offlce of Information and Regulaloly AffallB, (3150-0104), Altn: Delk Officer for the Nuclear Regufaby Commlalion, 725 17th Slreel NW, (See NUREG-1022, R.3 for Instruction and guidance for completing this fonn Washington, DC 20503; ernall: oira submlssicn@omb 80J) gov. The NRC may not conduct or htto·/fwww.nrc.gov/reading-rm/doe:collections/nuregs/staff/s.l1022lQLl sponsor, and a pe!S011 la not required to respond to, a c:olledion of lnfonnatlon unless the d0a1ment requesting or requiring the c:ollection displays a cum,ntly valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV IEdwin I. Halch, Unit 2 00366 _□t5- I NUMBER 1-NO0. I 052 003 | EVENT DESCRIPTION On November 1, 2023, reactor power was being lowered on Unit 2 to support removal of the 'A' Reactor Feed Pump (RFP) [EIIS Code: SJ] from service due to a leak on a drain line connected to the suction piping of the pump. At 0642 EDT with the reactor at approximately 56% rated thermal power, the 'A' RFP was removed from service and isolated. While removing the 'A' RFP from service, water from the leak on the drain line of the 'A' RFP entered various electrical cabinets and components related to the 'B' RFP, causing the 'B' RFP to trip at 0648 EDT. The trip of the 'B' RFP resulted in a loss of feedwater and reactor water level lowering. Due to the lowering reactor water level, operators manually inserted a reactor trip in anticipation of water level dropping to the automatic trip setpoint. The Reactor Core Isolation Cooling (RCIC) [EIIS Code: BN] and High Pressure Coolant Injection (HPCI) [EIIS Code: BJ] pumps automatically started and were used to restore reactor water level. Secondary containment isolated and Standby Gas Treatment (SBGT) [EIIS Code: BH] autostarted, and Group 2 and Group 5 primary containment isolation valves [EIIS Code: JM] isolated as expected when their setpoints were reached. There was no safety related equipment inoperable at this time and no other nonfunctional, non-safety equipment that contributed to this event. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual actuation of the reactor protection system and automatic actuation of general containment isolation signals affecting containment isolation valves in more than one system. Additionally, HPCI and RCIC automatically started when their reactor water level setpoints were reached. EVENT CAUSE ANALYSIS A root cause analysis was performed and determined that the direct cause of the leak from the 'A' RFP suction drain line was a pipe shear due to excessive stresses from thermal cycling and flow induced vibration. The cause of the 'B' RFP trip was electrical grounding due to water intrusion from the 'A' RFP leak resulting in an Invalid low suction pressure trip on the 'B'RFP. SAFETY ASSESSMENT There were no safety consequences as a result of this event. All safety related systems functioned as designed during this event. The operating crew responded correctly to the event. The applicable abnormal/emergency operating procedures were entered. The event was within the analysis of the Updated Final Safety Analysis Report (UFSAR) Chapter 15. No radiological release occurred due to this event. CORRECTIVE ACTION The leak from the 'A' RFP suction piping drain line was corrected by implementing a design change that cut and capped that portion of piping. The cause of the 'B' RFP trip was electrical grounding due to water intrusion from the 'A' RFP leak resulting in an invalid low suction pressure trip on the 'B' RFP. All electrical components related to the 'B' RFP were investigated. Impacted components were dried out or replaced as required. PREVIOUS SIMILAR EVENTS None. NRC FORM 386A (1~1-2023) Page 2 of 2 | ML23353A109
Nine Mile Point | Unit 1 | Average Power Range Monitors Declared Inoperable Due to Trip of Reactor Recirculation Pump 12 | 12-15-2023 | On October 21, 2023, at 2048 EDT, Reactor Recirculation Pump #12 (RRP 12) tripped. Following the RRP trip, the Average Power Range Monitors (APRMs) flow bias trips were inoperable due to reverse flow through the RRP. The APRMS were restored to operable on October 21, 2023, at 2058 EDT, the RRP 12 discharge blocking valve was closed, eliminating the reverse flow condition, and returning the APRMs to operable. This event is reportable under 10 CFR 50. 73(a)(2)(v)(A) as any event or condition that could have prevented the fulfillment of a safety function of structures or systems that are needed to shut down the reactor and maintain it in a safe shutdown condition. The cause of the RRP 12 trip is a failed coupling on the tachometer generator. Corrective actions included restoring the tachometer to functional. The event described in this LER is documented in the plant's corrective action program report 04711520. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (03-14-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A1 0M), U. S Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington. DC 20503: email: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor. and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nureqs/staff/sr1022/r3D requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 SEQUENTIAL REV YEAR NUMBER NO. Nine Mile Point Unit 1 50-220 □ 052 2023 - 002 - 00 | THE ENERGY INDUSTRY IDENTIFICATION SYSTEM (EIIS) COMPONENT FUNCTION IDENTIFIED AND SYSTEM NAME OF EACH COMPONENT OR SYSTEM REFERRED TO IN THIS LER ARE ENCLOSED WITHIN [BRACKETS] I. DESCRIPTION OF EVENT A. PRE-EVENT PLANT CONDITIONS: Prior to the event, NMP1 was in Mode 1 (Power Operation) at 100% power. B. EVENT: On October 21, 2023, at 2048 EDT, with Nine Mile Point Nuclear Station Unit 1 operating at 100% power, Reactor Recirculation Pump (RRP) [AD] 12 tripped due to a loss of coupling in the tachometer generator, and reactor power lowered to 88%. This trip also resulted in a reverse flow condition through RRP 12. This reverse flow condition results in an unconservative total flow input to the Average Power Range Monitor (APRM) [IG] logic resulting in the APRM flow biased trip set point being higher than the allowable Technical Specification value. As a result, Operations declared the APRMs inoperable. At 2058 EDT, operators stopped reverse flow through RRP 12 by closing the discharge blocking valve, and all APRMs were returned to operable. Control room operators subsequently made an 8-hour report (EN-56810) under 10 CFR 50. 72(b)(3)(v)(A). This event is reportable in accordance with 10 CFR 50. 73(a)(2)(v)(A). C. INOPERABLE SYSTEMS, STRUCTURES, OR COMPONENTS THAT CONTRIBUTED TO THE EVENT: None. D. DATES AND APPROXIMATE TIMES OF MAJOR OCCURENCES AND OPERATOR ACTIONS: The dates, times, major occurrences, and operator actions for this event are as follows. October 21, 2023: 2048 - RRP 12 trips due to loss of tachometer generator coupling, resulting in a reverse flow condition through the pump. APRMs are inoperable due to the reverse flow condition. 2058 - Operators close the RRP 12 discharge blocking valve, arresting the reverse flow condition. APRMs are operable. E. METHOD OF DISCOVERY: This event was self-revealed when reactor recirc pump 12 tripped and control room operators received annunciators for Recirculation Motor Generator Set 12. F. SAFETY SYSTEM RESPONSES: | ML23363A151
Browns Ferry Nuclear Plant | Unit 1 | Standby Liquid Control Inoperable due to Demineralized Water In-leakage | 01-29-2024 | A past operability evaluation determined that for a period of time from January 18 to January 19, 2023, the Standby Liquid Control (SLC) system tank sodium pentaborate (SPB) concentration dropped below the requirements of Technical Specification (TS) Surveillance Requirement 3.1.7.3 which requires the SPB solution to be greater than or equal to 8.0% by weight. The cause of this event was leakage past valve 1-SHV-002-1208, “SLC Demin Water Supply Shutoff Valve,” that allowed demineralized water to dilute the SPB solution in the SLC tank. The past operability evaluation performed by engineering concluded that although SPB concentration dropped below the TS minimum requirements, sufficient SPB solution was available to provide the required pH buffering function; therefore, the safety function of the SLC system was maintained. An engineering change to physically separate the SLC tank from the demineralized water system has been implemented to prevent leakage into the SLC tank. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME (cid:1409) 050 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 1 00259 NUMBER NO. (cid:1407) 052 2023 - 003 - 00 | I. Plant Operating Conditions before the Event At the time of this event, Browns Ferry Nuclear Plant (BFN) Unit 1 was in Mode 1 at approximately 100 percent power. II. Description of Event A. Event Summary On January 19, 2023, engineering noted that the Standby Liquid Control (SLC) system [BR] tank level had increased greater than 1 inch. The SLC tank level was validated by Chemistry per dipstick method and discovered to have risen approximately 2 inches. The cause of the SLC tank level increase was determined to be demineralized water [KC] leaking past valve 1-SHV-002-1208, “SLC Demin Water Supply Shutoff Valve.” The valve was adjusted to stop the leakage of demineralized water into the SLC tank. Chemistry added sodium pentaborate (SPB) to the tank and then analyzed the SLC tank contents to ensure proper limits were met. Following a similar event in November 2023, the operability of the SLC system between the start of the water intrusion and the addition of SPB by Chemistry was questioned for both events. Past operability evaluations were requested for these events on November 14, 2023. Past operability evaluations were performed by engineering on the two events. On November 30, 2023, it was determined that on January 18, 2023, the SLC tank SPB concentration dropped below the requirements of Technical Specification (TS) Surveillance Requirement (SR) 3.1.7.3 which requires the SPB solution to be greater than or equal to 8.0% by weight. Failure to meet TS SR 3.1.7.3 resulted in the SLC system being inoperable. Because the SLC tank is common to both SLC subsystems, the Tennessee Valley Authority (TVA) is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(v)(C) & (D), as any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material; or mitigate the consequences of an accident. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML24029A241
River Bend Station | Unit 1 | Automatic Reactor Scram Due to a Turbine Trip Following a Disconnect Failure at Switchyard | 02-08-2024 | On December 13, 2023, at 01 :02 CST, with River Bend Station, Unit 1, operating in Mode 1 at 100% power, a turbine trip signal resulted in an automatic reactor scram. All control rods fully inserted and there were no complications. All systems responded as designed. The turbine trip signal was caused by a switchyard disconnect that was not properly seated in the saddle of the disconnect fingers, which resulted in an open circuit condition on the output of the main generator. Following a trip of the Reactor Feedwater System due to a Reactor Feedwater Heating isolation, Reactor Core Isolation Cooling was utilized to maintain reactor vessel inventory. The Reactor Feedwater System was restarted once the Reactor Feedwater Heating isolation signal was reset. Reactor water level control was transitioned back to the Reactor Feedwater System. This report is made pursuant to 10 CFR 50. 73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of the Reactor Protection System. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply wnh this mandatory collection request: 80 hours. Reported LICENSEE EVENT REPORT (LER) lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington. DC 20555-0001, or by e-mail to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Ottice of Information and Regulatory Affairs. (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW. Washington, DC 20503; e-mail: oira submission@omb.eop.gov. The NRG may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.n re. gov/reading-rm/doc-collections/nu regs/staff /sr1 022/r3/) requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER River Bend Station, Unit 1 ■ 050 YEAR SEQUENTIAL REV NUMBER NO, 458 2023 006 00 □ 052 | EVENT DESCRIPTION On December 13, 2023, at 01 :02 CST, River Bend Station (RBS), Unit 1, was operating in Mode 1 at 100% power when a turbine trip signal resulted in an automatic reactor scram. All control rods fully inserted and there were no complications. All systems responded as designed. Following the scram, the Reactor Feedwater System (FWS) [SJ] tripped on low suction pressure caused by isolations to both trains of Reactor Feedwater Heating [SJ]. At 01 :08 CST, reactor water level control was transitioned to the Reactor Core Isolation Cooling (RCIC) [BN] system to maintain inventory of the reactor vessel. At 01 :10 CST, Reactor Feedwater System Pump B (FWS-P1 B) [SJ] was restarted. At 01 :14 CST, reactor water level control was transitioned back to FWS and RCIC was secured. Reactor pressure was maintained by the Turbine Bypass Valves (JI). This event was reported under 10 CFR 50.72(b)(2)(iv)(B), as any event or condition that results in actuation of the Reactor Protection System (RPS) when the reactor is critical and 10 CFR 50.72(b)(3)(iv)(A) Specified System Actuation as result of Group 3 isolations (EN 56887). This report is made pursuant to 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of the Reactor Protection System. EVENT CAUSE The cause of the turbine trip signal was due to a Generator Side Disconnect [DISC] switch failing as a result of not being fully seated in the saddle of the disconnect fingers. This created a hotspot that melted the pads to the point where the cable connections faulted between the disconnect and the triad jumper cable to the next length of bus work. The damaged disconnects resulted in an open circuit condition on the output of the Main Generator. After further investigation, it was determined that the disconnects were not properly seated in the saddle of the disconnect fingers because of personnel error. During the closing of the disconnects following maintenance activities, the disconnects were locked in a partially closed position. The movable members were closed, but not all the way to their mechanical stops. SAFETY ASSESSMENT There were no actual Nuclear or Radiological safety consequences due to this event. Thus, this event was of minimal significance to the health and safety of the public. The plant response to this event was bounded by the Updated Safety Analysis Report analysis of a Main Turbine Trip with Steam Bypass Valves/Pressure Regulators in service. NRC form 366A (10-01-2023) Page _2_ of _3_ | ML24039A130
Edwin I. Hatch Nuclear Plant | Unit 2 | Unit 2 High Pressure Coolant Injection (HPCI) System Inoperable | 02-14-2024 | At 0223 EST on 12/18/2023, while Unit 2 was at 100% power in MODE 1, the High Pressure Coolant Injection (HPCI) outboard steam isolation valve received a spurious close signal resulting in the HPCI system being isolated and unavailable to automatically start. Consequently, HPCI was declared inoperable. The cause of HPCI isolating was electronic noise stemming from the age-related failure of a Reactor Core Isolation Cooling (RCIC) Analog Transmitter Trip System (ATTS) card. The manner in which the RCIC ATTS card failed did not adversely affect the operability of RCIC. However, due to the proximity of the RCIC ATTS card and the HPCI ATTS card (both located on the same instrument rack), the electronic noise caused the HPCI ATTS card to introduce a spurious signal to isolate the HPCI system. The RCIC System and the low pressure Emergency Core Cooling Systems (ECCS) were operable and available during this event. Subsequently, the failed RCIC A TTS card was replaced and operability of the HPCI System was restored at 0512 EST on 12/18/2023 by resetting the isolation signal and returning the system to standby line up. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ~ 050 I SEQUENTIAL REV YEAR NUMBER NO. Edwin I. Hatch Nuclear Plant Unit 2 00366 • 120241 -I 1-G □ 052 I 001 | EVENT DESCRIPTION At 0223 EST on 12/18/2023, while Unit 2 was at 100% power in MODE 1, the High Pressure Coolant Injection (HPCI) (EIIS: BJ) outboard steam isolation valve received a spurious close signal resulting in the HPCI system being isolated and unavailable to automatically start. Consequently, HPCI was declared inoperable. The spurious HPCI isolation was due to electronic noise stemming from a failed Reactor Core Isolation Cooling (RCIC) (EIIS: BN) Analog Transmitter Trip System (ATTS) card (EIIS: TIS). The RCIC ATTS card was replaced and HPCI was restored to operable status at 0512 EST on 12/18/2023. The RCIC System and the low pressure Emergency Core Cooling Systems (ECCS) were operable and available during this event. FAILED COMPONENTS INFORMATION: Master Parts List Number: 2E51 N666B Manufacturer: General Electric Model Number: GE P/N 184C5988G201 Type: Analog Transmitter Trip System (ATTS) EVENT CAUSE ANALYSIS The cause of HPCI isolating was electronic noise stemming from the age-related failure of a RCIC ATTS card. The manner in which the RCIC ATTS card failed did not adversely affect the operability of RCIC. However, due to the proximity of the RCIC ATTS card and the HPCI ATTS card (both located on the same instrument rack), the electronic noise caused the HPCI ATTS card to introduce a spurious signal to isolate the HPCI system. SAFETY ASSESSMENT Even though HPCI lost its ability to automatically start, the RCIC System and the low pressure ECCS were operable and available during this event. However, because HPCI does not have a redundant system the isolation of the HPCI System and loss of its automatic functions represents a condition that could have prevented the fulfillment of the HPCI safety function to mitigate the consequences of an accident and is reportable per 50.73(a)(2)(v)(D). There were no actual safety consequences as a result of this event. The event was within the analysis of the UFSAR Chapter 15. CORRECTIVE ACTIONS The failed RCIC ATTS card was successfully replaced and operability for the HPCI System was restored at 0512 EST on 12/18/2023 by resetting the isolation signal and returning the system to standby line up. An extent of condition is being performed to identify other ATTS cards located in the same panels that could potentially be susceptilble to failure due to electronic noise. Additionally, preventative maintenance strategies are being created to replace ATTS cards prior to age-related failure. PREVIOUS SIMILAR EVENTS On March 28, 2023, with Unit 1 at 100% rated thermal power, an operability review concluded that the High Pressure Coolant Injection (HPCI) pump would not have automatically started during a 22 minute period on March 18, 2023 when an invalid high suppression pool water level signal was received and before the signal was reset. Causal analysis determined that the failure of an unrelated instrument card, located on the same instrument rack as the instrument card monitoring Unit 1 suppression pool water level, caused a momentary voltage perturbation on the rack, likely leading to an invalid suppression pool water level high signal from the suppression pool water level instrument card. This high-level signal caused the Unit 1 HPCI system trip solenoid to actuate. There was no actual high level in the Unit 1 suppression pool. Corrective actions included resetting the invalid suppression pool level high signal and replacing the failed instrument card. | ML24045A152
Catawba Nuclear Station | Unit 2 | Condition Prohibited by Technical Specifications and Loss of Safety Function due to Failed Damper Controller for the 2A 1 Emergency Diesel Generator Room Ventilation Fan | 03-04-2024 | On January 2, 2024, the 2A Emergency Diesel Generator (DG) was unloaded and secured prior to the completion of a periodic 5-hour run due to rising temperatures and air quality conditions in the 2A DG room. It was determined that the 2A1 Emergency Ventilation Fan Damper Controller was failed and did not allow the normal amount of outside air to circulate into the room. Additionally, the 2A2 Emergency Ventilation Fan was out of service in support of maintenance activities. As a result, 2A DG room temperatures increased to an off-normal level less than the alarm setpoint. The 2A DG was declared inoperable until the degraded damper controller was repaired. Further investigation revealed Catawba Nuclear Station had evidence the condition of the failed 2A 1 Damper Controller, combined with the out of service 2A2 Ventilation Fan, had existed since December 5, 2023. A review performed for the timeframe between December 5, 2023, and January 2, 2024, identified the 2A DG VD system was non-functional during this time, resulting in the 2A DG being inoperable. This resulted in instances which represented conditions prohibited by Technical Specifications, and instances of a loss of safety function. There was no impact to the health and safety of the public. NRC FORM 366A (10-01-2023) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nureqs/staff/sr1022/r3/) 1. FACILITY NAME Catawba Nuclear Station, Units 1 and 2 | BACKGROUND ■ 050 □ 052 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A 10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001 , or by email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Offcer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 2. DOCKET NUMBER YEAR 00413, 00414 2024 - 3. LER NUMBER SEQUENTIAL NUMBER 001 REV NO. 00 The following information is provided to assist readers in understanding the event described in this LER. Applicable Energy Industry Identification System [EIIS] and component codes are enclosed within brackets. Catawba's unique system and component identifiers are contained within parentheses. !This event is being reported under 10 CFR 50. 73(a)(2)(i)(B) for condition prohibited by Technical Specifications (TS) and 10 CFR 50. 73(a)(2)(v)(A), (B), and (D) for an event or condition that could have prevented the fulfillment of a Safety Function. The onsite standby power source for each 4160 volt Engineered Safety Features (ESF) bus at Catawba is a dedicated Diesel Generator (DG)[EK]. For each unit, DGs A and Bare dedicated to ESF buses ETA and ETB, respectively. Each DG starts automatically on a Safety Injection (SI) signal (i.e., low pressurizer pressure or high containment pressure) or on an ESF bus degraded voltage or undervoltage signal. After the DG has started, it will automatically tie to its respective bus after offsite power is tripped as a consequence of ESF bus undervoltage or degraded voltage, independent of or coincident with an SI signal. The DGs will also start and operate in the standby mode without tying to the ESF bus on an SI signal alone. Following the trip of offsite power, a sequencer strips loads from the ESF bus. When the DG is tied to the ESF bus, loads are then sequentially connected to its respective ESF bus by the automatic load sequencer. In the event of a loss of preferred power, the ESF electrical loads are automatically connected to the DGs in sufficient time to provide for safe reactor shutdown and to mitigate the consequences of a Design Basis Accident such as a Loss of Coolant Accident (LOCA). There are also provisions to accommodate the connecting of the Emergency Supplemental Power Source (ESPS) ~o one train of either unit's Class 1 E AC Distribution System (ESF). The ESPS consists of two 50% capacity non- safety related commercial grade DGs. Manual actions are required to align the ESPS to the station and only one of the station's four onsite Class 1 E Distribution System trains can be supplied by the ESPS at any given time. The ESPS is made available to support extended Completion Times in the event of an inoperable DG as well as a defense-in-depth source of AC power to mitigate a station blackout event. The ESPS would remain disconnected rom the Class 1 E AC Distribution System unless required for supplemental power to one of the four 4.16 kV ESF buses. The primary purpose of the Diesel Building Ventilation System (VD)[VJ] is to maintain the temperature within ~he minimum and maximum limits for operation of equipment and personnel access for inspection, testing, and maintenance. The ESF Actuation System actuates the Diesel Building Ventilation System to maintain proper ventilation of the Diesel Building for equipment operation. The Diesel Generator Emergency Ventilation portion of the VD System is required to maintain the Diesel Building temperature between 60 and 120-degrees Fahrenheit during any Design Basis Event (such as a LOCA) coincident with a Loss of Offsite Power (LOOP). Emergency Ventilation Fans 2A 1 and 2A2 automatically start when the 2A DG starts. NRG FORM 366A (10-01-2023) Page_2_ of _5_ | ML24064A190
Cooper Nuclear Station 298 1 of 5 | Unknown Unit | Inoperable Turbine Stop Valve Limit Switch Causes Condition Prohibited by Technical Specifications | 03-04-2024 | During the performance of surveillance testing on January 3, 2024, turbine stop valve (TSV)-1 open limit switch, MS-LMS-SVOS1(1 ), failed to actuate. This failure prevented actuation of the Reactor Protection System (RPS) scram logic for channel A 1. At 0400, Operations declared TSV-1 limit switch inoperable and entered the applicable Technical Specifications (TS) Limiting Condition for Operation (LCO) 12-hour action statement to place the RPS channel in trip and inserting a half-scram. A pre-planned contingency power reduction was initiated to replace the limit switch. When the switch linkage was disassembled for replacement, the arm was found loose and not fully engaged onto the limit switch shaft. The switch was replaced, and Operations exited the TS LCO action statement at 0249 on January 4, 2024. The cause of the failure was due to looseness in the limit switch linkage that attached to the limit switch cam. This prevented proper engagement to actuate the limit switch when it was exercised for testing. There were no safety consequences as a result of this event. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process LICENSEE EVENT REPORT (LER) and fed back to industry. Send comments regarding burden estimate to the FOIA, CONTINUATION SHEET Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: (See NUREG-1022, R.3 for instruction and guidance for completing this form oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a http://www.nrc.gov/reading-rm/doc-collections/nureqs/staff/sr1022/r3/) person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Cooper Nuclear Station 05000-298 NUMBER NO. 2024 001 00 | PLANT STATUS Cooper Nuclear Station (CNS) was in Mode 1, Power Operation, at 100 percent power at the time of the event on January 3, 2024. BACKGROUND The Reactor Protection System (RPS) [El IS:JC] provides timely protection against the onset and consequences of conditions that threaten the integrity of the fuel barrier and the reactor coolant pressure boundary. The RPS limits the uncontrolled release of radioactive material from the fuel and reactor coolant pressure boundary by terminating excessive temperature and pressure increases through the initiation of an automatic scram. The RPS includes sensors, relays [EIIS:RL Y], bypass circuits, and switches that are necessary to cause initiation of a reactor [EIIS:RPV] scram. The input parameters to the scram logic are from instrumentation that monitors reactor vessel water level, reactor vessel pressure, neutron flux, main steam line isolation valve position, turbine control valve fast closure, turbine stop valve (TSV) position, drywell pressure, and scram discharge volume water level. The RPS is arranged as two separately powered trip systems (trip system A and trip system 8). Each trip system has three logics. Two of the logics (A 1, A2; 81, 82) are used to produce automatic trip signals. The input parameters mentioned above are represented by at least one input to each of these logic channels. The remaining logic is used for a manual trip signal. The outputs of the automatic logic channels in a trip system are combined in a "one-out-of-two" logic so that either channel can trip the associated trip system. The tripping of both systems will produce a reactor scram. The operability of RPS is dependent on the operability of individual instrumentation channel functions specified in Technical Specifications 3.3.1.1, RPS Instrumentation, Table 3.3.1.1-1. For the Turbine Stop Valve-Closure Function (Table 3.3.1.1-1, Function 8), each RPS trip system receives two Turbine Stop Valve-Closure channel inputs from a TSV, each consisting of one position (i.e., limit) switch [EIIS:33] assembly with two contacts, each inputting to a relay. The relays provide a parallel logic input to an RPS trip logic channel. The logic for the Turbine Stop Valve-Closure Function is such that both TSVs must be closed to produce a reactor scram. Single TSV closure will produce a half scram. Four channels of Turbine Stop Valve-Closure Function, with two channels in each trip system, are required to be operable. EVENT DESCRIPTION On January 3, 2024, TSV-1 limit switch MS-LMS-SVOS1 (1 ), failed to actuate during surveillance testing. Testing of the limit switch function is required to meet Technical Specifications (TS) Surveillance Requirement 3.3.1.1.9 for Table 3.3.1.1-1, Function 8 - TSV Closure. Failure of limit switch MS-LMS-SVOS1 (1) to actuate revented makin u the RPS scram lo ic for channel A1. The other TSV-1 limit switch, MS-LMS-SVOS1 2 , | ML24064A252
cooper nuclear station | Unknown Unit | Technical Specifications Prohibited Condition for Inoperable Service Water Booster Pump | 03-04-2024 | On August 27, 2022, Residual Heat Removal Service Water Booster pump 'D' (SW-P-BPD) outboard pump bearing temperature reached the high warning temperature alarm. Upon investigation of the alarm, a three drops per minute oil leak was observed on the pump inboard, radial bearing. At 2120 hours, Operations declared SW-P-BPD inoperable and entered the applicable Technical Specification Limiting Condition for Operation. The pump bearing oil leakage was repaired and both inboard and outboard booster pump bearings replaced. SW-P-BPD was declared operable at 1614 on September 1, 2022. The cause of the pump inboard bearing oil leakage was a fabrication issue by the original pump manufacturer. The cause of the pump thrust bearing elevated temperature was that the maintenance procedure used for the previous pump rebuild in July 2022 was not as detailed in accordance with the original manufacturer's recommendations with respect to installation of the pump thrust bearing. There were no safety consequences as a result of this event. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process LICENSEE EVENT REPORT (LER) and fed back to industry. Send comments regarding burden estimate to the FOIA, CONTINUATION SHEET Library, and Information Collections Branch (T-6 A 1O M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: (See NUREG-1022, R.3 for instruction and guidance for completing this form oira submission@omb.eop.gov. The NRC may not conduct or sponsor, and a http://www.nrc.gov/readinq-rm/doc-collections/nureqs/staff/sr1022/r3/) person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Cooper Nuclear Station 05000-298 YEAR SEQUENTIAL REV NUMBER NO. 2024 002 00 | PLANT STATUS At the time of the event on August 27, 2022, Cooper Nuclear Station (CNS) was in Mode 1, Power Operation, at 81 percent power for end-of-cycle power coast down. BACKGROUND The Residual Heat Removal [EIIS:BO] Service Water Booster (RHRSWB) system is designed to provide cooling water for the Residual Heat Removal system (RHR) heat exchangers [EIIS:HX], required for a safe reactor shutdown following a Design Basis Accident or transient. The RHRSWB system is operated whenever the RHR heat exchangers are required to operate in the shutdown cooling or suppression pool cooling mode. The system is initiated manually from the Control Room. If operating during a loss of coolant accident (LOCA), the system is automatically tripped to allow the diesel generators [EIIS:DG] to automatically power only that equipment necessary to reflood the core. The RHRSWB system removes heat from the suppression pool via the RHR system to limit the suppression pool temperature and primary containment [EIIS:NH] pressure following a LOCA. This ensures that the primary containment can perform its function of limiting the release of radioactive materials to the environment following a LOCA. The RHRSWB system consists of two independent and redundant subsystems. Each subsystem is made up of a header, two pumps [EIIS:P], a suction source, valves, piping, heat exchanger, and associated instrumentation. Two RHRSWB pumps per subsystem are required to be operable to satisfy the requirements of Technical Specifications (TS), Limiting Condition for Operation (LCO) 3.7.1. EVENT DESCRIPTION RHRSWB pump 'D' (SW-P-BPD) was removed from service at 0202 ~ours on July 27, 2022, and was replaced as part of routine preventive maintenance. SW-P-BPD was restored to operable status after this replacement at 0333 hours on July 29, 2022. On August 27, 2022, at approximately 1330 hours, SW-P-BPD was placed in service to support SW chemical injection to control zebra mussels within the SW system. At approximately 1942 hours, a high thrust bearing temperature alarm was received on the Plant Management Information System (PMIS). While investigating the condition, a separate oil leak of three drops per minute (dpm) was observed on the pump inboard radial bearing, and a one dpm oil leak observed on the pump outboard thrust bearing. Due to the excessive oil leakage of the pump inboard bearing and pump outboard bearing high temperature, Operations declared SW-P-BPD inoperable at 2120 hours and entered TS LCO 3.7.1, Condition A, Required Action A.1, to restore SW-P-BPD to operable status within 30 da s. | ML24064A255
Hope Creek Generating Station | Unknown Unit | Inadvertent Main Turbine Control Valve Closure Caused Reactor Scram | 03-19-2024 | On December 14, 2023, at 1939 EST, while attempting to manually close a failed open #4 turbine control valve (TCV), the #4 TCV closed rapidly. This caused a scram on average power range monitor (APRM) high neutron flux due to a rise in reactor pressure. Hope Creek Generating Station (HCGS) repaired the #4 TCV by replacing the servo valve. In addition, the fast-acting solenoid (FAS) valve and the shutoff valve were replaced. HCGS synchronized the Main Generator to the grid on December 17, 2023, at 1537 EST. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments ~c,J>P.REGt,(,.>O f~t?. LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to ~ CONTINUATION SHEET ~ ,i Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory ..;.+-, ••11t•• +O' Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ~ 050 YEAR SEQUENTIAL REV I □ NUMBER D NO. Hope Creek Generating Station 00354 2023 I □ 052 I - 003 I - 01 | ABSTRACT (continued) A Root Cause Evaluation (RCE) was performed. The root cause of this event was inadequate adherence to applicable administrative tools and processes. Corrective actions include procedure revisions and reinforcement of expectations regarding procedure adherence. HCGS reported this per 10 CFR 50.72(b)(2)(iv)(B) as event notification 56889 and now reports this event per 10 CFR 50.73(a)(2)(iv)(A). PLANT AND SYSTEM IDENTIFICATION General Electric - Boiling Water Reactor (BWR/4) Turbine Control Valve/ Electro-Hydraulic Control System (EHC) - TG IDENTIFICATION OF OCCURRENCE Event Date: December 14, 2023 Discovery Date: December 14, 2023 CONDITIONS PRIOR TO OCCURRENCE OPCON 1, POWER OPERATION. Reactor power was at 88 percent. No other structures, systems or components that could have contributed to the event were inoperable during the event. DESCRIPTION OF OCCURRENCE On December 11, 2023, an EHC leak was discovered on the #4 turbine control valve (TCV). Reactor power was reduced to 90 percent, the #4 TCV was closed, and EHC was isolated to stop the leak while the plant was at 90 percent power. HCGS further lowered power to 70% to facilitate conditions for repairs. On December 14, 2023, HCGS was at 88 percent power after #4 TCV FAS oil supply tubing repairs. During restoration, foreign material that entered and damaged the servo o-rings during the leak repair caused the #4 TCV to go full open despite having a closed demand signal. While taking action to manually close the #4 TCV, the valve unexpectedly closed in approximately one second causing an automatic actuation of the reactor protection system (RPS) due to high average power range monitor (APRM) high neutron flux. All control rods fully inserted into the core. All safety systems responded as designed and expected. There were no emergency core cooling system actuations during the event. | ML24079A283
Peach Bottom Atomic Power Station | Unit 2 | Automatic Reactor Scram due to an Invalid Generator Lockout | 03-31-2024 | On 01/29/2024 at 1202 hours, Unit 2 experienced a Generator lockout, Turbine trip and automatic Reactor Scram. All control rods inserted, and all safety systems responded as designed. Reactor level was initially maintained by Feedwater and pressure controlled with bypass valves. During the scram response, condenser vacuum degraded due to the loss of Turbine steam seals, resulting in level and pressure control being transferred to Reactor Core Isolation Cooling (RCIC) and High Pressure Coolant Injection (HPCI), respectively. The cause of the Generator lockout is under investigation, with the suspected cause being a spurious trip of the Audio Tone system. The system has been removed from service with a redundant system providing the protective function. The Audio Tone system is scheduled for replacement in the 2024 refueling outage. This event is reportable under 10CFR50.73(a)(2)(iv)(A) due to manual or automatic actuation of systems listed in 10CFR50.73(a)(2)(iv)(B) including the Reactor Protection System, containment isolation signals, actuation of an emergency core cooling system and Reactor Core Isolation Cooling. An ENS notification was made within 4 hours of the event and was updated within 8 hours, reference ENS 56936. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 SEQUENTIAL REV YEAR NUMBER NO. Peach Bottom Atomic Power Station, Unit 2 00277  052 2024 - 001 - 00 | Plant Operating Conditions Before the Event Prior to the event, Peach Bottom Atomic Power Station, Unit 2 was operating at approximately 100% power in MODE 1. There were no structures, systems or components (SSC) that were inoperable at the start of the event that contributed to the event. Event Description On 01/29/2024 at 1140 hours, the Main Control Room (MCR) received a Generator Tone Trouble Alarm, which immediately reset once acknowledged. A second Generator Tone Trouble Alarm was received, which remained locked in for a short period of time (approximately 15 seconds) before resetting. At 1202 hours, Unit 2 experienced a Generator lockout, Turbine trip and automatic Reactor Scram. Turbine control valves (EIIS: TA) closed as expected. Safety relief valves (EIIS: SB) were used to control the expected pressure increase and were not reopened after the initial transient. Primary Containment Group II and III Isolations (EIIS: JM) occurred as expected. Reactor vessel level was initially controlled by Feedwater (EIIS: SJ). Condenser vacuum slowly degraded due to an issue with the turbine steam seal system (EIIS: TC) and, therefore, after approximately 20 minutes level control was transferred to the Reactor Core Isolation Cooling (RCIC) system (EIIS: BN). Pressure control was maintained by turbine bypass valves (EIIS: SO) and the High Pressure Coolant Injection (HPCI) system (EIIS: BJ), which was only used for pressure control and not injection. Steam seals were restored and condenser vacuum was re-established. Vessel level control was transferred to Condensate (EIIS: SD) and the unit was safely transitioned to a cold shutdown condition. A review of the plant event logs confirmed that a generator lockout and power-load unbalance occurred. The 2-50F-386A, Main Transformer Over Head Line Protection Lock Out Relay was the first actuating device. The ‘TTR-1’ Audio Tone drawers indicated that a trip signal was transmitted from the Audio Tone drawers in the Cable Spreading Room to the drawers in the substation. The substation drawers opened the CB-225 and CB- 215 breakers (EIIS: EL) upon receipt of the trip signal. At this time, the cause of the Generator lockout is still under investigation by a Root Cause analysis. The most probable cause is a failure of the Audio Tone trip system cables which are planned for abandonment in the upcoming 2024 refueling outage as part of a planned system upgrade. Currently, there is no plan to supplement this LER; however, this LER will be supplemented if the conclusions of the Root Cause analysis substantially change the information presented in this LER. An investigation was performed and the cause of the loss of condenser vacuum is attributed to the setting of the sealing steam header pressure control valve. This resulted in the valve not opening to admit steam to the sealing steam header following the trip of the main turbine, which provided a path for air in-leakage and degraded condenser vacuum. Unit 3 was unaffected by this event. Unit 2 start up was commenced at 2028 hours on 01/30/2024 and the unit was synchronized to the grid at 1427 hours on 01/31/2024. This event is reportable under 10CFR50.73(a)(2)(iv)(A) due to manual or automatic actuation of systems listed in 10CFR50.73(a)(2)(iv)(B) including RPS, containment isolation signals, actuation of an emergency core | ML24081A121
Prairie Island Nuclear Generating Plant | Unit 1 | Reactor trip, Auxiliary Feedwater and Emergency Service Water system actuation due to electrical transient in DC control power cables | 03-21-2024 | At 11:10 on October 19, 2023, with Prairie Island Nuclear Generating Plant Unit 1 operating at 100 percent power in Mode 1, power operations, multiple substation breakers unexpectedly opened and multiple grounds were detected on DC control power cabling from the plant to the substation control house. This resulted in a Unit 1 Turbine Trip and subsequent Reactor Trip with a loss of all non-safety related busses and the actuation of Auxiliary Feedwater and Emergency Service Water. Operators responded to the event in accordance with approved procedures and safely placed the plant in Mode 3. Horizontal directional drilling in progress at the site damaged DC control cables resulting in the identified plant response. This was caused by weakness in the Excavation Permit approval process as well as inadequate oversight of the personnel performing the work. DC cable replacement has been completed and multiple procedure changes have been initiated to address the identified gaps and prevent recurrence of this event. There were no radiological impacts from the event. The health and safety of the public and site personnel were not impacted during this event. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) due to a Reactor Trip, a valid Auxiliary Feedwater actuation of Emergency Service Water system. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 03/31/2024 (10-01-2023) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; email: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 YEAR SEQUENTIAL REV NUMBER NO. Prairie Island Nuclear Generating Plant, Unit 1 -282 2023 052 - 001 - 01 | Plant Operating Conditions Prior to the Event: Unit 1 - Mode 1, 100 percent Power Unit 2 - Defueled EVENT DESCRIPTION At 11:10 on October 19, 2023, with Prairie Island Nuclear Generating Plant (PINGP) Unit 1 operating at 100 percent power and Unit 2 defueled in a scheduled refueling outage, multiple substation breakers, including the Unit 1 generator output breaker, unexpectedly opened causing a Unit 1 Turbine [TA] Trip and subsequent Reactor Trip. In addition, multiple grounds were detected on DC control cabling for both Units from the plant to the substation control house. The Turbine Trip caused 1M Main Transformer to become deenergized, which is the normal power supply to non-safety related (NSR) busses on Unit 1. 1R Auxiliary Transformer was also deenergized as a result of the event and therefore was not available for a Fast Bus Transfer, which resulted in a loss of all NSR busses on both Units. The reactor trip resulted in Steam Generator Water Level (SGWL) in both Steam Generators rapidly shrinking to below the setpoint for an automatic start of both Auxiliary Feedwater (AFW)[BA] pumps. These pumps ensure that at least one Steam Generator contains enough water to serve as the heat sink for reactor decay heat and sensible heat removal following a reactor trip. Both the 11 Turbine Driven AFW Pump and 12 Motor Driven AFW Pump actuated upon reaching the automatic start setpoint for low SGWL. The 121 Motor Driven Cooling Water Pump (MDCLP) auto started on low header pressure due to the loss of the NSR 11 Cooling Water (CL) Pump. The 121 MDCLP is designed to start automatically if CL header pressure drops to 80 pounds per square inch gauge (psig). The 121 MDCLP is a part of the PINGP Cooling Water (CL) System [BI]. The CL system is a ring header which is shared by Units 1 and 2 that provides a heat sink for the removal of process and operational heat from safety-related components during a design basis accident or transient. At 14:15 on October 19, 2023, Event Notification (EN) # 56803 was reported to the NRC as a 4-hour Non-Emergency report under 10 CFR 50.72(b)(2)(iv)(B) actuation of the reactor protection system and 8-Hr Non-Emergency report under 10 CFR 50.72(b)(3)(iv)(A) for an Auxiliary Feedwater Actuation. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) due to a trip of the Unit 1 reactor, a valid Pressurized Water Reactor (PWR) Auxiliary Feedwater actuation for Unit 1 and actuation of Emergency Service Water system (121 MDCLP for Unit 1 and Unit 2). ASSESSMENT OF SAFETY CONSEQUENCES All control rods were fully inserted into the core following the trip. All safety functions operated as designed. This event does not represent a safety system functional failure for Unit 1 or Unit 2. AFW actuated as expected. The AFW System automatically supplied feedwater to the Steam Generators to remove decay heat from the Reactor Coolant System when SGWL shrunk after the reactor trip. Decay heat was removed by the Steam Generators through the Steam Generator Power Operated Relief Valves. The auto start of 121 MDCLP did not challenge nuclear safety as the Cooling Water system responded as designed. | ML24081A153
Monticello Nuclear Generating Plant | Unknown Unit | Reactor Scram, Containment Isolation, and Cooldown Rate outside of limits following technician adjustment of wrong component | 04-25-2024 | On February 28, 2024 at 0839 CST, with Monticello Nuclear Generating Plant in Mode 1 at 100 percent power, an inadvertent Anticipated Transient Without Scram (A TWS) system initiation resulted in trip of both Reactor Recirculation pumps, venting of the Scram Air Header, and Control Rod insertion. Control Room Operators inserted a manual Reactor Scram. Containment Isolation valves actuated and closed on a valid Group 2 signal post Reactor Scram. On March 08, 2024 at 1400 CST it was identified that within an hour following the Reactor Scram, the bottom head of the Reactor Pressure Vessel exceeded the Pressure and Temperature Limit cooldown rate of less than or equal to 100 degrees Fahrenheit per hour. The event was caused when a technician did not perform verification that the physical component matched the Surveillance Procedure step. The technician adjusted the potentiometer in the C module rather than the A module while the A channel was in trip which made up the required two trip signals and actuated the ATWS system. The Surveillance Procedure will be updated in a planned procedure change to improve human performance factors and to remove the steps to adjust the potentiometers in the A and C modules. An analytical evaluation determining the effects of the out-of-limit condition on the structural integrity of the Reactor Coolant System will be submitted to the Nuclear Regulatory Commission for review and approval per 10 CFR 50.55a(b)(2)(xliii). NRG FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects. Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-col1ections/nuregs/staff/sr1022/r3/) displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ~ 050 I IG SEQUENTIAL REV NUMBER NO. Monticello Nuclear Generating Plant 263 0 □ 052 -I 001 - I | EVENT DESCRIPTION On February 28, 2024 at 0839 CST, with Monticello Nuclear Generating Plant (MNGP) in Mode 1 at 100 percent power, an inadvertent Anticipated Transient Without Scram (ATWS) [EIIS CODE: JC] system initiation resulted in trip of both Reactor Recirculation [EIIS CODE: AD] pumps, venting of the Scram Air Header, and Control Rod insertion. Control Room Operators inserted a manual Reactor Scram. Containment Isolation [EIIS CODE: JM] valves actuated and closed on a valid Group 2 signal post Reactor Scram. On March 08, 2024 at 1400 CST it was identified that within an hour following the Reactor Scram, the bottom head of the Reactor Pressure Vessel [EIIS CODE: SB] exceeded the Pressure and Temperature Limit cooldown rate of less than or equal to 100 degrees Fahrenheit per hour. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) for an event or condition that resulted in the manual actuation of the Reactor Protection System (RPS) [EIIS CODE: JC] including Reactor Scram and automatic actuation of Containment Isolation signals affecting Containment Isolation valves in more than one system. This event is reportable under 10 CFR 50.73(a)(2)(i)(B) for an operation or condition which was prohibited by Technical Specification Limiting Condition of Operation (LCO) 3.4.9, Reactor Coolant System (RCS) Pressure and Temperature (PIT) Limits, specifically the requirement to determine the RCS is acceptable for continued operation within 72 hours of not meeting the Pressure and Temperature limit cooldown rate per required action A.2. EVENT ANALYSIS The function of the ATWS system is to mitigate the consequences of a failure of the RPS to achieve reactor shutdown when required. The A TWS system consists of two separately powered trip systems, Division I and Division II, each made up of two sub-channels: A and C for Division I and B and D for Division II. Each sub-channel receives an input from an independent sensor monitoring each of the A TWS trip parameters. A trip occurring in both sub-channels of logic Division I or a trip occurring in both sub-channels of logic Division II will cause an ATWS trip which opens both 11 and 12 Recirculation MG set generator field breakers and causes Control Rod insertion by venting the Scram Air Header. During performance of the quarterly Technical Specification Surveillance Procedure, ATWS - Recirc Trip for Reactor Pressure and Level Trip Unit Test and Calibration, a human performance error occurred. There were no systems, structures, or components that were inoperable at the start of the event that contributed to the event. During the first quarter of each year during the quarterly Surveillance Requirement 3.3.4.1.6 performance of the logic system functional test on A sub-channel ATWS RCP Trip Reactor Pressure relay, the Surveillance Procedure directs the MNGP Instrumentation and Control Technician to adjust the module's trip adjusting potentiometer. This step is done in accordance with an obsolete manufacturer's recommendation in order to preclude potential equipment degradation. The Technician successfully performed the functional test on A sub-channel and then, with A sub-channel remaining in trip, obtained a different tool to perform the potentiometer adjustment. The Technician did not verify the physical component to the procedural step and incorrectly adjusted the potentiometer of the adjacent C module, which is located in the same panel as the intended A module, which cause the trip of the C sub-channel. As both A sub-channel and C sub-channel were in trip, the Division I A TWS system actuated. The inadvertent ATWS system initiation resulted in trip of both Reactor Recirculation pumps, venting of the Scram Air Header, and Control Rod insertion. Control Room Operators inserted a manual Reactor Scram. Containment Isolation valves actuated and closed on a valid Group 2 signal post Reactor Scram. NRG FORM 366A (04-02-2024) Page 2 of 3 | ML24116A117
LaSalle County Station | Unit 1 | Core Operating Limits Report Thermal Limits Exceeded | 04-26-2024 | On February 21, 2024, while performing the water rod inspection of fuel bundle GGJ319 during a planned refueling outage, it was identified that several fuel spacers had propagated up within the bundle toward the upper tie plate. It was determined through analysis that spacer positioning had a direct effect on the Minimum Critical Power Ratio (MCPR). On March 4, 2024, an analysis of the operating conditions by Global Nuclear Fuel (GNF) of fuel bundle GGJ319 was reviewed and accepted by the station. The report confirmed that during the previous cycle, the Operating Limit MCPR exceeded limits set by Technical Specifications (TS) 3.2.2. Since the Operating Limit MCPR was exceeded for longer than allowed by TS Limiting Condition for Operation (LCO) 3.2.2, this event is reportable as a condition prohibited by TS per 10 CFR 50.73(a)(2)(i)(B). The fuel bundle spacers shifted out of position over the previous operating cycle. This condition was identified during the process of inspections in response to GNF 10 CFR Part 21 communication SC 22-04. This fuel bundle has been removed from the reactor core, is currently located in the spent fuel pool, and will not be re-loaded into the core. There was no impact to the health and safety of the public or plant personnel because the Safety Limit MCPR was not exceeded in the previous cycle operation. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported : ~ - - ¥ ~ ,.· . " ' . . . lessons learned are inco!J)Orated into the licensing process and fed back to industry. Send comments . LICENSEE EVENT REPORT (LER) regarding burden estimate lo the FOIA, library, and Information Collections Branch (T-6 A10M), U. S. ; ~. . . ~ Nuclear Regulatory Commission, Washington, DC 20555-0001, or by emai lo \ ..... .,,J CONTINUATION SHEET lnfooollecls.Resource@nrc.gov, and the 0MB reviewer al: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Corrrnission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required lo (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of infonnation unless lhe document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nu regs/staff/ sr1022/r3D displays a currently valid 0MB control number. 1. FACILITY NAME (cid:127) 2. DOCKET NUMBER 3. LER NUMBER 050 SEQUENTIAL REV YEAR NUMBER NO. LaSalle County Station, Unit 1 00373 0 052 2024 - 001 00 | Plant and System Identification LaSalle Country Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the reactor core system. The affected component was the GNF3 fuel bundle GGJ319. Condition Prior to Event Unit(s): 1 Date: March 4, 2024 Time: 00:00 CDT Reactor Mode(s): 4 Mode(s) Name: Cold Shutdown Power Level: 0 percent Description On February 21, 2024, during planned in-core fuel inspections for misoriented water rods of susceptible GNF3 fuel bundles in response to GNF 10 CFR Part 21 communication SC 22-04, an unexpected condition for fuel bundle GGJ319 was discovered where spacers 6, 7, and 8 were found near the top of the bundle upper tie plate. After initial discovery, subsequent inspection revealed that spacers 4 and 5 had also moved upward to the top of the fuel assembly. Fuel spacers 1 through 3 had not moved from their expected position. Fuel bundle GGJ319 was permanently discharged to the spent fuel pool. Fuel vender GNF evaluated the impact of this condition for the previous operating cycle. The evaluation conservatively assumed the spacers were displaced for the entirety of the previous cycle, since it could not be determined when the spacers had moved. The evaluation was reviewed and accepted by the station on March 4, 2024. The evaluation report determined that • there were no penalties or adjustments associated with Linear Heat Generation Rate (LHGR) and Average Planar Linear Heat Generation Rate (APLHGR) and no discernable impact to thermal limits and margins. • there was no discernable impact to thermal limits and margins for co-resident fuel in the Unit 1 reactor core during the previous cycle of operation. • the Operating Limit MCPR exceeded limits set by TS 3.2.2 for the previous cycle. • the Safety Limit MCPR requirements set by TS 2.1.1.2 were never violated for the previous cycle. Cause The apparent cause of the spacer relocation was determined to be the misoriented water rod in fuel bundle GGJ319. The misorientation of the water rod would have occurred during fuel bundle fabrication. The misorientation caused the spacers to not be locked into position, causing them to propagate up the bundle due to hydraulic force during normal operation. Reportability and Safety Analysis Fuel bundle GGJ319 must satisfy the requirements of TS 3.2.1, AVERAGE PLANAR HEAT GENERATION RATE (APLHGR); TS 3.2.2, MINIMUM CRITICAL POWER RATIO (MCPR); TS 3.2.3, LINEAR HEAT GENERATION RATE (LHGR); AND T.S. 2.1.1.2, SAFETY LIMITS. The report determined that the requirements of TS 3.2.1 for APLHGR and TS 3.2.3 for LHGR were met for the previous cycle operation. The report confirmed the requirements of TS 2.1.1.2 for the Safety Limit MCPR was never violated for the previous cycle operation. | ML24117A127
Calvert Cliffs Nuclear Power Plant | Unit 1 | Emergency Diesel Generators Automatic Start due to Loss of a 13kV Bus | 04-29-2024 | On February 28, 2024, with Calvert Cliffs Unit 1 in Mode 5 (Cold Shutdown) and Unit 2 in Mode 1 (Power Operation), a 13kV Service Electric Bus de-energized when a breaker tripped open due to a protective relay contact inadvertently closing. The loss of the electric bus resulted in the loss of 4kV unit service transformers and 4kV busses. The 1A and 2A emergency diesel generators automatically started as designed, when the 4kV busses were lost. The cause of the loss of the number 13kV Bus was due to mechanical agitation of a relay mounted on a breaker cabinet door in the Electrical Distribution Reliability Improvement Project (EDRIP) building. The relay contact inadvertently closed due to mechanical agitation during clearance and tagging activities. The relay was subsequently replaced. Operations restricted access to the EDRIP building, restricted operation of the associated circuit breakers, and added cautions to Operations Procedures. Planned corrective actions include relocating the relays from the EDRIP switchgear doors to a location better suited for these type relays. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 SEQUENTIAL REV YEAR NUMBER NO. Calvert Cliffs Nuclear Power Plant, Unit 1 05000317  052 2024 - 002 - 00 | PLANT AND SYSTEM IDENTIFICATION Calvert Cliffs Nuclear Power Plant, Units 1 and 2, are Combustion Engineering Pressurized Water Reactors each with a licensed maximum power level of 2737 megawatts thermal. The Energy Industry Identification System code used in the text is identified as [EA]. A. CONDITION PRIOR TO EVENT Unit: 1 Date: February 28, 2024 Power level: 0 Mode: Unit 1 was in Mode 5 when the event occurred. Unit: 2 Date: February 28, 2024 Power level: 65 Mode: Unit 2 was in Mode 1 when the event occurred. B. DESCRIPTION OF EVENT At 13:50 on February 28, 2024, with Calvert Cliffs Unit 1 in Mode 5 (Cold Shutdown), and Unit 2 in Mode 1 (Power Operation), the number 11 13kV Service Electric Bus de-energized when a breaker tripped open due to a protective relay contact inadvertently closing. The loss of 11 13kV Bus resulted in the loss of 4kV unit service transformers U-4000-11 and U-4000-12, and the 11 4kV and 21 4kV busses were deenergized. The Unit 1 1A emergency diesel generator (EDG) automatically started when the 11 4kV bus was deenergized and the Unit 2 2A EDG automatically started when the 21 4kV bus was deenergized. There were no safety consequences as a result of the event based on all safety systems functioning and operating as designed. C. DATES AND APPROXIMATE TIMES OF MAJOR OCCURRENCES February 28, 2024: 13:50: The number 11 13kV Service Electric Bus deenergized. The Unit Service Transformers U-4000-11, U-4000-12 and U-4000-13 were lost. The Unit 1 11 4kV bus deenergized. 1A EDG automatically started. The Unit 2 21 4kV bus deenergized. 2A EDG automatically started. February 28, 2024: 16:32: The Unit 1 11 4kV bus was powered from its alternate feeder breaker and the 1A EDG was separated from the bus and secured in accordance with normal operating procedures. February 28, 2024: 18:00: The Unit 2 21 4kV bus was powered from its alternate feeder breaker and the 2A EDG was separated from the bus and secured in accordance with normal operating procedures. | ML24121A002
Comanche Peak Nuclear Power Plant | Unknown Unit | Potential Loss of Safety Function Due to the lnoperability of Both Trains of the Un interruptible Power Supply Heating, Ventilation, and Air Conditioning (UPS HVAC) | 05-06-2024 | On March 05, 2024, Units 1 and 2 were operating at 100% power. At 0720 the Uninterrupted Power Supply, Heating, Ventilation, and Air Conditioning (UPS HVAC) X-02 automatically shutdown, which caused the station to determine that there was a potential loss of safety function for the equipment in the UPS and Distribution Rooms, due to losing the ability to control the temperature during a postulated emergency condition. This meets the safety system functional failure criteria. This was due to the failure of the UPS HVAC X-02 unit, concurrent with the UPS HVAC X-01 unit and the Emergency Fan Coil Units (EFCUs) being out of service for maintenance. The immediate corrective actions were for the station to start the EFCUs at 0729 which restored cooling to three of the four UPS and Distribution Rooms. This restored the safety function after approximately nine minutes. The station then restored operability to the UPS HVAC X-01 system by switching the cooling system to the other unit (Unit 2, Train A) approximately 41 minutes after the UPS HVAC X-02 trip, which restored the temperature control to all four UPS and Distribution Rooms. The root cause of this event was the station exhibiting a less than adequate conservative bias to the unique operability concerns associated with the UPS HVAC Cooling System when performing off-normal maintenance. NRG FORM 3668 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported ~(,,._,,v,AA£11u,,.,, lessons learned are incorporated into the licensing process and fed back to industry. Send comments .f • ' :.0~ .t LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to ~ ~ ,.,,., ~o,e, ~ , (FAILURE CONTINUATION) lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory ........ Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17~ Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection httR://www.nre.gov/read ing-rm/doc-co llections/n u regs/staff/ sr1 022/r3/) displays a currently valid 0MB control number. 1. FACILITY NAME 0 050 2. DOCKET NUMBER S 3 E . Q LE U R E N N U T M IA B L E R REV 10 NUMBER NO. Comanche Peak Nuclear Power Plant □ 052 I 445 -I 001 1- 1 00 I 13. COMPLETE ONE LINE FOR EACH COMPONENT FAILURE DESCRIBED IN THIS REPORT CAUSE SYSTEM COMPONENT MANUFACTURER REPORTABLE TO IRIS D EF COND GMC N NRC FORM 3668 (04-02-2024) Page 2 of 6 NRG FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimale to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email lo CONTINUATION SHEET lnfocollecls.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to http://www. nrc.g ov/reading-rm/doc-collections/nu reqs/staff/sr1 022/r3/) respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 0YE AR SEQUENTIAL REV I NUMBER NO. Comanche Peak Nuclear Power Plant ~- I 1-0 445 □ 052 I 001 | I. DESCRIPTION OF REPORTABLE EVENT On March 05, 2024, Units 1 and 2 were operating at 100% power. At 0720 the Uninterrupted Power Supply, Heating, Ventilation, and Air Conditioning (UPS HVAC) X-02 unit tripped, which caused the station to potentially lose a safety function. Specifically, the station lost the ability to properly control the temperature of the UPS and Distribution Rooms during a postulated emergency condition. The other factors leading to this were the Emergency Fan Coil Units (EFCUs) being off, which renders them inoperable, and UPS HVAC X-01 being inoperable, due to the support system, Component Cooling Water (CCW) Unit 1, Train A (1-A), being inoperable . The station restored the safety function after approximately nine minutes, by starting all of the EFCUs at 0729, which restored cooling to three of the four UPS and Distribution Rooms (EFCU 1-A was only functional, due to the support system CCW 1-A being inoperable, however forced air circulation was returned). The station then connected UPS HVAC X-01 to CCW Train 2-A approximately 41 minutes after the event, which restored temperature control to all four UPS and Distribution Rooms. A REPORTABLE EVENT CLASSIFICATION This event is reportable under 1 0CFR50.73(a)(2)(v)(D), "Any event or condition that could have prevented the fulfillment of the safety function of the structures or systems that are needed to ... Mitigate the consequences of an accident." This is based on the station losing both trains that provide temperature control to the UPS and Distribution Rooms, during a postulated Large-Break Loss of Cooling Accident (LBLOCA), or a similar postulated event which causes a high containment pressure, Hl-3, signal (18.0 psig). This is due to losing all three cooling systems in the UPS and Distribution Rooms, specifically: 1) The cooling system supporting UPS HVAC X-01, CCW Train 1-A, being inoperable for planned maintenance on the heat exchanger (Hx). Even-though CCW is cross-connected to the 1-B train for all alternative conditions, a Hl-3 signal would cause CCW to isolate Train 1-A from Train 1-B to support containment spray. 2) The four EFCUs being turned off at the time of the event, based on procedural allowance, which renders them inoperable due to no auto-start mechanism. 3) UPS HVAC X-02 being inoperable due to a failure of the evaporator blower motor, causing the system to shutdown. B. PLANT CONDITION PRIOR TO EVENT On March 05, 2024, prior to the event, both Units 1 and 2 were operating at approximately 100% power. C. STATUS OF STRUCTURES, SYSTEMS, OR COMPONENTS THAT WERE INOPERABLE AT THE START OF THE EVENT AND CONTRIBUTED TO THE EVENT The event caused the station to immediately lose UPS HVAC X-02, due to the motor shutdown The EFCUs in the UPS and Distribution Rooms were inoperable prior to the event, due to being turned off, based on maintenance personnel working in UPS and Distribution Room associated with Train 1-A. UPS HVAC X-01 was inoperable prior to the event, based on the CCW Train 1-A Hx maintenance. D. NARRATIVE SUMMARY OF THE EVENT, INCLUDING DAYS AND APPROXIMATE TIMES On March 05, 2024, Units 1 and 2 were operating at 100% power. At 0720 a failure occurred for UPS HVAC X-02 [EIIS: (EF)(ACU)], specifically, the evaporator blower motor [EIIS: (EF)(MO)] had a immediate failure. This event, coupled with the EFCUs [EIIS: (EF)(FCU)] being inoperable and the support system for UPS HVAC X-01 being inoperable, CCW Train 1-A Hx [EIIS (CW)(Hx)], resulted in the station losing all trains of UPS HVAC, and hence potentially losing the safety function to mitigate consequences of a postulated accident by losing the ability to control the temperature of the UPS and Distribution Rooms during an accident. | ML24127A155
Edwin I. Hatch Nuclear Plant | Unit 1 | Unit 1 Manual Reactor Trip Due to Loss of Feedwater | 05-09-2024 | At 1338 EDT on 3/11/2024, while Unit 1 was in MODE 1 at 35% power and performing power ascension activities, the reactor was manually tripped due to reactor water level decreasing following the trip of the 'A' Reactor Feed Pump (RFP) on low suction pressure. Due to the power level at the time, the 'B' RFP had not been placed in service. Closure of Containment Isolation Valves (CIV's) in multiple systems and actuation of High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) pumps occurred as a result of reaching the respective actuation setpoints on reactor water level as designed. The 'B' RFP was placed in service to control water level at 1340 EDT on 3/11/2024. The cause of the 'A' RFP trip was the use of the incorrect procedure section for isolation of a condensate pump while the main condenser was under vacuum. This allowed air leakage into the system which resulted in the low suction pressure trip of the 'A' RFP. The Condensate & Feedwater System procedure has been revised to clearly direct the performer to the appropriate section. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and lnfonmation Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of lnfonmation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRG may not conduct or sponsor, and a person is not required to respond to, a collection of infonmation unless the document requesting or requiring the collection http://www,nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/l displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV Edwin I. Hatch Nuclear Plant Unit 1 321 ~ NUMBER NO. ~-I 1-0 □ 052 002 I I | EVENT DESCRIPTION At 1338 EDT on 3/11/2024, while Unit 1 was in MODE 1 at 35% power and performing power ascension activities, the reactor was manually tripped due to reactor water level decreasing following the trip of the 'A' Reactor Feed Pump (RFP)(EIIS Code: P) on low suction pressure. Due to the power level at the time, the 'B' RFP had not been placed in service. Closure of Containment Isolation Valves (CIVs)(EIIS Code: ISV) in multiple systems and actuation of High Pressure Coolant Injection (HPCl)(EIIS Code: BJ) and Reactor Core Isolation Cooling (RCIC)(EIIS Code: BN) pumps occurred as a result of reaching the respective actuation setpoints on reactor water level as designed. The 'B' RFP was placed in service to control water level at 1340 EDT on 3/11/2024. Once the 'B' RFP was placed in service, HPCI and RCIC were secured at 1340 EDT and 1342 EDT respectively. EVENT CAUSE ANALYSIS Based on causal analysis, the cause of the 'A' RFP trip was the use of the incorrect procedure section for isolation of a condensate pump while the main condenser was under vacuum. This allowed air leakage into the system which resulted in the low suction pressure trip of the 'A' RFP. SAFETY ASSESSMENT AND REPORTABILITY There were no actual safety consequences as a result of this event. All safety related systems functioned as designed during this event. The operating crew responded correctly to the event. The applicable abnormal/emergency operating procedures were entered. The event was within the analysis of the Updated Final Safety Analysis Report (UFSAR) Chapter 15. This event is reportable per 10 CFR 50.7 3(a)(2)(iv)(A), as any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section. Systems that actuated during this event that are listed in (a)(2)(iv)(B) include; the Reactor Protection System (RPS)(EIIS Code: IG), general Containment Isolation Valves (CIV) in more than one system, ECCS including the HPCI system, and the RCIC system. CORRECTIVE ACTIONS The Condensate & Feedwater System procedure has been revised to clearly direct the performer to the appropriate section for isolating a condensate pump when the main condenser is under vacuum. PREVIOUS SIMILAR EVENTS On 09/29/2000 at 1357 EDT, Unit 1 was in the Run mode at a power level of approximately 1520 CMWT (55 percent rated thermal power). At that time, the reactor was scrammed manually following a trip of the operating Reactor Feedwater Pump (RFP) and a decrease in water level. Personnel inserted the scram in anticipation of an automatic scram on low water level. A RFP was placed into service to maintain level. This event was caused by component failure. During the implementation of a clearance to isolate a condensate pump, air was introduced into the condensate pump suction header through a leaking pump suction isolation valve. The presence of air led to the trip of the operating RFP on low suction pressure. LER 2000-011-00. | ML24130A268
Cooper Nuclear Station 298 1 of 4 | Unknown Unit | Main Turbine Stop Valve Position Switches Do Not Meet Channel Independence Criteria Results In Two Channels Being Declared Inoperable And A Condition Prohibited bv Technical Specifications | 05-09-2024 | On March 11, 2024, a question was raised concerning the mechanical separation criteria of the Reactor Protection System Turbine Stop Valve (TSV) closure function position switches as the position switches on each TSV are connected together with all-thread for actuation. On March 29, 2024, it was determined that the two position switches for each TSV do not have channel independence and one position switch for each TSV was declared inoperable because the switches are mechanically linked together. The direct cause of the failure to meet the requirement of channel separation comes from the position switches not being mechanically separated due to sharing a common linkage. A causal factor for this was the initial assumption was incorrect that the plant is constructed consistently with the design basis. The channel independence issue will be resolved by the engineering change process. A seminar will be presented to engineering personnel to address the assumption the plant was constructed consistent with the licensing basis. There were no safety consequences as a result of this event. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process LICENSEE EVENT REPORT (LER) and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC (See NUREG-1022, R.3 for instruction and guidance for completing this form may not conduct or sponsor, and a person is not required to respond to, a collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/} of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Cooper Nuclear Station 05000-298 NUMBER NO. 2024 004 00 | PLANT STATUS At the time of the event on March 11, 2024, Cooper Nuclear Station (CNS) was in Mode 1, Power Operation, at 100 percent steady-state power. BACKGROUND The Reactor Protection System (RPS) [EIIS:JC] initiates a reactor [EIIS:RPV] scram when one or more monitored parameters exceed their specified limits to preserve the integrity of the fuel cladding and the reactor coolant pressure boundary and minimize the energy that must be absorbed following a loss of coolant accident. This can be accomplished either automatically or manually. RPS is arranged as two separately powered trip systems. Each trip system has three logics. Two of the logics are used to produce automatic trip signals. The remaining logic is used for a manual trip signal. Each of the two logics used for automatic trip signals receives input signals from at least one channel for each monitored variable. Thus, two channels are required for each monitored variable to provide independent inputs to the logics of one trip system. At least four channels for each monitored variable are required for the logics of both trip systems. Closure of the Turbine Stop Valves (TSV) results in the loss of a heat sink that produces reactor pressure, neutron flux, and heat flux transients. A reactor scram is initiated at the start of TSV closure in anticipation of the transients that would result from the closure of these valves. TSV closure signals are initiated from position switches (also referred to as limit switches) [EIIS:33] located on each of the two TSVs. Two independent position switches are associated with each stop valve. Both of the switches from one TSV provide input to RPS trip system A; the two switches from the other TSV provide input to RPS trip system B. Thus, each RPS trip system receives two TSV closure channel inputs from a TSV, each consisting of one position switch assembly with two contacts, each inputting to a relay [EIIS:RL Y]. The relays provide a parallel logic input to an RPS trip logic channel. The logic for the TSV closure function is such that both TSVs must be closed to produce a scram. Single valve closure will produce a half scram. This function must be enabled at thermal power greater than or equal to 29.5 percent reactor thermal power as measured by turbine supply pressure. Four channels of TSV closure function, with two channels in each trip system, are required to be operable for Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.3.1.1 to ensure that no single instrument failure will preclude a scram from this function if both TSVs should close. | ML24131A023
Nine Mile Point | Unit 2 | LER 2024-001-00, Automatic Reactor Scram on Turbine Trip due to Low Condenser Vacuum | 05-01-2024 | On 3/3/24 at 1942 while performing a plant shutdown in preparation for a refuel outage, Nine Mile Point Unit 2 experienced a Reactor Scram due to a Main Turbine trip on low condenser vacuum. The plant was at ~ 55% power at the time of the Reactor Scram. Following the scram, a Low RPV Level scram and containment isolation signal on Level 3 was received, as expected. The containment isolation signal impacted RHR Shutdown Cooling, RHR letdown to radwaste, and RHR sampling. All impacted valves were in the closed position at the time the isolation occurred. All control rods were fully inserted. Plant response was as expected. Post scram the Main Turbine Bypass Valves were used to control decay heat and normal post scram level control via the feed/ condensate system. The event notification (EN 57004) was made pursuant to 10 CFR 50.72(b)(2)(iv)(B) RPS Actuation and 10 CFR 50.72(b)(3)(iv)(A) Specified System Actuation and is reportable pursuant to 1O CFR 50.73(a)(2)(iv)(A). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to http://www. nrc.q ov/reading-rm/doc-collecti ons/nuregs/s taff/sr1 022/r30 respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 YEAR SEQUENTIAL REV Nine Mile Point Unit 2 410 NUMBER NO. □ 052 2024 - 001 - 00 | THE ENERGY INDUSTRY IDENTIFICATION SYSTEM (EIIS) COMPONENT FUNCTION IDENTIFIED AND SYSTEM NAME OF EACH COMPONENT OR SYSTEM REFERRED TO IN THIS LER ARE ENCLOSED WITHIN [BRACKETS] I. DESCRIPTION OF EVENT A. PRE-EVENT PLANT CONDITIONS: Prior to the event, NMP2 was in Mode 1 (Power Operation) at 55% power. B. EVENT: At 19:15 on March 3, 2024, NMP2 was continuing with a downpower in preparation for a refueling outage with normal gland sealing steam [TC] in service. As expected around 55% reactor power, the extraction steam [SB] pressure lowered to the 50 psig setpoint causing the extraction steam valve (2ESS-STV104 REBOILERS 1A &1 B EXTR SUPPLY ISOL VLV) to Clean Steam Reboiler A (CSR 'A') [RBLR] to close. By design, a main steam [SB] valve (2ASS-STV112 REBOILERS 1A & 1 B MAIN STM TRIP VLV) is intended to open as soon as the extraction steam valve closes, raising pressure to 95 psig. Upon closure of 2ESS-STV104, 2ASS-STV112 failed to open automatically. Operators attempted to open the valve manually by taking the control switch to the open position, however the valve indicated on the main control board that it remained closed and steam pressure to the CSR 'A' began to lower rapidly. To restore pressure, operators re-opened 2ESS-STV104 to re-establish the extraction steam source. CSR 'A' outlet pressure remained adequate to supply turbine seal glands, however pressure was lowering slowly consistent with extraction steam pressure. Without operator action, 2ASS-STV112 opened approximately 6 minutes later causing CSR 'A' inlet pressure to rise rapidly. Within 40 seconds, the CSR 'A' drain tank [TK] reached the high-level alarm and the hi-hi level trip was reached 6 seconds later sending a signal to isolate the inlet steam (2ASS-MOV3A REBOILER 1A STM INLET VLV) [ISV] to the CSR. The hi-hi level cleared and recurred six additional times. During this time operators attempted to reopen 2ASS-MOV3A to CSR 'A', however it auto isolated each time. When regulated turbine gland seal pressure dropped below the 6.3 psig setpoint for the Emergency Gland Sealing [SB] steam line, the system was unavailable to support turbine glands as it had been isolated due to failures occurring during the September 2023 forced outage. While Auxiliary Boilers [SA] were at normal pressure and temperature, valve 2ASS-AOV145 (AUX BLR STM INLET VLV) to the clean steam reboilers was gagged closed and not readily available to the operators As a result of degrading CSR pressure and unavailability of redundant Emergency Gland Sealing steam supply, gland sealing steam pressure was lost at 19:38 and condenser [COND) vacuum rapidly degraded. Operators stopped actions to restore the CSR to brief on a manual reactor trip. Prior to initiating the manual trip an automatic trip (JC] occurred at 19:42 at an indicated condenser vacuum of 24.5". At 19:59, CSR 'A' was restored to service by opening 2ASS-MOV3A. No additional hi-hi level conditions occurred. Operators requested maintenance support to close 2ASS-STV112 because it has an interlock that prevents 2ASS AOV145 from being opened unless 2ASS-STV112 is closed. Once closed, the gagging device on 2ASS-AOV145 was removed and steam was supplied to the CSR from the Auxiliary boilers. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). | ML24136A202
Fermi 2 | Unknown Unit | Primary Containment Isolation Valve Declared Inoperable for a Period Prohibited by Technical Specifications | 05-16-2024 | At 1718 EDT on March 17, 2024, it was identified that E4150-F042, HPCI Booster Pump Suction from Suppression Pool Inboard Iso MOV, was not fully closing without holding down the pushbutton in the Main Control Room. The Primary Containment Isolation function (PCIV) of E4150-F042 was declared inoperable. This condition did not challenge the ability of Primary Containment to perform its overall safety function. On March 19th, actions were taken to replace the associated Closed Auxiliary Seal-in contact block and restore the PCIV function of E4150-F042. A Past Operability evaluation was conducted, which determined that upon a HPCI System steam line isolation signal from the HPCI control logic, E4150-F042 would not fully close. The PCIV function of E4150-F042 was declared inoperable for a period exceeding that which is allowable per TS 3.6.1.3. This condition is being reported under 10CFR50.73(a)(2)(i)(B), operation or condition which is prohibited by plant technical specifications. There were no safety consequences or radiological releases associated with this event. The cause of the E4150-F042 not fully closing is due to the Closed Auxiliary Seal-in Contact failing to keep the close contactor coil energized due to high resistance across the electrical contacts. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments f ~ ~ c,J>P. t REG ? t,<,.>O . LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to ~ CONTINUATION SHEET ~ ,i Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory ..;.+-, ••11t•• +O' Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ~ 050 YEAR SEQUENTIAL REV I □ NUMBER NO. Fermi 2 00341 D □ 052 I 2024 - I 002 I - 00 | INITIAL PLANT CONDITIONS Mode – 1 Reactor Power – 099 There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT At 1718 (EDT) on March 17, 2024, it was identified that E4150-F042, High-Pressure Coolant Injection (HPCI) [BJ] Booster Pump Suction from Suppression Pool Inboard Isolation [ISV] Motor Operated Valve (MOV) (Manufacturer Powell Co., Model 3023WE), was not fully closing without holding down the pushbutton in the Main Control Room (MCR). The Primary Containment Isolation function (PCIV) [BD] of the E4150-F042 was declared inoperable. This condition did not challenge the ability of Primary Containment [JM] to perform its safety function as containment integrity would have been maintained by the redundant water seal and by E4150-F041, HPCI Booster Pump Suction from Suppression Pool Outboard Isolation MOV. This condition also did not challenge the ability of E4150-F042 to automatically open when required, therefore the High-Pressure Coolant Injection (HPCI) system remained operable. This condition was first identified in Fermi 2 condition report (CR) 2023-30437 (05/23/2023) and again in CR 2024-36518 (02/25/2024). Both earlier CRs drew the same inaccurate operability conclusion that the manual seal-in contact via the open pushbutton is not used when E4150-F042 is closed due to a containment isolation signal. Due to this inaccurate operability conclusion in those 2 CRs, a past operability and reportability review were not conducted (action in CR 2024-36518 to understand the inaccurate operability conclusions). During a pre-refueling outage (RF22) review of Main Control Room Deficiency work orders, a DTE Electrician generated CR 2024-36970 (03/17/2024) to review the associated information with E4150-F042. The operability determination with that CR placed the PCIV function of E4150-F042 inoperable. Operations entered Limiting Condition for Operation (LCO) 2024-0087 on 03/17/2024 at 2345 with an expiration date of 03/20/2024 at 2345 to isolate the affected flow path and align Emergency Core Cooling System operations and instrumentation per TS 3.6.1.3, TS 3.5.1, and TS 3.3.5.1. Those actions were completed and LCO 2024-0087 was exited on 03/18/2024 at 0851. At that time operations moved to revised LCO 2024-0087B with an expiration date of 04/01/2024 at 0851 to support the necessary repairs per TS 3.5.1 and TS 3.3.5.1. LCO 2024-0087B was exited on 03/19/2024 at 1039 when repairs were made and the PCIV function of E4150-F042 was restored to operable status. Based on the past operability review, the time period used to declare the PCIV function of E4150-F042 inoperable is from when the condition was first identified in CR 2023-30437 on 05/23/2023, until the appropriate repairs were made on 03/19/2024. Per Technical Specification (TS) 3.6.1.3 Primary Containment Isolation Valves (PCIV), each PCIV shall be operable in MODES 1, 2 and 3. CONDITION E states that if any required action and associated completion time of CONDITION A, B, C or D are not met, ACTION E.1 requires the plant to be in MODE 3 in 12 hours, and ACTION E.2 requires the plant to be in MODE 4 in 36 hours. Immediate troubleshooting was conducted on E4150-F042 failing to fully close. It was determined that E4150-F042 Closed Auxiliary Seal-in contact was intermittently failing to keep the close contactor coil energized due to high resistance across the electrical contacts. This resulted in E4150-F042 failing to fully stroke closed during required surveillances without holding the pushbutton closed in the Main Control Room. | ML24137A008
LaSalle County Station | Unit 1 | Reactor Protection System Half Scram due to Motor Generator Set Electric Power Monitoring Assembly Output Breaker Trip | 05-17-2024 | On March 25, 2024, LaSalle Unit 1 was operating at 100 percent power, when the 1B reactor protection system (RPS) motor- generator (MG) set electric power monitoring assembly (EPMA) output breaker tripped due to an underfrequency condition, which resulted in the loss of the 1B RPS bus. The loss of power to this bus created a half-scram condition and initiated closure of isolation valves in multiple systems. The condition was an invalid actuation because it was not the result of actual plant conditions and not an intentional manual action. Actuations and isolations that occurred performed as designed. The cause of the MG set EPMA output breaker trip was the EPMA trip card for the output breaker being out of range high for the underfrequency setpoint which caused the trip on underfrequency. The loss of the 1B RPS bus resulted in general containment isolation signals that affected containment isolation valves in more than one system while the unit was critical. Therefore, the condition is reportable in accordance with 10 CFR 50. 73(a)(2)(iv)(A). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA. Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission. Washington. DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104). Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRG may not conduct or sponsor. and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection http://www. n re.gov/read ing-rm/doc-collections/nuregs/staff/sr1 022lr3D displays a currently valid 0MB control number. 1. FACILITY NAME (cid:127) 2. DOCKET NUMBER 3. LER NUMBER 050 SEQUENTIAL REV YEAR NUMBER NO. LaSalle County Station, Unit 1 (cid:143) 00373 052 2024 - 002 00 | Plant and System Identification LaSalle Country Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was "8" reactor protection system (RPS) logic and associate isolation functions. The affected component is the 18 electric power monitoring assembly (EPMA) output breaker. Condition Prior to Event Unit(s): 1 Date: March 25, 2024 Time: 04:04 CDT Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 100 percent Description On March 25, 2024, the main control room (MCR) received a "B" RPS half scram due to a loss of power to the Unit 1 "B" (1 B) RPS bus. Operations entered the applicable abnormal operation procedures for the loss of the 18 RPS bus. Field operators determined that the 18 RPS motor-generator (MG) set EPMA output breaker had tripped. The loss of power to the 1B RPS bus resulted in a half-scram condition and closure of isolation valves in multiple systems. The condition was considered an invalid actuation because it was not the result of a valid input signal to the RPS and was not an intentional manual action. Troubleshooting identified the frequency supplied by the MG set was approximately 60 Hz, as expected. All actuations and isolations performed as designed. The loss of the 18 RPS bus resulted in isolations of the reactor water cleanup system, main steam line drains, reactor coolant system sampling, instrument nitrogen system, reactor recirculation hydraulic power units, and containment monitoring system. The loss of the 18 RPS bus also resulted in the loss of power to portions of the average power range monitor, local power range monitor, oscillation power range monitor, and control rod block systems; as well as portions of the radiation monitoring for the main steam lines, reactor building vent, and fuel pool vent. Appropriate actuations and primary containment isolations occurred as designed. After the loss of power to the 18 RPS bus, the applicable Technical Specification (TS) timeclocks and actions were entered. Power was restored to the 18 bus by transferring the bus to the alternate power supply in accordance with plant procedures. The half-scram and isolations were reset, and the equipment was returned to operable status. All applicable TS timeclocks and actions were exited. Cause The 1B RPS MG set EPMA output breaker tripped due to an underfrequency trip signal from the EPMA trip card. The EPMA trip card was out of range high for the underfrequency setpoint which caused the 1B RPS MG set EPMA output breaker to trip due to underfrequency, even if there was no underfrequency condition present. Reportability and Safety Analysis The loss of a RPS bus and associated RPS actuation is considered an invalid actuation because it was not the result of a valid signal and not an intentional manual action. TS Surveillance Requirement (SR) 3.3.8.2.2 requires that the EPMA to have a frequency setpoint of greater than or equal to 57.3 Hz. The EPMA trip card underfrequency setpoint was discovered to be out of range high, therefore the EPMA output breaker trip is considered conservative and in compliance with SR 3.3.8.2.2. The loss of the RPS bus resulted in general containment isolation signals that actuated containment isolation valves in more than one system or multiple main steam isolation valves while the unit was critical. Therefore, the loss of the RPS bus is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). NRG FORM 366A (04-02-2024) Page_2_ of _3_ | ML24138A030
Grand Gulf Nuclear Station | Unknown Unit | Automatic Actuation of Reactor Protection System | 05-28-2024 | On March 26, 2024 at 1115 CDT, Grand Gulf Nuclear Station experienced an automatic actuation' of the reactor protection system (RPS) due to high reactor coolant system (RCS) pressure while performing in-service leak testing. The plant was in Mode 4 at zero percent power with all control rods inserted at the time of the RPS actuation. The RPS actuation occurred due to a valid high RCS pressure signal and all plant systems responded as designed. The high pressure condition occurred due to inadvertent isolation of the blowdown discharge flow path. There were no safety consequences impacting the plant or public as a result of this event. The reactor was shutdown and subcritical at the time of the actuation. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request. 80 hours Reported lessons learned are incorporated into the licensing process and fed back to Industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M). U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104). Attn: Desk Officer for the Nuclear Regulatory ComrT11ss10n 725 17th Street NW. (See NUREG-1022, R_3 for instruction and guidance for completing this form Washington, DC 20503. The NRG may not conduct or sponsor, and a person is not required to IJi!R 1/\/'f::!:IW nrc gov/reading-rrn/doc-collect1on!.!/nuregs/staff/sr1022/r~/) respond to, a collection of information unless the document requesting or requinng the collecton displays a currently valid 0MB control number. 1. FACILITY NAME 00 050 2. DOCKET NUMBER 18 3. LER NUMBER SEQUENTIAL REV NUMBER NO. Grand Gulf Nuclear Station 416 1- 0 I -I □ 052 002 | PLANT CONDITIONS At the time of the event, Grand Gulf Nuclear Station (GGNS) was in Mode 4 (Cold Shutdown) with all control rods inserted at 0% reactor power. The station was performing in-service leak testing with reactor coolant system (RCS) pressure at approximately 1025 psig. DESCRIPTION OF EVENT During the performance of in-service leak testing, RCS pressure was being maintained with control rod drive (CRD) flow and reactor water cleanup (RWCU) blowdown to the main condenser. The Control Room was transferring RWCU blowdown to the radwaste system when RCS pressure began to rise. Reactor operators took action to reduce CRD flow, but RCS pressure did not reduce rapidly. The reactor protection system actuated as designed on high RCS pressure. Operators responded per the off-normal event procedure and the RPS was reset. REPORTA BILITY The automatic RPS actuation was initially reported to the NRC as a 4-hour report per 10 CFR 50.72(b)(2)(iv)(B) on March 26, 2024. This report is made in accordance with 10 CFR 50. 73(a)(2)(iv)(A) for any event or condition that resulted in manual or automatic actuation of any system listed in paragraph 1O CFR 50. 73(a)(2)(iv)(B). CAUSE The cause of the event was RWCU blowdown discharge flow path was isolated with the RCS at high pressure. Operators believed that the RWCU blowdown flow path to the main condenser could be isolated before aligning a discharge flow path to the radwaste system. CORRECTIVE ACTIONS Completed actions: • The RWCU discharge flow path was re-established. • The RPS was reset. Planned action: • Revise integrated operating instruction procedure 03-1-01-6 "Reactor Vessel In-Service Leak Test" to add specific guidance for swapping RWCU discharge flow paths. SAFETY SIGNIFICANCE There were no safety consequences, real or potential, resulting from the event. The reactor was sub-critical with all rods inserted at the time of the event and all systems responded as designed. PREVIOUS SIMILAR EVENTS None | ML24149A159
River Bend Station | Unit 1 | Manual Reactor Scram Due to Lowering Feedwater Temperature Following an Automatic Isolation of Feedwater Heater String | 06-04-2024 | On November 17, 2023, at 22:15 CST, with River Bend Station, Unit 1, operating in Mode 1 at 30% power, an isolation of Low-Pressure Feedwater Heater String ‘A’ occurred. Operators entered the applicable Abnormal Operating Procedure (AOP) and reduced power to mitigate the lowering feedwater temperature. Reactor power was lowered to 24% and a manual reactor scram was inserted at 23:55 CST. All control rods fully inserted and there were no complications. All systems responded as designed. A direct cause of the Heater String isolation cannot be determined. This report is made pursuant to 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of the Reactor Protection System. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported ~c; , ,>A AEG<,l ..> LICENSEE EVENT REPORT (LER) l r e e s g s a o r n d s in g le a b r u n r e d d e n a r e e s t i i n m c a o t r e p o to ra t t h e e d F in O to IA t , h e L ib lic ra e r n y s , in a g n d p r In o f c o e r s m s a a ti n o d n f C e o d l l b e a c c ti k o n to s B in r d a u n s c t h ry ( . T S -6 e n A d 1 c 0 o M m ), m U e . n S ts . !~o\ .: Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to ~ ~ . 0 CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory '(,..., *••·· 0~ Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid OMB control number. 1. FACILITY NAME ■ 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV I I~ I I □ NUMBER NO. River Bend Station, Unit 1 00458 D 2023 052 - I 005 - 01 I | Event Description On November 17, 2023, at 22:15 CST, River Bend Station (RBS), Unit 1, was operating at 30% power while performing plant startup activities when an isolation of Low-Pressure Feedwater Heater String ‘A’ [SJ] occurred. Main Control Room Operators entered Abnormal Operating Procedure – Loss of Feedwater Heating (AOP-0007) for transients involving lowering feedwater temperature. AOP-0007, Attachment 1 (Feedwater Temperature vs Core Thermal Power Graph), provides guidance for power operations with reduced feedwater temperature from 100% reactor power to 25% reactor power. In accordance with AOP-0007, Attachment 1, operators began to manually insert control rods using the Control Rod Drive System [AA] to exit the restricted region for power operations at the lower feedwater temperature. Control rod insertion lowered power to 24%, which placed the unit below the graph start point of AOP-0007, Attachment 1. At 23:55 CST, while RBS was operating at 24% power, a manual reactor scram was inserted due to operation below the graph start point of AOP-0007, Attachment 1, caused by continued lowering of feedwater temperature. All control rods fully inserted and there were no complications. All systems responded as designed. AOP-0007, Attachment 1, contains a graph of feedwater temperature versus core thermal power; however, no information is provided for power levels below 25.7% of rated power. With reactor power lowering to 24%, the operators were not able to determine if the unit was operating in an acceptable region. Therefore, the conservative decision was made to manually scram the reactor. Following the initial investigation, engineering input from calculations performed as part of an engineering change has provided new information for operating at power levels below 25.7%. This event was reported under 10 CFR 50.72(b)(2)(iv)(B), as any event or condition that results in actuation of the Reactor Protection System (RPS) when the reactor is critical and 10 CFR 50.72(b)(3)(iv)(A) Specified System Actuation as result of Group 3 isolations (EN 56863). This report is made pursuant to 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of the Reactor Protection System. Event Cause There is insufficient evidence to determine a direct causal factor for the Low-Pressure Feedwater Heater String isolation event. An independent third-party review of this incident has determined the most probable cause of the isolation was a level switch actuation due to steam backflow from the drain receiver tank volume flashing as a result of a rapid pressure transient event. Safety Assessment The actual consequence was the initiation of a manual scram. Following the scram, reactor pressure was maintained by the Turbine Steam Drains [TF] and reactor water level was maintained by the Feedwater [SJ] system. The RBS power to flow map continued to meet the licensing acceptance criteria parameters. There were no actual consequences to general safety of the public, nuclear safety, industrial safety, and radiological safety for this event. | ML24156A040
Cooper Nuclear Station 298 1 of 5 | Unknown Unit | Secondary Containment Differential Pressure Perturbation Exceeds Technical Specifications | 06-06-2024 | On October 22, 2023, Reactor Building pressure exceeded the Technical Specifications limit of -0.25 inches of water gauge (wg) resulting in Secondary Containment being declared inoperable. Operations personnel walked down the ventilation systems and found that the first discharge duct hatch for EF-R-1 B was open. The hatch was subsequently closed, and Secondary Containment pressure returned to the normal operating set point of -0.33 inches wg. The cause of the event was the opened first discharge duct hatch for EF-R-1 B. The cause of the open hatch has been determined to be looseness of the latching mechanism likely due to normal vibrations from system operations. There was no impact on nuclear safety, plant reliability, radiological safety, or industrial safety. Event Notification 56811 was submitted on October 22, 2023, due to the unplanned inoperability of Secondary Containment. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process LICENSEE EVENT REPORT (LER) and fed back to industry. Send comments regarding burden estimate to the FOIA, CONTINUATION SHEET Library, and Information Collections Branch (T-6 A 1O M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC (See NUREG-1022, R.3 for instruction and guidance for completing this form may not conduct or sponsor, and a person is not required to respond to, a collection http://www. nrc.g ov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Cooper Nuclear Station 05000-298 NUMBER NO. 2023 002 01 | PLANT STATUS Cooper Nuclear Station was in Mode 1, Power Operation, at 100 percent power at the time of the event on October 22, 2023. Both Standby Gas Treatment (SGT) [EIIS: BH] trains were in normal standby lineup. Reactor Building Heating and Ventilation (RB HV) [EIIS: VA] was controlling Secondary Containment pressure. Single exhaust fan EF-R-1 B was in service, with an indicated exhaust flow rate of 35,000 standard cubic feet per minute, for cold weather operation. BACKGROUND Secondary Containment serves as a barrier to confine and monitor potential releases during fuel handling operations and is a system that limits the release of radioactive materials to the environment and consists of four subsystems. One of the subsystems is the Reactor Building [EIIS: NG], which encloses the Reactor Pressure Vessel [EIIS: RPV] and Primary Containment [EIIS: NH]. The Secondary Containment area (most of the Reactor Building) has supply and exhaust ventilating systems. The supply system furnishes filtered 100% outdoor air to all floors of the building through ductwork. The supply unit has an operating and standby (100% capacity) fan, each with vortex dampers [EIIS: COMP], which deliver supply air at a rate proportional to a static pneumatic signal set manually by operations personnel. The exhaust air is induced from the ventilated areas to a common plenum connected to the two exhaust fans, each of 100% capacity. The air is then exhausted to the atmosphere. During normal plant operation, a minimum average negative pressure (vacuum) of 0.25 inches of water gauge (wg) is maintained by differential pressure (DP) controllers which receive signals proportional to the pressure difference between outside air and the Secondary Containment atmosphere, and control the position of the exhaust fan vortex dampers. The DP is detected by four separate probes, with one on each side of the Reactor Building. Control action is initiated from the average value of the four sensor probes. If a Loss of Coolant Accident should occur, all ventilation systems of the Primary Containment area and Secondary Containment area will trip, Secondary Containment is isolated automatically, and the SGT system will be automatically initiated. Each exhaust fan has a transition piece between the round fan barrel and the following rectangular duct work. Each exhaust fan has an air operated discharge damper installed in the duct work immediately downstream of the transition piece. On each exhaust fan discharge duct, there is a duct hatch on the upstream side of the | ML24158A065
Limerick Generating Station | Unit 1 | Core Operating Limits Report Thermal Limit Exceeded for Unit 1 Fuel Bundle GGK123 | 06-18-2024 | On April 12, 2024, while performing a water rod inspection of fuel bundle GGK123 during a planned refuel outage, it was(cid:3) identified that several fuel spacers had propagated up within the bundle toward the upper tie plate. It was determined through(cid:3) analysis that spacer positioning had a direct effect on the Minimum Critical Power Ratio (MCPR). On April 22, 2024, an(cid:3) analysis of the operating conditions by Global Nuclear Fuel (GNF) of fuel bundle GGK123 was reviewed and accepted by the(cid:3) station. The report confirmed that, during the previous cycle, the Operating Limit MCPR exceeded limits set by Technical(cid:3) Specifications (TS) 3.2.3. Since the Operating Limit MCPR was exceeded for longer than allowed by TS Limiting Condition for(cid:3) Operation (LCO) 3.2.3, this event is reportable as a condition prohibited by TS per 10 CFR 50.73(a)(2)(i)(B). The fuel bundle spacers shifted out of position over the previous operating cycle. This condition was identified during the(cid:3) inspections in response to GNF 10 CFR Part 21 communication SC 22-04, GNF3 Raised Water Rod. This fuel bundle has(cid:3) been removed from the reactor core, is currently located in the spent fuel pool, and will not be re-loaded into the core. There(cid:3) was no impact to the health and safety of the public or plant personnel because the Safety Limit MCPR was not exceeded in(cid:3) the previous cycle operation(cid:17) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments ~¥' LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. ; i CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to ..... Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory <--+_, ~o' Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 •YEAR SEQUENTIAL REV I I~ I NUMBER NO. Limerick Generating Station Unit 1 352 I D 052 2024 - I 003 - 00 I | Condition Prior to Event On April 22, 2024, prior to the determination that fuel bundle GGK123 had exceeded a thermal limit, Limerick Generating Station Unit 1 was in Operational Condition (OPCON) 4 (Cold Shutdown) with reactor coolant temperature of 132 degrees Fahrenheit. Event Description On April 12, 2024, during planned in-core fuel inspections for mis-oriented water rods of susceptible GNF3 fuel bundles [EIIS System AC] in response to GNF 10 CFR Part 21 communication SC 22-04, an unexpected condition for fuel bundle GGK123 was discovered where four spacers visibly collocated below the upper tie plate. The four spacers located in the bottom portion of the fuel bundle were found at their expected (installed) axial locations. Fuel bundle GGK123 was permanently discharged to the spent fuel pool. Fuel vendor GNF evaluated the impact of this condition for the previous operating cycle. The evaluation conservatively assumed the spacers were displaced for all but the first week of the cycle. The inspection results showed the spacer contact marks indicated prolonged contact with the fuel indicating the spacers did not move early in the cycle. On April 22, 2024, the station completed the evaluation for fuel bundle GGK123. Analysis of the Event The evaluation report determined that: (cid:118) There were no penalties or adjustments associated with Linear Heat Generation Rate (LHGR) and Average Planar(cid:3)Linear Heat Generation Rate (APLHGR) and no (cid:71)(cid:76)(cid:86)(cid:70)(cid:72)(cid:85)(cid:81)(cid:76)(cid:69)(cid:79)(cid:72) impact to thermal limits and margins. (cid:118) There was no discernible impact to thermal limits and margins for co-resident fuel in the Unit 1 reactor core during the(cid:3)previous cycle of operation. (cid:118) The Operating Limit Minimum Critical Power Ratio (MCPR) exceeded limits set by TS 3.2.3 for the previous cycle. (cid:118) The Safety Limit MCPR requirements set by TS 2.1.2 were never violated for the previous cycle. The report determined that the requirements of TS LCO 3.2.3 MCPR were not met for Unit 1 Cycle 20. TS LCO 3.2.3 requires all MCPR values to be greater than or equal to the MCPR operating limits specified in the Core Operating Limits Report (COLR). If the MCPR value is less than the MCPR value in the COLR, TS LCO 3.2.3 Action b requires corrective actions to be initiated within 15 minutes and the MCPR value restored to within the required limits within two-hours or reduce thermal power to less than 25 percent within the next 4 hours. Since the station conservatively assumed the condition existed for most of the operating cycle, the station exceeded the two-hour requirement to restore MCPR within limits and did not reduce thermal power to less than 25 percent within the next 4 hours. Therefore, this event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant’s TS. Safety Consequences There were no actual safety consequences to this condition. The MCPR Safety Limit was not exceeded and there was no breach of fuel cladding for fuel bundle GGK123. | ML24170A772
Joseph M. Farley Nuclear Plant | Unit 2 | Manual Reactor Trip due to Loss of Power to the 2A 125 Volt DC Distribution Panel | 06-19-2024 | On February 16, 2024, at 00:48 CDT while in Mode 1 and at 100% power, Farley Nuclear Plant (FNP) operators manually tripped Unit 2 following a loss of control of critical air-operated valves due to a partial loss of A-train DC power. LA08-2, the feeder breaker to the 2A 125VDC Distribution Panel, was found tripped open. This event resulted in a loss of letdown and the reactor makeup system. With volume control tank (VCT) makeup capability lost, operators made the decision to trip the reactor prior to charging pump suction rollover to the refueling water storage tank (RWST). The cause of the breaker opening was due to a short between wires on the A phase current transformer (CT)/ sensor wiring harness in breaker LA08-2 because of poor workmanship. Immediate corrective action included replacing breaker LA08-2 with a spare breaker to restore plant equipment to operation and stabilize the plant. This event is reportable under 10 CFR 50.73(a)(2)(iv)(A) due to the automatic actuation of multiple systems listed in 10 CFR 50.73(a)(2)(iv)(B). FNP Unit 1 was not affected during this event. However, the 10 CFR 21 notification does apply to Unit 1. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid 0MB control number. .1. -FA-CIL-ITY- NA-ME- ----------, ~ 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV Joseph M. Farley Nuclear Plant, Unit 2 364 □ NUMBER NO. ~- I 1-0 □ 052 I I 002 | EVENT DESCRIPTION: On February 16, 2024, at 00:48 CDT, with reactor power at 100% and in Mode 1, Farley Nuclear Plant (FNP) operators manually tripped Unit 2 following a partial loss of A-train 125V DC power which affected critical air-operated valves. Breaker LA08-2 [EIIS: EJ/BKR] the supply breaker to the 2A 125VDC Distribution Panel, was found tripped open. Loss of power to the 2A 125VDC Distribution Panel resulted in a loss of letdown and the reactor makeup system. With the volume control tank (VCT) [EIIS: CB / TK] makeup capability lost operators made the decision to trip the reactor prior to the charging pump suction rollover to the refueling water storage tank (RWST). Operating events and actions occurred in the following timeline on February 16, 2024: 00:35 Multiple Main Control Room Alarms are received. 00:35 Breaker LA08-02 Tripped (Entry into TS 3.8.9) 00:35 Entry into Abnormal Operating Procedure for CVCS Malfunction 00:36 Entry into Abnormal Operating Procedure of Loss of Instrument Air 00:36 Letdown confirmed isolated and loss of makeup capability. 00:48 Operators Manually Trip Reactor based on VCT level. 01 :42 Reactor Coolant Pump 2B secured due to low seal leak off. 01 :45 Pressurizer (PZR) level rises to Technical Specification (TS) high value of 63.5%. (Entry into TS 3.4.9) 02:09 Instrument Air realigned to Containment. 03:08 Commenced Reactor Coolant System (RCS) Cooldown 04:20 Following troubleshooting and breaker replacement, closed Breaker LA08-02 and restored Letdown (Exit TS 3.8.9) 04:34 NRC notified per 10 CFR 50. 72 (EN# 56971) 04:54 PZR level restored (Exit TS 3.4.9) Following the reactor trip, main feedwater [EIIS: JB] continued to be available. An actuation of the Auxiliary Feedwater System [EIIS: BA] occurred following the manual reactor trip as designed due to low level in the steam generators [EIIS: SB/SG]. BASIS FOR REPORTABILITY AND SAFETY ASSESSMENT: The safety consequences of this event were low. Although the component failure had downstream interrelation system effects on letdown and makeup, the operating crew appropriately mitigated the transient with abnormal and emergency operating procedures. Additionally, all TS required actions were met and parameters restored well within required action times. The operating crew responded appropriately to the event. This event was within the analysis of the UFSAR Chapter 15. This event is reportable per 10 CFR 50. 73(a)(2)(iv)(A) due to the automatic actuation of the Reactor Protection System [EIIS: AA] and AFW system as listed in 10 CFR 50.73(a)(2)(iv)(B). FNP Unit 1 was not affected during this event. CAUSE: The 125 Volt DC AKW breaker was built by Siemens and equipped with SIGMATRIP DC Analog Trip Unit built by SURE-TRIP. Framatome was the vendor used to qualify the safety related breakers and trip units. The analysis determined that the vendor QA/QC program was not sufficient to identify poor practices when interfacing with third party products. It was determined that during installation of the SIGMAT RIP DC Analog Trip Unit that the stranded wires that were terminated in the harness protruded in such a manner they were able to short to an adjacent wire in the harness. The short occurred in breaker LA08-2 (Serial Number R-300950258102B-001) on the A phase current transformer (CT)/sensor harness. For the SIGMATRIP DC Analog Trip Unit, Siemens and Framatome do not currently have a verification step/QA/QC check or any instruction for inspecting the wires connected in the wiring harnesses mounted to the CTs/sensors or the trip uniUlogic box. | ML24171A018
i | Unknown Unit | : | 06-20-2024 | From March 25, 2024 to March 31, 2024, in Mode 1 at 100% power, Residual Heat Removal (RHR) loops B and C were not configured to the dedicated waterleg pump, a condition prohibited by Technical Specifications (TS). This condition, and an unanalyzed condition of the alternate keepfill configuration, were determined April 25, 2024. Based on the Cause Investigation: Cause 1 was a series of human performance errors processing an improper operating procedure revision; Cause 2 was ineffective communication between Operations and Engineering; a Contributing Cause was that past evaluations of the requested procedure change had missed the opportunity to clearly state in the procedure that the change did not support single active component failure licensing basis requirements The RHR procedure was revised to reflect the licensing basis. Planned corrective actions include: implementing an operations procedure department’s guidance document; authoring a new Training case study about communications; revising RHR and inservice testing program procedures to explain why alternate keep fill configuration causes RHR loop inoperability. The March 2024 RHR operational configurations are being reported as a condition prohibited by TS under 10 CFR 50.73(a)(2)(i)(B), and as an unanalyzed condition under 10 CFR 50.73(a)(2)(ii)(B). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Services Branch (T-6 A10M), U. S. CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ~ 050 YEAR SEQUENTIAL REV NUMBER NO. Perry Nuclear Power Plant 00440 2024 - 001 - 00 □ 052 | Energy Industry Identification System and Component (EIIS) codes are identified in the text as [XX]. System Description The Perry Residual Heat Removal (RHR) System [BO] is part of the Emergency Core Cooling System (ECCS) that is designed to provide cooling water (the RHR’s Low Pressure Coolant Injection (LPCI) function) to the reactor vessel [RPV] as protection against postulated loss-of-coolant accidents (LOCA). The RHR System has three loops (A, B, C), each with its own injection pump [P], which differ from the waterleg pumps. The licensing basis, as stated in the Updated Safety Analysis Report (USAR), requires that RHR cooling water flow from the Suppression Pool [BT] to the reactor vessel be initiated rapidly when the RHR System is called on to perform its function. The lag between the signal to start an RHR pump and the initiation of flow can be minimized by keeping the pumps’ discharge lines full. The licensing basis credits only the specific safety related, seismically qualified RHR waterleg pumps to automatically provide water to the RHR loops, downstream of each loop’s main RHR pump, to maintain the loops water solid. One waterleg pump supplies water to the RHR A loop, and another waterleg pump supplies water to both the RHR B and RHR C loops. An alternate keep fill configuration, relying upon water from non-safety related, non-seismically qualified, and non-essentially powered Condensate Transfer and Storage System [KA] piping, can be used to provide initial filling of the RHR discharge lines. The Condensate Transfer and Storage System piping water enters, via the alternate keep fill lineup, at each RHR loop’s piping downstream of where each loop would receive the waterleg pump’s water. At the interface of RHR and Condensate Transfer and Storage piping, each RHR loop has a single 8-inch safety-related check valve [V]. This alternate keep fill configuration is not a licensing basis credited method of keeping the RHR discharge lines water solid. Perry Technical Specification (TS) 3.5.1 is "ECCS - Operating." Limiting Condition for Operation (LCO) 3.5.1 requires each ECCS injection/spray subsystem be Operable in Modes 1, 2, and 3. With one low pressure ECCS injection/spray subsystem inoperable, TS LCO 3.5.1 Required Action A.1 requires the subsystem be restored to Operable status in 7 days. With two ECCS injection subsystems inoperable, Required Action C.1 requires one subsystem be restored to Operable status in 72 hours. If the C.1 Required Action and associated Completion Time are not performed and met, Required Action D.1 requires the unit be in Mode 3 Hot Shutdown in 12 hours, and Required Action D.2 requires the unit be in Mode 4 Cold Shutdown in 36 hours. DESCRIPTION OF EVENT 1. Operation in a condition prohibited by Technical Specifications. On February 22, 2024, operating procedure SOI-E12 Revision 79, “Residual Heat Removal System,” had been updated to Revision 80. The main purpose of that revision had been to delete revision 79’s directives pertaining to waterleg pump and alternate keep fill operation. Revision 79 reflected the licensing basis by stating as a Precaution and Limitation (P&L) that “If RHR A, B, or C are placed on alternate keep fill or the respective Waterleg pump is shutdown the affected RHR loop will be inoperable,” and by directing as a procedure step to “DECLARE the affected RHR loop inoperable.” Revision 80 of SOI-E12 deleted directives to declare an RHR loop inoperable, whenever that RHR loop has an inoperable waterleg pump or is in alternate keep fill configuration. Revision 80 directed in a new Precaution and Limitation that “If RHR A, B, OR C are placed on alternate keep fill AND the RHR PUMP A(B,C) DISCHARGE PRESSURE HI/LO. . . is received the RHR loop will be inoperable,” thereby allowing the system to be considered operable otherwise. | ML24172A162
Browns Ferry Nuclear Plant | Unit 1 | Reactor Scram due to Generator Step-Up Transformer Failure | 06-24-2024 | On April 24, 2024, at 2215 Central Daylight Savings Time, while Unit 1 was at 100 percent rated thermal power, Browns Ferry Nuclear Plant Unit 1 experienced an automatic reactor scram due to a fault within the 1B Main Transformer. All plant equipment responded as expected, and Unit 1 was transitioned to Mode 4. The cause of the transformer failure is currently under investigation. The root cause of the transformer failure will not be known until a forensic tear down is complete. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), as an automatic actuation of the Reactor Protection System, Primary Containment Isolation System, the High-Pressure Coolant Injection System, and the Reactor Core Isolation Cooling System. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ☒ 050 SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 1 00259 NUMBER NO. ☐ 052 2024 - 002 - 00 | I. Plant Operating Conditions before the Event At the time of discovery of this event on April 24, 2024, Browns Ferry Nuclear Plant (BFN) Unit 1 was in Mode 1 at approximately 100 percent Rated Thermal Power (RTP). II. Description of Event A. Event Summary On April 24, 2024, at 2215 Central Daylight Savings Time (CDT), while Unit 1 was at 100 percent RTP, Browns Ferry Nuclear Plant (BFN) Unit 1 experienced an automatic reactor scram from a turbine control valve (TCV) [XCV] fast closure signal due to a fault within the 1B Main Transformer [XFMR]. All plant equipment responded as expected, and Browns Ferry Unit 1 was transitioned to Mode 4. Primary Containment Isolation Systems (PCIS) [JM] Groups 2, 3, 6, and 8 isolation signal reactor water level (RWL) Level 3 (+2”) was received. Upon receipt of this signal, all components actuated as required. Following the reactor scram, due to reactor water level reaching Level 2 (-45”), reactor recirculation pumps tripped as expected and both High Pressure Coolant Injection (HPCI)[BJ] and Reactor Core Isolation Cooling (RCIC) [BN] initiation signals were received, and both systems initiated as designed. All safety systems operated as expected. At no time was public health and safety at risk. The Tennessee Valley Authority (TVA) is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(iv)(A), as an automatic actuation of the Reactor Protection System (RPS) [JC], the Primary Containment Isolation System (PCIS) [JM], the High-Pressure Coolant Injection (HPCI) [BJ] System, and the Reactor Core Isolation Cooling (RCIC) [BN] System. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML24176A102
Browns Ferry Nuclear Plant | Unit 1 | Inoperability of Unit 3 Diesel Generator due to Relay Failure | 07-03-2024 | On February 14, 2024, while performing Surveillance Procedure 3-SR-3.8.1.9(3D OL), “Diesel Generator 3D Emergency Load Acceptance Test with Unit 3 Operating,” the Unit 3 D Emergency Diesel Generator (DG) did not start on an undervoltage condition on its associated safety bus as expected. BFN-3-RLY-082-D/SUDR (Single Unit Defeat Relay) contacts 3 and 4 are designed as normally closed but were found electrically open in the normal state causing the Diesel fast start circuit to not be made up. The apparent cause of the misalignment of the SUDR relay contacts was the lack of effective Preventative Maintenance (PM). Improved PM Strategy to provide more detailed relay inspections /testing requirements for DG starting logic relays that have critical functions will be implemented. During this event, the 3D DG would have continued to support the safety function of starting on the receipt of an accident signal as designed. Although the 3D DG would not have automatically started during a loss of offsite power, operators are directed to immediately ensure DGs are started and tied to their respective safety busses. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME ☒ 050 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 1 00259 NUMBER NO. ☐ 052 2024 - 001 - 01 | I. Plant Operating Conditions before the Event At the time of this event on December 14, 2022, Browns Ferry Nuclear Plant (BFN) Unit 1 was in Mode 1 at approximately 100 percent power, Unit 2 was in Mode 1 at approximately 100 percent power, and Unit 3 was in Mode 1 at approximately 96 percent power. II. Description of Event A. Event Summary On February 14, 2024, while performing Surveillance Procedure 3-SR-3.8.1.9(3D OL), “Diesel Generator 3D Emergency Load Acceptance Test with Unit 3 Operating,” the Unit 3 D Emergency Diesel Generator (DG) [EK] did not start on an undervoltage condition on its associated safety bus [EB] as expected. Troubleshooting identified that the DG did not start due to a failure (open circuit) of Single Unit Defeat Relay (SUDR) [RLY] normally closed contacts (3-4). The relay was repaired and the surveillance test was reperformed satisfactorily on February 15, 2024. A past operability evaluation was performed by engineering that determined that the relay had been inoperable since December 14, 2022 when the 3D EDG started slower than expected during the performance of Surveillance Procedure 3-SR-3.8.1.1(3D), “Diesel Generator 3D Monthly Operability Test.” It was not originally recognized that the slower than expected DG start time could be an indication of the inability of the DG to start on a loss of voltage signal. Unit 3 Technical Specifications (TS) 3.8.1, “AC Sources - Operating,” and 3.8.2, “AC Sources - Shutdown,” requires the Unit 3 DGs to be operable in MODES 1, 2, 3, 4 and 5, and during movement of irradiated fuel assemblies in the secondary containment. Units 1 and 2 TSs 3.8.1 and 3.8.2 require the Unit 3 DGs associated with AC Boards needed to support equipment required for Units 1 and 2 to be Operable in Modes 1, 2, 3, 4, and 5, and during movement of irradiated fuel assemblies in the secondary containment. Because the 3D DG was inoperable from December 14, 2022, until February 15, 2024, the associated TS Actions were not complied with. Additionally, Mode changes were made with the 3D DG inoperable which is prohibited by TS 3.0.4. The Tennessee Valley Authority (TVA) is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant’s TSs. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML24185A151
Edwin I. Hatch Nuclear Plant | Unit 2 | Incorrectly Installed Temporary Modification Results in Multiple Conditions Prohibited by Plant Technical Specifications | 04-30-2027 | At 1301 EST on 2/27/2024 while Unit 2 was at 100% power in MODE 1 and Unit 1 was at 0% power in MODE 4, it was discovered that a temporary Plant Service Water (PSW) modification was incorrectly installed on the Bravo condensing unit (CDU) of the Main Control Room Air Conditioning (MCRAC) subsystem. This temporary modification was installed on 1/30/2024 and then removed on 2/28/2024. For the time period that the incorrectly installed temporary PSW modification was in place, a past operability review (POR) was performed. The POR confirmed that the temporary PSW modification was installed incorrectly, rendering the Bravo MCRAC subsystem inoperable for a period of 29 days. Additionally, it was determined that the Alpha MCRAC subsystem was inoperable due to low refrigerant between 1/25/2024 and 2/8/2024. Due to these inoperabilities, several conditions prohibited by Technical Specifications (TS) were experienced as discussed below. With the removal of the temporary PSW modification on 2/28/2024 the operability of the Bravo MCRAC subsystem was restored. The Alpha MCRAC subsystem was repaired by adding refrigerant on 2/8/2024. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid 0MB control number. .1. -FA-CIL-ITY- NA-ME- ----------, ~ 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV Edwin I. Hatch Nuclear Plant Unit 2 00366 □ NUMBER NO. ~- I 1-0 □ 052 I I 002 | EVENT DESCRIPTION At 1301 EST on 2/27/2024 while Unit 2 was at 100% power in MODE 1 and Unit 1 was at 0% power in MODE 4, it was discovered that a temporary Plant Service Water (PSW) (EIIS Code: Bl) modification was incorrectly installed on the Bravo condensing unit (CDU) of the Main Control Room Air Conditioning (MCRAC) subsystem (EIIS Code: VI). This temporary modification was installed on 1/30/2024 @ 1020 and then restored on 2/28/2024 @ 1441. For the time period that the incorrectly installed temporary PSW modification was in place, a past operability review (POR) was performed. The POR confirmed that the temporary PSW modification was installed incorrectly, rendering the Bravo MC RAC subsystem inoperable for a period of 29 days, between 1/30/2024 @ 1020 and 2/28/2024 @ 1441. Additionally, it was determined that the Alpha MCRAC subsystem was inoperable due to low refrigerant between 1/25/2024@ 0416 - 2/8/2024@0410. Due to these inoperabilities, twelve conditions prohibited by Technical Specifications (TS) were experienced as discussed below. For reference, Unit 1 and Unit 2 share MCRAC and Main Control Room Environmental Control (MCREC) subsystems and have a common refueling floor. Unit 2 was in MODE 1 throughout the duration of these events. Unit 1 was in MODE 1 until 2/4/2024 @ 0008 when it entered MODE 3. Unit 1 was cooled down to MODE 4 on 2/4/2024 @ 0653 and then entered MODE 5 on 2/5/2024 @ 1211. Unit 1 transitioned back to MODE 4 on 2/23/2024 @ 1850. Prohibited Condition 1 & 2: Unit 1 & Unit 2 were not brought to MODE 3 in 12 hours as required by TS 3.7.4.E The design of the MCREC system requires one operable MCRAC subsystem per MCREC subsystem. With the Bravo MCRAC subsystem inoperable, the other two subsystems (Alpha and Charlie) have to be in-service to meet the requirements of the MCREC TS condition 3.7.4. The POR revealed that this condition was not continuously met. From 2/1/2024@ 0824 until 2/1/2024@ 2147 all three MCRAC units were inoperable_ Alpha and Bravo were inoperable for reasons discussed above and Charlie was inoperable due to a cooling water tagout. This condition, which resulted in both MCREC trains being rendered inoperable, existed in excess of the Unit 1 & Unit 2 TS condition 3.7.4.E (two MCREC subsystems inoperable) completion time of 12 hours to be in MODE 3. Prohibited Conditions 3 & 4: Unit 2 was not brought to MODE 3 in 12 hours as required by TSs 3.7.4.C and 3.7.5.D Once the Bravo MCRAC unit was rendered inoperable due to the PSW modification, concurrent with the Alpha MCRAC inoperability, one of the MCREC subsystems was rendered inoperable. The required actions for Unit 2 TS conditions 3.7.4.A (one MCREC inoperable) and 3.7.5.B (two MCRAC subsystems inoperable) each have a 7 day completion time. These completion times began on 1/30/2024 @ 1020 and expired on 2/6/2024 @ 1020 requiring entry into TS conditions 3.7.4.C and 3.7.5.D, each with a 12 hour completion time to be in MODE 3. These completion times expired on 2/6/2024@ 2220, but Unit 2 was not brought into MODE 3. Prohibited Condition 5: Unit 2 was not brought to MODE 3 in 12 hours as required by TS 3.7.4.E From 2/6/2024 @ 2350 until 2/8/2024 @ 0410, all three MCRAC units were inoperable (Note: Unit 1 was not in a MODE of applicability specified in TS 3.7.4.E during this time). Alpha and Bravo were inoperable for reasons discussed above and Charlie was inoperable due to an electrical bus tagout. This condition, which resulted in both MCREC trains being rendered inoperable, existed in excess of the Unit 2 TS condition 3.7.4.E (two MCREC subsystems inoperable) completion time of 12 hours to be in MODE 3. | ML24185A259
Edwin I. Hatch Nuclear Plant | Unit 1 | Reactor Core Isolation Cooling (RCIC) System Inoperable Due to Mispositioned Link | 07-03-2024 | At 1133 EDT on 5/8/2024, with Unit 1 operating at 99. 7% power in MODE 1, maintenance was performing a surveillance on Reactor Core Isolation Cooling (RCIC) and identified an open electrical link that should have been in the closed position. This link being open defeated the RCIC High Reactor Water Level trip function. The High Reactor Water Level trip is a Technical Specification (TS) required function, without which RCIC is inoperable. At 1725 on 5/8/2024 the link was closed, restoring the High Reactor Water Level trip function and RCIC operability. Causal analysis determined that, due to a gap in the usage of human performance (HU) tools, the link was inadvertantly left open after restoration of a tagout on 3/8/2024 during the refueling outage. Corrective actions for this event focused on management reinforcement of HU Tool usage. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV Edwin I. Hatch Nuclear Plant Unit 1 00321 □ NUMBER NO. ~- I 1-G □ 052 I I 003 | EVENT DESCRIPTION At 1133 EDT on 5/8/2024, with Unit 1 operating at 99. 7% power in MODE 1, maintenance was performing a surveillance on Reactor Core Isolation Cooling (RCIC)(EIIS: BN) and identified an open electrical link that should have been in the closed position. This link being open defeats the RCIC High Reactor Water Level trip function. The High Reactor Water Level trip is a Technical Specification required function, without which RCIC is inoperable. EVENT CAUSE ANALYSIS The link being inadvertently left open was due to a gap in the usage of HU tools such as task preview, validating assumptions, and having a questioning attitude when manipulating plant equipment. SAFETY ASSESSMENT There were no actual safety consequences as a result of this event. At any time while the link was open, RCIC would have started at its low reactor water level setpoint and injected as required. If vessel level continued to rise during RCIC injection moisture carryover into the main steam lines could, over the course of time, lead to RCIC turbine damage. However, the RCIC mission time is only 8 hours and RCIC can be manually secured at any time if needed. Furthermore, RCIC is not credited in the safety analysis. This event is reportable per 10 CFR 50.73 (a)(2)(i)(B) as a condition prohibited by TS. The RCIC system was inoperable between 3/8/2024 until the link was closed on 5/8/2024. During this time, Unit 1 entered the mode of applicability on 3/10/2024 @ 1150 and then exited the mode of applicability due to cooling down from a reactor scram on 3/11/2024 @ 1903. Then Unit 1 entered the mode of applicability again after the subsequent startup on 3/17/2024 @ 1928. The allowable TS 3.5.3.A (RCIC inoperable) completion time of 14 days plus the TS 3.5.3.B completion time of 12 hours to be in MODE 3 was exceeded on 4/1/2024 @ 0728. Addtionally, the High Pressure Coolant Injection (HPCl)(EIIS: BJ) pump was operable when RCIC was inoperable except from 3/10/2024@ 2331 until 3/11/2024@ 0027 for performance of a surveillance test. This overlapping time of RCIC and HPCI inoperabilities did not exceed the TS 3.5.1.G completion time of 12 hours to bring the unit to MODE 3 when both RCIC and HPCI are inoperable. All low pressure ECCS systems were operable during the time RCIC was inoperable. CORRECTIVE ACTIONS At 1725 on 5/8/2024 the link was closed, restoring the High Reactor Water Level trip function and RCIC operability. Immediate corrective actions for this event focused on management reinforcement of HU Tool usage. Additionally, actions are in progress to conduct oral boards to reinforce the use of HU Tools. PREVIOUS SIMILAR EVENTS None. | ML24185A269
Browns Ferry Nuclear Plant | Unit 3 | Main Steam Relief Valves Lift Settings Outside of Technical Specifications Required Setpoints | 07-08-2024 | On May 7, 2024, the Tennessee Valley Authority (TVA) was notified of as-found testing results that four (4) Main Steam Relief Valves (MSRVs) from Browns Ferry Nuclear Pant (BFN), Unit 3 were outside of their Surveillance Requirement limits for an indeterminate amount of time. These affected valves remained capable of maintaining reactor pressure within the American Society of Mechanical Engineers code limits and were still able to perform their safety function. It was determined that two MSRVs failed above their setpoints due to corrosion bonding to the valve seats and non-quantifiable leakage known as simmering. Two other MSRVs failed below their setpoints due to relaxed setpoint springs. All thirteen of the MSRV pilot valves were replaced during the Unit 3 Spring 2024 refueling outage. The Boiling Water Reactor Owners' Group is continuing to work toward a solution to improve the quality and adhesion of the platinum coating on the pilot discs. BFN will take additional actions to verify that the springs associated with each low failure passes Spring Rate testing or is replaced. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME ☒ 050 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 3 00296 NUMBER NO. ☐ 052 2024 - 003 - 2024 | I. Plant Operating Conditions before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN) Unit 3 was in Mode 1 at approximately 100 percent power. II. Description of Event A. Event Summary On May 7, 2024, NTS/Element notified TVA with the as-found testing results of the thirteen Main Steam Relief Valves (MSRVs) [RV], which were removed during the Spring 2024 Unit 3 Refueling Outage 21 (U3R21). Four (4) MSRVs (3-PCV-001-0004, 3-PCV-001-0005, 3-PCV-001-0022, and 3-PCV-001-0030) had as-found lift settings which were outside of the +/- 3 percent band of their setpoints required by Technical Specification (TS) 3.4.3, Safety/Relief Valves (S/RVs) for an indeterminate amount of time. Throughout this event, the two stage MSRV pilot valves remained capable of maintaining reactor pressure below 1375 pounds per square inch gauge (psig), which is the American Society of Mechanical Engineers (ASME) code limit of 110 percent of the vessel design pressure. The valves remained capable of performing their required safety function. TVA is submitting this report in accordance with Title 10 of the Code of Federal Regulations 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant’s TS. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML24190A129
Perry Nuclear Power Plant | Unit 1 | : | 07-15-2024 | While operating in MODE 1 at 100% power on May 23, 2024 at 0000, Perry Nuclear Power Plant (PNPP) operators entered Technical Specification (TS) 3.4.5 due to the unidentified reactor coolant system (RCS) leak rate exceeding 5 gpm. PNPP operators commenced a manual reactor shutdown in accordance with site procedures at 0053 on May 23, 2024. Unable to reduce the unidentified RCS leakage, the shutdown transitioned to a TS required shutdown at 0400 and reported as Event Number 57136. The required safety systems and shutdown equipment performed as expected, resulting in an uncomplicated shutdown. The source of the unidentified RCS leakage was the reactor recirculation loop 'A' suction valve packing leak-off line via a failed sight glass flange. The leak-off line was isolated and sight glass repaired. The root causes were failing to maintain and operate the leak detection system leak-off lines as designed because of unrecognized potential consequences from a failure in inaccessible areas and not prioritizing permanent repairs for long standing equipment degradation during outage scoping. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(A) as completion of a plant shutdown required by the Technical Specifications. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150--0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported ,.r)P·'w.fl~5Gul.t \ . LICENSEE EVENT REPORT (LER) l r e e s g s a o rd n i s n g le a b r u n r e d d e n a r e e s i t n im co a r te p o t r o a t t e h d e in F t O o IA th , e L l i i b ce ra n r s y i , n g a n p d r o In ce fo s r s m a a n ti d o n fe S d e b r a vi c c k e s to B in ra d n u c s h tr y ( . T S -6 e n A d 1 0 c M om ), m U e . n S ts . ; • \ ;. 'I i CONTINUATION SHEET N ln u fo c q le o a ll r e cts R .R e e g s u o la u t r o c r e y @ nr C c o .g m o m v, is a s n io d n t , h e 0 W M a B s h r i e n v g i t e o w n, e r at D : C 0 MB 2 0 O 5 f 5 fic 5 e -0 o 0 f 0 1 In , form o a r tion b y a nd e R - e m g a u il l ator to y ··~·41 Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17'" Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rrn/doc-collections/nureqs/staff/sr1022/r3D displays a curren~y valid 0MB control number. 2. DOCKET NUMBER 3. LER NUMBER 1. FACILITY NAME 181 050 SEQUENTIAL REV YEAR NUMBER NO. Perry Nuclear Power Plant Unit 1 440 □ 052 2024 003 00 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. Background: The Perry Nuclear Power Plant (PNPP) reactor coolant recirculation system [AD] is designed to provide a forced coolant flow through the core to remove heat from the fuel. The pressure containing components of the reactor coolant system (RCS) and the portions of connecting systems out to and including the isolation valves define the reactor coolant pressure boundary (RCPB). During plant life, the joint and valve interfaces can produce varying amounts of reactor coolant leakage through either normal operational wear or mechanical deterioration. Limits on RCS operational leakage are required to ensure appropriate action is taken before the integrity of the RCPB is impaired. The safety significance of leaks from the RCPB varies widely depending on the source, rate, and duration; therefore, detection of leakage in the drywell is necessary. Methods for quickly separating the identified LEAKAGE from the unidentified LEAKAGE are necessary to provide the operators quantitative information to permit them to take corrective action should a leak occur detrimental to the safety of the facility or the public. A limited amount of leakage inside the drywell is expected from auxiliary systems that cannot be made 100% leak tight. Leakage from these systems should be detected and isolated from the drywell atmosphere, if possible, so as not to mask RCS operational LEAKAGE detection. Twenty-one drywell valves, including the reactor coolant recirculation pump suction valves [AD-V], have packing leak-off lines routed to the drywell equipment drain sump [WK]. Leakage directed to the drywell equipment drain sump is considered identified leakage while leakage collected through the floor drains to the floor drain sump is unidentified. Both leakage rates display and alarm in the Control Room. Each valve packing leak-off line has a temperature transmitter [AD-TT] that provides an alarm in the Control Room on high temperature in the line. A manually operated solenoid valve [AD-TSV] can then be closed from the Control Room to isolate the line. Located in the drywell and inaccessible while at power, the leak- off lines have a manual isolation valve [AD-ISV] upstream and a sight glass [AD-FG] downstream of the solenoid valves. Technical Specifications: PNPP Technical Specification (TS) Limiting Condition for Operation (LCO) 3.4.5, "RCS Operational LEAKAGE" applies in MODES 1, 2, and 3 and requires: no pressure boundary LEAKAGE; less than or equal to 5 gpm unidentified LEAKAGE; less than or equal to 30 gpm total LEAKAGE over the previous 24 hour period; and less than or equal to 2 gpm increase in unidentified LEAKAGE within the previous 24 hour period in MODE 1. When unidentified or total leakage is not within the limits, TS 3.4.5 Action B.1 requires the leakage to be within limits in 4 hours, and Action C.1 requires verification that the unidentified LEAKAGE increase is not service sensitive austenitic material within 4 hours. If the required actions and associated completion times are not met, TS 3.4.5 Action D.1 requires the plant to be placed in MODE 3 within 12 hours, and Action D.2 requires the plant to be placed in MODE 4 within 36 hours. DESCRIPTION OF EVENT: With PNPP operating in MODE 1 and 100 percent power, the drywell unidentified rate of change high alarm was received at 0000 on May 23, 2024. The drywell floor drain sump rate indicated 7.7 gpm. Condition B of TS 3.4.5 was entered to reduce the unidentified leakage to less than or equal to 5 gpm within 4 hours and lowering reactor power to achieve MODE 3 was started, in accordance with site procedures. Subsequently, the operations crew received the valve stem leak-off temperature alarm, indicating at least one of the 21 drywell valve leak-off line temperatures were greater than or equal to180 degrees F. Four lines were identified as potential sources. Simple troubleshooting found none of the four manually operated solenoid valves functioned. At 0400 on Page iof ! | ML24198A025
LaSalle County Station | Unit 1 | Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.1.3 Completion Time Exceeded | 07-31-2024 | On April 9, 2024, while preparing for the Unit 1 traversing in-core probe (TIP) system shear valve actuating cartridge operability test to meet Technical Specification (TS) Surveillance Requirement (SR) 3.6.1.3.9, it was identified that three of the five installed shear valve squib cartridges had expired in October 2023. The Bases for SR 3.6.1.3.9 requires that the controls that limit shelf life and operating life of the explosive charge be followed, as applicable. Since the five-year expiration date was exceeded for the three identified TIP shear valves, the Bases requirements of SR 3.6.1.3.9 were not met and rendered the three TIP shear valves INOPERABLE. Due to SR 3.6.1.3.9 Bases not being met, TS Limiting Condition for Operation (LCO) 3.6.1.3 is required to be entered. The station exceeded the completion time for TS LCO 3.6.1.3; therefore, this this event is reportable as a condition prohibited by TS per 10 CFR 50.73(a)(2)(i)(B). Since three TIP shear valves were inoperable simultaneously due to the same cause, this event is also reportable per 10 CFR 50.73(a)(2)(vii) as a common cause inoperability of independent trains or channels. There was no impact to the health and safety of the public or plant personnel because all five squib cartridges were removed and tested successfully. The successful completion of the test demonstrated that the TIP shear valves with the expired squib cartridges were still capable of performing their function with the expired squib cartridges installed. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported ......... ~"( "'> lessons learned are incorporated into the licensing process and fed back to industry. Send comments f~V~' \ LICENSEE EVENT REPORT (LER) regarding burden estimate lo the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. . Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to \~...Y..✓ .i CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection http:l/www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D displays a currently valid 0MB control number. 1. FACILITY NAME (cid:127) 2. DOCKET NUMBER 3. LER NUMBER 050 SEQUENTIAL REV YEAR NUMBER NO. LaSalle County Station, Unit 1 (cid:143) 00373 052 2024 - 003 01 | Plant and System Identification LaSalle Country Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the traversing in-core probe (TIP) system. The affected components are the 1C 51- J004A/D/E TIP system shear valves. Condition Prior to Event Unit(s): 1 Date: April 9, 2024 Time: 18:30 CDT Reactor Mode(s): 1 Mode(s) Name: Power Operation Power Level: 100 percent Description On April 9, 2024, while preparing for the Unit 1 traversing in-core probe (TIP) system shear valve actuating cartridge operability test, it was identified that squib cartridges installed in three out of the five Unit 1 TIP shear valves had expired ('A', 'D', and 'E' trains). The squib cartridges have an expiration date of five years from the time the charge is packed into the firing mechanism. The five-year expiration date is based on the manufacturer's operating experience of squib charges not reliably firing after five years. The previous performance of this test on October 18, 2021, replaced and tested the squib cartridge from the 'B' train TIP shear valve while noting the other four squib cartridges were set to expire in October 2023, prior to the next performance of the test. A separate surveillance performed on January 31, 2023, replaced, and tested the squib cartridge from the 'C' train TIP shear valve. Upon identification, all applicable Technical Specification (TS) timeclocks were entered, and actions were taken to isolate the affected penetration flow path. The operability test was performed on April 10, 2024, and all five squib charges were replaced, and the removed charges were actuated successfully. The TIP shear valves were declared operable and all applicable TS timeclocks were exited. The successful completion of the test demonstrated that the TIP shear valves with the expired squib cartridges were still capable of performing their function. Cause The cause of the event is that the test surveillance did not factor in the expiration date of the squib cartridges for future surveillance test performances. Instead, an alternative tracking method was used to ensure the squib cartridges did not expire prior to the next performance of the operability test, which was ineffective. Additionally, during the last performance of the operability test, the expiration dates of the squib cartridges were not documented in the Corrective Action Program (CAP) to ensure expiration dates were not exceeded. Reportability and Safety Analysis The TIP valve assembly contains both a ball valve and a shear valve. When the TIP system is in standby, the system is retracted, and the ball valves are closed to maintain primary containment integrity. When the TIP system is operating and the detectors are in the core, the ball valve is open. In the event of a primary containment isolation signal, the TIP system is automatically withdrawn from the core and the ball valves are closed to maintain containment integrity. The shear valve is only used if a leak occurs when the TIP is beyond the ball valve and the power to the TIP system fails. The shear valve is actuated manually and can cut through and close off the tubing to preserve primary containment integrity. Therefore, both the ball valve and the shear valve are primary containment isolation valves (PCIVs) and must meet the requirements of TS Limiting Condition for Operation (LCO) 3.6.1.3, each PCIV shall be OPERABLE. | ML24213A022
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | EDG Lube Oil Check Valve Bonnet Cap Leak due to Failed Gasket | 04-30-2027 | On April 24, 2024, at 1948, with James A. FitzPatrick Nuclear Power Plant at 100% power, the “B” Emergency Diesel Generator (EDG) was being operated for surveillance testing when lube oil leaked from the bonnet cap of check valve 93EDG-57B. The leak originated when a gasket between the body-to-bonnet connection failed. The gasket was installed on October 11, 2023. The cause of the gasket failure was uneven compression during installation when the bonnet cap was over tightened and yielded the thread root. Work planning instruction and the technical evaluation did not identify a change to the metal-to-metal tightening standard when installing a gasket as a corrective action on October 11, 2023. This deficiency would have prevented the fulfillment of the “B” EDG subsystem safety function due to not meeting the lube oil inventory requirement. The other 3 EDG units were not affected by this deficiency, no gaskets were installed. This condition was prohibited by Technical Specifications (TS), which is reportable per 10 CFR 50.73(a)(2)(i)(B). In addition, during this period, when “A” EDG subsystem was inoperable for planned maintenance, both subsystems were inoperable, a condition reportable per 10 CFR 50.73(a)(2)(v)(A). The condition was corrected by replacing the check valve on April 25, 2024. A case study will be developed and shared. NRC FORM 366 (04-02-2024) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 LICENSEE EVENT REPORT (LER) hours. Reported lessons learned are incorporated into the licensing process and fed CONTINUATION SHEET back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory (See NUREG-1022, R.3 for instruction and guidance for completing this form Commission, 725 17th Street NW, Washington, DC 20503; email: http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 YEAR SEQUENTIAL REV NUMBER NO. James A. FitzPatrick Nuclear Power Plant 05000333  052 2024 – 001 – 01 | Background The Emergency Onsite Power Supply System [EIIS identifier: EK] consists of two redundant Emergency Diesel Generator (EDG) subsystems. Each EDG subsystem consists of two EDG units. The capability of the two units in the subsystem to start, force parallel, and attain rated voltage and frequency together within 10 seconds, and run the necessary engineered safeguard loads, meets the requirements for the Emergency AC Power System. The EDG lubrication system [LA] is designed to provide sufficient lubrication (lube oil) to permit proper operation by circulating the lube oil to the diesel engine working surfaces and to remove excess heat generated by friction during operation. The lube oil inventory volume required to ensure 7 days continuous operation is 168 gallons based on the manufacturer's consumption values and without reaching the recommended minimum level. In standby, the system circulates warmed oil through the EDG engines to promote successful quick starts. This is accomplished by a 5/8-inch line with a swing check valve (93EDG-57B for “B” EDG unit), which closes during EDG operation to prevent bypassing flow. The check valve has a bonnet cap to access internals for preventive maintenance. Event Description On April 24, 2024, with James A. FitzPatrick Nuclear Power Plant (JAF) at 100% power, a surveillance test was started at 1912, involving an operational test of the “B” EDG subsystem. Operators were monitoring the performance when they discovered lube oil spraying from the top of check valve 93EDG-57B. At 1948, the “B” EDG unit was declared inoperable. Operators secured the EDG as well as the circulating and turbocharger lube oil pumps. The leak originated from the bonnet cap. With the engine in standby, the leak rate was approximately 60 drops per minute (dpm). A leak rate could not be observed with the system pressurized during the event; however, it was estimated that 11.5 gallons of lube oil was lost due to the leak. The operations staff estimated that the engine was running for approximately 5 minutes with the leak before the engine was secured. Therefore, the leak rate was approximately 2.3 gallons per minute (gpm), or 138 gallons per hour (gph). The magnitude of the lube oil leak would have exhausted the lube oil supply and this deficiency would have prevented the function of “B” EDG unit to fulfill its mission time. The A, C, and D check valves did not have any similar leaking condition. The “A” EDG subsystem remained Operable and the “D” EDG unit remained available during this event. The check valve 93EDG-57B was replaced on April 25 by 1300. There was no leakage following the repair. The Post Maintenance Testing was completed satisfactory restoring the “B” EDG subsystem to Operable. Page 2 of 4 | ML24234A140
i | Unknown Unit | Emergency Diesel Generator Auto-Start and Load due to Loss of System Auxiliary Transformer 6. Evant Data 6. LER Number 7. Report Data 8. Other Facilities Involved Month Day Year Year S N eq u u m e b n e ti r a l Re N vi o s . io n Month Day Year F N a A cll ltyName (cid:143) 050 N Do A ck et Number 04 20 2024 2024 - 004 - 01 08 22 2024 N Fa A cil ity Name (cid:143) 052 D N o A ck et Number 9. Operating Mode 10. Power Laval 1 100 percent 11. This Report Is Submitted Pursuant to the Requirements of 10 CFR §: (Check all that apply) (cid:143) D D D (cid:143) 10 CFR Part 20 20.2203(a)(2)(vl) (cid:143) 10 CFR Part 60 SO. 73(a)(2)(11)(A) SO. 73(a)(2)(vlll)(A) (cid:143) 73.1200(a) D 0 D 20.2201(b) 20.2203(a)(3)(I) 50.36(c)(1)(I)(A) so. 73(a)(2)(11)(B) SO. 73(a)(2)(vlll)(B) 73.1200(b) (cid:143) 0 D D 0 D 20.2201(d) 20.2203(a)(3)(11) 50.36(c)(1)(11)(A) SO. 73(a)(2)(111) SO. 73(a)(2)(Ix)(A) 73.1200(c) (cid:143) D D D D 20.2203(a)(1) 20.2203(a)(4) 50.36(c)(2) ~ SO. 73(a)(2)(Iv)(A) SO. 73(a)(2)(x) 73.1200(d) D 20.2203(a)(2)(I) 10 CFR Part 21 D S0.46(a)(3)(11) D so. 73(a)(2)(v)(A) 10 CFR Part 73 D 73.1200(e) (cid:143) (cid:143) D D D D 20.2203(a)(2)(11) 21.2(c) 50.69(g) so. 73(a)(2)(v)(B) 73.77(a)(1) 73.1200(f) (cid:143) (cid:143) D D D 20.2203(a)(2)(111) 50. 73(a)(2)(I)(A) so. 73(a)(2)(v)(C) 73. 77(a)(2)(I) 73.1200(g) (cid:143) 0 D D D 20.2203(a)(2)(Iv) SO. 73(a)(2)(I)(B) 50.73(a)(2)(v)(D) 73. 77(a)(2)(11) 73.1200(h) (cid:143) D D 20.2203(a)(2)(v) SO. 73(a)(2)(I)(C) SO.7 3(a)(2)(vll) 0 OTHER (Specify here, in abstract, or NRG 366A). 12. Licensee Contact for this LER licensee Contact Phone Number (Include area coda) Joseph Reda, Operations Director (815) 415-2200 13. Complete One Line for each Component Failure Described In this Report Cause System Component Manufacturer Reportable to IRIS Cause System Component Manufacturer Reportable to IRIS X FK BKR W120 y X EB BKR 1005 y 14. Supplemental Report Expected Month Day Year [8J No I D Yes (If yes, complete 15. Expected Submission Dale) 16. Expected Submission Date I 16. Abstract (Limit to 1326 spaces, i.e .• approximately 13 single-spaced typewritten lines) On April 20, 2024, with LaSalle Unit 1 operating at 100 percent power and gas circuit breaker (GCB) 11-13 open to support transmission system operator testing of power line L0104 relays, oil circuit breaker (OCB) 1-13 tripped open on differential current resulting in the loss of the Unit 1 system auxiliary transformer (SAT). Bus 141 Y (Division 1) , normally supplied by the I Unit 1 SAT, failed to fast transfer to the Unit 1 unit auxiliary transformer (UAT), resulting in the Division 1 emergency diesel generator (EDG) to automatically start and load onto the 141Y bus, causing a load shed of the 141Y bus and momentary loss of power to the 141Y bus. The loss of the Unit 1 SAT also caused the Division 3 EDG to automatically start and load, as designed, onto bus 143 (Division 3). The load shed on bus 141Y caused power to be lost to the Unit 1 "A" (1A) reactor protection system (RPS) bus, resulting in a "A" RPS half-scram condition and closure of isolation valves in multiple systems. All actuations and isolations performed as designed. During the fast transfer of Division 2 from the Unit 1 SAT to UAT, the Unit 1 reactor building ventilation system (VR) 'B' supply isolation damper and "A' exhaust isolation damper went shut unexpectedly causing a loss of Unit 1 VR. These events are reportable in accordance with 10 CFR 50.7 3(a)(2)(iv)(A). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) r ......, Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments f:I.J.i LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to i~..... / CONTINUATION SHEET lnfocollec1S.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 72517th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection http://www. nrc.g o v/readinq-rm/doc-col leclions/nuregs/staff/sr1 022/r3Q displays a currently valid 0MB control number. 1. FACILITY NAME (cid:127) 2. DOCKET NUMBER 3. LER NUMBER 050 SEQUENTIAL REV YEAR NUMBER NO. LaSalle County Station, Unit 1 (cid:143) 00373 052 2024 - 004 01 NARRATIVE Plant and System Identification LaSalle Country Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the alternating current (AC) power system. The affected component is 345 kV oil circuit breaker (OCB) 1-13, the mechanism operated contacts (MOC) 15 and 16 of air circuit breaker (ACB) 1412, and the TSC switch contacts on ACB 1415. Condition Prior to Event Unit(s): 1 Date: April 20, 2024 Time: 07:04 CDT Reactor Mode( s): 1 Mode(s) Name: Power Operation Power Level: 100 percent Description Emergency Diesel Generator (EOG) Actuation and Load On April 20, 2024, with gas service breaker (GCB) 11-13 open to support transmission system operator (TSO) testing of power line L0104 relays, OCB 1-13 tripped open on differential current resulting in the loss of the Unit 1 system auxiliary transformer (SAT). Bus 141Y (engineered safety feature (ESF) Division 1), which is normally supplied by the Unit 1 SAT, failed to fast transfer to the Unit 1 unit auxiliary transformer (UAT), resulting in the Division 1 EOG to automatically start and load onto the 141Y bus, causing a load shed of the 141Y bus and a momentary loss of power to the 141Y bus. The loss of the Unit 1 SAT also caused the Division 3 EOG to automatically start and load, as designed, onto bus 143 (ESF Division 3), which is normally supplied by the Unit 1 SAT. Bus 142Y (ESF Division 2) fast transferred to the Unit 1 UAT, as expected, resulting in no requirement for the Division 2 EOG to automatically start. The automatic starting of the Division 1 and Division 3 EDGs is considered a valid actuation due to the loss of power to ESF buses. During the fast transfer of ESF Division 2 from the Unit 1 SAT to UAT, the Unit 1 reactor building ventilation system (VR) 'B' supply isolation damper and "A' exhaust isolation damper went shut unexpectedly causing a loss of Unit 1 VR. This resulted in a main steam tunnel high temperature condition which was bypassed per station procedure. The dampers were reopened, and Unit 1 VR was restored. Reactor Protection System (RPS) Unit 1 "A" Half-Scram As a result of the load shed on bus 141Y, power was lost to the Unit 1 "A" (1A) RPS bus, resulting in a "A" RPS half-scram condition and closure of isolation valves in multiple systems. The condition was considered an invalid actuation because it was the result of losing power to the bus and not the result of a valid input signal to the RPS or intentional manual action. All actuations and isolations performed as designed. The loss of the 1A RPS bus resulted in isolations of the reactor water cleanup system, main steam line drains, reactor coolant system sampling, instrument nitrogen system, reactor recirculation hydraulic power units, and containment monitoring system. The loss of the 1A RPS bus also resulted in the loss of power to portions of the average power range monitor, local power range monitor, oscillation power range monitor, and control rod block systems; as well as portions of the radiation monitoring for the main steam lines, reactor building vent, and fuel pool vent. Appropriate actuations and primary containment isolations occurred as designed. After the loss of power to the 1A RPS bus, the applicable Technical Specification (TS) timeclocks and actions were entered. Power was restored to the 1A bus by transferring the bus to the alternate power supply in accordance with plant NRC FORM 366A (04-02-2024) Page_2_ of _s_ NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and lnfonnation Collections Branch (T-6A10M), U.S. Nuclear Regulatory Commission, Washington, DC 2055!>-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of lnfonnation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of infonnation unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-colleclions/nuregs/stafflsr1022/r3D displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER (cid:127) 050 SEQUENTIAL REV YEAR NUMBER NO. LaSalle County Station, Unit 1 (cid:143) 052 00373 2024 - 004 - 01 NARRATIVE procedures. The half-scram and isolations were reset, and the equipment was returned to operable status. All applicable TS timeclocks and actions were exited. Cause EOG Actuation and Load The root cause of OCB 1-13 tripping open was an absence of procedural guidance requiring the switchyard owner to provide the details of their modification testing plan, including work instructions, and the required performance of a quality station review of testing plan / work instructions. Causal factors that were identified with the root cause are the following: 1. Placement of dispatched grounds by the switchyard owner with the presence of induced voltage on power line L0104. 2. Failure of LaSalle County Station personnel to recognize the possibility of induced voltage being present on the out-of-service 345 kV power line L0104 after switching, caused by the in-service 345 kV power line L0103 that runs parallel with power line L0104, flowing to ground via the bus 13-dispatched ground when GCB 11-13 was moved to the closed position. Contributing causes to the event that were identified in the root cause are the following: 1. The TSC switch for ACB 1415 was not closed as expected. 2. Failure to follow the maintenance strategy template recommendation to verify contact resistance or cycle the MOC switch on a regular interval. Troubleshooting determined the cause of the fast transfer failure of bus 141 Y from the Unit 1 SAT to the Unit 1 UAT was increased resistance across MOC 15 and 16 of ACB 1412, and the TSC switch contacts were open on ACB 1415, Unit 1 UAT feed breaker to bus 141Y, even though they were verified to be closed the last time the breaker was racked in during refueling outage L 1R 20 earlier in 2024. RPS Unit 1A Half-Scram The cause of the RPS Unit 1A loss of power and half scram was the momentary loss of power from the 141Y bus due to the load shed caused by the fast transfer failure. The loss of power from the 141 Y bus resulted in a loss of power to the 1A RPS motor-generator set that normally powers the 1A RPS. Reportability and Safety Analysis EOG Actuation and Load The loss of the Unit 1 SAT and actuation of the Division 1 and Division 3 emergency diesel generators was initially reported as an 8-hour notification (ENS 57083) in accordance with 10 CFR 50. 72(b)(3)(iv)(A) for a valid actuation of the emergency AC electrical power systems. This event is also required to be reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that results in the valid actuation of the emergency AC electrical power systems. NRC FORM 366A (04-02-2024) Page_3_ of _s_ NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2,0,2,4,) /1.¥.....~... Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments s i LICENSEE EVENT REPORT (LER) N re u g c a l r e d a in r g b R ur e d g e u n l a e to s r ti y m ate C o to m t m he is s F i O on IA , , Li W bra a r s y h , in a g n t d o n ln , fonn D a C t ion 2 C 0 o 5 l 5 le 5 c - t 0 io 0 n 0 s 1 , B ran o c r h (T b - y 6 A10 em M a ). i l U.S to . \ ... ..... ,r- J CONTINUATION SHEET lnfocollecls.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of lnfonnation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, OC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of infonnation unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D displays a currently valid 0MB control number. 1. FACILITY NAME (cid:127) 2. DOCKET NUMBER 3. LER NUMBER 050 SEQUENTIAL REV YEAR NUMBER NO. LaSalle County Station, Unit 1 (cid:143) 00373 052 2024 - 004 01 NARRATIVE RPS Unit 1A Half-Scram The loss of the Unit 1A RPS bus and associated RPS actuation is considered an invalid actuation because it was not the result of a valid signal and not an intentional manual action. The loss of the RPS bus resulted in general containment isolation signals that actuated containment isolation valves in more than one system or multiple main steam isolation valves while the unit was critical. Therefore, the loss of the RPS bus is reportable in accordance with 10 CFR 50. 73(a)(2)(iv)(A). Safety System Functional Failure Review The system equipment responses do not result in a safety system functional failure (SSFF) as defined in accordance with NEI 99-02, "Regulatory Assessment Performance Indicator Guideline." The EOG and RPS safety systems performed their as-designed safety functions. Corrective Actions Corrective actions taken in response to the conditions were: • Entered the required TS timeclocks and actions and notified the TSO to secure all testing. • Transferred the 1A RPS bus to the alternate power supply, reset the half-scram, and exited applicable TS timeclocks and actions. • Closed OCB 1-13 and reenergized the Unit 1 SAT • Transferred buses 141Y, 142Y, and 143 to the Unit 1 SAT; shutdown the Division 1 and Division 3 EDGs; and exited applicable TS timeclocks and actions. • Transferred the 1A RPS bus back to the normal power supply. • Racked out and then racked in ACB 1415 to close the TSC switch contacts. • Cleaned MOC 15 and 16 on ACB 1412 to decrease the resistance back to acceptable levels. • Develop electrical maintenance procedure to check all 4 kV and 6 kV switchgear breaker contacts to confirm alignment for fast transfer logic. • Update the normal startup procedure to incorporate new electrical maintenance procedure during bus alignment. • Revise the Switchyard Services Agreement procedure to add guidance for the station to perform a quality review for all modification testing instructions when modifications and testing are to be performed in the switchyard. • Update 4 kV and 6 kV breaker inspection and operational test procedures to include preventative maintenance strategies for either verifying resistances or burnishing MOC switch contacts. • Prioritize and expedite the engineering change for the removal of TSC switches. • Remove and send the TSC switch on ACB 1415 for failure analysis. Previous Occurrences There have been no previous occurrences of an EOG actuation in the past 3 years. There have been two occurrences of RPS half-scrams in the past 3 years that were attributed to a loss of power. Unit 1 LER 373-2024-002-00 On March 25, 2024, LaSalle Unit 1 was operating at 100 percent power, when the 1B RPS MG set electric power monitoring assembly (EPMA) output breaker tripped due to an underfrequency condition, which resulted in the loss of the 18 RPS bus. The loss of power to this bus created a half-scram condition and initiated closure of isolation valves in NRG FORM 366A (04-02-2024) Page_4_ of _5_ NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) ,,.,.,..-..., Estimated burden per response to comply with this mandatory colection request 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to indusby. Send comments ;~·) LICENSEE EVENT REPORT (LER) regaiding burden estimate to the FOIA, Library, and lnfonnation Collections Branch (T-6A10M), U.S. Nuclear Regulatory Commission, Washinglon, DC 20555-0001, or by email to \~ ..... / CONTINUATION SHEET lnfoco!ecls.Resoun;e@nrc.gov, and the 0MB reviewer at: 0MB Office of lnfonnation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of infonnation unless the document requesting or requiring the collection http :l/www.nrc.gov/readinq-rm/doc-collections/nuregs/staff/ sr1 022/r3D displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER (cid:127) 050 SEQUENTIAL REV YEAR NUMBER NO. LaSalle County Station, Unit 1 (cid:143) 052 00373 2024 - 004 - 01 NARRATIVE multiple systems. The condition was an invalid actuation because it was not the result of actual plant conditions and not an intentional manual action. The cause of the MG set EPMA output breaker trip was the EPMA trip card for the output breaker being out of range high for the underfrequency setpoint which caused the trip on underfrequency. As a result, the EPMA trip card was replaced, and the system was restored back to its original configuration. Unit 2 LER 374-2021-002-00 On May 31, 2021, LaSalle Unit 2 was operating at 100 percent power, when the 2A RPS motor generator (MG) set output breaker tripped due to an overload condition, which resulted in a loss of 2A RPS bus. Loss of power to this bus created a half-scram and initiated closure of outboard isolation valves in multiple systems. The condition was an invalid actuation because it was not the result of actual plant conditions and not an intentional manual action. The cause of the issue was a degraded voltage adjustment potentiometer (device 1P ) on the 2A RPS MG set, which was causing intermittent resistance readings. The intermittent resistance caused the output voltage of the RPS MG set to fluctuate. As a result, the degraded potentiometer and the voltage regulator were replaced as part of the trouble-shooting efforts, and the system was restored back to its original configuration. Component Failure Data Manufacturer: Westinghouse Electric Company Device: Oil Circuit Breaker, 345 kV Component ID: 0SYOCB1-13, 345 kV Oil Circuit Breaker 1-13 Manufacturer: ITE Circuit Breaker Limited Device: Air Circuit Breaker, 4160 V Component ID: ACB 1412 Bus Feed from SAT 1AP91E (TR 142) Manufacturer: ITE Circuit Breaker Limited Device: Air Circuit Breaker, 4160 V Component ID: ACB 1415 1AP04E / 1AP03E (141Y / 141X) Bus Tie NRC FORM 366A (04-02-2024) Page _L_ of _L_ NRC FORM 366 U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150--0104 EXPIRES: 04/30/2027 (04-02-2024) ............. Estimnd b..-den per response to compi'( will 11~ mandatory collection request 80 ho .... Reportsd lessons !¥1~ LICENSEE EVENT REPORT (LER) lea-nod are inCOIJ)orated i11D the licensing process aid fed bacl< ID industy. Send comments ragning burden estimate ID the FO/A, Librmy, and Information Collections Btaich (T-8 A10M), U. S. Nuclea- Regulatory \. ..... I Commissioo, Washington, DC 20555-0001, or by email to lnfocolleets.Resource@rve.gov, aid Ile OM:I revie- (See Page 2 for required number of digits/characters for each block) at OMS 01llee of Information and Regulaay Affais, (3150-0104), Attn: Desi< Offie" to, the Nuelea-Regulatory (See NUREG-1022, R.3 for instruction and guidance for completing this fom, Commissioo, 725 171h Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person Is httI;r/lwww .nrc.gov/reading-rm/doc-collections/n uregs/staff/ sr1 022/r3D not requred ID respond ID, a coleetion of information unless Ile document requesting or requring the collection displays a e11Tenli'( vale! 0MB contol num~. 1. Facility Name ~ 050 2. Docket Number 3.Page LaSalle County Station, Unit 2 (cid:143) 00374 1 OF 3 052 4. Title Air Circuit Breaker (ACB) Mechanically Operated Contacts (MOC) switch failed to actuate | 08-22-2024 | On April 20, 2024, with LaSalle Unit 1 operating at 100 percent power and gas circuit breaker (GCB) 11-13 open to support transmission system operator testing of power line L0104 relays, oil circuit breaker (OCB) 1-13 tripped open on differential current resulting in the loss of the Unit 1 system auxiliary transformer (SAT). Bus 141 Y (Division 1) , normally supplied by the I Unit 1 SAT, failed to fast transfer to the Unit 1 unit auxiliary transformer (UAT), resulting in the Division 1 emergency diesel generator (EDG) to automatically start and load onto the 141Y bus, causing a load shed of the 141Y bus and momentary loss of power to the 141Y bus. The loss of the Unit 1 SAT also caused the Division 3 EDG to automatically start and load, as designed, onto bus 143 (Division 3). The load shed on bus 141Y caused power to be lost to the Unit 1 "A" (1A) reactor protection system (RPS) bus, resulting in a "A" RPS half-scram condition and closure of isolation valves in multiple systems. All actuations and isolations performed as designed. During the fast transfer of Division 2 from the Unit 1 SAT to UAT, the Unit 1 reactor building ventilation system (VR) 'B' supply isolation damper and "A' exhaust isolation damper went shut unexpectedly causing a loss of Unit 1 VR. These events are reportable in accordance with 10 CFR 50.7 3(a)(2)(iv)(A). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) r ......, Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments f:I.J.i LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to i~..... / CONTINUATION SHEET lnfocollec1S.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 72517th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection http://www. nrc.g o v/readinq-rm/doc-col leclions/nuregs/staff/sr1 022/r3Q displays a currently valid 0MB control number. 1. FACILITY NAME (cid:127) 2. DOCKET NUMBER 3. LER NUMBER 050 SEQUENTIAL REV YEAR NUMBER NO. LaSalle County Station, Unit 1 (cid:143) 00373 052 2024 - 004 01 | Plant and System Identification LaSalle Country Station Unit 1 is a General Electric Boiling Water Reactor with 3546 Megawatts Thermal Rated Core Power. The affected system was the alternating current (AC) power system. The affected component is 345 kV oil circuit breaker (OCB) 1-13, the mechanism operated contacts (MOC) 15 and 16 of air circuit breaker (ACB) 1412, and the TSC switch contacts on ACB 1415. Condition Prior to Event Unit(s): 1 Date: April 20, 2024 Time: 07:04 CDT Reactor Mode( s): 1 Mode(s) Name: Power Operation Power Level: 100 percent Description Emergency Diesel Generator (EOG) Actuation and Load On April 20, 2024, with gas service breaker (GCB) 11-13 open to support transmission system operator (TSO) testing of power line L0104 relays, OCB 1-13 tripped open on differential current resulting in the loss of the Unit 1 system auxiliary transformer (SAT). Bus 141Y (engineered safety feature (ESF) Division 1), which is normally supplied by the Unit 1 SAT, failed to fast transfer to the Unit 1 unit auxiliary transformer (UAT), resulting in the Division 1 EOG to automatically start and load onto the 141Y bus, causing a load shed of the 141Y bus and a momentary loss of power to the 141Y bus. The loss of the Unit 1 SAT also caused the Division 3 EOG to automatically start and load, as designed, onto bus 143 (ESF Division 3), which is normally supplied by the Unit 1 SAT. Bus 142Y (ESF Division 2) fast transferred to the Unit 1 UAT, as expected, resulting in no requirement for the Division 2 EOG to automatically start. The automatic starting of the Division 1 and Division 3 EDGs is considered a valid actuation due to the loss of power to ESF buses. During the fast transfer of ESF Division 2 from the Unit 1 SAT to UAT, the Unit 1 reactor building ventilation system (VR) 'B' supply isolation damper and "A' exhaust isolation damper went shut unexpectedly causing a loss of Unit 1 VR. This resulted in a main steam tunnel high temperature condition which was bypassed per station procedure. The dampers were reopened, and Unit 1 VR was restored. Reactor Protection System (RPS) Unit 1 "A" Half-Scram As a result of the load shed on bus 141Y, power was lost to the Unit 1 "A" (1A) RPS bus, resulting in a "A" RPS half-scram condition and closure of isolation valves in multiple systems. The condition was considered an invalid actuation because it was the result of losing power to the bus and not the result of a valid input signal to the RPS or intentional manual action. All actuations and isolations performed as designed. The loss of the 1A RPS bus resulted in isolations of the reactor water cleanup system, main steam line drains, reactor coolant system sampling, instrument nitrogen system, reactor recirculation hydraulic power units, and containment monitoring system. The loss of the 1A RPS bus also resulted in the loss of power to portions of the average power range monitor, local power range monitor, oscillation power range monitor, and control rod block systems; as well as portions of the radiation monitoring for the main steam lines, reactor building vent, and fuel pool vent. Appropriate actuations and primary containment isolations occurred as designed. After the loss of power to the 1A RPS bus, the applicable Technical Specification (TS) timeclocks and actions were entered. Power was restored to the 1A bus by transferring the bus to the alternate power supply in accordance with plant | ML24235A178
Grand Gulf Nuclear Station | Unit 1 | Feedwater Inlet Check Valve Incorrectly Determined Operable | 04-30-2027 | On April 2, 2022, at 0301 CT, while the plant was in MODE 4 with all control rods inserted during a refuel outage, Grand Gulf Nuclear Station identified a failed post work leakage rate test of Feedwater Inlet Check Valve, 1 B21 F032B. An operability evaluation of the valve was performed, and the valve was inappropriately determined to be operable. The valve was returned to service, and the plant returned to MODE 1 at the end of the refuel outage. On June 27, 2024, NRC inspectors identified a Green finding and associated Non-Cited Violation of Technical Specification 3.6.1.3, "Primary Containment Isolation Valves" (PCIV) for failure to ensure each PCIV was operable. Valve 1 B21 F032B failed the leakage rate test due to degradation and wear of the valve seat. The operator failed to properly evaluate the operability due to a lack of understanding of the Primary Containment Leakage Rate Testing (Appendix J) program requirements. There was no impact on the health and safety of the public or reactor safety. The feedwater isolation shutoff valve 1B 21 F065B would have maintained leakage rates for the containment penetration; therefore, there was no significant risk to containment integrity. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 0 4 / 3 0 / 2 0 2 7 (04-02-2,0.2.4.). ,;\ Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) !~, regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S \~/ Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail lo ···-· CONTINUATION SHEET lnlocollects Resource@nrc gov, and the 0MB reviewer al: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer lor the Nuclear Regulatory Commission, 725 17th Street NW. (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRG may not conduct or sponsor, and a person is not required to respond https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r;m to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER 181 050 YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 NUMBER NO. 416 0 052 2024 003 00 | Plant Conditions: At the time of the event, Grand Gulf Nuclear Station was in MODE 4 (Cold Shutdown) with all control rods inserted at zero percent reactor power. The station was performing a post-work leakage rate test on Feedwater Inlet Check Valve 1821F032B. Description of Event: On April 2, 2022, during the performance of the post work leakage rate test of the Feedwater Inlet Check Valve 1821 F032B, a failing leakage rate of 7650 milliliters per minute was observed. A Condition Report was issued per procedure, and an operability evaluation was performed using the past operability, the technical specification surveillance requirement, and the Primary Containment Leakage Rate Testing (Appendix J) program requirements. An incorrect assumption about the Appendix J requirements was made, and it was determined that the identified leakage was within the allowable leakage rate based on the surveillance requirements. The operability evaluation incorrectly determined that Feedwater Inlet Check Valve 1821 F032B, was operable, and the valve remained in service for the 24- month fuel cycle. On June 27, 2024, as part of the Biennial Problem Identification and Resolution Inspection Report 05000416/2024010, the NRC inspectors identified a Green finding and associated Non-Cited Violation of Technical Specification (TS) 3.6.1.3, "Primary Containment Isolation Valves" (PCIV) for failure to ensure each PCIV was operable following a failed leakage rate test of 1821 F032B during a refueling outage. A violation of TS 3.0.4 was also identified for making a mode change without meeting the requirements to do so as a result of not meeting TS 3.6.1.3. Reportability: This report is made in accordance with 10 CFR 50.73(a)(2)(i)(B) for an operation of condition which was prohibited by the plant's Technical Specifications. TS LCO 3.6.1.3 requires each PCIV to be OPERABLE. Due to incorrect operability evaluation, Required Actions C and E were not taken. Cause(s): The direct cause of the event was degradation and wear of the valve's seat which resulted in the failed leakage rate test. An additional cause of insufficient knowledge of the Appendix J program requirements by the Senior Reactor Operators (SROs) was also identified as the cause of the incorrectly performed operability evaluation. Corrective Actions: Completed Actions: Repairs to the valve seat were made during 2024 refuel outage. Post-work leak rate testing was completed satisfactorily and indicated a leak rate of zero millimeters per minute. Planned Actions: Update Operability Training for SROs with a focus on Code testing requirements. Safety Significance: There was no impact on the health and safety of the public or reactor safety. The feedwater isolation shutoff valve 1821 F065B would have maintained leakage rates for the containment penetration; therefore, there was no significant risk to containment integrity. Previous Similar Events: LEA 2023-001-01 Valve Closure Test Failure Resulting in Condition Prohibited by Technical Specification LER 2021-001-01 Primary Containment Outer Airlock Door Inoperable Due To Unacceptable Leak Rate NRG FORM 366A (04-02-2024) Page 2 of 2 | ML24239A788
i | Unknown Unit | Manual Reactor Scram Due to Degraded Main Condenser Vacuum | 08-26-2024 | due to degrading Main Condenser vacuum caused by a failed turbine bearing waste water and oil (slop) drain. The event was reported by Event Notification 56846 in accordance with 10 CFR 50. 72(b )(2)(iv)(B) and 10 CFR 50.7 2(b) (3)(iv)(A). This event is also reportable in accordance with 10 CFR 50. 73(a)(2)(iv)(A) as an event that resulted in a manual actuation of the Reactor Protection System (including a reactor scram). Failure of the slop drain was caused by vibration/cyclic fatigue-induced failure of the socket weld on the 1.5" pipe to the 3" x 1.5" pipe reducer inside the Main Condenser. Key corrective action included plugging and welding the failed slop drain and reducing the length of the resulting pipe stub. There were no actual consequences to the health and safety of the public as a result of this event. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www. n re.gov /reading-rm/doc-collection sin u regs/staff/ sr1 022/r3/} displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 r:YE:A:RJ SEQUENTIAL REV Susquehanna Steam Electric Station Unit 1 I 00387 I ~-I NUMBER 1- NO 0 . □ 052 004 | CONDITIONS PRIOR TO EVENT Unit 1 - Mode 1, approximately 100% Rated Thermal Power (RTP) Unit 2 -Mode 1, approximately 100% RTP Vacuum rapidly degraded on the Susquehanna Steam Electric Station (SSES) Unit 1 Main Condenser, which resulted in the need for a manual reactor scram. EVENT DESCRIPTION On November 10, 2023, SSES Unit 1 was manually scrammed due to degraded Main Condenser [EIIS System Code/ Component Code: SG/COND] vacuum caused by a failed turbine bearing waste water and oil (slop) drain [EIIS System Code/Component Code: TF/DRN]. The following is a timeline of significant events associated with the scram: November 10, 2023, at approximately 01 :06 - Unit 1 Main Condenser vacuum was rapidly degrading along with indication of high offgas flow. A Recirculation Limiter 2 runback was inserted to lower reactor power. Main Condenser vacuum continued to degrade following the reduction in reactor power to approximately 70%. November 10, 2023, at approximately 01: 18 -A manual scram was inserted when Main Condenser vacuum reached 6 inches of mercury absolute. Plant response to the scram was per design, Reactor Protection System (RPS) [EIIS System Code: JC] channels all tripped and maintained the scram signal for the required 10 second period. Reactor Water Level lowered to -25" following the scram. Reactor Water Level 3 (+13 inch) containment isolation system signals were received and went to completion. The feedwater system [EIIS System Code: SJ] remained in service as the primary Reactor Pressure Vessel (EIIS System Code/Component Code: AC/RPV] water level control system. There were no Emergency Diesel Generator [EIIS System Code/Component Code: EK/DG] starts or Safety Relief Valve [EIIS System Code/ Component Code: SB/RV] actuations during the event. The event was reported by Event Notification 56846 in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3) (iv)(A). This event is also reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a manual actuation of the RPS (including a reactor scram). CAUSE OF EVENT Failure of the slop drain was caused by vibration/cyclic fatigue-induced failure of the socket weld on the 1.5" pipe to the 3" x 1.5" pipe reducer inside the Main Condenser. This failure was due to the original slop drain capping and piping removal modification in 2002 not being performed in accordance with the associated engineering change. In addition to the slop drain piping, pipe supports that were intended to support the remaining piping were erroneously removed. This allowed a remaining vertically suspended 1.5" diameter pipe stub of approximately 40 inches to vibrate, which eventually caused the weld failure. ANALYSIS/SAFETY SIGNIFICANCE The actual consequences from the drain leaking air into the Unit 1 Main Condenser were degraded Unit 1 Main Condenser vacuum, a forced down power, and subsequent manual scram. Without prompt operator action, an automatic scram would have been initiated. Additionally, High Pressure Coolant Injection (EIIS System Code: BJ) System and Reactor Core Isolation Cooling (EIIS System Code: BN) System could have initiated which would require initiating support systems as well as adding additional heat to the suppression pool. This would have necessitated using the Residual Heat Removal (EIIS System Code: BJ) System in Suppression Pool Cooling mode to transfer the suppression pool heat to the spray pond. NRG FORM 366A (04-02-2024) Page 2 of 3 | ML24239A847
Byron Station | Unit 1 | Both Trains of Control Room Ventilation Temperature Control System Inoperable | 09-05-2024 | At 1440 CDT on July 7, 2024, the OA and OB trains of the Control Room Ventilation (VC) Temperature Control System were simultaneously inoperable resulting in a condition that could have prevented the fulfillment of a safety function and was reported as an eight-hour, non-emergency notification per 10 CFR 50. 72(b)(3)(v)(D) under ENS 57211 to the NRC. OB Control Room Ventilation (VC) Temperature Control system was restored to operable status at 1634 CDT on 7/7/2024. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA. Library. and Information Collections Branch (T-6 A1 O M). U. S. Nuclear Regulatory Commission. Washington. DC 20555-0001. or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs. (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW. Washington. DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER (cid:127) 050 SEQUENTIAL REV YEAR NUMBER NO. Byron Station, Unit 1 05000454 (cid:143) 052 2024 - 001 00 | A. Plant Operating Conditions Before the Event: Event Date: July 7, 2024 Unit 1 - Mode 1 - Power Operations, Reactor Power 100 percent Unit 2 - Mode 1 - Power Operations, Reactor Power 100 percent Reactor Coolant System (RCS)[AB]: Normal Operating Temperature and Pressure No structures, systems, or components were inoperable at the start of this event that contributed to the event. B. Description of the Event: At 1310 CDT on 7/ 7 /24 the auxiliary building equipment operator (EO) noted the DA Control Room Ventilation (VC) Temperature Control System chiller oil level had dropped from a previous rounds reading of 37 percent to 15 percent. The EO notified the main control room and the operations field supervisor was dispatched to review the condition. The shift manager notified maintenance to request support to add oil to the DA VC chiller. At 1355 CDT, a briefing was held in the control room to perform the crosstie of the service building (VS) chilled water system to the 0A VC chilled water system per procedure BOP VC-20. At 1404 CDT, while the briefing was in progress, the auxiliary building EO notified the main control room that the oil level in the DA VC chiller had further decreased to 0 percent in the sight glass, but that oil was still visible with foam present. Following the briefing, two equipment operators obtained keys to unlock the individual valves needed to perform the crosstie. At approximately 1435 CDT, the operations field supervisor notified the main control room that the oil level in the DA VC chilled water system was no longer visible in the sight glass. At 1440 the DA VC chiller was secured and declared inoperable by Operations and the equipment operators began to perform the procedure steps to establish the VC to VS chilled water crosstie. While attempting to crosstie 0A VC train to the service building (VS) chilled water system, the equipment operators incorrectly operated valves on the OB VC chiller train. This caused the OB VC chiller train to become inoperable. With both trains of control room chillers inoperable, Unit 1 and Unit 2 entered TS 3.7.11 Condition D. Operations personnel returned to the field at 16:34 CDT on 7/7/24 and restored the valve lineup for the OB VC chiller returning the OB VC chiller to operable and exiting Condition D of TS 3.7.11. This event was determined to be a loss of safety function for the control room chilled water system and an 8-hour ENS (57211) was made to the NRC per 10 CFR 50.72(b)(3)(v)(D) at 22:12 CDT on 7/7/24. C. Causes of Event: The root cause of this event was determined to be an inadequate brief performed by the Operations SRO with the Reactor Operator and Equipment Operators. During the brief, the SRO supervisor did not clearly establish that each operator understood their role in the crosstie activity or utilize station prints to clearly establish the intended plant manipulations. As a result, the equipment operators manipulated incorrect valves while establishing the crosstie which resulted in both trains of VC Temperature Control System being declared inoperable. Contributing causes to the event were a lack of system knowledge and experience combined with less than adequate procedural guidance. The equipment operators performing the crosstie did not fully understand the flow path that needed to be established. Additionally, training provided in 2018 when the VS to VC crosstie | ML24249A074
Peach Bottom Atomic Power Station | Unit 2 | Automatic Reactor Scram Following Main Turbine Trip due to Degraded Condenser Vacuum | 09-05-2024 | While conducting power ascension following a maintenance outage, Peach Bottom Unit 2 began experiencing increasing condensate pump discharge chlorides because of a condenser tube leak. A condenser water box was isolated to facilitate repairs, but due to high river temperatures combined with elevated offgas inleakage, the water box isolation resulted in degrading condenser vacuum. Attempts to restore vacuum were unsuccessful and ultimately required a trip of the main turbine. Because the Reactor Protection System (RPS) input for Turbine Stop Valve (TSV) and Turbine Control Valve fast (TCV) closure was armed, the turbine valve closure generated a scram signal. Group II and III Primary Containment Isolation Valves isolated because reactor water level reached the isolation setpoint. Reactor water level was maintained with feedwater and pressure was maintained with bypass valves. The scram occurred without complication and all systems responded as expected. Unit 3 was not impacted by this event. This event is reportable under 10CFR50.73(a)(2)(iv)(A) due to manual or automatic isolation of systems listed in 10CFR50.73(a)(2)(iv)(B) including RPS and containment isolation signals. An ENS notification was made within 4 hours of the event, reference ENS 57221. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 SEQUENTIAL REV YEAR NUMBER NO. Peach Bottom Atomic Power Station, Unit 2 00277  052 2024 - 003 - 00 | Plant Operating Conditions Before the Event Prior to the event, on July 10, 2024, Peach Bottom Unit 2 was in Mode 1 conducting power ascension following a maintenance outage. It was identified that condensate pump discharge chloride conductivity was increasing, indicative of a condenser (EIIS: SG) tube leak. To facilitate investigation and repair of leaking tubes, a condenser waterbox was isolated with the reactor at approximately 62% power. Waterbox isolation combined with seasonally high river temperatures and elevated offgas (EIIS: WF) inleakage from a degraded valve in the offgas system resulted in degrading condenser vacuum. Although the waterbox was returned to service, condenser vacuum continued to degrade. The operating crew reduced power per station procedures, but condenser vacuum reached the threshold requiring a manual trip of the main turbine (EIIS: TA). Event Description The turbine was manually tripped on July 10, 2024 at 07:28 with the reactor at 25.6% power, which is within the physical capability of bypass valves (EIIS: SO). This is below the power level at which the Reactor Protection System (RPS) input for Turbine Stop Valve (TSV) and Turbine Control Valve (TCV) fast closure (EIIS: TA) is required to be armed per Technical Specifications, but due to conservative instrument setpoints, the input was still armed and the closure of the valves generated a scram signal. The scram occurred without complication. The Reactor Pressure Vessel (RPV) low level setpoint was reached, resulting in isolation of Group II and III Primary Containment Isolation System (PCIS) (EIIS: JM) valves as expected. Water level in the RPV was restored and maintained with Feedwater (EIIS: SJ) and pressure was maintained with bypass valves. This event is reportable under 10CFR50.73(a)(2)(iv)(A) due to manual or automatic isolation of systems listed in 10CFR50.73(a)(2)(iv)(B) including RPS and containment isolation signals. An ENS notification was made within 4 hours of the event, reference ENS 57221. Safety Consequences The reactor Scram occurred as designed and resulted in no safety consequences. All safety systems responded as expected. Use of emergency core cooling systems for level and pressure control was not required. Unit 3 was not impacted by this event. Cause and Corrective Actions The cause of the scram was RPS input from TSV and TCV fast closure due to a manual trip of the Main turbine. Procedures directed tripping the turbine if steam flow was within bypass valve capability but did not warn that the RPS logic may be armed. Actions have been taken to revise procedures from tripping the turbine “if within bypass valve capability” to “if it is known that the Main TCV/TSV closure is bypassed on A or B RPS”. Additionally, the cause of the degraded condenser vacuum condition was investigated. The root cause of this condition is that the station did not recognize and evaluate the cumulative effect of increased offgas air inleakage and isolation of a condenser waterbox with high river temperatures, culminating in a rapid lowering of main condenser vacuum. As a contributor, station models were unable to accurately predict the impact of elevated offgas inleakage on condenser performance. The corrective actions focus on enhancing the station governance for isolating a waterbox. | ML24249A109
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Reactor Protection System Electric Power Monitoring System Trip Caused Primary Containment Isolation | 09-04-2024 | On July 8, 2024, at 1927, James A. FitzPatrick Nuclear Power Plant (JAF) received annunciators and indication of a half-scram on the “B” side Reactor Protection System (RPS). The cause was determined to be an overvoltage condition that tripped the Electrical Protection Assembly (EPA) for the “B” RPS Motor Generator (MG) Set. This event caused invalid primary containment isolation signals in multiple systems, reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). The investigation into the cause of the event is ongoing. A supplement to this report will be submitted when the investigation is complete. NRC FORM 366 (04-02-2024) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 LICENSEE EVENT REPORT (LER) hours. Reported lessons learned are incorporated into the licensing process and fed CONTINUATION SHEET back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory (See NUREG-1022, R.3 for instruction and guidance for completing this form Commission, 725 17th Street NW, Washington, DC 20503; email: http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 YEAR SEQUENTIAL REV NUMBER NO. James A. FitzPatrick Nuclear Power Plant 05000333  052 2024 – 002 – 00 | Background Reactor Protection System (RPS) [EIIS: JE] Electric Power Monitoring System is provided to isolate the RPS bus from the motor generator (MG) set or an alternate power supply in the event of overvoltage, undervoltage, or underfrequency. This system protects the loads connected to the RPS bus against unacceptable voltage and frequency conditions and forms an important part of the primary success path of the essential safety circuits. Some of the essential equipment powered from the RPS buses includes the RPS logic, scram pilot valve solenoids, and various valve isolation logic. RPS electric power monitoring assembly will detect any abnormal high or low voltage or low frequency condition in the outputs of the two MG sets or the alternate power supply and will de-energize its respective RPS bus, thereby causing all safety functions normally powered by this bus to de-energize. (Safety functions powered by the RPS buses deenergize to actuate.) Two redundant Class IE circuit breakers are connected in series between each RPS bus and its MG set, and between each RPS bus and its alternate power supply. Each of these circuit breakers has an associated independent set of Class IE overvoltage, undervoltage, and under frequency sensing logic. Together, a circuit breaker and its sensing logic constitute an electric power monitoring assembly. If the output of the inservice MG set or alternate power supply exceeds predetermined limits of overvoltage, undervoltage, or underfrequency, a trip coil driven by this logic circuitry opens the circuit breaker, which removes the associated power supply from service. Event Description On July 8, 2024, at 1927 when James A. FitzPatrick Nuclear Power Plant (JAF) at 100% power, annunciators were received with indication of a half-scram on “B” side RPS. AOP-60, Loss of RPS Bus B Power, was entered and the cause was determined to be a trip of the “B” RPS MG set due to an overvoltage condition. The direct cause of the output breaker tripping was due to an Electric Power Monitoring System overvoltage trip on 71EPA-RPS1B1G, Electrical Protection Assembly (EPA). The condition was corrected when the RPS Bus was placed on the alternate power supply. The event resulted in invalid system actuations of "B" side half scram and Primary Containment Isolation System (PCIS) [JM] isolations. The following systems isolated as a result of the loss of “B” RPS bus: Reactor Water Cleanup [CE], Reactor Building ventilation [NG], “B” Containment Atmosphere Dilution [BB], Torus Vent and Purge, Drywell Equipment and Floor Drain Sumps [WK], “B” Drywell Containment Atmospheric Monitors [IP], Recirculation System Sample Line, and Main Steam Line Drains [SB]. “B” Standby Gas Treatment System [BH] started as designed. These system actuations were not initiated by signals in response to actual plant conditions or parameters satisfying the requirements for initiation of the system. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). Page 2 of 3 | ML24249A254
Clinton Power Station 00461 1 OF 3 | Unknown Unit | Reactor Core Isolation Cooling System Inoperable Prior to Mode Change | 09-24-2024 | On October 10, 2023, at 23:02 CST, the Reactor Core Isolation Cooling (RCIC) system tripped during performance of Surveillance Requirement (SR) 3.5.3.3. This SR is performed when RCIC steam supply pressure is at the higher operating ranges of the system to verify that the RCIC pump can develop the required flow rate against a system head corresponding to reactor pressure. The system was restored to operable on October 16, 2023, at 02:51 CST following replacement and calibration of the Electric Governor-Remote (EG-R). Engineering personnel suspected that the RCIC system trip was due to a faulty EG-R; however, subsequent failure analysis identified no significant issues with the EG-R. On December 19, 2023, Engineering personnel determined that work performed on August 28, 2023 affected functionality of the EG-R and caused RCIC to be inoperable per Technical Specifications (TS) 3.5.3, "RCIC System." This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS 3.0.4. Specifically, on October 9, 2023, at 05: 14 CST, during unit startup following a refueling outage, the Applicability for TS 3.5.3 was entered (i.e., Mode 2 with reactor steam dome pressure greater than 150 psig) with the RCIC system inoperable. In addition, the unit was taken to Mode 1 on October 10, 2023. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMIS APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection il tto ://wwv1. n re. qov.1r e 81j ina-rm/d oc-collecti ons/nureosist a ffi s r 1 022/ r3/) displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 SEQUENTIAL REV YEAR NUMBER NO. Clinton Power Station 00461 □ 052 2023 - 002 01 | CONDITION PRIOR TO THE EVENT Unit: 1 Event Date: December 19, 2023 Event Time: 0800 CST Mode: 1 Mode Name: Power Operation Reactor Power: 100 EVENT DESCRIPTION On October 8, 2023, Operations commenced reactor startup following a refueling outage. On October 10, 2023, at 23:02 CST, the Reactor Core Isolation Cooling (RCIC) system tripped on low suction pressure during performance of Surveillance Requirement (SR) 3.5.3.3 and the RCIC system was declared inoperable. This SR is performed when RCIC steam supply pressure is at the higher operating ranges of the system to verify that the RCIC pump can develop the required flow rate against a system head corresponding to reactor pressure. Troubleshooting activities commenced to determine the cause of the RCIC system trip. As part of the troubleshooting activities, the RCIC Electric Governor - Remote (EG-R) was replaced and calibrated. Following replacement of the EG-R, SR 3.5.3.3 was re performed satisfactorily and the RCIC system was declared operable at 02:51 CST on October 16, 2023. Based on the successful re-performance of SR 3.5.3.3 following replacement of the EG-R, Engineering personnel suspected that the RCIC system trip on low suction pressure was due to a faulty EG-R. The suspect EG-R was sent offsite for failure analysis. Results from the failure analysis were documented in a failure analysis report that was issued on November 17, 2023. The report stated that the EG-R showed no signs of degradation and that the sharp, rapid changes in the EG-R output that were observed on October 10, 2023, could not be replicated. Efforts continued to determine the cause of the RCIC system low suction pressure trip. On December 19, 2023, a review of Plant Process Computer data revealed an anomaly to the Electric Governor - Magnetic Pickup (EG-M) output that occurred on August 28, 2023. Further investigation determined that on August 28, 2023, with Unit 1 in Mode 1 at 100% power, work associated with a plant modification on the transient test system disturbed electrical connections for the EG-M. Transient Test is a high-speed data acquisition system which monitors and records analog and digital signals from various plant systems. The EG-M is the flow control system component that transmits an electrical signal to the EG-R proportional to the error signal developed between turbine speed demand and actual turbine speed. When the electrical connections were disturbed, EG-M output fell to 0% scale, indicating a loss of functionality of that component. This was unrecognized by station personnel at the time of occurrence. Further investigation has also found that between September 11, 2023 and October 8, 2023, through various maintenance activities performed on the RCIC system, there is a potential for air to have been entrained in the lubricating oil system. Air entrainment in the lubricating oil control subsystem can cause governor speed and ramp control issues. On December 19, 2023, at approximately 08:00 CST, it was determined that the work performed on August 28, 2023, affected functionality of the EG-M and potentially caused the RCIC system to be inoperable per Technical Specifications Section 3.5.3, "RCIC System." Condition A of TS 3.5.3 applies when the RCIC system is inoperable, with a Required Action to restore the RCIC system to operable status within 14 days. The Completion Time for this Required Action was not exceeded because the Applicability for TS 3.5.3 was exited prior to the expiration of the 14-day Completion Time to support the unit shutdown for a planned refueling outage. However, this event is reportable in accordance with 1 O CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS 3.0.4. Specifically, on October 9, 2023, at 05: 14 CST, during unit startup following the refueling outage, the Applicability for TS 3.5.3 was entered (i.e., Mode 2 with reactor steam dome pressure greater than 150 psig) with TS 3.5.3 not met because the RCIC system was inoperable. In addition, the unit was taken to Mode 1 on October 10, 2023. | ML24270A035
Prairie Island Nuclear Generating Plant | Unit 1 | Auxiliary Building Special Ventilation System Inoperable during movement of irradiated fuel assemblies. | 09-16-2024 | On May 02, 2024, the Prairie Island Nuclear Generating Plant (PINGP) Units 1 and 2 were operating at 100 percent power while performing fuel handling operations. For a 33-minute period between 12:52 and 13:25, radiation monitors 1R-37 and 2R-30 were both out of service while movement of irradiated fuel assemblies was occurring. On July 11, 2024, while completing a review of the design and licensing basis of radiation monitors 1[2]R-37, 1[2]R-30, it was determined that these monitors are required for Auxiliary Building Special Ventilation System (ABSVS) operability during movement of irradiated fuel assemblies per Technical Specification (TS) 3.7.12. Changes to fuel handling procedures have been initiated. TS Bases for the ABSVS were further clarified and communicated to the operating crews. This will ensure compliance with TS going forward when irradiated fuel is being moved. This event is reportable under 10 CFR 50.73(a)(2)(i)(B) for an Operation or Condition Prohibited by Technical Specifications. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 YEAR SEQUENTIAL REV NUMBER NO. Prairie Island Nuclear Generating Plant, Unit 1 -282 2024 052 - 001 - 01 | Plant Operating Conditions Prior to the Event: Unit 1 – Mode 1, 100 percent Power. Unit 2 – Mode 1, 100 percent Power. EVENT DESCRIPTION On May 02, 2024, the Prairie Island Nuclear Generating Plant (PINGP) was performing fuel handling operations in the Spent Fuel Pool area in support of a Cask loading campaign. For a 33-minute period between 12:52 and 13:25, Radiation Monitors [IL] 1R-37 (Unit 1, Train A) and 2R-30 (Unit 2, Train B) were both out of service while movement of irradiated fuel assemblies was occurring. This impacted the Auxiliary Building Special Ventilation System [VF] (ABSVS) and caused both Train A and Train B of the ABSVS to be inoperable during the movement of irradiated fuel assemblies. The implications of this condition were not known at the time. Radiation monitors 1[2]R-37, 1[2]R-30 are vent gas monitors that monitor for potential radiological releases out of the Auxiliary Building Normal Ventilation (ABNV) exhaust stacks. One of the safety functions of these monitors is to send an auto-start signal to the ABSVS upon detecting high radiation. The Unit 1 ABNV exhaust stack is monitored by 1R-37 (Train A) and 1R-30 (Train B) while the Unit 2 ABNV stack is monitored by 2R-37 (Train A) and 2R-30 (Train B). The ABSVS is a single system that serves both Unit 1 and Unit 2. The system consists of two redundant trains: Train A and Train B. Actuation of either train of the ABSVS will isolate the ABNV exhaust stacks on both Units. The high radiation signal from 1[2]R-37 and 1[2]R-30 is the credited ABSVS actuation signal during a Fuel Handling Accident (FHA) event. With 1R-37 out of service (OOS), the A Train ABSVS would not receive this auto-start signal from a release through the Unit 1 ABNV exhaust stack thus making Train A inoperable during the movement of irradiated fuel assemblies. With 2R-30 OOS, the B train ABSVS would not receive this auto-start signal from a release through the Unit 2 ABNV exhaust stack thus making Train B inoperable during the movement of irradiated fuel assemblies. Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.12 Auxiliary Building Special Ventilation System (ABSVS) requires "Two ABSVS trains shall be OPERABLE" and is applicable in MODES 1, 2, 3 and 4 and "During movement of irradiated fuel assemblies”. The radiation monitors only impact the operability of an ABSVS train during movement of irradiated fuel assemblies. There are no conditions in TS 3.7.12 that apply to two Trains of ABSVS being inoperable during movement of irradiated fuel assemblies due to radiation monitors out of service. With no applicable action provided in Tech Spec 3.7.12, LCO 3.0.3 applied since LCO 3.0.3 establishes the actions that must be implemented when an LCO is not met and an associated action is not provided. LCO 3.0.3 states that the unit shall be placed in a MODE or other specified condition in which the LCO is not applicable and delineates the time limits for placing the unit in a safe MODE. However, since the high radiation signal is only required for LCO 3.7.12 during movement of irradiated fuel, a unit shutdown would not provide appropriate remedial measures. The appropriate action in response to two trains of ABSVS being inoperable during movement of irradiated fuel assemblies due to radiation monitors out of service would be to immediately suspend the movement of irradiated fuel assemblies, but that did not happen. This event is reportable under 10 CFR 50.73(a)(2)(i)(B) for an Operation or Condition Prohibited by Technical Specifications. | ML24296B194
Browns Ferry Nuclear Plant | Unit 2 | Secondary Containment Isolation Valve Inoperable due to Mechanical Failure | 10-28-2024 | On November 18, 2023, at approximately 2038 Central Standard Time, during performance of Surveillance Requirement 3.6.4.2.1, Secondary Containment Isolation Valve (SCIV) Stroke Timing, Reactor Zone Outboard Supply Damper 2-DMP-0064-0013 failed to close upon securing Reactor Zone Supply Fans. Operations personnel declared 2-DMP-064-0013 inoperable for SCIV function and entered Technical Specification Limiting Condition for Operation 3.6.4.2 Condition A. On November 22, 2023, 1515 CST, following corrective maintenance on the damper, Operations personnel declared damper 2-DMP-064-0013 operable for SCIV function and exited TS LCO 3.6.4.2 Condition A. On December 18, 2023, a Past Operability Evaluation determined that the damper had been inoperable for longer than allowed by TS. This condition did not result in any loss of safety function. The apparent cause of this event was a lack of proper guidance in damper maintenance instructions. The corrective actions to reduce the possibility of recurrence for this condition are to replace broken and/or degraded components on the affected valve, and to revise maintenance procedures for the dampers to include an updated Preventative Maintenance plan with Electric Power Research Institute maintenance guidance. Revision 2 to this report includes applicability to BFN Units 1 and 3 which was not previously reported. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME (cid:1409) 050 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 2 00260 NUMBER NO. (cid:1407) 052 2024 - 001 - 02 | I. Plant Operating Conditions before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN) Units 1, 2, and 3 were each in Mode 1 at approximately 100 percent power. II. Description of Event A. Event Summary On November 18, 2023, at approximately 2038 Central Standard Time (CST), during performance of Surveillance Requirement (SR) 3.6.4.2.1, Secondary Containment [JM] Isolation Valve (SCIV) [ISV] Stroke Timing, Reactor Zone Outboard Supply Damper [DMP] 2-DMP-064-0013 failed to close upon securing Reactor Zone Supply Fans [FAN]. Operations personnel declared 2-DMP- 064-0013 inoperable for SCIV function and entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.4.2 Condition A. On November 22, 2023, 1515 CST, following implementation of a Temporary Modification (TMOD) to the damper, Operations personnel declared damper 2-DMP-064-0013 operable for SCIV function and exited TS LCO 3.6.4.2 Condition A. On December 18, 2023, TVA completed a Past Operability Evaluation (POE) which determined that the damper had been inoperable for longer than allowed by TS. The Tennessee Valley Authority is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant’s TS. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML24302A223
Quad Cities Nuclear Power Station | Unit 2 | Turbine Trip and Automatic Scram due to Digital EHC Power Supply Intermittent Failure | 10-30-2024 | On May 23, 2024, at 2223 CST, Quad Cities Unit 2 had an automatic scram from 38 percent power due to a trip of the main turbine. A Digital Electro-Hydraulic Control (DEHC) erroneous Speed Difference Trip signal initiated a Turbine Trip signal. The Unit 2 Main Turbine tripped as designed and generated an automatic reactor scram. All control rods inserted and the scram was uncomplicated. Containment isolation valves actuated closed in multiple systems on valid Group II and Group Ill signals as a result of low reactor water level. The cause of the DEHC trip signal was intermittent channel <R1 > core power supply failure, resulting in an erroneous speed demand value being generated. The power supply and several DEHC cards.were replaced with new components. This report is being submitted per 10 CFR 50. 73(a)(2)(iv)(A) for an event that resulted in manual or automatic actuation of the reactor protection system including a reactor scram, and containment isolation signals affecting more than one system. NRC FORM 366A (04-02-2024) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME • 050 Quad Cities Nuclear Power Station, Unit 2 • 052 | PLANT AND SYSTEM IDENTIFICATION Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A 10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Offcer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 2. DOCKET NUMBER YEAR 00265 2024 - 3. LER NUMBER SEQUENTIAL NUMBER 002 REV NO. 01 General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in text as [XX]. EVENT IDENTIFICATION Turbine Trip and Automatic Scram due to Digital EHC Power Supply Intermittent Failure CONDITION PRIOR TO EVENT Unit: 2 Reactor Mode: 1 Event Date: May 23, 2024 Mode Name: Power Operation Event Time: 2223 CST Power Level: 38 percent No structures, systems, or components that were inoperable at the start of the event contributed to the event. A. DESCRIPTION OF EVENT At 2223 CST on May 23, 2024, with Quad Cities Unit 2 at 38 percent power, the reactor automatically scrammed due to a turbine [TRB] trip signal resulting in turbine stop valve closure, creating a valid reactor protection system signal. Reactor vessel level reached the low-level set-point following the scram, resulting in valid Group II and Group Ill containment actuation signals. The trip was not complex with all systems responding as expected post-trip. This report is being submitted per 10 CFR 50. 73(a)(2)(iv)(A) for an event that resulted in manual or automatic actuation of the reactor protection system including a reactor scram, and containment isolation signals affecting more than one system. Prior to the scram, the unit was reducing power for planned transformer maintenance. A turbine speed versus speed demand comparison generated a Speed Difference Trip and turbine trip signal due to an erroneous speed demand signal. B. CAUSES OF EVENT The cause of the event is an intermittent power supply failure that was not recognized as a single point vulnerability due to the diversity of the system. The turbine trip signal was generated by Digital Electro-Hydraulic Control (DEHC) [TG] turbine speed and speed demand mismatch logic. An intermittent failure of the channel <R1 > core power supply [RJX] resulted in an erroneous speed demand value being generated. DEHC initiated a turbine trip due to a 100% actual speed compared to a 0% speed demand, which is larger than the 10% setpoint. While there was known degradation of this power supply, it was not recognized as a single point vulnerability to DEHC due to system redundancies. NRG FORM 366A (04-02-2024) Page _2_ of _4_ | ML24304A856
Edwin I. Hatch Nuclear Plant | Unit 1 | Manual Reactor Trip During Hurricane Helene Due to Degrading Condenser Vacuum | 11-19-2024 | At 0346 EDT on 9/27/24, with Unit 1 in Mode 1 at approximately 54% power, the reactor was manually tripped due to degrading condenser vacuum. The trip was not complex, with all systems responding normally including the closure of containment isolation valves in multiple systems. The Operating crew responded correctly to the event and the plant was stabilized. The degrading condenser vacuum was caused by debris from Hurricane Helene that accumulated and clogged the circulation water screens of the Unit 1 flume. The circulation water system was shutdown and the debris removed from the Unit 1 circulation water screens. The event is reportable per 10 CFR 50.73(a)(2)(iv)(A) as any event or condition that resulted in the manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section. Systems that actuated during this event that are listed in (a)(2)(iv)(B) include: the Reactor Protection System (RPS) and general Containment Isolation Valves (CIV) in multiple systems. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04--02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA. Library, and Information CoDections Branch (T-6 A10M), U.S. Nudear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrt:.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104). Attn: Desk Officer for lhe Nudear Regulatory Commission, 725 17th Street NW. Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of Information unless the document requesting or requiring the collection bttQ://www.nrc.gov/reading,_rm/doc-collectionsillY.(fillslstaff/sr.1022/r3I) displays a currently valid 0MB control number. 1. FACILITY NAME r-, 2. DOCKET NUMBER 3. LER NUMBER ..-----------------, ~ 050 cY:E:AR7 SEQUENTIAL REV Edwin I. Hatch Nuclear Plant Unit 1 00321 NUMBER NO. ~- I 1-G □ 052 I I 004 | EVENT DESCRIPTION At 0346 EDT on 9/27/24, with Unit 1 in Mode 1 at approximately 54% power, the reactor was manually tripped due to degrading condenser vacuum. The trip was not complex, with all systems responding normally including the closure of containment isolation valves {CIV)(EIIS Code: ISV) in multiple systems. The Operating crew responded correctly to the event and the plant was stabilized. There were no inoperable systems that contributed to this event. EVENT CAUSE ANALYSIS The degrading condenser vacuum was caused by debris from Hurricane Helene that accumulated and clogged the circulation water screens of the Unit 1 flume. SAFETY ASSESSMENT AND REPORTABILITY There were no actual safety consequences as a result of this event. All safety related systems functioned as designed during this event. The Operating crew responded correctly to the event. The applicable abnormal / emergency operating procedures were properly entered and the plant was stabilized. The event was within the analysis of the Updated Final Safety Analysis Report (UFSAR) Chapter 15. The event is reportable per 10 CFR 50.73(a)(2)(iv)(A) as any event or condition that resulted in the manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section. Systems that actuated during this event that are listed in (a)(2)(iv)(B) include: the Reactor Protection System (RPS)(EIIS Code: IG) and general Containment Isolation Valves (CIV) in multiple systems. CORRECTIVE ACTIONS The circulation water system was shutdown and the debris removed from the Unit 1 circulation water screens. PREVIOUS SIMILAR EVENTS None. | ML24324A187
Grand Gulf Nuclear Station | Unit 1 | High Pressure Core Spray Over Frequency Relay Trip | 11-22-2024 | On September 24, 2024, Grand Gulf Nuclear Station, Unit 1 was operating at 100 percent power with the High Pressure Core Spray (HPCS) offline for testing and all safety systems operable. At 22:04 CT, during planned surveillance testing of HPCS and the Division Ill diesel generator, the HPCS pump breaker unexpectantly tripped after the HPCS diesel generator started and powered the safety bus. The breaker performed its motor protection function and tripped due to an over-frequency indication. This resulted in a potential loss of safety function. Troubleshooting was performed, and the HPCS over-frequency relay was replaced. The system was returned to service. The cause of the trip was determined to be the failure of the over-frequency relay. The over-frequency relay was determined to be non-essential, and actions were created to remove the relay from the system. During the testing of the HPCS system, alternate ECCS systems were available to provide core cooling and injection to the reactor; therefore, there were no actual safety consequences to the event. This report is made in accordance with 10 CFR 50. 73a(2)(v)(D) for an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 0 4 / 3 0 / 2 0 2 7 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: BO hours. Reported rO\ lessons learned are incorporated into the licensing process and led back to industry Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch IT-6 A10M), U.S. \~.....l. j Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnlocollects.Resource@nrc.gov. and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRG may not conduct or sponsor, and a person is not required to respond https://www .nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/QL) to, a collection of information unless the document requesting or requiring the co lecllon displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER 181 050 YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 NUMBER NO. 00416 0 052 2024 004 00 | Plant Conditions: At the time of the event, Grand Gulf Nuclear Station, Unit 1 was in Mode 1 at 100% power. The station was conducting planned surveillance testing on the High Pressure Core Spray (HPCS) Division Ill Emergency Diesel Generator (EDG). Description of Event: On September 24, 2024, while performing a HPCS loss of offsite power surveillance, the Division Ill EDG started and loaded the safety bus as expected, but the HPCS pump breaker immediately tripped which resulted in a potential loss of safety function. Reportability: This report is made in accordance with 10 CFR 50.73a(2)(v)(D) for an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. HPCS is required to be able to inject water during a loss of cooling accident. Cause(s): The direct cause of the event was a failure of the HPCS over-frequency relay. The HPCS original system design included an over-frequency relay that is not required. This feature has existed since construction, and its need was not evaluated after HPCS was built without the Level-8 injection valve isolation bypass signal, per the GE system design criteria. Corrective Actions: Completed Actions: -Electrical Maintenance replaced the HPCS over-frequency relay. -A Failure Modes Analysis and a Root Cause Evaluation were performed to identify and correct the causes of the event. Planned Actions: -Revise current preventative maintenance to include capacitor checks based on EPRI guidance. -Revise over-frequency calibration procedure to state that all installation or reinstallation of the over frequency relay is required to be with a matched capacitor. -Remove the over-frequency relay protection (17 AC-181) from the HPCS motor protection circuit. Safety Significance: There were no actual safety consequences associated with this condition. The HPCS system functions as a part of the Emergency Core Cooling System (ECCS). It functions to provide and maintain an adequate coolant inventory inside the reactor vessel to limit the fuel cladding temperatures in the event of breaks in the reactor coolant pressure boundary. The system is initiated by either high pressure in the drywall or low water level in the reactor vessel. During the testing of the HPCS system, alternate ECCS systems were available to provide core cooling and injection to the reactor. Previous Similar Events: LER 24-001-00 High Pressure Core Spray Inoperable due to Minimum Flow Valve Failure to Close | ML24326A363
James A. FitzPatrick Nuclear Power Plant | Unknown Unit | Turbine Trip and Scram due to Automatic Voltage Regulator Protective Device during a Grid Transient | 11-22-2024 | At 0720 on September 23, 2024, James A. FitzPatrick Nuclear Power Plant (JAF) was at 100% power when an automatic scram occurred as a result of a main turbine trip due to an automatic trip of the generator output breakers. All control rods inserted and a subsequent Reactor Pressure Vessel (RPV) low water level resulted in Group 2 isolation and system initiation of High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC). RCIC did inject but HPCI did not inject as expected based on RPV water level recovery with the Feedwater System. The generator output breakers were tripped because of the energization of the digital Automatic Voltage Regulator (AVR) protective device crowbar circuit due to an overvoltage condition during a grid transient. A corrective action is planned to evaluate and model the event to determine if the min limiter function or software changes to the AVR should be implemented. This event is reportable in accordance with CFR 50.73(a)(2)(iv)(A) as a Reactor Protection System (RPS) actuation, including a general containment Group 2 isolation and HPCI and RCIC system actuation. NRC FORM 366 (04-02-2024) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 LICENSEE EVENT REPORT (LER) hours. Reported lessons learned are incorporated into the licensing process and fed CONTINUATION SHEET back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory (See NUREG-1022, R.3 for instruction and guidance for completing this form Commission, 725 17th Street NW, Washington, DC 20503; email: http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER  050 YEAR SEQUENTIAL REV NUMBER NO. James A. FitzPatrick Nuclear Power Plant 05000333  052 2024 – 003 – 00 | Background The main generator [EIIS identifier:TB] has an Exciter System [TL] to stabilize voltages from the electrical transmission grid. The excitation is controlled by a Digital Automatic Voltage Regulator (AVR). The AVR has two redundant channels. Reactive Power is measured in units of "mega volt-amperes reactive", or MVAR, and is taken into account when designing and operating power systems. The power associated with reactive power does no net work but current must still be supplied by the conductors, transformers and generators. They must be sized to carry the total current, not just the current that does useful work (active power). Insufficient reactive power can depress voltage levels on an electrical grid and, under certain operating conditions, collapse the network (a blackout). Therefore, the purpose of the AVR is to control the exciter based on changes on the grid, including reactive power. AVR may enable control parameters such as over excitation Protective Device Threshold – Trip / Disconnect limiter (OEL) to prevent overheating from excessive current; and an under excitation Limiter Threshold – Controls Parameter limiter (UEL) to prevent de-synchronization from the grid. Besides control parameters, the AVR is designed with protection devices to trip the system to protect components from being damaged. The protective device associated with this event is the crowbar circuit which is Time designed to respond to an overvoltage or surge condition. Event Description On September 23, 2024, at 0720 with James A. FitzPatrick Nuclear Power Plant (JAF) reactor operating at 100 percent power, an automatic reactor shutdown (scram) occurred because of a main turbine trip due to an automatic trip of the generator output breakers. All control rods inserted and a subsequent Reactor Pressure Vessel (RPV) low water level resulted in Group 2 isolation and system initiation of High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC). RCIC did inject but HPCI did not inject as expected based on RPV water level recovery with the Feedwater System. This event was reported at the time of the event by ENS 573331 and is reportable in accordance with CFR 50.73(a)(2)(iv)(A) as a Reactor Protection System (RPS) actuation, including a general containment Group 2 isolation and HPCI and RCIC system actuation. Page 2 of 3 | ML24327A098
Cooper Nuclear Station 298 1 of 3 | Unknown Unit | Inoperable Pressure Switch During Mode Change Results in Operation or Condition Prohibited by Technical Specifications | 12-31-2024 | On November 3, 2024, with the Cooper Nuclear Station (CNS) reactor in Mode 1, Power Operation, scheduled surveillance testing of the eight Safety Relief Valves (SRV) was being performed. During this testing, pressure switch (MS-PS-3008) did not actuate when SRV71 B was taken to the OPEN position. As such, Operations personnel declared MS-PS-3008 inoperable. Review of a picture taken in the area of SRV71 B on October 16, 2024, while the reactor was in Mode 5, Refueling, revealed that the flex hose that extends from the SRV tailpipe to the pressure switch may be damaged. This was later confirmed when maintenance personnel found the flex hose on top of the SRV tailpipe and the connection port for MS-PS-3008 damaged. Repairs were made and subsequent testing performed satisfactorily, and Operations personnel declared MS-PS-3008 operable. CNS made the change from Mode 4 to Mode 2 while this condition existed, violating Technical Speciation (TS) Limiting Condition for Operation 3.0.4, and is reporting this event as an operation or condition prohibited by plant TS. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process LICENSEE EVENT REPORT {LER) and fed back to industry. Send comments regarding burden estimate to the CO NTINUATION SHEET FOIA, Library, and Information Collections Branch (T-6 A10M), U. s. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. (See NUREG-1022, R.3 for instruction and guidance for completing this form The NRC may not conduct or sponsor, and a person is not required to respond http://www.nrc.gov/readinq-rm/doc-collections/nuregs/staff/sr1022/r3/) to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Cooper Nuclear Station 05000-298 NUMBER NO. 2024 007 00 | PLANT STATUS Cooper Nuclear Station (CNS) was in Mode 1, Power Operation, at 18 percent power at the time of the event on November 3, 2024. BACKGROUND The pressure relief system includes three American Society of Mechanical Engineers (ASME) code safety valves (SV) [EIIS: SB] and eight safety relief valves (SRV) [EIIS: RV], all of which are located on the main steam lines [EIIS: SB] within the drywell [EIIS: NH], between the reactor vessel [EIIS: RPV] and the first main steam isolation valve [EIIS: ISV]. The SVs provide protection against over pressurization of the nuclear system and discharge directly into the interior space of the drywell. The SRVs discharge to the suppression pool and provide three main functions: overpressure relief operation to limit the pressure rise and prevent safety valve opening, overpressure safety operation to prevent nuclear system over pressurization, and depressurization operation (opened automatically or manually) as part of the emergency core cooling system [EIIS: BJ, BM, BO]. Each SRV is equipped with a pressure switch mounted in its discharge tailpipe. When a SRVs associated discharge pressure switch senses tailpipe pressure of at least 30 psig, the SRV can be determined to be in the OPEN position. When the pressure switch is actuated at 30 psig, an amber indicating light will illuminate in the Control Room and the annunciator for the relief valve will alarm, indicating the SRV is open. EVENT DESCRIPTION On November 3, 2024, while performing scheduled surveillance testing of the eight Safety Relief Valves (SRV) during plant start-up activities from Refueling Outage (RE33), pressure switch (MS-PS-300B) did not actuate when SRV71 B was taken to the OPEN position. SRV71 B tailpipe temperature did immediately rise, however, the temperature was approximately 100 degrees Fahrenheit lower than expected for a fully open SRV and the temperature profile exhibited erratic behavior. The main turbine bypass valve position responded as expected, confirming SRV71 B did fully open. As such, MS-PS-300A was declared inoperable on November 3, 2024. As a result of the low temperatures on the SRV71 B tailpipe, questions arose regarding the possibility of a disconnected flex hose that extends from the SRV71 B tailpipe to MS-PS-300B. SRV71 B was not cycled open prior to RE33 and was not subjected to abnormal operating conditions that would have induced a vibration or fatigue failure of the flex hose. A picture taken near the area of SRV71 B on October 16, 2024, was reviewed and it was discovered that the flex hose may have been inadvertently disconnected. Maintenance personnel were dispatched to SRV71 B and confirmed that the flex hose was disconnected and was laying on top of the SRV71 B tailpipe. The threaded connections of the flex hose and the connection port on the SRV71 B tailpipe were found damaged. | ML24366A126
Grand Gulf Nuclear Station | Unit 1 | Loss of Seal Steam Controller Power Resulted in Manual Reactor Shutdown | 01-09-2025 | On November 10, 2024, at 0337 CST, Grand Gulf Nuclear Station, Unit 1 was operating at 100 percent power with all safety systems operable. A failed power supply resulted in a loss of seal steam controller power and led to a degraded condenser vacuum which resulted in a manual reactor shutdown. All control rods were fully inserted with no complications. Following initial scram response, a group 1 containment isolation signal resulted in the closure of all main steam isolation valves at 0545 CST. Later, an automatic Reactor Protection System actuation occurred at 0620 CST while in MODE 3 while all control rods were inserted. The cause of the loss of seal steam controller power was determined to be a failed power supply, 1 N21 K602B which had exceeded its expected life. The 1 N21 K602B power supply was replaced, and seal steam control was returned to service. This report is made in accordance with 10 CFR 50.73(a)(2)(iv)(A) for events or conditions that resulted in the manual or automatic actuation of the reactor protection system. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 0 4 / 3 0 / 2 0 2 7 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: BO hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M). U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnlocollects.Resource@nrc.gov, and the 0MB reviewer at. 0MB Office of Information and Regulatory Attairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503 The NRC may not conduct or sponsor, and a person is not required to respond https://www.nrc.gov/reading-rm/doc-colleclions/nuregs/staff/ sr1 022/r3/l to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER 181 050 YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 NUMBER NO. 00416 □ 052 2024 005 00 | Plant Conditions: At the time of the event, Grand Gulf Nuclear Station, Unit 1 was in Mode 1 at 100% power, and all safety systems were operable. Description of Event: On November 10, 2024, at 0337 CST, a power supply failure resulted in a loss of seal steam controller power and led to a degraded condenser vacuum which resulted in a manual reactor shutdown. All control rods fully inserted, and there were no complications. Following initial scram response, a group 1 containment isolation signal resulted in the closure of all main steam isolation valves at 0545 CST. This signal was due to the continued degradation of the condenser vacuum post-trip. An automatic RPS actuation occurred while in MODE 3 with all control rods currently inserted at 0620 CST. Following the second actuation of the reactor protection system (RPS), pressure was controlled by safety relief valves and reactor core isolation cooling was used to maintain water level. Reportability: This report is made in accordance with 10 CFR 50.73(a)(2)(iv)(A) for events or conditions which resulted in the manual or automatic actuation of the RPS. Cause(s): The direct cause of the 1 N21 K602B power supply failure was aged components exceeding their expected life. The root cause of the event was the determination of the life expectancy of the power supplies with electrolytic capacitors was incorrectly designed using the in-service date as the starting criteria; however, electrolytic capacitors begin degrading upon manufactured date. Starting the life expectancy for this power supply from the in-service date as opposed to manufactured date resulted in the power supply being installed with a projected life expectancy of 10 years when the component already had 6 years of shelf life and only 4 years of remaining life expectancy. Corrective Actions: Completed Actions: -The seal steam power supply 1 N21 K602B was replaced, and seal steam control was restored. Planned Actions: -Revise maintenance procedure to include steps which guide actual full age determination and evaluation of power supplies. This will include a signature requirement for Maintenance to contact Supply Chain, and it will require initiating a Condition Report to document and evaluate the power supply age prior to being installed. Safety Significance: There were no actual safety consequences associated with this condition. Plant systems responded as designed and the unit was brought to Mode 3 by Control Room Operators. Previous Similar Events: None identified. NRG FORM 366A (04-02-2024) Page 2 of 2 | ML25009A011
i | Unknown Unit | : | 01-23-2025 | On November 26, 2024, at 1158, with the reactor in Mode 1 and 100 percent rated thermal power, the Division 3 diesel generator (DG) was declared inoperable per Technical Specification (TS} 3.8.1, due to the right bank air start motor not operating properly during a monthly surveillance test. Subsequent troubleshooting found that the right bank air start motor air hoses were improperly connected during maintenance in June of 2024. Satisfactory testing of the DG, following proper air hose connection, resulted in correct operation of the right back air start motor, and the Division 3 DG was declared operable at 1731 on November 27, 2024. The cause was determined to be insufficient use of verification practices and/or use of vendor drawings during the air start motor air hose re-assembly during previous maintenance. Corrective actions include adding an independent verification procedure step to ensure the proper connection of the air start motor air hoses and revisions to maintenance procedures for configuration control. This event was reported on November 26, 2024, as a loss of safety function under 10 CFR 50.72(b)(3)(v)(D), for accident mitigation, due to the Division 3 DG being declared Inoperable. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 0 4130/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A1 0M}, U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond (See NUREG-1022, R.3 for instruction and guidance for completing this form to, a collection of information unless the document requesting or requiring the collection displays a http:// W'NW. n re. gov/reading-rm/doc-co 11 ecti o ns/nu regs/staffl s r1 022/r3/ currently valid 0MB control number. 2. DOCKET NUMBER ..__ ___3 _. _LE_R_N_U_M_B..,E_R_ ___ 1. FACILITY NAME t8l 050 SEQUENTIAL REV YEAR NUMBER NO. Perry Nuclear Power Plant 00440 2024 005 00 □ 052 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. BACKGROUND: The High Pressure Core Spray (HPCS) [BG] system power source, the Division 3 DG [DG], is self-contained, except for access to the preferred source of offsite power through the onsite AC power distribution system and the system actuation signal source. The system is operable as an isolated system independent of electrical connection to any other system by using the Division 3 DG. HPCS provides and maintains an adequate coolant inventory inside the reactor vessel to limit fuel cladding temperatures in the event of breaks in the reactor coolant pressure boundary. The system is initiated by either high pressure in the drywell or low water level in the reactor vessel [RCT). It operates independently of all other systems over the entire range of pressure differences from greater than normal operating pressure to zero. The HPCS cooling decreases vessel pressure to enable the low-pressure cooling systems to function. The HPCS system pump [P] motor [MO] is powered by a diesel generator if auxiliary power is not available; the system may also be used as a backup for the Reactor Core Isolation Cooling (RCIC) [BN] system. DESCRIPTION OF EVENT: On November 26, 2024, at 1158, with the reactor in Mode 1 and 100 percent rated thermal power, during a surveillance test of the Division 3 DG, it was identified that the right bank air start motor was not operating correctly, based on noting a lack of a sufficient pressure drop at the air storage tank. The Division 3 DG was declared Inoperable, but available, and TS 3.8.1, AC Sources - Operating, Condition B, one required DG inoperable, was entered. During troubleshooting, it was discovered that the air hoses to the right bank air start motor were not configured correctly, causing improper operation of the right bank air start motor. The air hoses were determined to have been configured incorrectly during maintenance in June of 2024. The air hoses were returned to the proper configuration and a post-maintenance run of the Division 3 DG was performed, resulting in a normal start using both right and left bank air start motors. On November 27, 2024, at 1731, the Division 3 DG was declared Operable and TS 3.8.1 was met. Although other power sources were available during this period, the inoperable condition of the Division 3 DG is reportable under 10 CFR 50.73(a)(2)(v)(D) for mitigating the consequences of an accident during a loss of offsite power/loss of coolant accident (LOOP/LOCA). Since the air hoses to the right bank air start motor were found to be misconfigured since June of 2024, the Division 3 DG has been inoperable since that time. As such, this is also reportable under 10 CFR 50.73(a)(2)(i)(B). CAUSE OF EVENT: Cause: Insufficient use of verification practices and/or use of vendor drawings to allow for correct re-assembly of the air start motor air hoses. NRG FORM 366A (04-02-2024) Page 2 of 3 | ML25023A193
i | Unknown Unit | : | 02-24-2025 | On October 29, 2024, at 1152, with the reactor in Mode 1 and 100 percent rated thermal power, Operations declared the Division 3 diesel generator (DG) Inoperable per Technical Specification (TS) 3.8.1, due to output voltage dropping below the TS acceptance value during a monthly surveillance run. Subsequent troubleshooting found potentiometers on the voltage regulator were oxidized, requiring exercise, which remediated the output voltage issue. Satisfactory testing of the DG, following the troubleshooting, resulted in a proper and steady output voltage, and the Division 3 DG was declared Operable on October 31, 2024, at 0030. This is a supplemental report to LER 2024-004-00 to update the causal investigation and the corrective actions. The cause was determined to be oxidation of the voltage regulator R1 and R3 potentiometers due to high humidity. Corrective actions include exercising potentiometer R1, R3, and R4 on the output voltage regulator to remove oxidation and revising operating procedures to perform cycling the output voltage adjustment monthly. This event was reported on October 29, 2024, as a loss of safety function, due to the loss of the Division 3 DG, under 10 CFR 50.72(b)(3)(v)(D), for accident mitigation. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A1 0M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond (See NUREG-1022, R.3 for instruction and guidance for completing this form to, a collection of information unless the document requesting or requiring the collection displays a http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/ currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER t------.-3_.L _E_R_N_U_M_BE.-R_ __- --1 050 SEQUENTIAL REV YEAR NUMBER NO. Perry Nuclear Power Plant 00440 □ 052 2024 004 01 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. BACKGROUND: The high pressure core spray (HPCS) [BG] system power source, the Division 3 DG [DG], is self-contained, except for access to the preferred source of offsite power through the onsite AC power distribution system and the system actuation signal source. The system is operable as an isolated system independent of electrical connection to any other system by using the Division 3 DG. HPCS provides and maintains an adequate coolant inventory inside the reactor vessel to limit fuel cladding temperatures in the event of breaks in the reactor coolant pressure boundary. The system is initiated by either high pressure in the drywall or low water level in the reactor vessel [RCT]. It operates independently of all other systems over the entire range of pressure differences from greater than normal operating pressure to zero. The HPCS cooling decreases vessel pressure to enable the low-pressure cooling systems to function. The HPCS system pump [P] motor [MO] is powered by a diesel generator if auxiliary power is not available; the system may also be used as a backup for the reactor core isolation cooling (RCIC) [BN] system. DESCRIPTION OF EVENT: On October 29, 2024, at 1152, with the reactor in Mode 1 and 100 percent rated thermal power, during a preventative maintenance run of the Division 3 DG, it was noticed that the generator output voltage had dropped below the Technical Specification (TS) acceptance value of 3994 volts (3900 volts, adjusted for instrument I inaccuracy). The lowest value recorded during the DG run was 3947 volts. The Division 3 DG was declared Inoperable, but available, and TS 3.8.1, AC Sources - Operating, Condition B, one required DG inoperable, was entered. During troubleshooting, it was discovered that an oxidation layer had built up on the R1 potentiometer in the output voltage regulator [RG]. Exercising the potentiometer throughout its range caused the oxidation layer to be removed, thereby eliminating the high resistance point and allowing the voltage regulator to function normally. A post-maintenance run of the Division 3 DG was performed resulting in a normal and steady output voltage. On October 31, 2024, at 0030, the Division 3 DG was declared Operable and TS 3.8.1 was met. Due to the lnoperability of the Division 3 DG, it was determined to be an event or condition that could have prevented fulfillment of a safety function under 10 CFR 50. 72(b )(3)(v)(D) for mitigating the consequences of an accident during a loss of offsite power/loss of coolant accident (LOOP/LOCA). The NRC was notified at 1732, on October 29, 2024, and this was documented on Event Notification 57406. No other failures of the Division 3 DG or the voltage regulator could be found during the previous three-year timeframe. Although outside of the three-year timeframe, a previous similar event was identified and is discussed later in this report. | ML25055A256
SEQUENTIAL REV | Unknown Unit | Loss of The Control Room Emergency Air Temperature Control System Due to a Chiller Oil Migration | 03-03-2025 | On January 4, 2025 at 0855 EST, with Unit 1 and Unit 2 at 100% rated thermal power, both trains of the Control Room Emergency Air Temperature Control System (CREATCS) were simultaneously inoperable. This condition occurred when the A-A Main Control Room (MCR) chiller experienced an oil migration event and tripped on oil failure while the B train of CREATCS had been previously declared inoperable for a B-B MCR chiller maintenance outage. The A train of CREATCS was later restored at 1408 EST on January 4, 2025 following the addition of MCR chiller oil, adjustment of the chiller’s temperature control valve (TCV) and subsequent observation of stable chiller parameters. Applicable technical specification (TS) limiting conditions for operability (LCO) were entered for less than six hours as a result. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond (See NUREG-1022, R.3 for instruction and guidance for completing this form to, a collection of information unless the document requesting or requiring the collection displays a http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) currently valid OMB control number 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ☒ 050 SEQUENTIAL REV YEAR NUMBER NO. Watts Bar Nuclear Plant, Unit 1 00390 ☐ 052 2025 - 001 - 00 | I. Plant Operating Conditions before the Event Watts Bar Unit 1 and Unit 2 were at 100 percent Rated Thermal Power (RTP) before the event. II. Description of Event A. Event Summary On January 4, 2025 at 0855 EST, with Unit 1 and Unit 2 at 100% rated thermal power, both trains of the Control Room Emergency Air Temperature Control System (CREATCS){EIIS:VI} were simultaneously inoperable. This condition occurred when the A-A Main Control Room (MCR) chiller experienced an oil migration event and tripped on oil failure while the B train of CREATCS had been previously declared inoperable for a B-B MCR chiller maintenance outage. The A train of CREATCS was later restored at 1408 EST on January 4, 2025 following the addition of MCR chiller oil, adjustment of the chiller’s temperature control valve (TCV){EIIS:TCV}, and subsequent observation of stable chiller parameters. Applicable technical specification (TS) limiting conditions for operability (LCO) were entered for less than six hours as a result. This condition is being reported to the Nuclear Regulatory Commission (NRC) in accordance with 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event The B-B MCR chiller had been removed from service for a maintenance outage when the A-A MCR chiller trip occurred. | ML25062A082
Donald C. Cook Nuclear Plant | Unit 2 | 2AB Emergency Diesel Generator Inoperable for longer than allowed by Technical Specifications | 03-27-2025 | On May 21, 2024, with Cook Nuclear Plant (CNP) Units 1 and 2 in Mode 1 at 100% power, the 2AB EDG failed to reach the required frequency during the slow speed start surveillance, per the required acceptance criteria range of 59.5 to 60.4 Hz. The failure to reach the required frequency was originally attributed to corroded connections on the Minimum Speed Threshold and Slow Start control relays. On July 23, 2024, the 2AB EOG, once again, failed to reach the required frequency during a surveillance run. The cause of the failure was determined to be an intermittent failure of the Digital Reference Unit (DRU). Due to the similar symptoms between the two failures of the 2AB EOG, it was determined that the 2AB EDG failure on May 21, 2024, was also due to a failure of the DRU. Due to the discovery that both EOG failures were a result of a failure of the DRU, the 2AB EOG was determined to be inoperable from the time the original condition was discovered on 05/21/2024 at 2115, until the time it successfully passed a surveillance after the DRU was replaced on 7/24/2024 at 2300. Therefore, the identified condition is reportable, for both units, in accordance with 10 CFR 50.73(a)(2)(i)(B) as a Condition prohibited by Technical Specifications. Furthermore, during this period of time, there were instances on Unit 2 where concurrent with the 2AB EOG, the 2CD EOG was inoperable, which results in being reportable per 10 CFR 50. 73(a)(2)(v) as an Event or Condition which could have prevented the fulfillment of a Safety Function. The Root Cause for the failure to properly identify and correct the May 21, 2024 EOG surveillance failure was I a lack of proper oversight and proper use of knowledge worker human performance tools during the Failure Investigation Process (FIP). Corrective Actions include formalization and improvements in qualifying FIP team management sponsors and team leaders. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nudear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nudear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nu regs/staff/ sr1 022/r3/) displays a currently valid 0MB control number. ■ 1. . FA - CIL - ITY - NA - ME - ----------, r ~ -, 050 I2. DOCKET NUMBER YEAR 3 S . E L Q E U R E N N U T M IA B L E R REV Donald C. Cook Nuclear Plant Unit 2 00316 I □ NUMBER NO. ~-I 1-0 □ 052 004 | EVENT DESCRIPTION On May 21, 2024, with Cook Nuclear Plant (CNP) Units 1 and 2 in Mode 1 at 100% power, the 2AB Emergency Diesel Generator (EOG) [DG] failed to reach the required frequency during the slow speed start surveillance, per the required acceptance criteria range of 59.5 to 60.4 Hz. The failure to reach the required frequency was originally attributed to corroded connections on the Minimum Speed Threshold and Slow Start control relays. On July 23, 2024, the 2AB EOG, once again, failed to reach the required frequency during a surveillance run. The cause of the failure was determined to be an intermittent failure of the Digital Reference Unit (DRU). Due to the similar symptoms between the two failures of the 2AB EOG, it was determined that the 2AB EDG failure on May 21, 2024, was also due to the failure of the DRU. Unit 2 Limiting Condition of Operation (LCO) 3.8.1 requires two diesel generators (DGs) capable of supplying the onsite Class 1E power distribution subsystem(s) to be OPERABLE in MODE 1. Additionally, Unit 1 LCO 3.8.1 requires the Unit 2 EDG(s) to be capable of supporting the associated equipment required to be OPERABLE by LCO 3.7.8, Essential Service Water (ESW) System [Bl]. If both Unit 1 ESW trains are cross-tied to Unit 2, then the two Unit 2 EDGs are required to be OPERABLE. The maximum COMPLETION TIME allowed to restore an inoperable EOG to OPERABLE status in MODE 1 is 14 days. With this COMPLETION TIME not met, then the affected Unit is required to be in MODE 3 in 6 hours and MODE 5 in 36 hours. Due to the discovery that both EOG failures were a result of a failure of the DRU, the 2AB EOG was determined to be inoperable from the time the original condition was discovered on 05/21/2024 at 2115, until the time it successfully passed a surveillance after the DRU was replaced on 7/24/2024 at 2300. The period of time that the 2AB EOG was determined to be INOPERABLE exceeds the time allowed by LCO 3.8.1. Therefore, the identified condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a Condition prohibited by Technical Specifications, for Units 1 and 2. Additionally, during this period of time, it was determined that the redundant EOG (2CD) was INOPERABLE for surveillance and maintenance activities during the following times: 05/22/2024 21 :08 -05/22/2024 22:33 U2 CD INOPERABLE for U1 ESW surveillance 05/30/2024 07:05 - 05/30/2024 14:50 U2 CD INOPERABLE for maintenance 06/03/2024 20: 15 -06/04/2024 01 :25 U2 CD INOPERABLE for surveillance activities 07/09/2024 19:34 - 07/10/2024 00:15 U2 CD INOPERABLE for surveillance activities 07/10/2024 20:52 - 07/10/2024 21:46 U2 CD INOPERABLE for U2 ESW surveillance Additionally, LCO 3.8.1 contains a Prescribed Action to declare supported systems inoperable upon discovery of the inoperability of redundant required features concurrent with DG inoperability, with a Completion Time of 4 hours. During the time that the 2AB EOG was determined to be inoperable, there were instances where supported systems should have been declared inoperable. Therefore, during these instances, as well as the 5 instances that 2CD EOG was INOPERABLE for surveillance and maintenance activities, the identified condition is reportable per 10 CFR 50.73(a)(2)(v) as an Event or Condition which could have prevented the fulfillment of a Safety Function for Unit 2. COMPONENT 2-DGAB-DRU - 2AB EOG DRU | ML25086A101
Quad Cities Nuclear Power Station | Unit 1 | Control Room Emergency Ventilation Air Conditioning System Inoperable Due to a Logic Issue | 03-27-2025 | On 01/26/2025 at 14:50, the Control Room Emergency Ventilation (CREV) Air Conditioning (AC) system was declared inoperable due to a trip of the Refrigeration Condensing Unit (RCU) feed breaker. Technical Specification (TS) 3. 7.5 Condition A was entered at that time. Control Room operators discovered that the indicating light for the RCU was not lit. An operator was dispatched and found that the feed breaker had tripped. After post maintenance testing of the breaker, TS 3.7.5 Condition A was exited on 02/07/2025 at 00:30. Initial troubleshooting narrowed down to two potential causes which includes breaker failure and loose breaker wiring. The causal product identified a design vulnerability where a simultaneous failure of a pressure switch and time delay relay could also cause the issue. The first two causes were addressed by breaker inspection and overhaul. The final cause will be addressed by replacement of a time delay relay and low suction pressure switch. This is being reported in accordance with 10 CFR 50. 73(a)(2)(v)(D), any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. NRC FORM 366A (04-02-2024) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 /rllll\oc,<.r,O: f~J·} LICENSEE EVENT REPORT (LER) ,~ CONTINUATION SHEET ..... (See NUREG-1022, R.3 for instruction and guidance for completing this form http:1/www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D 1. FACILITY NAME • 050 Quad Cities Nuclear Power Station Unit 1 • 052 | PLANT AND SYSTEM IDENTIFICATION Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate lo the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to lnfocollecls.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclea,- Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of infom1ation unless the document requesting or requiring the collection displays a currently valid 0MB control number. 2. DOCKET NUMBER YEAR 00254 2024 - 3. LE R NUMBER SEQUENTIAL NUMBER 002 REV NO. 00 General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Control Room Emergency Ventilation Air Conditioning System Inoperable Due to a Logic Issue A. CONDITION PRIOR TO EVENT Unit: 1 Reactor Mode: 1 Event Date: January 26, 2025 Mode Name: Power Operation Event Time: 1450 hours CST Power Level: 91% No systems, structures, or components that were inoperable at the start of the event contributed to the event. B. DESCRIPTION OF EVENT On January 26, 2025, at 14:50, Operations identified that there was no indicating light for the Control Room Emergency Ventilation (CREV)[VI] Refrigeration [RFU] Condensing Unit (RCU) 0-9400-102 on the Main Control Room (MCR)[NA] Panel 912-5. An operator was dispatched and found that local indications also showed the RCU to have no power and the breaker [BKR] in a tripped condition. The station entered Technical Specification (TS) 3.7.5 Condition A for an inoperable CREV Air Conditioning (AC) [ACU] system. ENS Notification #57515 was made in accordance with 10 CFR 50.72(b)(3)(v)(D) for any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. The CREV RCU is known to start with a high inrush of current. This was previously attributed to a "double start" condition where it would start once and then within seconds start again. Between 2009 and 2012, numerous trips of the CREV RCU breaker occurred. To eliminate these events a modification was installed in 2009 to add a time delay relay to the low suction pressure switch. The modification was to eliminate/reduce the number of "double starts" on the compressor and reduce the breaker tripping. In addition, the breaker dial setting was changed in 2012 from 8.1 to 9.4 to provide additional margin in the breaker trip setting. All these previous events and changes to the logic and breaker settings have made the system more robust over time. Between 2012 and 2020, and again after 2020, there were no CREV RCU breaker trip events. Because the CREV AC system is a single train system, this report is submitted in accordance with the requirements of 10 CFR 50.73(a)(2)(v)(D), which requires the reporting of an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. | ML25086A216
Grand Gulf Nuclear Station | Unit 1 | Manual Scram Due to Degraded Condenser Vacuum | 04-16-2025 | On February 15, 2025, at 2240 CT, Grand Gulf Nuclear Station, Unit 1 operators initiated a manual Reactor Protection System (RPS) actuation due to degrading condenser vacuum which resulted from a loss of seal steam. Rainwater intrusion had entered the enclosure building due to degraded roofing. The water entered a load control center which caused an overcurrent and loss of power in a static inverter. The loss of the static inverter resulted in a loss of seal steam that led to a degraded condenser vacuum. All control rods were fully inserted with no complications. The cause of the event was determined to be water intrusion due to degraded roofing of the enclosure building. This report is being made in accordance with 10 CFR 50.73(a)(2)(iv)(A) for any event that resulted in manual actuation of the RPS system. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Oflicer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond https://www_nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/QL) to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER [8J 050 YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 NUMBER NO. 00416 0 052 2025 001 00 | Plant Conditions: At the time of the event Grand Gulf Nuclear Station (GGNS), Unit 1 was in MODE 1 at 84 percent power. The Division 2 Emergency Diesel Generator was inoperable due to scheduled maintenance, and all other safety systems were operable. Description of Event: On February 15, 2025, rainwater intrusion entered the enclosure building due to degraded roofing. The water entered a load control center which caused an overcurrent and loss of power in a static inverter. At 2237 CT, the loss of power to the static inverter caused a loss of seal steam and degrading condenser vacuum. At 2240 CT, a manual Reactor Protection System (RPS) actuation was initiated due to degrading condenser vacuum. All control rods fully inserted, and there were no complications. Reportability: This report is being made in accordance with 1O CFR 50.73(a)(2)(iv)(A) for any event that resulted in manual actuation of the RPS system. Cause(s): The direct cause of the event was water intrusion due to degraded enclosure building roofing which entered the load control center and caused an overcurrent condition and loss of power to the static inverter. Corrective Actions: Completed Actions: -Restored the function of the enclosure building roof drains. -Replaced damaged Load Center Bus components Planned Actions: -Replace enclosure building roof. -Update preventative maintenance instructions for roof inspections to ensure that degradation is identified. -Review all single power source inverters to identify and correct any single point vulnerabilities. Safety Significance: There were no actual safety consequences associated with this condition. Plant systems responded as designed and the unit was brought to Mode 3 by Control Room Operators. Previous Similar Events: None identified. | ML25106A148
i | Unknown Unit | Inoperability of Keowee Hydroelectric Unit Due to Legacy Deficiencies in Generator Exciter Speed Switch Calibration Procedure Resulting in a Condition Prohibited by Technical Specifications | 04-21-2025 | On 2/20/2025, Keowee Hydroelectric Station Unit 1 (KHU-1) was determined to be inoperable based on observed generator excitation time exceeding design basis values. Troubleshooting determined that speed switches responsible for automatically initiating generator excitation during KHU startup were not fully calibrated following planned replacement on 2/18/2025 due to a legacy procedure deficiency and the scope of post-maintenance testing (PMT) was inadequate to detect the incomplete calibration. The switches removed on 2/18/2025 were reinstalled, correct excitation response timing verified, and KHU-1 was restored to operable on 2/21/2025. Planned corrective actions include speed switch calibration procedure revisions to correct the procedure deficiencies and PMT scope, reviews for similar deficiencies in other instrument procedures, and reviews for adequacy of PMT scope for other complex hardware configurable electronic devices. This event is reportable under 10 CFR 50.73(a)(2)(i)(B) as an Operation or Condition Prohibited by Technical Specifications. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION (04-02-2024) LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME Oconee Nuclear Station Unit 1 050 2. DOCKET NUMBER 00269 3. LER NUMBER YEAR 2025 SEQUENTIAL NUMBER - 001 REV NO. - 00 052 | Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. BACKGROUND At Oconee Nuclear Station (ONS), the Keowee Hydroelectric Station (KHS) [EK] serves the emergency power function typically performed by diesel generators [DG] at other nuclear facilities. The KHS consists of two (2) hydroelectric turbine/generator units (KHUs) and associated support equipment and auxiliaries. Each KHU is provided with its own automatic start equipment and both KHUs undergo simultaneous automatic emergency starts during an emergency. Emergency power can be provided to the main feeder buses (MFB)[EB] of any or all three ONS Units from the Keowee Hydroelectric Station via either of two emergency power paths: The Overhead Emergency Power Path, that includes the Unit¶s Start-up Transformer [XFMR] (CT-1, CT-2, or CT-3) on each ONS Unit The Underground Emergency Power Path, that includes Transformer CT-4 [XFMR] and both Standby Buses [EB]. Emergency onsite power may also be provided to the MFB of any or all three ONS Units from a Lee Combustion Turbine (LCT) [EK] on a dedicated 100kV transmission line through Transformer CT-5 [XFMR] via one or both Standby Buses. For any ONS Unit in Modes 1-4, Technical Specification (TS) 3.8.1 specifies that two KHUs be operable with one capable of automatically providing power through the Underground Emergency Power Path to both MFB via the Standby Bus and the other capable of automatically providing power through the Overhead Emergency Power Path to both MFB. An operable KHU and its required emergency power path are required to be able to provide sufficient power within specified limits of voltage and frequency within 23 seconds after an emergency start initiate signal. EVENT DESCRIPTION All times are Eastern Standard Time. On 2/18/2025, ONS Units 1, 2, and 3 were all in Mode 1 operating at approximately 100% full power, KHU-1 aligned as the Overhead KHU, and KHU-2 aligned as the Underground KHU. At 08:14, KHU-1 was removed from service for a planned maintenance outage. An item in the scope of the planned maintenance was planned replacement of speed switches in the KHU-1 generator exciter control circuit. These switches initiate generator field energization during KHU startup once the KHU reaches a preset speed. Following completion of maintenance and operational checks, KHU-1 was declared operable at 22:36. An alignment swap of the KHUs was completed at 23:09, resulting in KHU-1 being aligned as the Underground KHU and KHU- 2 being aligned as the Overhead KHU. During the normal operational check of KHU-1 performed on 2/18/2025 following maintenance, operators noted that KHU-1 generator excitation seemed to take longer than usual. However, no unexpected alarms were received. Operators continued to monitor performance of KHU-1 during normal commercial startups over the next few shifts. On 2/20/2025, Engineering was contacted to evaluate the KHU-1 startup performance. Data review indicated that a delay KHU-1 generator excitation ranged from approximately 50 seconds to as much as approximately 2 minutes during normal, non-emergency starts. Engineering confirmed that the excitation logic was the same for normal and emergency start and that, while KHU-1 continued to be capable of starting and supplying emergency power, the observed additional time delay challenged the ability of KHU-1 to meet the requirement to provide emergency power within 23 seconds of receipt of an emergency start signal. | ML25111A260
Limerick Generating Station | Unit 1 | Bypass Leakage on the B Train of Standby Gas Treatment System HEPA Filters Exceeded Technical Specification Value | 04-21-2025 | 12.Licensee Contact for this LER Licensee Contact Phone Number (Include area code) Jordan Rajan 610-718-3400 13.Complete One Line for each Component Failure Described in this Report Cause System Component Manufacturer Reportable to IRIS Cause System Component Manufacturer Reportable to IRIS A BH FLT A220 Yes 14. Supplemental Report Expected Month Day Year 15. Expected Submission Date □✔ No □ Yes (If yes, complete 15. Expected Submission Date) 16.(cid:3)Abstract (Limit to 1326 spaces, i.e., approximately 13 single-spaced typewritten lines) On February 19, 2025, at 08:40 the B (cid:85)(cid:83)ain of Standby Gas Treatment System (SGTS) was removed from service to test the charcoal adsorber and High-Efficiency Particulate Air (HEPA) filter banks. The test identified the as-found leakage for the upstream and downstream HEPA filter banks exceeded the Technical Specification (TS) leakage allowance. The HEPA filters were replaced, and the system was satisfactor(cid:74)(cid:77)y retested. This condition was reportable per 10 CFR 50.73(a)(2)(i)(B). The B(cid:1)(cid:85)(cid:83)(cid:66)(cid:74)(cid:79)(cid:1)(cid:80)(cid:71) SGTS was previously tested on March 19, 2020, and the as-found leakage was elevated. Since the leakage was close to the TS acceptance criteria, the issue was entered into the corrective action process. The HEPA filters exceeded the leakage criteria (cid:67)(cid:70)(cid:68)(cid:66)(cid:86)(cid:84)(cid:70)(cid:1)(cid:38)(cid:79)(cid:72)(cid:74)(cid:79)(cid:70)(cid:70)(cid:83)(cid:74)(cid:79)(cid:72)(cid:1)(cid:69)(cid:74)(cid:69)(cid:1)(cid:79)(cid:80)(cid:85)(cid:1)(cid:70)(cid:79)(cid:84)(cid:86)(cid:83)(cid:70)(cid:1)(cid:78)(cid:66)(cid:74)(cid:79)(cid:85)(cid:70)(cid:79)(cid:66)(cid:79)(cid:68)(cid:70)(cid:1)(cid:88)(cid:66)(cid:84)(cid:1)(cid:84)(cid:68)(cid:73)(cid:70)(cid:69)(cid:86)(cid:77)(cid:70)(cid:69)(cid:1)(cid:66)(cid:79)(cid:69)(cid:1)(cid:70)(cid:89)(cid:70)(cid:68)(cid:86)(cid:85)(cid:70)(cid:69)(cid:1)(cid:81)(cid:83)(cid:74)(cid:80)(cid:83)(cid:1)(cid:85)(cid:80)(cid:1)(cid:70)(cid:89)(cid:68)(cid:70)(cid:70)(cid:69)(cid:74)(cid:79)(cid:72)(cid:1)(cid:85)(cid:73)(cid:70)(cid:1)(cid:53)(cid:52)(cid:1) (cid:77)(cid:74)(cid:78)(cid:74)(cid:85). An action to perform post trending analysis will be added to the Surveillance Test package to ensure the filters do not exceed the TS leakage criteria before the next scheduled performance. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported /¥,...,..,.., .,,. ... lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. \ ~ . .i g CONTINUATION SHEET Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to ....... Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory ......+. . 0~ Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 YEAR SEQUENTIAL REV I I~ I I □ NUMBER NO. Limerick Generating Station Unit 1 352 D 052 2025 - I 001 - 00 I | Unit Condition Prior to the Event Unit 1 was in Operational Condition (OPCON) 1 (Power Operation) at approximately 100% power. Unit 2 was in Operational Condition (OPCON) 1 (Power Operation) at approximately 100% power. There were no other structures, systems or components out of service that contributed to this event. Description of the Event On February 19, 2025, at 08:40 the B (cid:87)rain of Standby Gas Treatment System (SGTS) [EIIS:BH] was removed from service to test the charcoal adsorber and High-Efficiency Particulate Air (HEPA) filter banks. Each SGTS train has two HEPA filter banks and a charcoal adsorber. The upstream HEPA filter bank removes radioactive particulates, while the charcoal adsorber removes gaseous iodine that may be present in the air stream. The downstream HEPA filter bank removes any carbon fines that may become entrained in the air stream after leaving the charcoal adsorber and providing redundant protection against failure of the upstream HEPA filter. (cid:47)(cid:72)(cid:68)(cid:78)(cid:68)(cid:74)(cid:72)(cid:3)(cid:80)(cid:88)(cid:86)(cid:87)(cid:3)(cid:69)(cid:72)(cid:3)(cid:79)(cid:72)(cid:86)(cid:86)(cid:3)(cid:87)(cid:75)(cid:68)(cid:81)(cid:3)(cid:19)(cid:17)(cid:19)(cid:24)(cid:3)(cid:83)(cid:72)(cid:85)(cid:70)(cid:72)(cid:81)(cid:87)(cid:3)(cid:87)(cid:82)(cid:3)(cid:80)(cid:72)(cid:72)(cid:87)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:55)(cid:72)(cid:70)(cid:75)(cid:81)(cid:76)(cid:70)(cid:68)(cid:79)(cid:3)(cid:54)(cid:83)(cid:72)(cid:70)(cid:76)(cid:73)(cid:76)(cid:70)(cid:68)(cid:87)(cid:76)(cid:82)(cid:81)(cid:3)(cid:11)(cid:55)(cid:54)(cid:12)(cid:3)(cid:79)(cid:76)(cid:80)(cid:76)(cid:87)(cid:3)(cid:73)(cid:82)(cid:85)(cid:3)(cid:76)(cid:81)(cid:3)(cid:83)(cid:79)(cid:68)(cid:70)(cid:72)(cid:3)(cid:83)(cid:72)(cid:81)(cid:72)(cid:87)(cid:85)(cid:68)(cid:87)(cid:76)(cid:82)(cid:81)(cid:3)(cid:68)(cid:81)(cid:71)(cid:3) (cid:79)(cid:72)(cid:68)(cid:78)(cid:68)(cid:74)(cid:72)(cid:3)(cid:87)(cid:72)(cid:86)(cid:87)(cid:76)(cid:81)(cid:74)(cid:3)(cid:82)(cid:73)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:43)(cid:40)(cid:51)(cid:36)(cid:3)(cid:73)(cid:76)(cid:79)(cid:87)(cid:72)(cid:85)(cid:3)(cid:69)(cid:68)(cid:81)(cid:78)(cid:86)(cid:17)(cid:3) The test identified the as-found leakage for the upstream HEPA filter bank was 0.11 percent and the as-found downstream HEPA filter bank leakage was 0.16 percent. The HEPA filters were replaced, and the system was retested. The system was declared operable on February 20, 2025, at 11:44. The B (cid:87)rain of SGTS was last tested on March 19, 2020. The as-found leakage of the upstream filter bank was 0.044 percent, and the as-found downstream HEPA filter bank was 0.046 percent. Since the leakage was close to the TS acceptance criteria, the issue was entered into the corrective action process. A note was added to the Issue Report (IR 4328138) stating the HEPA filters should be replaced prior to the next performance of the test. The exact time the B (cid:87)rain of SGTS was inoperable cannot be determined. (cid:37)(cid:68)(cid:86)(cid:72)(cid:71)(cid:3)(cid:82)(cid:81)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:79)(cid:72)(cid:68)(cid:78)(cid:68)(cid:74)(cid:72)(cid:3)(cid:80)(cid:72)(cid:68)(cid:86)(cid:88)(cid:85)(cid:72)(cid:71)(cid:3)(cid:76)(cid:81)(cid:3)(cid:21)(cid:19)(cid:21)(cid:19)(cid:3)(cid:68)(cid:81)(cid:71)(cid:3) (cid:87)(cid:75)(cid:72)(cid:3)(cid:68)(cid:86)(cid:16)(cid:73)(cid:82)(cid:88)(cid:81)(cid:71)(cid:3)(cid:79)(cid:72)(cid:68)(cid:78)(cid:68)(cid:74)(cid:72)(cid:3)(cid:80)(cid:72)(cid:68)(cid:86)(cid:88)(cid:85)(cid:72)(cid:71)(cid:3)(cid:76)(cid:81)(cid:3)(cid:21)(cid:19)(cid:21)(cid:24)(cid:15)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:79)(cid:72)(cid:68)(cid:78)(cid:68)(cid:74)(cid:72)(cid:3)(cid:79)(cid:76)(cid:78)(cid:72)(cid:79)(cid:92)(cid:3)(cid:72)(cid:91)(cid:76)(cid:86)(cid:87)(cid:72)(cid:71)(cid:3)(cid:73)(cid:82)(cid:85)(cid:3)(cid:74)(cid:85)(cid:72)(cid:68)(cid:87)(cid:72)(cid:85)(cid:3)(cid:87)(cid:75)(cid:68)(cid:81)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:55)(cid:54)(cid:3)(cid:68)(cid:70)(cid:70)(cid:72)(cid:83)(cid:87)(cid:68)(cid:81)(cid:70)(cid:72)(cid:3)(cid:70)(cid:85)(cid:76)(cid:87)(cid:72)(cid:85)(cid:76)(cid:68)(cid:3)(cid:73)(cid:82)(cid:85)(cid:3)(cid:74)(cid:85)(cid:72)(cid:68)(cid:87)(cid:72)(cid:85)(cid:3) (cid:87)(cid:75)(cid:68)(cid:81)(cid:3)(cid:86)(cid:72)(cid:89)(cid:72)(cid:81)(cid:3)(cid:71)(cid:68)(cid:92)(cid:86)(cid:17) Additionally, since the exact date the B (cid:87)rain of SGTS became inoperable cannot be determined, there were times that the A (cid:87)(cid:85)(cid:68)(cid:76)(cid:81)(cid:3)(cid:82)(cid:73)(cid:3)SGTS was (cid:79)(cid:76)(cid:78)(cid:72)(cid:79)(cid:92)(cid:3)inoperable while the B(cid:3)(cid:87)(cid:85)(cid:68)(cid:76)(cid:81)(cid:3)(cid:82)(cid:73) SGTS was also inoperable. The action for both SGTS trains being inoperable was not entered. This condition is reportable per 10 CFR 50.73(a)(2)(i)(B). Analysis of the Event The HEPA filters failed (cid:69)(cid:72)(cid:70)(cid:68)(cid:88)(cid:86)(cid:72)(cid:3)(cid:40)(cid:81)(cid:74)(cid:76)(cid:81)(cid:72)(cid:72)(cid:85)(cid:76)(cid:81)(cid:74)(cid:3)(cid:71)(cid:76)(cid:71)(cid:3)(cid:81)(cid:82)(cid:87)(cid:3)(cid:72)(cid:81)(cid:86)(cid:88)(cid:85)(cid:72)(cid:3)(cid:80)(cid:68)(cid:76)(cid:81)(cid:87)(cid:72)(cid:81)(cid:68)(cid:81)(cid:70)(cid:72)(cid:3)(cid:90)(cid:68)(cid:86)(cid:3)(cid:86)(cid:70)(cid:75)(cid:72)(cid:71)(cid:88)(cid:79)(cid:72)(cid:71)(cid:3)(cid:68)(cid:81)(cid:71)(cid:3)(cid:72)(cid:91)(cid:72)(cid:70)(cid:88)(cid:87)(cid:72)(cid:71)(cid:3)(cid:83)(cid:85)(cid:76)(cid:82)(cid:85)(cid:3)(cid:87)(cid:82)(cid:3)(cid:72)(cid:91)(cid:70)(cid:72)(cid:72)(cid:71)(cid:76)(cid:81)(cid:74)(cid:3) (cid:87)(cid:75)(cid:72)(cid:3)(cid:55)(cid:54)(cid:3)(cid:79)(cid:76)(cid:80)(cid:76)(cid:87)(cid:17) (cid:3)The issue report for the degraded high HEPA filter bank leakage was not flagged as system health issue and the subsequent reviews did not identify the challenge to the TS limit. | ML25111A262
Browns Ferry Nuclear Plant | Unit 3 | Reactor Coolant System Pressure Boundary Leakage Identified from Recirculation System Small Bore Piping | 04-24-2025 | On June 3, 2024, an increase in Browns Ferry (BFN) Unit 3 Drywell Unidentified Leakage was identified. This condition was monitored and trended from June 3, 2024, to October 4, 2024. The unidentified leakage came from two different sources. Prior to shutdown, total drywell unidentified leakage was approximately 1.0 gallon per minute. On October 5, 2024, at 0456, during the initial drywell entry of BFN Unit 3 Planned Outage 13 for replacement of a suspected defective fuel bundle, the drone operator observed water leaking from the elbow near the 1-inch sensing line off the 3B recirculation pump. In addition to this, the drone operator also observed water leaking from near the 3A recirculation pump vent line on a 3/4-inch elbow. The direct cause of the code class boundary leakage were cracks in two socket welds. The corrective actions for the direct cause were to replace the small bore piping elbows. The apparent cause was high-cycle fatigue. The corrective actions to address this are to implement modifications on the 3A and 3B Recirculation Pump Vent and Seal Vent Line Piping and sensing lines. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ☒ 050 SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 3 00296 NUMBER NO. ☐ 052 2024 - 004 - 01 | I. Plant Operating Conditions before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN) Unit 3 was in Mode 4 at 0 percent power. II. Description of Event A. Event Summary On June 3, 2024, an increase in BFN Unit 3 Drywell Unidentified Leakage was identified. This condition was monitored and trended from June 3, 2024, to October 4, 2024. The unidentified leakage came from two different sources. Prior to shutdown, total drywell unidentified leakage was approximately 1.0 gallons per minute (gpm). On October 21, 2024, Tennessee Valley Authority (TVA) completed a Past Operability Evaluation (POE). Technical Requirements Manual (TRM) Limiting Condition of Operability (LCO) 3.4.3, Structural Integrity states that the structural integrity of American Society of Mechanical Engineers (ASME) Code Class 1, 2, and 3 equivalent components shall be maintained in accordance with Technical Specification Requirement (TSR) 3.4.3.1 and TSR 3.4.3.2 throughout the life of the plant. Technical Specification (TS) 3.4.4 LCO (a) states that Reactor Coolant System (RCS) operational leakage shall be limited to no pressure boundary leakage while in Modes 1, 2, and 3. The structural integrity of the Reactor Coolant Pressure Boundary (RCPB) was inoperable for both TRM LCO 3.4.3 and TS LCO 3.4.4 (a) due to the cracks in the 1-inch elbow on the high pressure side sensing line for 3-PDT-068-0082 (BFN-3-VTV-068-0255) and the 3/4-inch recirculation pump vent elbow weld, which are both ASME Code Class 2 pipes. The starting date of inoperability is June 3, 2024, when Unit 3 showed an increase in Drywell Unidentified Leakage, and the ending date is October 5, 2024, when Unit 3 shutdown for BFN Unit 3 Planned Outage 13 (F313) and the sources of the leaks were discovered. The Tennessee Valley Authority is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant’s Technical Specifications. | ML25114A051
Limerick Generating Station | Unit 2 | HPCI Valve Isolated During a Surveillance Test Due to a Degraded Test Connector | 05-02-2025 | On March 03, 2025, at 10:44 during planned surveillance testing, the High Pressure Coolant Injection (HPCI) system Turbine Exhaust Line Vacuum Breaker Outboard primary containment isolation valve (PCIV) closed. The valve closed due to a degraded cannon plug connector that caused a short within the Emergency Core Cooling System (ECCS) Contact Test Unit being used for the test. The test equipment was removed, and the valve was re-opened. This event is being reported because it resulted in an unplanned inoperability of a single train safety system that could have prevented fulfillment of a safety function. An eight (8) hour ENS notification was completed on March 03, 2025, at 18:09 (ENS 57582). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024> Estimated burden per response to oomply with this mandatory collection request: 00 tiours. Reported lesso11S learned are incorporated into the licensing process and red back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to Ille FOIA, Library, and lnfonmatioo Collecllons Brandl (T-6 A1 0Ml, U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resourte@nrc.gov, and the 0MB reviewer al: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nudear Regulatory Commission, 72517th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor. and a person is not required lo http:l/www.nrc govtreadjng-rmtdoc-collectionslnuregs/staff/sr10221r3/l respond to, a collection of information unless the document requesting or requiring Ille collection displays a C1Jrrenlly valid 0MB conlrol number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ~------------~oo 050 r:Y:E:A:R7 SEQUENTIAL REV ~-I NUMBER 1-NO0. Limerick Generating Station, Unit 2 I □ 052 353 I 001 | Unit Condition Prior to the Event Prior to the event, Unit 2 was in Operational Condition (OPCON) 1 (Power Operation) at approximately 100% power. There were no other structures, systems, or components out of service that contributed to this event. Description of the Event On March 03, 2025, a surveillance test was being conducted for Unit 2 High Pressure Coolant Injection (HPCI) System (BJ] to verify that the HPCI logic circuit actuated on a simulated HPCI Steam Supply Pressure- Low signal. At 10:44, the HPCI Turbine Exhaust Line Vacuum Breaker Outboard primary containment isolation valve (PCIV) closed and the HPCI system was declared inoperable. The test was aborted by removing the ECCS Contact Test Unit (test box), resetting the isolation, and restoring operability of the system. The HPCI System was returned to service on March 03, 2025, at 13:51. An eight (8) hour ENS notification (57582) was completed on March 03, 2025, at 18:09 hours. Analysis of the Event The HPCI System was operable during the performance of the instrument testing. The Limerick Technical Specifications allows the system to remain operable for up to eight hours during the instrument testing provided at least one operable channel in the same trip system is monitoring that parameter. During the instrument testing, when the isolation signal was actuated (Low Steam Line Pressure) the HPCI Turbine Exhaust Line Vacuum Breaker Outboard PCIV closed rendering HPCI inoperable. Immediately following the isolation, the ECCS Contact Test Unit was removed from the HPCI System circuit by unplugging the cannon plug from the panel. Resistance checks were performed of the unit and one electrical short circuit was found. This electrical short circuit resulted in the closure of HPCI Turbine Exhaust Line Vacuum Breaker Outboard PCIV. Safety Consequence There was no actual safety consequences associated with this event and the potential safety consequences of this event were minimal. The Reactor Core Isolation {RCIC) System, Automatic Depressurization System (ADS), Residual Heat Removal (RHR) System, and Core Spray (CS) System remained operable during the period that HPCI was inoperable. This condition resulted in a loss of safety function for the HPCI System and is reportable per 10 CFT 50. 73(a)(2)(v)(D). Cause of the Event The cannon plug connector was degraded resulting in a short within the ECCS Contact Test Unit. | ML25122A139
Grand Gulf Nuclear Station | Unit 1 | Automatic Emergency Diesel Generator Actuation Caused by Grid Transient | 05-13-2025 | On March 15, 2025, Grand Gulf Nuclear Station (GGNS), Unit 1 was in MODE 1 at 100 percent power with all safety systems operable. At 12:48 CDT, a grid transient caused the 17AC breaker to trip open. In response, the division Ill emergency diesel generator automatically started and repowered the 17 AC safety-related electrical bus as designed. The grid transient was caused by degraded voltage of the offsite grid. The 17 AC breaker was successfully closed after the grid transient with no further issues. No other safety systems actuated, and no radiological release occurred. All remaining offsite power sources remained energized. This report is being made in accordance with 10 CFR 50.73(a)(2)(iv)(A) for any event that resulted in automatic actuation of an emergency diesel generator. NRC ,F,O RM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024..). .... Estimated b'urden per response to comply with this mandatory collection request: 80 hours. Reported , lessons learned are incorporated into the licensing process and fed back to industry. Send comments f~'\ LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. \~.... , ~ . l CONTINUATION SHEET N ln u fo c c le o a ll r e cts R .R e e g s u o la u t r o c r e y @ nr C c. o g m ov m , i a ss n i d on t , h e 0 W M a B s h r i e n v g i t e o w n e , r a D t: C 0 MB 2 0 O 5 f 5 fi 5 ce -0 0 o 0 f 1 In , form or a tion b y a nd e R -m eg a u il lator t y o Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRG may not conduct or sponsor, and a person is not required to respond https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LEA NUMBER C8l 050 YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 NUMBER NO. 00416 □ 052 2025 002 00 | Plant Conditions: At the time of the event Grand Gulf Nuclear Station (GGNS), Unit 1 was in MODE 1 at 100 percent power and all safety systems were operable. Description of Event: On March 15, 2025, at 12:48 CDT, a grid transient caused the 17AC breaker to trip open. In response, the division Ill emergency diesel generator (EOG) automatically started and repowered the 17A C safety-related electrical bus as designed. No other safety systems actuated, and no radiological release occurred. All remaining offsite power sources remained energized. Reportability: This report is being made in accordance with 10 CFR 50.73(a)(2)(iv)(A) for any event that resulted in automatic actuation of an emergency diesel generator. Cause(s): A degraded voltage of the offsite grid caused the event to occur. Corrective Actions: Completed Actions: - After the grid transient passed, the 17A C offsite source feeder breaker was successfully closed in and the division Ill EOG was secured with no further issues. Safety Significance: There were no actual safety consequences associated with this condition. Plant systems responded as designed and the plant remained at 100 percent power. Previous Similar Events: None identified. NRG FORM 366A (04-02-2024) Page 2 of 2 | ML25133A192
Edwin I. Hatch Nuclear Plant | Unit 2 | 2A Emergency Diesel Generator Inoperable Due to Inadvertent Overspeed Trip | 05-23-2025 | The 2A Emergency Diesel Generator (EDG) unexpectedly tripped during a test on 2/13/2025, due to its emergency overspeed switch (EOS) falsely signaling an overspeed condition. An initial investigation and operability review found no firm evidence suggesting that the 2A EDG was unable to perform its safety function prior to the trip. Subsequently, the EOS was replaced, the 2A EDG successfully completed its operability surveillance on 2/15/2025, and the original EOS was sent off for failure analysis. On 3/26/2025, at 14:53 EDT, Unit 2 was operating at approximately 22 percent power in MODE 1 when results from the failure analysis of the EOS for the 2A EDG were received. Contrary to the findings of the initial investigation and operability review, the analysis revealed that the condition experienced with the EOS during the 2/13/2025 test most likely caused the 2A EDG to be inoperable longer than allowed by Technical Specifications (TS). Additionally, during the time period the 2A EDG was inoperable, the 1B EDG was tagged out in support of planned maintenance for the standby plant service water pump resulting in two EDGs being inoperable for Unit 2 longer than allowed by TS. Having two EDGs inoperable for the same unit resulted in an event or condition that could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/l displays a currently valid 0MB control number. ~1. FAC-ILITY- NAM-E ------~ ~ 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV Edwin I. Hatch Nuclear Plant Unit 2 00366 □ NUMBER NO. ~-I 1-G □ 052 I 002 I | EVENT DESCRIPTION The 2A Emergency Diesel Generator (EOG) (EIIS: DG) unexpectedly tripped during a test on 2/13/2025, due to its emergency overspeed switch (EOS) falsely signaling an overspeed condition. An initial investigation and operability review found no firm evidence suggesting that the 2A EOG was unable to perform its safety function prior to the trip. Subsequently, the EOS was replaced, the 2A EOG successfully completed its operability surveillance on 2/15/2025, and the original EOS was sent off for failure analysis. On 3/26/2025, at 14:53 EDT, Unit 2 was operating at approximately 22 percent power in MODE 1 when results from the failure analysis of the EOS for the 2A EOG were received. Contrary to the findings of the initial investigation and operability review, the analysis revealed that the condition experienced with the EOS during the 2/13/2025 test most likely caused the 2A EOG to be inoperable from 6/6/2024, the date the EOS was installed, to when the 2A EOG successfully completed its operability surveillance on 2/15/2025, which is longer than allowed by Technical Specifications {TS) 3.8.1.B. Additionally, while reviewing the 2A EOG EOS trip event, it was discovered that the 1 B EOG {EIIS: DG) was tagged out for eighteen hours and forty-nine minutes in support of planned maintenance for the standby plant service water pump on 6/21/2024, during the same time the 2A EOG was inoperable. The overlapping time of the inoperabilities of the 2A EOG and the 1 B EOG resulted in two EDGs being inoperable for Unit 2 longer than allowed by TS 3.8.1.F. Having two EDGs inoperable for the same unit resulted in an event or condition that could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident. FAILED COMPONENTS Name: Emergency Overspeed Switch (EOS) Master Parts List Number: N/A; the EOS is a subcomponent of the 2A EOG (2R43S001A) Manufacturer: Honeywell Model: BZE6-RQ Type: Limit Switch EVENT CAUSE ANALYSIS Analysis showed that a loose retaining nut on the EOS impacted switch operation and caused the EOS to falsely signal an overspeed condition during the 2/13/2025 test. The EOS installed near the actuation point also contributed to the inadvertent trip of the 2A EOG. SAFETY ASSESSMENT There were no actual safety consequences as a result of these events. However, while the 2A EOG was inoperable, both the 2C EOG and the 1 B swing EOG remained operable for Unit 2, except when TS surveillances were performed and when the 1 B EOG was required to be tagged out for eighteen hours and forty-nine minutes on 6/21/24 in support of planned maintenance for the standby plant service water pump. Due to the 2A EOG being inoperable longer than allowed by TS and the overlapping time of the inoperabilities of the 2A EOG and the 1 B EOG, resulting in two EDGs being inoperable for Unit 2 longer than allowed by TS, the completion times of TS 3.8.1.B and TS 3.8.1.F were not met. Additionally, the completion time associated with TS 3.8.1.H to be in MODE 3 in 12 hours was also not met. Therefore, these events are reportable as conditions prohibited by TS per 10 CFR 50.73(a)(2)(i)(B). Additionally, having the 2A EDG and the 18 EDG simultaneously inoperable on the same unit is a condition that could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident and is, therefore, reportable per 10 CFR 50.73(a)(2)(v)(D). | ML25143A260
Browns Ferry Nuclear Plant | Unit 3 | Automatic Reactor Scram Following Main Generator Trip | 05-29-2025 | On February 8, 2025, at 2248 Central Standard Time, while at approximately 70 percent rated thermal power, Unit 3 experienced a main generator trip causing an automatic reactor scram. Plant equipment responded as expected and Unit 3 was transitioned to Mode 4. The Unit 3 isophase bus electrical fault was most likely initiated by a combination of particulate buildup on standoff insulators and elevated humidity. The root cause of the event was that the station failed to maintain an adequate maintenance strategy for the bus duct system due to perceived system reliability. Repairs were made to the main generator bus which allowed the reactor to restart and sync to the electrical grid on March 6, 2025. Actions planned include revising the applicable Preventive Maintenance items and procedure to inspect and clean all insulators and ensure proper grounding connections. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME ☒ 050 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 3 00296 NUMBER NO. ☐ 052 2025 - 001 - 01 | I. Plant Operating Conditions before the Event At the time of this event, Browns Ferry Nuclear Plant (BFN) Unit 3 was in Mode 1 at approximately 70 percent Rated Thermal Power (RTP). II. Description of Event A. Event Summary On February 8, 2025, at 2248 Central Standard Time (CST), while at approximately 70 percent RTP, BFN Unit 3 experienced a main generator [EL] trip causing an automatic reactor scram [JC]. Plant equipment responded as expected and Unit 3 was transitioned to Mode 4. During the scram response, there was a valid actuation of the Primary Containment Isolation System (PCIS) [JM] Groups 2, 3, 6, and 8. Upon receipt of these signals, components actuated as required. A loss of power to the 3EA and 3EB 4KV shutdown boards resulted in a valid actuation of the 3A and 3B emergency diesel generators (EDGs) [EK] which successfully re-energized the boards as designed. The Tennessee Valley Authority (TVA) is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(iv)(A), as an automatic actuation of the Reactor Protection System (RPS), the PCIS, and the EDGs. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components whose inoperability contributed to this event. | ML25149A021
Monticello Nuclear Generating Plant | Unknown Unit | Low Pressure Coolant Injection Inoperable Due To Motor Valve Failure | 05-30-2025 | On June 28, 2024 at 0110 CDT, Monticello Nuclear Generating Plant was in Mode 1 at 100 percent power and performing OSP-RHR-0556 “Residual Heat Removal (RHR) Water Fill Verification” Technical Specification Surveillance Procedure. When the RHR Low Pressure Coolant I Injection (LPCI) Motor Valve MO-2012 "RHR Division 1 LPCI Injection Outboard Valve" was attempted to be cycled, the Outboard Motor I Valve opened approximately one inch then stopped. With the Outboard Motor Valve incapable of opening, the A LPCI injection path was inoperable for injection as an Emergency Core Cooling system; and due to the plant design of the LPCI Loop Select Logic, this rendered both I subsystems of LPCI inoperable. Subsequent evaluation determined that the Outboard Motor Valve was considered inoperable when it was I configured closed based on the potential to have Reactor pressure on the inboard side of the valve due to leakage past the associated RHR I Division 1 LCPI Injection Inboard Motor Valve. I The cause of the event was that the Outboard Motor Valve's motor pinion was not secured to the motor shaft because an incorrect-sized set screw was installed. The shorter motor pinion set screw relaxed, allowing the motor pinion to move axially along the motor shaft until it no longer engaged the worm shaft clutch gear. I On June 29, 2024, the Outboard Motor Valve's motor pinion was adjusted back into position on the motor shaft. On August 7, 2024, the I incorrect motor pinion set screw on the Outboard Motor Valve was replaced with the correct set screw. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 YEAR SEQUENTIAL REV NUMBER NO. Monticello Nuclear Generating Plant 263 I 2024 052 - 002 - 01 | EVENT DESCRIPTION On June 28, 2024 at 0110 CDT, Monticello Nuclear Generating Plant (MNGP) was in Mode 1 at 100 percent power and performing OSP-RHR-0556 “Residual Heat Removal (RHR) Water Fill Verification” Technical Specification Surveillance Procedure. When the RHR Low Pressure Coolant Injection (LPCI) [EIIS CODE: BO] Motor Valve MO-2012 “RHR I Division 1 LPCI Injection Outboard Valve” was attempted to be opened via the control room hand switch, the Outboard I Motor Valve opened approximately one inch then stopped. With the Outboard Motor Valve incapable of opening, the A LPCI injection path was inoperable for injection as an Emergency Core Cooling system; and due to the plant design of the LPCI Loop Select Logic, this rendered both subsystems of LPCI inoperable. Specifically, if the B Recirc loop was I determined to be broken, the automatic logic would be incapable of opening the path to the A LPCI injection path and I neither division would automatically inject. Subsequent evaluation determined that the Outboard Motor Valve was I inoperable when it was configured closed based on the potential to have Reactor pressure on the inboard side of the I valve due to leakage past the associated Inboard Motor Valve MO-2014 "RHR Division 1 LCPI Injection Inboard valve." This event is reportable per 10 CFR 50.73(a)(2)(i)(B) for a condition prohibited by Technical Specifications and 10 CFR I 50.73(a)(2)(v)(B) and 10 CFR 50.73(a)(2)(v)(D) for an event or condition that could have prevented the fulfillment of a I safety function of structures or systems that are needed to remove residual heat and mitigate the consequences of an accident based on the safety function at the RHR LPCI system level. This issue was evaluated for a Safety System Functional Failure (SSFF) in accordance with NEI 99-02. This event is a Safety System Functional Failure (SSFF) due to meeting reporting criteria per 10 CFR 50.73(a)(2)(v)(B) and 10 CFR 50.73(a)(2)(v)(D). DATES AND APPROXIMATE TIMES OF MAJOR OCCURANCES I • October 18, 2023 at 1407 CDT: The Outboard Motor Valve was closed due to leakage past the Inboard Motor Valve. I I • October 22, 2023 at 0207 CDT: The required completion time to be in Mode 3 due to Technical Specification 3.5.1 Condition F, as directed by Condition D. I I • November 15, 2023 at 1619 CST: The Outboard Motor Valve was opened. I • April 14, 2024 at 1455 CDT: The Outboard Motor Valve was closed due to leakage past the Inboard Motor Valve. I • April 18, 2024 at 0255 CDT: The required completion time to be in Mode 3 due to Technical Specification 3.5.1 I Condition F, as directed by Condition D. I • June 27, 2024 at 2158 CDT: Technical Specification 3.5.1 Condition D entered for Technical Specification I Surveillance Procedure OSP-RHR-0556. I • June 28, 2024 at 0110 CDT: Event Date. The Outboard Motor Valve was incapable of fully opening during Technical I Specification Surveillance Procedure SP-RHR-0556. I • June 29, 2024 at 1533 CDT: Technical Specification 3.5.1 Condition D exited following completion of maintenance on the Outboard Motor Valve. I I • August 05, 2024: Identification that the adjustment made to the Outboard Motor Valve’s motor pinion, completed on June 29, 2024, should not have been possible if the motor pinion had been installed per the vendor technical I manual. I • August 07, 2024 at 0500 CDT: Technical Specification 3.5.1 Condition B and D entered for investigation of and I repairs to the Outboard Motor Valve. I • August 08, 2024 at 1058 CDT: Technical Specification 3.5.1 Condition B and D exited following installation of the I correct motor pinion set screw on the Outboard Motor Valve. I I • April 03, 2025: Determination that the Outboard Motor Valve should have been considered inoperable when it was I configured closed with the incorrect motor pinion set screw and had the potential to have Reactor pressure on the I inboard side of the valve due to leakage past the Inboard Motor Valve. NR C FORM 366A (04-02-2024) Page 2 of 4 | ML25150A333
Quad Cities Nuclear Power Station | Unit 1 | Loss of Suppression Chamber Vacuum Breaker Safety Function due to Configuration Control Error | 06-04-2025 | On 04/05/2025 at 04:00, Operations determined that a mispositioned manual isolation valve made both trains of Reactor Building to Suppression Chamber Vacuum Breakers simultaneously inoperable. The vacuum breaker inoperability could have prevented fulfillment of primary containment function following a design-basis accident with no operator intervention. The valve was not properly repositioned following refuel outage activities in March of 2025. The cause of the valve mispositioning was inadequate standards in Procedure Use and Adherence during refuel outage activities. Immediate corrective action was to open the isolation valve. Subsequent actions will be to make the valve a locked- open valve, to improve related procedures, and to provide training related to this event. This is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D), any event or condition that could have prevented the fulfillment of the safety function of systems needed to mitigate the consequences of an accident, and 1 O CFR 50.73(a)(2)(i)(B), any operation or condition prohibited by Technical Specifications. NRC FORM 366A (04-02-2024) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME ■ 050 Quad Cities Nuclear Power Station Unit 1 □ 052 | PLANT AND SYSTEM IDENTIFICATION Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and led back to industry. Send comments regarding burden estimate to the FOIA. Library. and lnlormation Collections Branch (T-6 A10M), U. S. Nuclear Regulatory Commission. Washington, DC 20555·0001, or by email to lnlocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office ol Information and Regulatory Aflairs, (3150-0104), Alln: Desk Ollicer for the Nuclear Regulatory Commission. 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection ol information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 2. DOCKET NUMBER YEAR 00254 2025 - 3. LE R NUMBER SEQUENTIAL NUMBER 004 REV NO. 00 General Electric - Boiling Water Reactor, 2957 Megawatts Thermal Rated Core Power Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. EVENT IDENTIFICATION Loss of Suppression Chamber Vacuum Breaker Safety Function due to Configuration Control Error A. CONDITION PRIOR TO EVENT Unit: 1 Reactor Mode: 1 Event Date: May 5, 2025 Mode Name: Power Operation Event Time: 0400 hours CST Power Level: 100% No systems, structures, or components that were inoperable at the start of the event contributed to the event. B. DESCRIPTION OF EVENT On 04/05/2025 at 04:00, Operations discovered that manual isolation valve [V] 1-1601-84B, U1 Torus Line 1- 1635B-1/2 inch LA Root Valve, was in the closed position. Closure of the 1-1601-84B (-84B) valve prevents operation of air operated Reactor Building to Suppression Chamber Vacuum Breakers [VACB][BF] 1-1601- 20A and 1-1601-20B, hereafter denoted as "the vacuum breakers." The -84B valve isolated differential pressure sensors [DPS] from the suppression pool atmosphere, subsequently preventing the operation of solenoid valves [PDSV] providing air to the vacuum breakers. Technical Specification {TS) 3.6.1.7, Reactor Building to Suppression Chamber Vacuum Breakers, Conditions C and E were entered for each vacuum breaker. Condition C is for one line with one or more reactor building to suppression chamber vacuum breakers inoperable for opening; Condition E is for two lines with one or more vacuum breakers inoperable for opening. The -84B valve was opened, and TS 3.6.1.7 was exited on 04/05/2025 at 0400. The vacuum breaker inoperability could have prevented fulfillment of primary containment function following a design-basis accident with no operator intervention. Additionally, the TS 3.6.1.7 Condition E Completion Time of 1 hour was not met based on the Required Action to restore vacuum breakers in one of two lines to operable status following entry into Mode 2. Also, TS Limiting Condition for Operation (LCO) 3.0.4 was not met when Mode 2 was entered without any specific allowances or risk assessments performed for the vacuum breaker inoperability related to TS 3.6.1.7. During the refuel outage, March 10, 2025, through April 1, 2025, Local Leak Rate Tests (LLRTs) and valve maintenance activities included closure of the -84B valve. At the conclusion of the as-left LLRT on 03/28/25, steps to open the -84B and other valves were annotated that they were to be left closed per the Unit Supervisor, with a Senior Reactor Operator (SRO) having an expectation that subsequent outage clearance order activities would later recover the desired valve position. No peer reviews were performed on the incomplete steps, nor were any verifications made related to the applicable clearance order, resulting in the isolation valves remaining closed the duration of the refuel outage. | ML25155A098
River Bend Station | Unit 1 | Human Performance Error Results in Manual Reactor Trip | 06-05-2025 | At 1607 CDT on April 8, 2025, with River Bend Station, Unit 1 operating in Mode 1 at 81 % power, control room operators responded to alarms received for a total loss of normal service water. The control room operators entered AOP-0009, Loss of Normal Service Water, and subsequently inserted a manual reactor trip. The direct cause of the loss of normal service water was the result of non-licensed operators failing to close SWP- MOV55A block valve, SWP-V3302, prior to post maintenance testing. Two causal factors were identified during the investigation: (1) Non-licensed operators did not appropriately apply human performance tools and verification practices when performing equipment protection tagout task; and, (2) Operations supervisor did not ensure adequate pre-job brief in accordance with EN-OP-102 and EN-HU-102 during briefing of equipment protection tagout installation - specifically, the risks involved if the work was performed incorrectly, stop-work criteria, and the key role of engagement by both performer and peer checker. This event is reportable in accordance with 10 CFR 50.73 (a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73 (a)(2)(iv)(B). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and lnfonmation Collection Branch (T-6 A1 OM), U S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of lnfonmation and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond https:/lwww.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) to, a collection of infonmation unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LERNUMBER ~ 050 YEAR SEQUENTIAL REV River Bend Station, Unit 1 NUMBER NO. 00458 0 052 2025 001 00 | Event Description At 1607 CDT on April 8, 2025, with River Bend Station (RBS), Unit 1 operating in Mode 1 at 81 % power, control room operators responded to alarms received for a total loss of normal service water [Bl]. The control room operators entered AOP-0009, Loss of Normal Service Water and subsequently inserted a manual reactor trip. The control room operators entered the appropriate post trip procedures and appropriately responded to the uncomplicated reactor trip. This event was reported on April 8, 2025, at 1911 EDT in accordance with 10 CFR 50.72(b)(2)(iv)(B) for reactor protection system actuation and 10 CFR 50.72(b)(3)(iv)(A) due to an expected reactor water level 3 isolation signal (EN 57655). Event Cause The direct cause of a loss of normal service water was the result of non-licensed operators failing to close SWP-V3302 [Bl:SHV], SWP-MOV55A block valve, prior to post maintenance testing. During post maintenance testing, maintenance personnel requested Operations to open SWP-MOV55A [Bl:ISV], Standby Cooling Tower Division 1 Return Isolation Valve, as the valve opened all normal service water pumps [Bl:P] received a low-pressure lockout condition due to an open flow path to the Standby Cooling Tower. Two causal factors were identified during the investigation: (1) Non-licensed operators did not appropriately apply human performance tools and verification practices when performing equipment protection tagout task; and, (2) Operations supervisor did not ensure adequate pre-job brief in accordance with EN-OP-102, Protective and Caution Tagging, and EN-HU-102, Human Performance Traps and Tools, during briefing of equipment protection tagout installation - specifically, the risks involved if the work was performed incorrectly, stop-work criteria, and the key role of engagement by both performer and peer checker. Safety Assessment The actual consequence of this human performance error was a loss of normal service water and a subsequent manual plant trip. Standby Service Water initiated as expected and Normal Service Water was restored 37 minutes after loss. There were no other actual consequences to general safety of the public, nuclear safety, industrial safety and radiological safety for this event. Corrective Actions Completed: • Performance management actions were taken with the operators involved in the event. In progress: • Operations Shift Managers perform standards reset blitz. • Create and implement verification challenge activity utilizing the simulator for non-licensed individuals. • Operations Management perform standards reset with Senior Reactor Operators on utilizing quizzing during reverse briefs/pre-job briefs to ensure operations clearly understand the risk, probability of one, all instructions, and components to be manipulated. The discussion will include "I own the risk" and risk presented by operator performance. Previous Occurrences No previous similar events at RBS have occurred within the past 5 years in which a component misposition results in a reactor trip. | ML25156A246
Cooper Nuclear Station 298 1 of 5 | Unknown Unit | Inoperable Diesel Generator Jacket Water Pump Results in Condition Prohibited by Technical Specifications | 06-06-2025 | On April 8, 2025, with Cooper Nuclear Station (CNS) reactor in Mode 1, Power Operation, scheduled monthly surveillance testing of Diesel Generator (DG) 1 was being performed. During this test, a low jacket water (DGJW) temperature alarm was received. Initial investigation identified that the DGJW pump may not be providing sufficient cooling water to the DG. DG1 was subsequently secured and declared inoperable. During disassembly of the DGJW pump on April 9, 2025, it was discovered that the pump impeller had slipped on the shaft. Repairs were made, subsequent testing performed satisfactorily, and Operations personnel declared DG1 operable. Investigation into the pump impeller failure identified the direct cause to be that the impeller to shaft fit with an inadequate fit during pump seal replacement on February 5, 2025. DG1 was determined to have been potentially inoperable from as early as February 5, 2025 until April 8, 2025, resulting in a past operation or condition prohibited by Technical Specifications and a condition that could have prevented the fulfillment of a safety function. Corrective actions include purchase of new impellers with correct tolerances and revision to Preventative Maintenance and Vendor Manual work instructions. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process LICENSEE EVENT REPORT (LER) and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104 ), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC (See NUREG-1022, R.3 for instruction and guidance for completing this form may not conduct or sponsor, and a person is not required to respond to, a collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER YEAR SEQUENTIAL REV Cooper Nuclear Station 05000-298 NUMBER NO. 2025 001 00 | PLANT STATUS Cooper Nuclear Station (CNS) was in Mode 1, Power Operation, at 100% power at the time the condition was discovered on April 8, 2025. Diesel Generator (DG) 1 was declared inoperable due to failure of the Diesel Generator Jacket Water (DGJW) [EIIS:LB] pump [EIIS:P] during the monthly operability test. BACKGROUND The purpose of the standby (emergency) Alternating Current (AC) power system [EIIS:EK] is to provide a single failure proof source of on-site AC power adequate for maintaining the safe shutdown of the reactor following abnormal operational transients and postulated accidents. This system consists of two independent AC power sources, the Emergency Diesel Generators (EOG) [EIIS:DG]. Each DG shall be capable of automatic start at any time and capable of continued operation at rated load, voltage, and frequency until manually stopped. During normal plant operations both DGs are in standby. A DG starts automatically on a loss of coolant accident (LOCA) signal (i.e., low reactor water level signal or high drywell pressure) or on loss of voltage on a critical bus or Loss of Offsite Power (LOOP) event. The DG automatically connects to its respective bus after off-site power is tripped as a consequence of critical bus loss of voltage or degraded voltage. Each DG has an associated DGJW subsystem. The DGJW subsystem is a closed recirculating water circuit containing treated demineralized water for engine cooling. It consists of a standpipe, an engine driven pump, a heat exchanger, a bypass pump, a heater and the associated piping and instrumentation. The DGJW subsystem is required to be operable to support the associated DG operability. CNS Technical Specifications (TS) require that two EDGs be operable when the plant is in Modes 1, 2, or 3, and that one DG be operable when the plant is in Modes 4 or 5. EVENT DESCRIPTION On April 8, 2025, with CNS reactor in Mode 1, Power Operation, scheduled monthly surveillance testing of DG1 was being performed. The engine started and loaded as expected per procedure, however, at full load, the jacket water low temperature alarm [EIIS:TA] was received. Upon reading local DG1 jacket water temperature indication, the jacket water entering the engine was approximately 82 degrees F and the outlet temperature was reading approximately 182 degrees F. Expected condition is for the inlet and outlet jacket water temperatures to converge between 162-166 degrees F. | ML25157A104
Columbia Generating Station | Unknown Unit | Pressure Boundary Leakage Resulting in a Technical Specification Required Plant Shutdown, Degraded Condition, and Condition Prohibited by Technical Specifications | 06-10-2025 | At 02:23 on April 12, with the unit in Mode 3 at 0 percent power, pressure boundary leakage was identified on the bonnet vent line elbow connection of the Reactor Recirculation (RRC) Pump 1B discharge isolation valve, RRC-V-67B. Leakage from the area was initially identified during a drywell entry at 15 percent reactor power and later confirmed as pressure boundary leakage during a subsequent entry in Mode 3. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(A) as a Plant Shutdown Required by Technical Specifications, 10 CFR 50.73(a)(2)(ii)(A) as a Degraded or Unanalyzed Condition that Resulted in the condition of the nuclear power plant, including its principal safety barriers being seriously degraded, and 10 CFR 50.73(a)(2)(i)(B) as an Operation or Condition Prohibited by Technical Specifications. There were no structures, systems, or components that were inoperable at the beginning of the event that contributed to the event. (cid:16)(cid:28)(cid:21)(cid:32)(cid:30)(cid:25)(cid:23)(cid:27)(cid:1)(cid:17)(cid:27)(cid:33)(cid:22)(cid:26)(cid:28)(cid:29)(cid:22)(cid:1)(cid:19)(cid:16)(cid:13)(cid:1) (cid:5)(cid:16)(cid:14)(cid:15)(cid:12) (cid:6)(cid:2)(cid:5)(cid:12)(cid:4)(cid:4)(cid:2)(cid:7)(cid:8)(cid:3)(cid:3)(cid:2)(cid:12)(cid:8)(cid:8)(cid:4)(cid:2)(cid:4)(cid:15)(cid:8)(cid:16)(cid:15)(cid:15)(cid:4) (cid:18)(cid:10)(cid:11)(cid:12) NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments . :/¥ 0-"''"•"'-<,. . . . LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. E i Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET 0 t -s," ......... . 0~ <> I A n f f f o a c ir o s l , l e ( c 3 t 1 s 5 .R 0- e 0 s 1 o 0 u 4 rc ), e A @ tt n n r : c . D go e v s , k a O n f d fi c th e e r f O or M t B he r e N v u ie c w le e a r r a R t: e g O u M lat B o r O y f C fic o e m o m f i I s n s f i o o r n m , a 7 t 2 io 5 n 1 a 7 n th d S R t e re g e u t l a N to W ry , (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER I I~ (cid:374) 050 YEAR SEQUENTIAL REV NUMBER NO. Columbia Generating Station 397 □ D 052 2025 - I 001 - 00 I | Description of events: (cid:36)(cid:87)(cid:3)(cid:19)(cid:21)(cid:29)(cid:21)(cid:22)(cid:3)(cid:82)(cid:81)(cid:3)(cid:36)(cid:83)(cid:85)(cid:76)(cid:79)(cid:3)(cid:20)(cid:21)(cid:15)(cid:3)(cid:21)(cid:19)(cid:21)(cid:24)(cid:15)(cid:3)(cid:76)(cid:81)(cid:3)(cid:48)(cid:82)(cid:71)(cid:72)(cid:3)(cid:22)(cid:15)(cid:3)(cid:68)(cid:3)(cid:79)(cid:72)(cid:68)(cid:78)(cid:3)(cid:76)(cid:81)(cid:3)(cid:82)(cid:81)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:69)(cid:82)(cid:81)(cid:81)(cid:72)(cid:87)(cid:3)(cid:89)(cid:72)(cid:81)(cid:87)(cid:3)(cid:79)(cid:76)(cid:81)(cid:72)(cid:3)(cid:72)(cid:79)(cid:69)(cid:82)(cid:90)(cid:3)(cid:70)(cid:82)(cid:81)(cid:81)(cid:72)(cid:70)(cid:87)(cid:76)(cid:82)(cid:81)(cid:3)(cid:82)(cid:73)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:53)(cid:72)(cid:68)(cid:70)(cid:87)(cid:82)(cid:85)(cid:3)(cid:53)(cid:72)(cid:70)(cid:76)(cid:85)(cid:70)(cid:88)(cid:79)(cid:68)(cid:87)(cid:76)(cid:82)(cid:81)(cid:3) (cid:11)(cid:53)(cid:53)(cid:38)(cid:12)(cid:3)(cid:83)(cid:88)(cid:80)(cid:83)(cid:3)(cid:20)(cid:37)(cid:3)(cid:71)(cid:76)(cid:86)(cid:70)(cid:75)(cid:68)(cid:85)(cid:74)(cid:72)(cid:3)(cid:76)(cid:86)(cid:82)(cid:79)(cid:68)(cid:87)(cid:76)(cid:82)(cid:81)(cid:3)(cid:89)(cid:68)(cid:79)(cid:89)(cid:72)(cid:15)(cid:3)(cid:53)(cid:53)(cid:38)(cid:16)(cid:57)(cid:16)(cid:25)(cid:26)(cid:37)(cid:3)(cid:62)(cid:36)(cid:39)(cid:16)(cid:44)(cid:54)(cid:57)(cid:64)(cid:3)(cid:90)(cid:68)(cid:86)(cid:3)(cid:76)(cid:71)(cid:72)(cid:81)(cid:87)(cid:76)(cid:73)(cid:76)(cid:72)(cid:71)(cid:3)(cid:68)(cid:86)(cid:3)(cid:83)(cid:85)(cid:72)(cid:86)(cid:86)(cid:88)(cid:85)(cid:72)(cid:3)(cid:69)(cid:82)(cid:88)(cid:81)(cid:71)(cid:68)(cid:85)(cid:92)(cid:3)(cid:79)(cid:72)(cid:68)(cid:78)(cid:68)(cid:74)(cid:72)(cid:17)(cid:3)(cid:47)(cid:72)(cid:68)(cid:78)(cid:68)(cid:74)(cid:72)(cid:3) (cid:73)(cid:85)(cid:82)(cid:80)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:68)(cid:85)(cid:72)(cid:68)(cid:3)(cid:90)(cid:68)(cid:86)(cid:3)(cid:76)(cid:81)(cid:76)(cid:87)(cid:76)(cid:68)(cid:79)(cid:79)(cid:92)(cid:3)(cid:76)(cid:71)(cid:72)(cid:81)(cid:87)(cid:76)(cid:73)(cid:76)(cid:72)(cid:71)(cid:3)(cid:71)(cid:88)(cid:85)(cid:76)(cid:81)(cid:74)(cid:3)(cid:71)(cid:85)(cid:92)(cid:90)(cid:72)(cid:79)(cid:79)(cid:3)(cid:72)(cid:81)(cid:87)(cid:85)(cid:92)(cid:3)(cid:68)(cid:87)(cid:3)(cid:20)(cid:24)(cid:3)(cid:83)(cid:72)(cid:85)(cid:70)(cid:72)(cid:81)(cid:87)(cid:3)(cid:85)(cid:72)(cid:68)(cid:70)(cid:87)(cid:82)(cid:85)(cid:3)(cid:83)(cid:82)(cid:90)(cid:72)(cid:85)(cid:3)(cid:82)(cid:81)(cid:3)(cid:36)(cid:83)(cid:85)(cid:76)(cid:79)(cid:3)(cid:20)(cid:20)(cid:15)(cid:3)(cid:21)(cid:19)(cid:21)(cid:24)(cid:15)(cid:3)(cid:68)(cid:81)(cid:71)(cid:3)(cid:79)(cid:68)(cid:87)(cid:72)(cid:85)(cid:3) (cid:70)(cid:82)(cid:81)(cid:73)(cid:76)(cid:85)(cid:80)(cid:72)(cid:71)(cid:3)(cid:68)(cid:86)(cid:3)(cid:83)(cid:85)(cid:72)(cid:86)(cid:86)(cid:88)(cid:85)(cid:72)(cid:3)(cid:69)(cid:82)(cid:88)(cid:81)(cid:71)(cid:68)(cid:85)(cid:92)(cid:3)(cid:79)(cid:72)(cid:68)(cid:78)(cid:68)(cid:74)(cid:72)(cid:3)(cid:71)(cid:88)(cid:85)(cid:76)(cid:81)(cid:74)(cid:3)(cid:68)(cid:3)(cid:86)(cid:88)(cid:69)(cid:86)(cid:72)(cid:84)(cid:88)(cid:72)(cid:81)(cid:87)(cid:3)(cid:72)(cid:81)(cid:87)(cid:85)(cid:92)(cid:3)(cid:76)(cid:81)(cid:3)(cid:48)(cid:82)(cid:71)(cid:72)(cid:3)(cid:22)(cid:17)(cid:3)Technical Specification (TS) (cid:47)(cid:76)(cid:80)(cid:76)(cid:87)(cid:76)(cid:81)(cid:74)(cid:3) (cid:38)(cid:82)(cid:81)(cid:71)(cid:76)(cid:87)(cid:76)(cid:82)(cid:81)(cid:3)(cid:82)(cid:73)(cid:3)(cid:50)(cid:83)(cid:72)(cid:85)(cid:68)(cid:87)(cid:76)(cid:82)(cid:81)(cid:3)3.4.5(cid:17)(cid:68)(cid:3)(cid:85)(cid:72)(cid:84)(cid:88)(cid:76)(cid:85)(cid:72)(cid:86)(cid:3)(cid:81)(cid:82)(cid:3)(cid:83)(cid:85)(cid:72)(cid:86)(cid:86)(cid:88)(cid:85)(cid:72)(cid:3)(cid:69)(cid:82)(cid:88)(cid:81)(cid:71)(cid:68)(cid:85)(cid:92)(cid:3)(cid:79)(cid:72)(cid:68)(cid:78)(cid:68)(cid:74)(cid:72)(cid:3)(cid:76)(cid:81)(cid:3)(cid:48)(cid:82)(cid:71)(cid:72)(cid:86)(cid:3)(cid:20)(cid:15)(cid:3)(cid:21)(cid:15)(cid:3)(cid:82)(cid:85)(cid:3)(cid:22)(cid:17)(cid:3)(cid:55)(cid:72)(cid:70)(cid:75)(cid:81)(cid:76)(cid:70)(cid:68)(cid:79)(cid:3)(cid:54)(cid:83)(cid:72)(cid:70)(cid:76)(cid:73)(cid:76)(cid:70)(cid:68)(cid:87)(cid:76)(cid:82)(cid:81)(cid:3) (cid:36)(cid:70)(cid:87)(cid:76)(cid:82)(cid:81)(cid:86) (cid:22)(cid:17)(cid:23)(cid:17)(cid:24)(cid:3)C(cid:17)(cid:20) (cid:68)(cid:81)(cid:71)(cid:3)(cid:38)(cid:17)(cid:21)(cid:3)(cid:85)(cid:72)(cid:84)(cid:88)(cid:76)(cid:85)(cid:72)(cid:3)(cid:87)he unit to be in Mode 3 within 12 hours and Mode 4 in 36 hours. The unit was in Mode 3 at the time(cid:3)of(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:72)(cid:89)(cid:72)(cid:81)(cid:87). Mode 4 was entered at 09:32 on April 12, 2025. Plant Conditions: At the time of the event, the plant was (cid:76)(cid:81)(cid:3)(cid:48)(cid:82)(cid:71)(cid:72)(cid:3)(cid:22)(cid:3)at (cid:19)(cid:3)percent po(cid:90)(cid:72)(cid:85). Energy Industry Identification System (EIIS) codes are identified as [XX]. Background: On 7/1/2023 (approximately 2 weeks after startup from the previous refueling outage) an indication was received that a Reactor Coolant System (RCS) [AB] leak existed wh(cid:72)(cid:81)(cid:3)(cid:69)(cid:82)(cid:87)(cid:75)(cid:3)Containment Monitoring System Radiation Ratemeters [IK(cid:16) (cid:48)(cid:55)(cid:53)] were reading higher than normal and tracking similarly. During this time Equipment Drain Radioactive (EDR) [WK] leakage and Floor Drain Radioactive (FDR) [WK] leakage, containment temperature, and containment pressure were steady and did not indicate a leak.(cid:3)Chemistry performed an isotopic analysis of a grab sample of the containment atmosphere which did not indicate leakage.(cid:3)(cid:44)(cid:81)(cid:3)(cid:45)(cid:88)(cid:79)(cid:92)(cid:3)2023, a Technical Issues Resolution Process was initiated to analyze trends indicating potential leaks in containment.(cid:3)(cid:44)(cid:81)(cid:3)(cid:36)(cid:88)(cid:74)(cid:88)(cid:86)(cid:87) 2023, an (cid:50)perational (cid:39)ecision-(cid:48)aking (cid:44)ssue (cid:11)(cid:50)(cid:39)(cid:48)(cid:44)(cid:12)(cid:3)was created to establish RCS leakage monitoring criteria and identify trigger points with actions. The leakage remained constant throughout the operating cycle and did not challenge the TS RCS Operational limits of 5 gallons per minute of unidentified leakage, or an increase of 2 gallons per minute over 24 hours of unidentified leakage. Root Cause: Vent piping attached to the bonnet of RRC-V-(cid:25)(cid:26)B was not designed to prevent high cycle fatigue. This resulted in cyclic fatigue of a weld on a 3/4-inch vent line from the RRC-V-67B socket welded connection. This is a legacy issue associated with the original design’s lack of dynamic analysis, or with the 1996 and 1997 GE analysis and testing of small-bore piping in support of Adjustable Speed Drive modifications. (cid:36)(cid:71)(cid:77)(cid:88)(cid:86)(cid:87)(cid:68)(cid:69)(cid:79)(cid:72)(cid:3)(cid:86)(cid:83)(cid:72)(cid:72)(cid:71)(cid:3)(cid:71)(cid:85)(cid:76)(cid:89)(cid:72)(cid:3)(cid:70)(cid:82)(cid:81)(cid:87)(cid:85)(cid:82)(cid:79)(cid:86)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:86)(cid:83)(cid:72)(cid:72)(cid:71)(cid:3)(cid:82)(cid:73)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:53)(cid:53)(cid:38)(cid:3)(cid:62)(cid:36)(cid:39)(cid:64)(cid:17)(cid:3) Safety Significance: The (cid:53)(cid:72)(cid:68)(cid:70)(cid:87)(cid:82)(cid:85)(cid:3)(cid:38)(cid:82)(cid:82)(cid:79)(cid:68)(cid:81)(cid:87)(cid:3)(cid:54)(cid:92)(cid:86)(cid:87)(cid:72)(cid:80)(cid:3)(cid:11)(cid:53)(cid:38)(cid:54)(cid:12)(cid:3)(cid:62)(cid:36)(cid:37)(cid:64)(cid:3)(cid:79)(cid:72)(cid:68)(cid:78) was (cid:76)(cid:81)(cid:76)(cid:87)(cid:76)(cid:68)(cid:79)(cid:79)(cid:92)(cid:3)estimated to be between 0.05 and 0.10 gallons per minute. While the leak remained below the TS RCS(cid:3)(cid:50)(cid:83)(cid:72)(cid:85)(cid:68)(cid:87)(cid:76)(cid:82)(cid:81)(cid:68)(cid:79)(cid:3)(cid:79)(cid:76)(cid:80)(cid:76)(cid:87)(cid:86)(cid:3)(cid:73)(cid:82)(cid:85)(cid:3)(cid:88)(cid:81)(cid:76)(cid:71)(cid:72)(cid:81)(cid:87)(cid:76)(cid:73)(cid:76)(cid:72)(cid:71)(cid:3)(cid:79)(cid:72)(cid:68)(cid:78)(cid:86)(cid:3)(cid:73)(cid:85)(cid:82)(cid:80)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:87)(cid:76)(cid:80)(cid:72)(cid:3)(cid:82)(cid:73)(cid:3)(cid:76)(cid:81)(cid:76)(cid:87)(cid:76)(cid:68)(cid:79)(cid:3)(cid:76)(cid:81)(cid:71)(cid:76)(cid:70)(cid:68)(cid:87)(cid:76)(cid:82)(cid:81)(cid:3)(cid:88)(cid:81)(cid:87)(cid:76)(cid:79)(cid:3) (cid:83)(cid:82)(cid:86)(cid:76)(cid:87)(cid:76)(cid:89)(cid:72)(cid:3)(cid:76)(cid:71)(cid:72)(cid:81)(cid:87)(cid:76)(cid:73)(cid:76)(cid:70)(cid:68)(cid:87)(cid:76)(cid:82)(cid:81), (cid:76)(cid:73)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:79)(cid:72)(cid:68)(cid:78)(cid:3)(cid:75)(cid:68)(cid:71)(cid:3)(cid:76)(cid:81)(cid:70)(cid:85)(cid:72)(cid:68)(cid:86)(cid:72)(cid:71)(cid:3)(cid:68)(cid:81)(cid:71)(cid:3)(cid:72)(cid:91)(cid:70)(cid:72)(cid:72)(cid:71)(cid:72)(cid:71)(cid:3)(cid:55)(cid:54)(cid:3)(cid:88)(cid:81)(cid:76)(cid:71)(cid:72)(cid:81)(cid:87)(cid:76)(cid:73)(cid:76)(cid:72)(cid:71)(cid:3)(cid:79)(cid:72)(cid:68)(cid:78)(cid:3)(cid:85)(cid:68)(cid:87)(cid:72)(cid:3)(cid:79)(cid:76)(cid:80)(cid:76)(cid:87)(cid:86)(cid:15)(cid:3)(cid:68)(cid:81)(cid:3)(cid:82)(cid:85)(cid:71)(cid:72)(cid:85)(cid:79)(cid:92)(cid:3)(cid:86)(cid:75)(cid:88)(cid:87)(cid:71)(cid:82)(cid:90)(cid:81)(cid:3)(cid:90)(cid:82)(cid:88)(cid:79)(cid:71)(cid:3) (cid:75)(cid:68)(cid:89)(cid:72)(cid:3)(cid:69)(cid:72)(cid:72)(cid:81)(cid:3)(cid:76)(cid:81)(cid:76)(cid:87)(cid:76)(cid:68)(cid:87)(cid:72)(cid:71)(cid:3)(cid:68)(cid:81)(cid:71)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:85)(cid:72)(cid:68)(cid:70)(cid:87)(cid:82)(cid:85)(cid:3)(cid:90)(cid:82)(cid:88)(cid:79)(cid:71)(cid:3)(cid:75)(cid:68)(cid:89)(cid:72)(cid:3)(cid:69)(cid:72)(cid:72)(cid:81)(cid:3)(cid:83)(cid:79)(cid:68)(cid:70)(cid:72)(cid:71)(cid:3)(cid:76)(cid:81)(cid:3)(cid:70)(cid:82)(cid:79)(cid:71)(cid:3)(cid:86)(cid:75)(cid:88)(cid:87)(cid:71)(cid:82)(cid:90)(cid:81)(cid:3)(cid:70)(cid:82)(cid:81)(cid:71)(cid:76)(cid:87)(cid:76)(cid:82)(cid:81)(cid:3)(cid:76)(cid:81)(cid:3)(cid:68)(cid:70)(cid:70)(cid:82)(cid:85)(cid:71)(cid:68)(cid:81)(cid:70)(cid:72)(cid:3)(cid:90)(cid:76)(cid:87)(cid:75)(cid:3)(cid:87)(cid:75)(cid:72)(cid:3)(cid:55)(cid:54)(cid:17)(cid:3) Immediate Corrective Actions: The RRC-V-67B weld leak was re(cid:83)(cid:68)(cid:76)(cid:85)(cid:72)(cid:71)(cid:17) | ML25161A146
Catawba Nuclear Station | Unit 1 | lnoperability of 1B Emergency Diesel Generator due to Fuel Oil Leak | 07-21-2025 | On 4/23/2025, Catawba Unit 1 was in Mode 1 operating at approximately 100 percent power. At 0248 hours, the 1B Emergency Diesel Generator (EOG) was started for a 24 hour surveillance. Approximately 11 hours into the surveillance a leak originated on the common fuel supply line under a compression fitting. The leak was estimated to be greater than 0.5 gpm and at 1457 hours the 1 B EOG was secured and declared inoperable at 1459 hours. Repairs were made and the 1B EOG was returned to service on 4/25/2025 at 0600 hours. Investigation revealed a circumferential crack located within a tubing fitting. The crack originated prior to the attempted 24 hour surveillance but was not through-wall and there was no indication of leakage. The crack propagated during the surveillance due to high cycle fatigue. The existence of the crack, even though no leakage was present, prior to the 24-hour surveillance is evidence that the 1B EOG was inoperable for a time longer than allowed by Technical Specifications. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) as operation or condition prohibited by Technical Specifications. There was no impact to the health and safety of the public. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04..02-2024) ...... Estimated burden per response to comply with this mandatory collection request: 80 ..,,.. hours. Reported lessons learned are incorporated into the licensing process and fed l.\ . LICENSEE EVENT REPORT (LER) back to industry. Send comments regarding burden estimate to the FOIA, Library, • II and Information Collections Branch (T-6 A10M), U. S. Nuclear Regulatory ~ ~ l CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by email to *••·· lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information (See NUREG-1022, R.3 for instruction and guidance for completing this form and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3D Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of 2. DOCKET NU~~ER - .s. • ;" ~~~ia·a -lililillilllilioiil . 1. - FA - CIL - ITY - N - AM - E -----------,I [lg 050 YEAR SEQUENTIAL REV 00413, 00414 ~ NUMBER NO. I-~ Catawba Nuclear Station, Units 1 and 2 0 □ -1 052 002 | BACKGROUND The following information is provided to assist readers in understanding the event described in this LER. Applicable Energy Industry Identification System [EIIS] and component codes are enclosed within brackets. Catawba's unique system and component identifiers are contained within parentheses. The onsite standby power source for each 4160 volt Engineered Safety Features (ESF) bus at Catawba is a dedicated EOG. For each unit, EDGs A and Bare dedicated to ESF buses ETA and ETB, respectively. Each EOG starts automatically on a Safety Injection signal (i.e., low pressurizer pressure or high containment pressure) or on an ESF bus degraded voltage or undervoltage signal. After the EOG has started, it will automatically tie to its respective bus after offsite power is tripped as a consequence of ESF bus undervoltage or degraded voltage, independent of or coincident with an SI signal. The EDGs will also start and operate in the standby mode without tying to the ESF bus on an SI signal alone. Following the trip of offsite power, a sequencer strips loads from the ESF bus. When the EOG is tied to the ESF bus, loads are then sequentially connected to its respective ESF bus by the automatic load sequencer. In the event of a loss of preferred power, the ESF electrical loads are automatically connected to the EDGs in sufficient time to provide for safe reactor shutdown and to mitigate the consequences of a Design Basis Accident such as a Loss of Coolant Accident (LOCA). There are also provisions to accommodate the connecting of the Emergency Supplemental Power Source (ESPS) to one train of either unit's Class 1E AC Distribution System. The ESPS consists of two 50% capacity non-safety related commercial grade EDGs. Manual actions are required to align the ESPS to the station and only one of the station's four onsite Class 1E Distribution System trains can be supplied by the ESPS at any given time. The ESPS is made available to support extended Completion Times in the event of an inoperable EOG as well as a defense-in-depth source of AC power to mitigate a station blackout event. The ESPS remains disconnected from the Class 1 E AC Distribution System unless required for supplemental power to one of the four 4.16 kV ESF buses. The primary purpose of the Diesel Fuel Oil System (FD) [DC] is to store and supply fuel to the diesel generators' engines for a period of operation of no less than seven days. Each diesel is equipped with two 45,000 gallon fuel oil storage tanks with a combined capacity sufficient to operate the diesel at full load for a period of no less than seven days, plus a margin to allow for periodic testing. Fuel oil is transferred by gravity from the storage tanks to the day tank which is located within retaining walls inside the Diesel Building. The day tank capacity is sufficient to operate the diesel generator engine for a minimum of 60 minutes at full load. The fuel oil is pumped from the day tank to the engine by an engine driven fuel oil pump. Excess fuel not consumed by the engine is returned to the day tank via the fuel return line. | ML25202A164
Edwin I. Hatch Nuclear Plant | Unit 1 | Unit 1 High Pressure Coolant Injection System Inoperable | 07-29-2025 | At 2137 EDT on 06/03/2025, while Unit 1 was operating at 98% power in MODE 1, the High Pressure Coolant Injection (HPCI) turbine stop valve (TSV) failed to open as required during the testing of the auxiliary oil pump, resulting in the HPCI system being declared INOPERABLE. The cause of the TSV failing to open was a degraded reset spring located in the trip knob assembly of the valve. The reset spring was replaced, the valve was tested satisfactorily, and the safety function was restored at 0115 EDT on 06/05/2025 when the HPCI system was declared OPERABLE. The Reactor Core Isolation Cooling (RCIC) and low pressure Emergency Core Cooling Systems (ECCS) were OPERABLE during the time HPCI was INOPERABLE. However, because HPCI does not have a redundant system, the failed TSV resulting in HPCI being INOPERABLE represents a condition that could have prevented the fulfillment of the HPCI safety function to mitigate the consequences of an accident and is reportable per 50.73(a)(2)(v)(D). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to CONTINUATION SHEET lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/l displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ~ 050 YEAR SEQUENTIAL REV NUMBER NO. Edwin I. Hatch Nuclear Plant Unit 1 □ 052 00321 I 2025 I - I 001 1-G I I | EVENT DESCRIPTION At 2137 EDT on 06/03/2025, while Unit 1 was operating at 98% power in MODE 1, the High Pressure Coolant Injection (HPCI) (EIIS: BJ) turbine stop valve (TSV) failed to open as required during the testing of the auxiliary oil pump, resulting in the HPCI system being declared INOPERABLE. The safety function was restored at 0115 EDT on 06/05/2025 when HPCI was declared OPERABLE. The Reactor Core Isolation Cooling (RCIC) System (EIIS: BN) and the low-pressure Emergency Core Cooling Systems (ECCS) remained operable during the time the HPCI was INOPERABLE. FAILED COMPONENT INFORMATION: Master Parts List Number: 1 E41 F3053 Manufacturer: AMETEK Model Number: 69-XC-103 Type: Turbine Stop Valve (TSV) EVENT CAUSE ANALYSIS The cause of the TSV failing to open was a degraded reset spring located in the trip knob assembly of the valve. The degradation of the reset spring occurred because there was no preventive maintenance scheduled for replacing the spring. As a result, the degraded reset spring lacked the necessary spring force to assist in opening the valve. SAFETY ASSESSMENT Even though HPCI was declared INOPERABLE, the RCIC System and the low-pressure ECCS remained OPERABLE during the event. However, because HPCI does not have a redundant system, the failed TSV resulting in HPCI being INOPERABLE represents a condition that could have prevented the fulfillment of the HPCI safety function to mitigate the consequences of an accident and is reportable per 50.73(a)(2)(v)(D). There were no actual safety consequences as a result of this event, and the operating crew responded correctly. The event was within the analysis of UFSAR Chapter 15. CORRECTIVE ACTIONS The reset spring was replaced, the valve was tested satisfactorily, and the safety function was restored at 0115 EDT on 06/05/2025 when the HPCI system was declared OPERABLE. Additionally, the HPCI maintenance procedure and the HPCI twelve-year preventive maintenance overhaul are being revised to include the replacement of the reset spring. Also, the HPCI surveillance procedure is being updated with a more conservative spring force acceptance criteria. PREVIOUS SIMILAR EVENTS None. | ML25210A397
Fermi 2 | Unknown Unit | Division I Transformer 64 Load Tap Changer Failure Potentially Prohibited by Technical Specifications and Potential Loss of Safety Function | 04-30-2027 | On 6/17/25 around 1755 Eastern Prevailing Time (EPT), Station Service Transformer (SST) 64 low voltage alarm was received on Division I Bus after starting Circulating Water Pump #4. SST 64 Load Tap Changer (LTC) was found to be non-functional requiring manual operation of the LTC to be initiated. Subsequent diagnostics revealed a failed time- delay closing relay in the LTC circuitry, which was replaced on 6/19/25 at 1932 EPT. After reviewing historical data, the LTC was last found to be functioning on 2/7/2024. The non-functional LTC could potentially result in lower than minimum required voltages during a postulated loss of coolant accident coincident with degraded voltage conditions. This Licensee Event Report (LER) is being made under the corresponding requirement in Title 10 of the Code of Federal Regulations (CFR) 50.73(a)(2)(i)(B), due to a condition that is potentially prohibited by Technical Specifications. This LER is also being made pursuant to 10 CFR 50.73(a)(2)(v)(D) as a potential condition that could have prevented the fulfillment of the safety function needed to mitigate the consequences of an accident. Further investigation is being conducted to determine the extent of the condition, and a supplement is planned. The event had no significant effect on public health and safety. <)P~ ••c,,._. /·"~ .<I'\ ~ ·n i ~ - ._,, C 91'11i!")l-l!:'""_lfS 'o:-/,,_,:;'-0 4'+0# ···~· I □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ □ ~ ~ □ □ □ □ □ □ 11 □ 1~ NRC FORM 366A (04-02-2024) Page 2 of 3 NRC FORM 366A (04-02-2024) U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk ail: oira_submission@omb.eop.gov. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. LICENSEE EVENT REPORT (LER) CONTINUATION SHEET (See NUREG-1022, R.3 for instruction and guidance for completing this form https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER Fermi 2 05000-341 YEAR SEQUENTIAL NUMBER REV NO. 2025 - 001 - 00 | INITIAL PLANT CONDITIONS MODE – 1 Reactor Power – 100 There were no structures, systems, or components (SSCs) that were inoperable at the start of this event that contributed to this event. DESCRIPTION OF THE EVENT On 6/17/25 around 1755 Eastern Prevailing Time (EPT), Station Service Transformer (SST) [XFMR] 64, Maximo Location Number R1200S002, low voltage alarm was received on Division I Bus [EB] [BU] after starting Circulating Water Pump #4 [KA][P]. SST 64, Load Tap Changer (LTC) [TTC] (General Electric, Model LR-65) was found to be non-functional requiring manual operation of the LTC to be initiated. The LTC was manually adjusted, which cleared the alarm and raised the bus voltage to 118 V. The LTC was then returned to automatic mode. SST 64 voltage was recorded hourly to ensure voltage was maintained within the operability band (122-to-124-meter volts) and adjusted as necessary to maintain the band. The transformer was confirmed to be operable after manual voltage control was maintained within the required band. Subsequent diagnostics revealed a failed time-delay closing relay [TDC] in the LTC circuitry, which was replaced and tested on 6/19/25 at 1932 EPT. After reviewing historical data, the LTC was last found to be working on 2/7/2024. The primary function of SST 64 is to provide a means to step down voltage (13.8 kV) from Bus 11 to 4160V for distribution to Division 1 Engineered Safety Feature (ESF) (class 1E power requirements) and Balance of Plant loads. Operability is based on the ability to supply power from the 120 kV switchyard, through SST 64, to 4160V buses 64B and 64C. This transformer is also sized to accommodate the simultaneous starting of all ESF loads on receipt of an accident signal, without the need for load sequencing. The LTC modulates the voltage on the transformer to keep a nominal 121.8 meter-Volts to ensure Division 1 offsite source has adequate voltage to support the startup and subsequent functionality of the Fermi 2, Division 1 ESF loads without tripping during a Loss of Offsite Coolant Accident (LOCA) transient. While SST 64, LTC control switch was set to automatic, would not automatically tap to control voltage. While the LTC is in manual mode, procedure states that if the voltage range of 122-to-124-meter volts is not met, then Buses 64B and 64C are considered INOPERABLE. The basis of this requirement is the offsite circuit cannot be lost (i.e. by actuation of the degraded voltage relaying) during a design basis accident and must be capable of starting all required ESF loads on the receipt of an accident signal, so this condition impacts the ability to meet the requirements of Technical Specification (TS) 3.8.1. TS 3.8.1 “AC Sources – Operating” requires (During MODES 1,2 and 3) two qualified circuits between the offsite transmission network and the onsite Class IE AC Electrical Power Distribution System and two emergency diesel generators (EDGs) per division. When one offsite circuit is inoperable, then CONDITION D is entered to restore the offsite circuit to OPERABLE status within 72 hours. If the REQUIRED ACTION and COMPLETION TIME is not met, MODE 3 needs to be entered within 12 hours. Further investigation is being done to determine when the voltage level was outside of the voltage band exceeding the completion time of 72 hours along with determining whether the condition was a potential loss of a safety function. The results from the investigation will be provided in a supplemental report. SIGNIFICANT SAFETY CONSEQUENCES AND IMPLICATIONS Further investigation is being conducted for the safety consequences and implications and will be supplemented. I oJ>"llfGc,~ I l·~ '.'\ \ ~,,; ... . ·~•"' | ML25226A116
River Bend Station | Unit 1 | Turbine Control Valve Closure Results in Loss of Safety Function | 08-14-2025 | On June 18, 2025, at 0553 CDT, with River Bend Station (RBS), Unit 1 operating in Mode 1 at 100% power, High Pressure Turbine Main Steam Supply Line “D” Control Valve (MSS-HYVCV3) closed causing both Turbine Bypass Valves to open. Reactor power was lowered to approximately 95% and the Bypass Valves Closed. At 0646 CDT, MSS-HYVCV3 was observed opening and all other Turbine Control Valves intermittently changing position causing the Bypass Valves to open again. Reactor power was lowered to approximately 90% and the Bypass Valves closed. The Bypass Valves were open for approximately one minute for each of the two occurrences. With the Bypass Valves open, Technical Specification (TS) required instrumentation that utilize turbine first stage pressure were declared inoperable. The direct cause of this event was a failure of the Redundant Valve Positioner “B” (RVP-B) for MSS-HYVCV3. The RVP-B was replaced on June 19, 2025. This event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(A) and 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of the safety function of structures or systems that are needed to: (A) shut down the reactor and maintain it in a safe shutdown condition and (D) mitigate the consequences of an accident. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) to, a collection of information unless the document requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 050 YEAR SEQUENTIAL REV River Bend Station, Unit 1 NUMBER NO. 00458 052 2025 003 00 | Event Description On June 18, 2025, at 0553 CDT, with River Bend Station (RBS), Unit 1 operating in Mode 1 at 100% power, the High- Pressure Turbine Main Steam Supply Line “D” Control Valve (MSS-HYVCV3) [TG:VLV] closed causing both Turbine Bypass Valves [JI:V] to open. Control room operatorsentered appropriate procedures and began to lower reactor power. Reactor power was lowered to approximately 95% and the Turbine Bypass Valves closed. At 0646 CDT, MSS-HYVCV3 was observed opening and all other High-Pressure Turbine Main Steam Supply Line Control Valves were observed intermittently changing positions causing the Turbine Bypass Valves to open again. Reactor power was lowered to approximately 90% and the Bypass Valves closed. During the time the Turbine Bypass Valves were open, Technical Specification (TS) required instrumentation that utilizes turbine first stage pressure were declared inoperable. Safety Related Functions of TS 3.3.1.1 (RPS Instrumentation), TS 3.3.2.1 (Control Rod Block Instrumentation) and TS 3.3.4.1 (End of Cycle Recirculation Pump Trip) were declared inoperable. This event was reported on June 18, 2025, at 1126 CDT in accordance with 10 CFR 50.72(b)(3)(v)(A) and 10 CFR 50.72(b)(3)(v)(D) as an event or condition that at the time of discovery could have prevented fulfillment of a safety function of structures or systems that are needed to: (A) shut down the reactor and maintain it in a safe shutdown condition and (D) mitigate the consequences of an accident. (EN 57767) Event Cause The direct cause of this event was a failure of the Redundant Valve Positioner “B” (RVP-B) for MSS-HYVCV3. This failure resulted in the closing of MSS-HYVCV3 resulting in the opening of the Turbine Bypass Valves to maintain reactor pressure at the selected setpoint. The RVP-B was replaced on June 19, 2025. Safety Assessment During the transient there were no radiological impacts and therefore no actual impact to the health and safety of the public. The event is considered of small safety significance from the Probabilistic Risk Assessment (PRA) perspective as no PRA related mitigative components or strategies were affected by this event. While the corresponding functions were declared inoperable from a Technical Specification perspective, functionality was maintained, therefore this is not considered a safety system functional failure. Corrective Actions Planned: Perform a vendor analysis for the failed RVP module. Investigate a possible solution to mitigate or eliminate similar failures of the RVP modules. Previous Occurrences None Energy Industry Identification System (EIIS) codes are identified in the text as [XX]. River Bend equipment codes are identified as (XX). | ML25226A231
Grand Gulf Nuclear Station | Unit 1 | Manual Reactor Scram due to Degraded Main Condenser Vacuum Caused by Circulating Water Pump Trip | 08-18-2025 | On June 17, 2025, Grand Gulf Nuclear Station (GGNS) Unit 1 was in MODE 1 at 70 percent power with all safety systems operable. At 04:26 CT, a manual scram was initiated due to degraded main condenser vacuum caused by the loss of the 'A' Circulating Water Pump. The event was caused by a failure of an embedded winding Resistance Temperature Device (RTD) in the Circulating Water Pump 'A' Motor which resulted in false high winding temperatures and actuation of the motor thermal overload protection function. All control rods fully inserted, and no radiological release occurred. Immediately after the scram, an expected reactor water Level 3 isolation signal was received. The reactor level was maintained by main feedwater. Actions were taken to replace the failed RTD and update the trip logic in order to prevent recurrence. This report is being made in accordance with 10 CFR 50.73(a)(2)(iv)(A) for any event that resulted in manual actuation of the Reactor Protection System. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) .,,, ........ Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported !'¥\ lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) { ) i regarding burden estimate to the FOIA, Library, and Information Collection Branch (T-6 A10M), U.S. \ if/ Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to CONTINUATION SHEET .,...,1(-1, lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond https://www.nrc.gov/reading-rm/doc-collections/nureqs/staff/sr1022/r3Q to, a collection of information unless the document requesting or requiring the collection displays a currently valid 0MB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER 181 050 YEAR SEQUENTIAL REV Grand Gulf Nuclear Station, Unit 1 NUMBER NO. 00416 0 052 2025 003 00 | Plant Conditions: At the time of the event, Grand Gulf Nuclear Station (GGNS) Unit 1 was in MODE 1 at 70 percent power and all safety systems were operable. Description of Event: On June 17, 2025, at 04:26 CT, a manual scram was initiated due to degraded main condenser vacuum [SG] caused by the loss of the 'A' Circulating Water Pump [KE:P]. All control rods fully inserted and there were no complications. Immediately after the scram, an expected reactor water Level 3 isolation signal was received. The reactor level was maintained by main feedwater [SJ]. No other safety systems actuated, and no radiological release occurred. Reportability: This report is being made in accordance with 10 CFR 50.73(a)(2)(iv)(A) for any event that resulted in manual actuation of the Reactor Protection System. Cause(s): The direct cause of the event was a failure of an embedded winding Resistance Temperature Device (RTD) in the Circulating Water Pump A Motor which resulted in false high winding temperatures and actuation of the motor thermal overload protection function. Corrective Actions: Completed Actions: - The failure was corrected by removing the failed RTD from the circuit and utilizing an installed spare. - The thermal overload trip logic was changed from a "1 out of 2" configuration to a "2 out of 2" configuration. Safety Significance: There were no actual safety consequences associated with this condition. Plant systems responded as designed. Previous Similar Events: LEA 2025-001-00, Manual Scram Due to Degraded Condenser Vacuum, described a manual scram due to degrading condenser vacuum and loss of seal steam caused by a loss of power to the static inverter. The loss of power to the static inverter was due to rainwater intrusion to load control center. NRG FORM 366A (04-02-2024) Page 2 of 2 | ML25230A099
Browns Ferry Nuclear Plant (BFN) | Unit 2 | Main Steam Relief Valves Lift Settings Outside of Technical Specifications Required Setpoints | 08-25-2025 | On June 25, 2025, the Tennessee Valley Authority (TVA) was notified of as-found test results that four Main Steam Relief Valves (MSRVs) from Browns Ferry Nuclear Pant (BFN), Unit 2, were outside of their Surveillance Requirement limits for an indeterminate amount of time. These affected valves remained capable of maintaining reactor pressure within the American Society of Mechanical Engineers code limits and could perform their safety function. It was determined that four MSRVs failed above their setpoints due to corrosion bonding to the valve seats. One of these four had been declared inoperable during the fuel cycle due to simmering and gross leakage. All thirteen of the MSRV pilot valves were replaced during the Unit 2 Spring 2025 refueling outage (2R23). NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to (See NUREG-1022, R.3 for instruction and guidance for completing this form respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ☒ 050 SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 2 00260 NUMBER NO. ☐ 052 2025 - 004 - 00 | I. Plant Operating Conditions before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN) Unit 2 was in Mode 1 at approximately 100 percent power. II. Description of Event A. Event Summary On June 25, 2025, NTS/Element notified the Tennessee Valley Authority (TVA) with the as-found test results of the thirteen Main Steam Relief Valves (MSRVs) [RV], which were removed during the Spring 2025 Unit 2 Refueling Outage 23 (2R23). Four MSRVs (2-PCV-001-0023, 2-PCV-001-0031, 2-PCV-001-0041, and 2-PCV-001-0179) had as-found lift settings which were outside of the +/- 3 percent band of their setpoints required by Technical Specification (TS) 3.4.3, Safety/Relief Valves (S/RVs), for an indeterminate amount of time. Throughout this event, the two-stage MSRV pilot valves remained capable of maintaining reactor pressure below 1375 pounds per square inch gauge (psig), which is the American Society of Mechanical Engineers (ASME) code limit of 110 percent of the vessel design pressure. The valves remained capable of performing their required safety function. TVA is submitting this report in accordance with Title 10 of the Code of Federal Regulations 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant’s TS. B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML25237A236
Browns Ferry Nuclear Plant | Unit 2 | Reactor SCRAM due to Low Electro-Hydraulic Control Pressure | 09-09-2025 | On May 12, 2025, at 1353 Central Standard Time (CST), Browns Ferry Nuclear Plant, Unit 2, experienced a significant electro-hydraulic control (EHC) leak, resulting in a turbine trip and automatic reactor SCRAM on low EHC pressure. The trip was not complex with all systems responding normally post trip except for the turbine bypass valves, which subsequently failed closed due to loss of EHC pressure. At 1407 CST, with Unit 2 in Mode 3, there was a second automatic RPS actuation due to a low reactor water level transient caused by manually opening and closing a main steam relief valve. Event Notification 57705 was made to the Nuclear Regulatory Commission (NRC) Operations Center on May 12, 2025, at 1731 CST. It was documented that three broken mounting cap screws were found. Failure analysis was completed on the broken cap screws and determined that the cap screws failed due to hydrogen embrittlement. Investigation into the source of hydrogen intrusion determined that there were two potential sources: environmental intrusion and pickling during the manufacturing process. The Tennessee Valley Authority is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(iv)(A), as any event or condition that resulted in manual or automatic actuation of the Reactor Protection System and the Primary Containment Isolation System. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed back to industry. Send comments regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. LICENSEE EVENT REPORT (LER) Nuclear Regulatory Commission, Washington, DC 20555-0001, or by e-mail to Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory CONTINUATION SHEET Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503; e-mail: oira_submission@omb.eop.gov. The NRC may not conduct or (See NUREG-1022, R.3 for instruction and guidance for completing this form sponsor, and a person is not required to respond to, a collection of information unless the document http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) requesting or requiring the collection displays a currently valid OMB control number. 1. FACILITY NAME ☒ 050 2. DOCKET NUMBER 3. LER NUMBER SEQUENTIAL REV YEAR Browns Ferry Nuclear Plant, Unit 2 00260 NUMBER NO. ☐ 052 2025 - 001 - 00 | I. Plant Operating Conditions before the Event At the time of discovery, Browns Ferry Nuclear Plant (BFN), Unit 2, was in Mode 1 at 100 percent power. II. Description of Event A. Event Summary On May 12, 2025, at 1353 Central Standard Time (CST), BFN Unit 2, experienced a significant electro-hydraulic control (EHC)[JA] leak resulting in a turbine trip and automatic reactor SCRAM on low EHC pressure. The trip was not complex with all systems responding normally post trip except for the turbine bypass valves [V], which subsequently failed closed due to loss of EHC pressure. Operations responded and stabilized the plant. At 1407, with Unit 2 in Mode 3, there was a second automatic Reactor Protection System (RPS) actuation due to a low reactor water level transient caused by manually opening and closing a main steam relief valve. Event Notification 57705 was made to the Nuclear Regulatory Commission (NRC) Operations Center. The Tennessee Valley Authority (TVA) is submitting this report in accordance with Title 10 of the Code of Federal Regulations (10 CFR) 50.73(a)(2)(iv)(A), as any event or condition that resulted in manual or automatic actuation of the Reactor Protection System and the Primary Containment Isolation System (PCIS). B. Status of structures, components, or systems that were inoperable at the start of the event and that contributed to the event There were no structures, systems, or components (SSCs) whose inoperability contributed to this event. | ML25252A080
South Texas Project | Unit 1 | Loss of Offsite Power Resulting in Unit 1 Automatic Reactor Trip and Actuation of Emergency Diesel Generators and Auxiliary Feedwater Pumps | 09-11-2025 | 12.Licensee Contact for this LER Licensee Contact Phone Number (Include area code) Chris Warren, Licensing Engineer 361-972-7293 13.Complete One Line for each Component Failure Described in this Report Cause System Component Manufacturer Reportable to IRIS Cause System Component Manufacturer Reportable to IRIS X N/A INS G080 Y 14. Supplemental Report Expected Month Day Year 15. Expected Submission Date □✔ No □ Yes (If yes, complete 15. Expected Submission Date) 16.(cid:3)Abstract (Limit to 1326 spaces, i.e., approximately 13 single-spaced typewritten lines) On July 24, 2024, STP Unit 1 experienced a Loss of Offsite Power (LOOP), resulting in an automatic reactor trip and actuation of all three Unit 1 Standby Diesel Generators (SBDG) and all four Auxiliary Feedwater (AFW) pumps. All three trains of Engineered Safety Feature (ESF) buses were energized and all equipment responded as expected without any complications with the exception of Steam Generator Power Operated Relief Valve "1C." Unit 2 experienced a partial LOOP and automatic actuation of SBDG 22 and one of four AFW pumps. The systems for each unit actuated due to the Switchyard experiencing electrical faults during the Shunt Reactor RT-2 fire event, which was caused by the insulation breakdown on the C-Phase (H3) GE Type U high- voltage bushing. Immediate corrective actions included restoring offsite power circuits. A Transmission Distribution Service Provider (TDSP) had not established and implemented adequate management controls governing design changes to equipment in the Switchyard to ensure that changes were consistent with design requirements and aligned with requirements and recommendations of applicable Industry Standards; and subsequently, STPNOC did not rigorously implement management controls during the review and approval of design changes developed by the TDSP. Planned corrective actions include enhancements to STP procedure 0PGP05-ZA-0002, "10CFR50.59 Evaluations" and development and implementation of written instructions that include management controls to govern the review and approval of all four TD(cid:54)(cid:51)(cid:86)' Switchyard changes. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY OMB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported /~•,.µ...-, .', \ lessons learned are incorporated into the licensing process and fed back to industry. Send comments LICENSEE EVENT REPORT (LER) regarding burden estimate to the FOIA, Library, and Information Collections Branch (T-6 A10M), U. S. ; .i Nuclear Regulatory Commission, Washington, DC 20555-0001, or by email to . CONTINUATION SHEET Infocollects.Resource@nrc.gov, and the OMB reviewer at: OMB Office of Information and Regulatory <--+ o' Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, ♦--·· (See NUREG-1022, R.3 for instruction and guidance for completing this form Washington, DC 20503. The NRC may not conduct or sponsor, and a person is not required to respond to, a collection of information unless the document requesting or requiring the collection http://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr1022/r3/) displays a currently valid OMB control number. 1. FACILITY NAME 2. DOCKET NUMBER 3. LER NUMBER ■ 050 YEAR SEQUENTIAL REV I I~ I I □ NUMBER D NO. South Texas Project Unit 1 00498 2024 I 052 - 004 - 01 I | 1. Description of the Reportable Event A. Reportable Event Classification This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in the valid actuation of the Reactor Protection System (RPS) including reactor trip (10 CFR 50.73(a)(2)(iv)(B)(1)), and automatic actuation of all four Unit 1 Auxiliary Feedwater (AFW) Pumps and Unit 2 AFW Pump 22 (10 CFR 50.73(a)(2)(iv)(B)(6), and automatic actuation of all three Unit 1 Standby Diesel Generators (SBDG) and Unit 2 SBDG 22 (10 CFR 50.73(a)(2)(iv)(B)(8)). B. Plant Operating Conditions Prior to Event Prior to the event, Units 1 and 2 were in Mode 1 at 100% power. C. Status of Structures, Systems, and Components That Were Inoperable at the Start of the Event that Contributed to the Event At the start of the event, there were no structures, systems, or components (SSCs) that were inoperable that contributed to the event. D. Narrative Summary of the Event Timeline (Note: All times are in Central Daylight Time) Unit 1 - 07/24/2024 (0702) - Unit 1 reactor trip due to fire in the switchyard. The 345kV North Bus and the Unit 1 Generator tripped. All SBDGs automatically actuated and sequenced on a Loss of Offsite Power. The following busses were deenergized: 13.8kV Auxiliary busses 1F, 1G, 1H, and 1J, 13.8kV Standby busses 1F, 1H, and 1G, and 480V Load Center 1W. Units 1 and 2 - 07/24/2024 (0702) - Due to loss of two independent offsite power circuits, entered Technical Specification 3.8.1.1, Action 'e'. Unit 1 - 07/24/2024 (0702) - All four Reactor Coolant Pumps (RCP) lost power. Entered Technical Specification 3.4.1.2. Unit 2 - 07/24/2024 (0703) - Report of explosion and fire in the switchyard. Entered off-normal procedure 0POP04-ZO-0008, Fire/Explosion. Unit 1 - 07/24/2024 (0735) - Verified natural circulation with Steam Generator (S/G) Power Operated Relief Valves (PORV) open in Manual. 07/24/2024 (0800) - Bay City Fire Department arrive on site at the switchyard. Unit 1 - 07/24/2024 (0848) - Spent Fuel Pool pump 1B is running, restoring cooling to the Spent Fuel Pool. 07/24/2024 (0925) - Fire in Shunt Reactor RT-2 is extinguished. | ML25254A061
Catawba Nuclear Station | Unit 2 | 2B Emergency Diesel Generator Field Failed to Flash | 09-15-2025 | On 7/15/2025, Catawba Unit 2 was in Mode 1 operating at approximately 100 percent power. At 8:34 EDT the 2B Emergency Diesel Generator (DG)[EK] was manually started for scheduled testing. Upon start, voltage and frequency parameters indicated the 2B DG field did not flash. Investigation determined a sliding link in the field flash circuit was not in the closed position. This portion of the system energizes the field flash contactor to allow voltage buildup during 2B DG startup. The previous successful operation of the 2B DG was on 7/1/2025 for an approximate 12 hour run. During the time between 7/1/2015 and 7/15/2025 there were two instances when the 2A DG was removed from service. This condition resulted in both an "operation or condition prohibited by Technical Specifications" reportable under 1O CFR 50. 73(a)(2)(i)(B) and a "condition that could have prevented fulfillment of a safety function" reportable under 1O CFR 50.7 3(a)(2)(v)(D). There was no impact on the health and safety of the public. NRC FORM 366A U.S. NUCLEAR REGULATORY COMMISSION APPROVED BY 0MB: NO. 3150-0104 EXPIRES: 04/30/2027 (04-02-2024) Estimated burden per response to comply with this mandatory collection request: 80 hours. Reported lessons learned are incorporated into the licensing process and fed LICENSEE EVENT REPORT (LER) back to industry. Send comments regarding burden estimate to the FOIA. Library, and Information Collections Branch (T-6 A 1O M), U. S. Nuclear Regulatory CONTINUATION SHEET Commission, Washington, DC 20555-0001, or by email to lnfocollects.Resource@nrc.gov, and the 0MB reviewer at: 0MB Office of Information (See NUREG-1022, R.3 for instruction and guidance for completing this form and Regulatory Affairs, (3150-0104), Attn: Desk Officer for the Nuclear Regulatory Commission, 725 17th Street NW, Washington, DC 20503. The NRC may not http://www.nrc.gov/reading-rm/doc-colleclions/nuregs/staff/sr1022/r3Q conduct or sponsor.., and a person is not req - u - ired to respond .. to, a collection of ~1. FA-CIL-ITY- N-AME- -------~•IB] 050 2. DOCKET NUMBER YEAR 3 S . E L Q t: U K E N N U T M IA t: L 11 :K REV 00413, 00414 ~ NUMBER NO. I-~ Catawba Nuclear Station, Units 1 and 2 0 □ -1 052 003 | BACKGROUND The following information is provided to assist readers in understanding the event described in this LER. Applicable Energy Industry Identification System [EIIS] and component codes are enclosed within brackets. Catawba's unique system and component identifiers are contained within parentheses. The onsite standby power source for each 4160 volt Engineered Safety Features (ESF) bus at Catawba is a dedicated DG. For each unit, DGs A and Bare dedicated to ESF buses ETA and ETB, respectively. Each DG starts automatically on a Safety Injection (SI) signal (i.e., low pressurizer pressure or high containment pressure) or on an ESF bus degraded voltage or undervoltage signal. After the DG has started, it will automatically tie to its respective bus after offsite power is tripped as a consequence of ESF bus undervoltage or degraded voltage, independent of or coincident with an SI signal. The DGs will also start and operate in the standby mode without tying to the ESF bus on an SI signal alone. Following the trip of offsite power, a sequencer strips loads from the ESF bus. When the DG is tied to the ESF bus, loads are then sequentially connected to its respective ESF bus by the automatic load sequencer. In the event of a loss of preferred power, the ESF electrical loads are automatically connected to the DGs in sufficient time to provide for safe reactor shutdown and to mitigate the consequences of a Design Basis Accident such as a Loss of Coolant Accident (LOCA). There are also provisions to accommodate the connecting of the Emergency Supplemental Power Source (ESPS) to one train of either unit's Class 1E AC Distribution System. The ESPS consists of two 50% capacity non-safety related commercial grade DGs. Manual actions are required to align the ESPS to the station and only one of the station's four onsite Class 1 E Distribution System trains can be supplied by the ESPS at any given time. The ESPS is made available to support extended Completion Times in the event of an inoperable DG as well as a defense-in-depth source of AC power to mitigate a station blackout event. The ESPS remains disconnected from the Class 1E AC Distribution System unless required for supplemental power to one of the four 4.16 kV ESF buses. Technical Specifications: Catawba TS 3.8.1 governs the DGs for each unit that is in Modes 1, 2, 3, and 4. Limiting Condition for Operation (LCO) 3.8.1( b) requires two operable DGs capable of supplying the Onsite Essential Auxiliary Power Systems. With one LCO 3.8.1 (b) DG inoperable, the inoperable DG must be restored to operable status within 72 hours per Required Action 8.6. LCO 3.8.1 (d) requires two DGs from the opposite unit necessary to supply power to the shared systems and the Nuclear Service Water System (NSWS) pump(s). With one LCO 3.8.1 (d) DG inoperable, the inoperable DG must be restored to operable status within 72 hours per Required Action D.6. If an inoperable DG is not restored to operable status within 72 hours, the unit must be placed in Mode 3 within 6 hours and in Mode 5 within 36 hours per LCO 3.8.1 Required Actions 1.1 and 1.2. In order to extend the Completion Time for an inoperable DG from 72 hours to 14 days, it is necessary to ensure the availability of the ESPS within 1 hour of entry into TS 3.8.1 LCO and every 12 hours thereafter. | ML25258A159